## Readme
This spreadsheet will show the loss table each month, based on the 8760 output from HelioScope.
Step 1: paste in the hourly 8760 data into the "8760" tab. Ensure that the table starts in cell A1 (the final column should be "AN")
Step 2: Verify the annual values shown in the green cells in "monthly-losses":
Step 3: view/use the monthly loss factors in the table

## 8760
hour_index | timestamp | global_horizontal_irradiance | direct_normal_irradiance | diffuse_horizontal_irradiance | dry_bulb_temperature | windspeed | albedo | solar_altitude_angle | solar_azimuth_angle | solar_incident_angle | horizon_elevation_angle | adjusted_ghi | poa_direct_irradiance | poa_diffuse_irradiance | poa_reflected_irradiance | shaded_direct_irradiance | shaded_diffuse_irradiance | shaded_reflected_irradiance | effective_direct_irradiance | effective_diffuse_irradiance | effective_reflected_irradiance | soiled_irradiance | total_irradiance | nameplate_power | avg_cell_temp | module_irradiance_derated_power | module_mpp_power | module_power | optimizer_input_power | optimizer_output_power | optimal_dc_power | optimal_dc_voltage | inverter_overpower_loss | inverter_underpower_loss | inverter_overvoltage_loss | inverter_undervoltage_loss | actual_dc_power | actual_dc_voltage | ac_power | grid_power
1 | 1998-01-01 | 0 | 0 | 0 | 13.93 | 5.29 | 0
2 | 1998-01-01 01:00 | 0 | 0 | 0 | 13.63 | 5.29 | 0
3 | 1998-01-01 02:00 | 0 | 0 | 0 | 13.79 | 5.29 | 0
4 | 1998-01-01 03:00 | 0 | 0 | 0 | 13.95 | 5.61 | 0
5 | 1998-01-01 04:00 | 0 | 0 | 0 | 14.12 | 5.61 | 0
6 | 1998-01-01 05:00 | 0 | 0 | 0 | 13.8 | 5.61 | 0
7 | 1998-01-01 06:00 | 0 | 6 | 0 | 13.48 | 3.6 | 0
8 | 1998-01-01 07:00 | 72 | 534 | 23 | 13.16 | 3.6 | 0 | 5.1626 | 122.56 | 72.0566 | 0 | 72 | 167.764 | 39.3072 | 0.67458 | 19.0661 | 36.7852 | 0.0035211 | 16.9251 | 35.4238 | 0.0026532 | 50.7809 | 50.7205 | 113912 | 14.4133 | 93231.9 | 97748.1 | 85789.2 | 0 | 0 | 85684.1 | 645.166 | 0 | 0 | 0 | 286.704 | 85397.4 | 660 | 82631.4 | 80978.8047
9 | 1998-01-01 08:00 | 254 | 808 | 45 | 13.52 | 3.6 | 0 | 14.9694 | 132.434 | 59.364 | 0 | 254 | 412.316 | 63.1915 | 2.3798 | 277.258 | 59.137 | 0.012422 | 263.917 | 56.9484 | 0.00936 | 311.248 | 311.317 | 699068 | 21.2125 | 662948 | 667872 | 561224 | 0 | 0 | 558394 | 703.62 | 0 | 0 | 0 | 1858.06 | 556536 | 711.439 | 547236 | 536291.125
10 | 1998-01-01 09:00 | 413 | 913 | 54 | 13.89 | 5.49 | 0 | 23.2013 | 144.17 | 47.7799 | 0 | 413 | 612.344 | 73.1042 | 3.8695 | 569.417 | 68.4137 | 0.020197 | 555.519 | 65.8818 | 0.015219 | 602.773 | 602.724 | 1353560 | 27.0537 | 1326750 | 1312630 | 1191940 | 0 | 0 | 1180980 | 722.283 | 0 | 0 | 0 | 0 | 1180980 | 722.283 | 1161200 | 1137977.875
11 | 1998-01-01 10:00 | 527 | 959 | 61 | 14.25 | 5.49 | 0 | 29.1909 | 158.043 | 38.3524 | 0 | 527 | 749.284 | 81.2304 | 4.9376 | 749.284 | 76.0185 | 0.025773 | 738.975 | 73.2051 | 0.01942 | 787.833 | 787.83 | 1769260 | 31.4566 | 1758780 | 1710780 | 1665710 | 0 | 0 | 1644790 | 716.852 | 0 | 0 | 0 | 0 | 1644790 | 716.852 | 1614430 | 1582143.75
12 | 1998-01-01 11:00 | 582 | 978 | 62 | 15.62 | 5.49 | 0 | 32.2213 | 173.719 | 33.0051 | 0 | 582 | 817.874 | 82.1863 | 5.4529 | 817.874 | 76.9131 | 0.028462 | 810.005 | 74.0666 | 0.021447 | 857.57 | 857.564 | 1925870 | 34.3496 | 1923180 | 1847590 | 1800400 | 0 | 0 | 1775460 | 708.51 | 0 | 0 | 0 | 0 | 1775460 | 708.51 | 1741200 | 1706371.75
13 | 1998-01-01 12:00 | 574 | 976 | 61 | 16.98 | 6.27 | 0 | 31.8215 | 190.005 | 33.746 | 0 | 574 | 808.997 | 80.9611 | 5.3779 | 808.997 | 75.7665 | 0.028071 | 800.801 | 72.9624 | 0.021152 | 847.571 | 847.572 | 1903430 | 34.584 | 1899600 | 1822990 | 1773470 | 0 | 0 | 1749240 | 708.361 | 0 | 0 | 0 | 0 | 1749240 | 708.361 | 1715830 | 1681516.75
14 | 1998-01-01 13:00 | 504 | 952 | 57 | 18.35 | 6.27 | 0 | 28.0586 | 205.346 | 40.2394 | 0 | 504 | 725.418 | 76.2885 | 4.7221 | 725.418 | 71.3936 | 0.024648 | 714.173 | 68.7514 | 0.018573 | 759.455 | 759.45 | 1705530 | 34.1237 | 1692010 | 1626560 | 1588070 | 0 | 0 | 1568450 | 705.497 | 0 | 0 | 0 | 0 | 1568450 | 705.497 | 1540740 | 1509925.75
15 | 1998-01-01 14:00 | 379 | 895 | 52 | 18.72 | 6.27 | 0 | 21.4917 | 218.733 | 50.2982 | 0 | 379 | 570.152 | 70.809 | 3.5509 | 526.008 | 66.2658 | 0.018535 | 511.137 | 63.8133 | 0.013966 | 557.715 | 557.633 | 1252310 | 30.302 | 1220860 | 1191640 | 1137590 | 0 | 0 | 1127490 | 709.325 | 0 | 0 | 0 | 0 | 1127490 | 709.325 | 1109550 | 1087356.75
16 | 1998-01-01 15:00 | 209 | 767 | 38 | 19.09 | 7.95 | 0 | 12.8462 | 230.009 | 62.2049 | 0 | 209 | 358.643 | 54.6848 | 1.9582 | 275.86 | 51.1761 | 0.010221 | 260.074 | 49.2821 | 0.0077017 | 300.083 | 300.01 | 673751 | 24.69 | 636765 | 634102 | 555440 | 0 | 0 | 552684 | 698.558 | 0 | 0 | 0 | 0 | 552684 | 698.558 | 544176 | 533292.0625
17 | 1998-01-01 16:00 | 26 | 301 | 4 | 19.46 | 7.95 | 0 | 2.7565 | 239.528 | 75.0691 | 0 | 26 | 65.154 | 6.8843 | 0.2436 | 22.9603 | 6.4426 | 0.0012715 | 19.6526 | 6.2042 | 0.00095811 | 25.082 | 25.0585 | 56283.4 | 19.9277 | 42779 | 43782.7 | 31589.9 | 0 | 0 | 31570.4 | 563.155 | 0 | 0 | 0 | 3898.87 | 27671.5 | 660 | 26667.5 | 26134.1738
18 | 1998-01-01 17:00 | 0 | 0 | 0 | 18.77 | 7.95 | 0
19 | 1998-01-01 18:00 | 0 | 0 | 0 | 18.09 | 8.51 | 0
20 | 1998-01-01 19:00 | 0 | 0 | 0 | 17.4 | 8.51 | 0
21 | 1998-01-01 20:00 | 0 | 0 | 0 | 16.66 | 8.51 | 0
22 | 1998-01-01 21:00 | 0 | 0 | 0 | 15.91 | 10.47 | 0
23 | 1998-01-01 22:00 | 0 | 0 | 0 | 15.16 | 10.47 | 0
24 | 1998-01-01 23:00 | 0 | 0 | 0 | 14.44 | 10.47 | 0
25 | 1998-01-02 | 0 | 0 | 0 | 13.71 | 9.51 | 0
26 | 1998-01-02 01:00 | 0 | 0 | 0 | 12.98 | 9.51 | 0
27 | 1998-01-02 02:00 | 0 | 0 | 0 | 12.29 | 9.51 | 0
28 | 1998-01-02 03:00 | 0 | 0 | 0 | 11.61 | 13.7 | 0
29 | 1998-01-02 04:00 | 0 | 0 | 0 | 10.92 | 13.7 | 0
30 | 1998-01-02 05:00 | 0 | 0 | 0 | 10.24 | 13.7 | 0
31 | 1998-01-02 06:00 | 0 | 0 | 0 | 9.57 | 12.94 | 0
32 | 1998-01-02 07:00 | 28 | 0 | 28 | 8.9 | 12.94 | 0 | 5.1391 | 122.423 | 72.1298 | 0 | 28 | 0 | 27.0009 | 0.26234 | 0 | 25.2685 | 0.0013693 | 0 | 24.3333 | 0.0010318 | 23.6043 | 23.6031 | 53006.6 | 9.2251 | 38173.7 | 41395.4 | 40395.3 | 0 | 0 | 40379.6 | 641.509 | 0 | 0 | 0 | 350.596 | 40029 | 660 | 38604.1 | 37831.9844
33 | 1998-01-02 08:00 | 183 | 311 | 103 | 9.83 | 12.94 | 0 | 14.9645 | 132.29 | 59.4191 | 0 | 183 | 157.618 | 124.762 | 1.7146 | 105.932 | 116.757 | 0.0089495 | 100.818 | 112.436 | 0.0067436 | 206.863 | 206.84 | 464485 | 12.6793 | 425150 | 448791 | 403630 | 0 | 0 | 402405 | 733.55 | 0 | 0 | 0 | 0 | 402405 | 733.55 | 394224 | 386339.5
34 | 1998-01-02 09:00 | 260 | 226 | 171 | 10.76 | 10.6 | 0 | 23.2203 | 144.019 | 47.8082 | 0 | 260 | 151.607 | 191.721 | 2.436 | 140.971 | 179.42 | 0.012715 | 137.525 | 172.78 | 0.0095811 | 301.005 | 300.98 | 675926 | 15.5283 | 633336 | 660101 | 622034 | 0 | 0 | 619230 | 738.784 | 0 | 0 | 0 | 0 | 619230 | 738.784 | 608637 | 596464.125
35 | 1998-01-02 10:00 | 493 | 757 | 124 | 11.69 | 10.6 | 0 | 29.2386 | 157.893 | 38.3398 | 0 | 493 | 592.537 | 167.002 | 4.619 | 592.537 | 156.287 | 0.02411 | 584.391 | 150.503 | 0.018167 | 712.865 | 712.855 | 1600900 | 22.9834 | 1582570 | 1595770 | 1550570 | 0 | 0 | 1533620 | 742.507 | 0 | 0 | 0 | 0 | 1533620 | 742.507 | 1505520 | 1475409.75
36 | 1998-01-02 11:00 | 584 | 979 | 63 | 12.39 | 10.6 | 0 | 32.2995 | 173.582 | 32.9372 | 0 | 584 | 818.307 | 83.4044 | 5.4716 | 818.307 | 78.0531 | 0.02856 | 810.471 | 75.1644 | 0.021521 | 859.087 | 859.083 | 1929280 | 26 | 1926770 | 1918500 | 1866070 | 0 | 0 | 1841310 | 737.974 | 0 | 0 | 0 | 0 | 1841310 | 737.974 | 1804400 | 1768315.125
37 | 1998-01-02 12:00 | 570 | 970 | 59 | 13.08 | 9 | 0 | 31.9266 | 189.896 | 33.6296 | 0 | 570 | 804.558 | 78.3876 | 5.3405 | 804.558 | 73.3581 | 0.027875 | 796.472 | 70.6432 | 0.021005 | 841.122 | 841.12 | 1888950 | 27.7826 | 1884380 | 1862260 | 1810220 | 0 | 0 | 1786480 | 730.443 | 0 | 0 | 0 | 0 | 1786480 | 730.443 | 1751440 | 1716406.5
38 | 1998-01-02 13:00 | 506 | 952 | 58 | 13.78 | 9 | 0 | 28.1828 | 205.272 | 40.1021 | 0 | 506 | 725.566 | 77.5085 | 4.7408 | 725.566 | 72.5354 | 0.024746 | 714.416 | 69.8509 | 0.018646 | 760.757 | 760.754 | 1708460 | 27.0778 | 1695080 | 1680080 | 1633120 | 0 | 0 | 1613830 | 732.097 | 0 | 0 | 0 | 0 | 1613830 | 732.097 | 1583930 | 1552248.125
39 | 1998-01-02 14:00 | 381 | 871 | 61 | 13.71 | 9 | 0 | 21.6266 | 218.691 | 50.1583 | 0 | 381 | 556.263 | 86.9326 | 3.5697 | 513.194 | 81.3549 | 0.018632 | 498.803 | 78.344 | 0.01404 | 559.846 | 559.791 | 1257150 | 23.495 | 1225840 | 1232670 | 1175590 | 0 | 0 | 1165520 | 733.704 | 0 | 0 | 0 | 0 | 1165520 | 733.704 | 1145620 | 1122708.75
40 | 1998-01-02 15:00 | 174 | 496 | 62 | 13.64 | 8.44 | 0 | 12.9857 | 229.992 | 62.0692 | 0 | 174 | 233.465 | 88.4168 | 1.6302 | 188.557 | 82.7438 | 0.0085093 | 177.857 | 79.6815 | 0.0064119 | 249.819 | 249.783 | 560953 | 18.1613 | 520531 | 535710 | 488914 | 0 | 0 | 487019 | 720.345 | 0 | 0 | 0 | 0 | 487019 | 720.345 | 478529 | 468958.1562
41 | 1998-01-02 16:00 | 23 | 198 | 8 | 13.56 | 8.44 | 0 | 2.897 | 239.53 | 74.9395 | 0 | 23 | 44.7998 | 14.9156 | 0.21549 | 15.8123 | 13.9586 | 0.0011248 | 13.5602 | 13.442 | 0.00084756 | 26.193 | 26.1655 | 58766.8 | 14.0336 | 43858.4 | 46333.3 | 37093.6 | 0 | 0 | 37075.8 | 610.122 | 0 | 0 | 0 | 970.572 | 36105.3 | 660 | 34812.2 | 34115.9727
42 | 1998-01-02 17:00 | 0 | 0 | 0 | 12.87 | 8.44 | 0
43 | 1998-01-02 18:00 | 0 | 0 | 0 | 12.18 | 8.38 | 0
44 | 1998-01-02 19:00 | 0 | 0 | 0 | 11.48 | 8.38 | 0
45 | 1998-01-02 20:00 | 0 | 0 | 0 | 10.83 | 8.38 | 0
46 | 1998-01-02 21:00 | 0 | 0 | 0 | 10.17 | 9.62 | 0
47 | 1998-01-02 22:00 | 0 | 0 | 0 | 9.51 | 9.62 | 0
48 | 1998-01-02 23:00 | 0 | 0 | 0 | 8.87 | 9.62 | 0
49 | 1998-01-03 | 0 | 0 | 0 | 8.24 | 7.29 | 0
50 | 1998-01-03 01:00 | 0 | 0 | 0 | 7.6 | 7.29 | 0
51 | 1998-01-03 02:00 | 0 | 0 | 0 | 7.24 | 7.29 | 0
52 | 1998-01-03 03:00 | 0 | 0 | 0 | 6.89 | 9.23 | 0
53 | 1998-01-03 04:00 | 0 | 0 | 0 | 6.53 | 9.23 | 0
54 | 1998-01-03 05:00 | 0 | 0 | 0 | 6.09 | 9.23 | 0
55 | 1998-01-03 06:00 | 0 | 0 | 0 | 5.64 | 6.45 | 0
56 | 1998-01-03 07:00 | 34 | 26 | 32 | 5.2 | 6.45 | 0 | 5.1214 | 122.28 | 72.1995 | 0 | 34 | 6.8493 | 27.4413 | 0.31855 | 0.77328 | 25.6806 | 0.0016627 | 0.68547 | 24.7302 | 0.0012529 | 24.6544 | 24.6548 | 55368.7 | 5.7062 | 40183.6 | 44307.2 | 42973.8 | 0 | 0 | 42956.7 | 655.529 | 0 | 0 | 0 | 14.875 | 42941.8 | 660 | 41420.8 | 40592.4258
57 | 1998-01-03 08:00 | 137 | 113 | 108 | 6.34 | 6.45 | 0 | 14.966 | 132.141 | 59.4698 | 0 | 137 | 57.0456 | 123.047 | 1.2836 | 38.3365 | 115.152 | 0.0066999 | 36.48 | 110.89 | 0.0050485 | 142.954 | 142.954 | 321028 | 9.2751 | 284949 | 306246 | 287421 | 0 | 0 | 286811 | 730.655 | 0 | 0 | 0 | 0 | 286811 | 730.655 | 279232 | 273647.3125
58 | 1998-01-03 09:00 | 347 | 558 | 127 | 7.47 | 8.13 | 0 | 23.2462 | 143.866 | 47.8312 | 0 | 347 | 374.198 | 162.052 | 3.2511 | 347.957 | 151.655 | 0.01697 | 339.439 | 146.042 | 0.012787 | 470.929 | 470.894 | 1057510 | 16.1609 | 1020480 | 1058480 | 976578 | 0 | 0 | 969823 | 750.143 | 0 | 0 | 0 | 0 | 969823 | 750.143 | 952844 | 933787.5
59 | 1998-01-03 10:00 | 462 | 603 | 168 | 8.6 | 8.13 | 0 | 29.2936 | 157.741 | 38.3208 | 0 | 462 | 471.419 | 211.41 | 4.3286 | 471.419 | 197.846 | 0.022594 | 464.946 | 190.524 | 0.017025 | 635.822 | 635.818 | 1427890 | 20.3347 | 1402230 | 1429690 | 1388930 | 0 | 0 | 1375500 | 748.045 | 0 | 0 | 0 | 0 | 1375500 | 748.045 | 1350580 | 1323564
60 | 1998-01-03 11:00 | 139 | 0 | 139 | 9.52 | 8.13 | 0 | 32.3851 | 173.445 | 32.8621 | 0 | 139 | 0 | 131.633 | 1.3023 | 0 | 123.187 | 0.0067977 | 0 | 118.628 | 0.0051222 | 115.074 | 115.067 | 258410 | 11.6437 | 224983 | 239698 | 232536 | 0 | 0 | 232114 | 711.996 | 0 | 0 | 0 | 0 | 232114 | 711.996 | 225495 | 220984.9688
61 | 1998-01-03 12:00 | 501 | 528 | 222 | 10.44 | 8.08 | 0 | 32.0388 | 189.79 | 33.5066 | 0 | 501 | 438.528 | 273.799 | 4.694 | 438.528 | 256.232 | 0.024501 | 434.158 | 246.749 | 0.018462 | 660.497 | 660.487 | 1483290 | 22.6684 | 1459890 | 1474040 | 1434170 | 0 | 0 | 1419550 | 739.76 | 0 | 0 | 0 | 0 | 1419550 | 739.76 | 1394200 | 1366321
62 | 1998-01-03 13:00 | 237 | 173 | 155 | 11.35 | 8.08 | 0 | 28.3133 | 205.203 | 39.9597 | 0 | 237 | 132.519 | 169.532 | 2.2205 | 132.519 | 158.655 | 0.01159 | 130.5 | 152.783 | 0.0087335 | 274.794 | 274.788 | 617105 | 16.4375 | 574464 | 596741 | 579987 | 0 | 0 | 577524 | 733.203 | 0 | 0 | 0 | 0 | 577524 | 733.203 | 567719 | 556364.4375
63 | 1998-01-03 14:00 | 384 | 660 | 140 | 11.19 | 8.08 | 0 | 21.7669 | 218.655 | 50.0151 | 0 | 384 | 422.809 | 176.507 | 3.5978 | 406.441 | 165.182 | 0.018779 | 395.138 | 159.069 | 0.01415 | 537.594 | 537.559 | 1207220 | 21.1425 | 1173760 | 1192860 | 1154090 | 0 | 0 | 1144580 | 739.649 | 0 | 0 | 0 | 0 | 1144580 | 739.649 | 1124810 | 1102312.5
64 | 1998-01-03 15:00 | 212 | 774 | 36 | 11.02 | 8.4 | 0 | 13.1298 | 229.982 | 61.9315 | 0 | 212 | 364.562 | 51.846 | 1.9863 | 294.437 | 48.5195 | 0.010368 | 277.871 | 46.7238 | 0.0078123 | 314.864 | 314.794 | 706953 | 16.7323 | 667702 | 689775 | 618970 | 0 | 0 | 615985 | 734.089 | 0 | 0 | 0 | 0 | 615985 | 734.089 | 605690 | 593576.5
65 | 1998-01-03 16:00 | 29 | 313 | 5 | 10.86 | 8.4 | 0 | 3.0414 | 239.538 | 74.8089 | 0 | 29 | 72.2866 | 8.6381 | 0.27171 | 28.5499 | 8.0838 | 0.0014182 | 24.5298 | 7.7847 | 0.0010687 | 31.346 | 31.3262 | 70357.3 | 11.4285 | 54800.6 | 58478.7 | 43368.7 | 0 | 0 | 43339.1 | 598.362 | 0 | 0 | 0 | 1046.08 | 42293 | 660 | 40795 | 39979.0586
66 | 1998-01-03 17:00 | 0 | 0 | 0 | 10.72 | 8.4 | 0
67 | 1998-01-03 18:00 | 0 | 0 | 0 | 10.58 | 6.81 | 0
68 | 1998-01-03 19:00 | 0 | 0 | 0 | 10.45 | 6.81 | 0
69 | 1998-01-03 20:00 | 0 | 0 | 0 | 10.13 | 6.81 | 0
70 | 1998-01-03 21:00 | 0 | 0 | 0 | 9.81 | 6.98 | 0
71 | 1998-01-03 22:00 | 0 | 0 | 0 | 9.49 | 6.98 | 0
72 | 1998-01-03 23:00 | 0 | 0 | 0 | 9.08 | 6.98 | 0
73 | 1998-01-04 | 0 | 0 | 0 | 8.67 | 7.36 | 0
74 | 1998-01-04 01:00 | 0 | 0 | 0 | 8.26 | 7.36 | 0
75 | 1998-01-04 02:00 | 0 | 0 | 0 | 7.75 | 7.36 | 0
76 | 1998-01-04 03:00 | 0 | 0 | 0 | 7.23 | 8.6 | 0
77 | 1998-01-04 04:00 | 0 | 0 | 0 | 6.72 | 8.6 | 0
78 | 1998-01-04 05:00 | 0 | 0 | 0 | 5.99 | 8.6 | 0
79 | 1998-01-04 06:00 | 0 | 4 | 0 | 5.27 | 9.33 | 0
80 | 1998-01-04 07:00 | 71 | 531 | 22 | 4.54 | 9.33 | 0 | 5.1095 | 122.133 | 72.2655 | 0 | 71 | 167.592 | 37.7439 | 0.66522 | 18.7631 | 35.3222 | 0.0034722 | 16.6213 | 34.0149 | 0.0026164 | 49.1197 | 49.1066 | 110288 | 5.381 | 90013.4 | 98554.4 | 85713.5 | 0 | 0 | 85617.5 | 685.558 | 0 | 0 | 0 | 0 | 85617.5 | 685.558 | 82641.5 | 80988.6875
81 | 1998-01-04 08:00 | 254 | 809 | 45 | 5.48 | 9.33 | 0 | 14.9738 | 131.989 | 59.5161 | 0 | 254 | 410.349 | 63.0614 | 2.3798 | 275.767 | 59.0153 | 0.012422 | 262.376 | 56.8312 | 0.00936 | 309.64 | 309.708 | 695459 | 10.784 | 659304 | 696217 | 583477 | 0 | 0 | 580682 | 736.856 | 0 | 0 | 0 | 1288.47 | 579393 | 741.66 | 568902 | 557524.4375
82 | 1998-01-04 09:00 | 414 | 913 | 54 | 6.42 | 9.6 | 0 | 23.279 | 143.709 | 47.8487 | 0 | 414 | 611.303 | 72.9769 | 3.8789 | 591.169 | 68.2946 | 0.020246 | 576.682 | 65.767 | 0.015256 | 623.19 | 623.144 | 1399440 | 16.9154 | 1374270 | 1419310 | 1289700 | 0 | 0 | 1278040 | 757.693 | 0 | 0 | 0 | 0 | 1278040 | 757.693 | 1254490 | 1229403.25
83 | 1998-01-04 10:00 | 529 | 961 | 59 | 7.36 | 9.6 | 0 | 29.3559 | 157.587 | 38.2953 | 0 | 529 | 752.435 | 78.574 | 4.9563 | 752.435 | 73.5326 | 0.02587 | 742.121 | 70.8112 | 0.019494 | 788.563 | 788.558 | 1770900 | 20.6414 | 1760500 | 1792140 | 1741680 | 0 | 0 | 1720860 | 752.107 | 0 | 0 | 0 | 0 | 1720860 | 752.107 | 1686570 | 1652841.5
84 | 1998-01-04 11:00 | 584 | 978 | 61 | 7.95 | 9.6 | 0 | 32.4781 | 173.309 | 32.7797 | 0 | 584 | 818.873 | 80.7903 | 5.4716 | 818.873 | 75.6067 | 0.02856 | 811.118 | 72.8085 | 0.021521 | 857.43 | 857.427 | 1925570 | 22.3914 | 1922860 | 1943310 | 1887050 | 0 | 0 | 1862490 | 749.061 | 0 | 0 | 0 | 0 | 1862490 | 749.061 | 1824040 | 1787555.5
85 | 1998-01-04 12:00 | 580 | 749 | 183 | 8.55 | 10.27 | 0 | 32.1581 | 189.687 | 33.3769 | 0 | 580 | 622.861 | 232.494 | 5.4341 | 622.861 | 217.577 | 0.028364 | 616.71 | 209.524 | 0.021373 | 801.468 | 801.461 | 1799880 | 21.505 | 1790900 | 1816640 | 1763800 | 0 | 0 | 1742450 | 751.255 | 0 | 0 | 0 | 0 | 1742450 | 751.255 | 1707570 | 1673417
86 | 1998-01-04 13:00 | 139 | 0 | 139 | 9.14 | 10.27 | 0 | 28.4502 | 205.138 | 39.8123 | 0 | 139 | 0 | 132.695 | 1.3023 | 0 | 124.181 | 0.0067977 | 0 | 119.585 | 0.0051222 | 116.003 | 115.995 | 260496 | 11.015 | 226957 | 242481 | 235634 | 0 | 0 | 235204 | 714.879 | 0 | 0 | 0 | 0 | 235204 | 714.879 | 228485 | 223915.125
87 | 1998-01-04 14:00 | 70 | 0 | 70 | 8.7 | 10.27 | 0 | 21.9126 | 218.625 | 49.8686 | 0 | 70 | 0 | 64.2295 | 0.65585 | 0 | 60.1084 | 0.0034233 | 0 | 57.8838 | 0.0025795 | 56.1498 | 56.1474 | 126092 | 9.6076 | 102291 | 110444 | 107405 | 0 | 0 | 107308 | 684.599 | 0 | 0 | 0 | 0 | 107308 | 684.599 | 103675 | 101601.3438
88 | 1998-01-04 15:00 | 149 | 159 | 112 | 8.25 | 10.11 | 0 | 13.2783 | 229.978 | 61.7918 | 0 | 149 | 76.1448 | 131.32 | 1.396 | 61.4981 | 122.894 | 0.0072867 | 58.0677 | 118.346 | 0.0054907 | 171.126 | 171.104 | 384256 | 11.043 | 345914 | 368535 | 348458 | 0 | 0 | 347552 | 731.194 | 0 | 0 | 0 | 0 | 347552 | 731.194 | 339658 | 332865
89 | 1998-01-04 16:00 | 20 | 65 | 15 | 7.81 | 10.11 | 0 | 3.1894 | 239.553 | 74.6774 | 0 | 20 | 15.187 | 19.396 | 0.18738 | 6.0268 | 18.1515 | 0.00097808 | 5.1878 | 17.4797 | 0.00073701 | 21.9882 | 21.9779 | 49357.8 | 8.1687 | 35240.1 | 38384.4 | 35273.1 | 0 | 0 | 35260.6 | 641.108 | 0 | 0 | 0 | 270.938 | 34989.7 | 660 | 33733.6 | 33058.9688
90 | 1998-01-04 17:00 | 0 | 0 | 0 | 7.33 | 10.11 | 0
91 | 1998-01-04 18:00 | 0 | 0 | 0 | 6.85 | 7 | 0
92 | 1998-01-04 19:00 | 0 | 0 | 0 | 6.37 | 7 | 0
93 | 1998-01-04 20:00 | 0 | 0 | 0 | 5.96 | 7 | 0
94 | 1998-01-04 21:00 | 0 | 0 | 0 | 5.54 | 7.33 | 0
95 | 1998-01-04 22:00 | 0 | 0 | 0 | 5.13 | 7.33 | 0
96 | 1998-01-04 23:00 | 0 | 0 | 0 | 4.49 | 7.33 | 0
97 | 1998-01-05 | 0 | 0 | 0 | 3.84 | 7.87 | 0
98 | 1998-01-05 01:00 | 0 | 0 | 0 | 3.19 | 7.87 | 0
99 | 1998-01-05 02:00 | 0 | 0 | 0 | 2.5 | 7.87 | 0
100 | 1998-01-05 03:00 | 0 | 0 | 0 | 1.81 | 11.2 | 0
101 | 1998-01-05 04:00 | 0 | 0 | 0 | 1.11 | 11.2 | 0
102 | 1998-01-05 05:00 | 0 | 0 | 0 | 0.66 | 11.2 | 0
103 | 1998-01-05 06:00 | 0 | 4 | 0 | 0.21 | 5.38 | 0
104 | 1998-01-05 07:00 | 71 | 531 | 22 | -0.24 | 5.38 | 0 | 5.1036 | 121.981 | 72.3279 | 0 | 71 | 167.215 | 37.6945 | 0.66522 | 19.6623 | 35.276 | 0.0034722 | 17.4069 | 33.9704 | 0.0026164 | 49.8386 | 49.8468 | 111947 | 0.85645 | 91635.6 | 102195 | 88873 | 0 | 0 | 88767.6 | 682.151 | 0 | 0 | 0 | 39.9284 | 88727.7 | 685.115 | 85667.8 | 83954.4766
105 | 1998-01-05 08:00 | 254 | 809 | 45 | 1.02 | 5.38 | 0 | 14.9881 | 131.833 | 59.5579 | 0 | 254 | 409.459 | 63.0078 | 2.3798 | 275.189 | 58.9651 | 0.012422 | 261.792 | 56.7828 | 0.00936 | 309.027 | 309.023 | 693919 | 7.8174 | 657738 | 701876 | 586602 | 0 | 0 | 583848 | 745.809 | 0 | 0 | 0 | 1356.48 | 582492 | 750.159 | 571724 | 560289.8125
106 | 1998-01-05 09:00 | 415 | 914 | 54 | 2.28 | 3.37 | 0 | 23.3187 | 143.55 | 47.861 | 0 | 415 | 611.872 | 72.9265 | 3.8882 | 591.837 | 68.2474 | 0.020295 | 577.323 | 65.7216 | 0.015293 | 623.768 | 623.832 | 1400980 | 17.9303 | 1375870 | 1414250 | 1284280 | 0 | 0 | 1272640 | 755.113 | 0 | 0 | 0 | 0 | 1272640 | 755.113 | 1249360 | 1224368.75
107 | 1998-01-05 10:00 | 531 | 961 | 60 | 3.54 | 3.37 | 0 | 29.4255 | 157.432 | 38.2634 | 0 | 531 | 752.743 | 79.7864 | 4.9751 | 752.743 | 74.6672 | 0.025968 | 742.445 | 71.9038 | 0.019568 | 789.937 | 789.937 | 1774000 | 23.3574 | 1763750 | 1775450 | 1728500 | 0 | 0 | 1707490 | 742.362 | 0 | 0 | 0 | 0 | 1707490 | 742.362 | 1674430 | 1640943.375
108 | 1998-01-05 11:00 | 588 | 979 | 63 | 4.6 | 3.37 | 0 | 32.5785 | 173.173 | 32.6903 | 0 | 588 | 820.572 | 83.2569 | 5.5091 | 820.572 | 77.915 | 0.028756 | 812.85 | 75.0314 | 0.021668 | 861.266 | 861.263 | 1934180 | 26.2068 | 1931910 | 1921790 | 1868320 | 0 | 0 | 1843580 | 738.267 | 0 | 0 | 0 | 0 | 1843580 | 738.267 | 1806590 | 1770455.75
109 | 1998-01-05 12:00 | 582 | 977 | 62 | 5.65 | 5.29 | 0 | 32.2845 | 189.586 | 33.2407 | 0 | 582 | 814.26 | 82.024 | 5.4529 | 814.26 | 76.7612 | 0.028462 | 806.295 | 73.9203 | 0.021447 | 853.83 | 853.826 | 1917480 | 24.541 | 1914360 | 1917620 | 1865420 | 0 | 0 | 1840960 | 741.489 | 0 | 0 | 0 | 0 | 1840960 | 741.489 | 1803910 | 1767834.625
110 | 1998-01-05 13:00 | 514 | 955 | 58 | 6.71 | 5.29 | 0 | 28.5933 | 205.078 | 39.6601 | 0 | 514 | 733.507 | 77.3419 | 4.8158 | 733.507 | 72.3795 | 0.025137 | 722.543 | 69.7008 | 0.018941 | 768.495 | 768.493 | 1725840 | 23.713 | 1713280 | 1722190 | 1673740 | 0 | 0 | 1653950 | 741.103 | 0 | 0 | 0 | 0 | 1653950 | 741.103 | 1622530 | 1590083.875
111 | 1998-01-05 14:00 | 390 | 901 | 52 | 7.09 | 5.29 | 0 | 22.0637 | 218.601 | 49.7189 | 0 | 390 | 581.757 | 70.5545 | 3.654 | 559.236 | 66.0276 | 0.019073 | 543.949 | 63.584 | 0.014372 | 589.321 | 589.28 | 1323370 | 20.1279 | 1293890 | 1320160 | 1273400 | 0 | 0 | 1262010 | 745.983 | 0 | 0 | 0 | 0 | 1262010 | 745.983 | 1239550 | 1214763.125
112 | 1998-01-05 15:00 | 219 | 779 | 38 | 7.46 | 5.68 | 0 | 13.4313 | 229.98 | 61.6503 | 0 | 219 | 370.022 | 54.3142 | 2.0519 | 298.846 | 50.8293 | 0.01071 | 282.321 | 48.9481 | 0.0080702 | 321.339 | 321.258 | 721471 | 14.3908 | 682296 | 711324 | 638681 | 0 | 0 | 635567 | 741.59 | 0 | 0 | 0 | 0 | 635567 | 741.59 | 624719 | 612224.8125
113 | 1998-01-05 16:00 | 30 | 326 | 5 | 7.84 | 5.68 | 0 | 3.3411 | 239.574 | 74.5451 | 0 | 30 | 76.5745 | 8.7427 | 0.28108 | 30.3896 | 8.1817 | 0.0014671 | 26.207 | 7.8789 | 0.0011055 | 33.0645 | 33.0325 | 74189.1 | 8.5526 | 58247.6 | 62939.9 | 46429.7 | 0 | 0 | 46396.8 | 609.4 | 0 | 0 | 0 | 708.623 | 45688.2 | 660 | 44079.4 | 43197.8516
114 | 1998-01-05 17:00 | 0 | 0 | 0 | 7.4 | 5.68 | 0
115 | 1998-01-05 18:00 | 0 | 0 | 0 | 6.95 | 7.82 | 0
116 | 1998-01-05 19:00 | 0 | 0 | 0 | 6.5 | 7.82 | 0
117 | 1998-01-05 20:00 | 0 | 0 | 0 | 6.09 | 7.82 | 0
118 | 1998-01-05 21:00 | 0 | 0 | 0 | 5.67 | 8.29 | 0
119 | 1998-01-05 22:00 | 0 | 0 | 0 | 5.25 | 8.29 | 0
120 | 1998-01-05 23:00 | 0 | 0 | 0 | 4.77 | 8.29 | 0
121 | 1998-01-06 | 0 | 0 | 0 | 4.29 | 6.55 | 0
122 | 1998-01-06 01:00 | 0 | 0 | 0 | 3.81 | 6.55 | 0
123 | 1998-01-06 02:00 | 0 | 0 | 0 | 3.52 | 6.55 | 0
124 | 1998-01-06 03:00 | 0 | 0 | 0 | 3.23 | 4.84 | 0
125 | 1998-01-06 04:00 | 0 | 0 | 0 | 2.94 | 4.84 | 0
126 | 1998-01-06 05:00 | 0 | 0 | 0 | 2.49 | 4.84 | 0
127 | 1998-01-06 06:00 | 0 | 3 | 0 | 2.05 | 5.43 | 0
128 | 1998-01-06 07:00 | 71 | 530 | 22 | 1.61 | 5.43 | 0 | 5.1036 | 121.824 | 72.3867 | 0 | 71 | 166.677 | 37.6325 | 0.66522 | 19.4782 | 35.2179 | 0.0034722 | 17.2336 | 33.9145 | 0.0026164 | 49.6162 | 49.5339 | 111243 | 2.6961 | 90966.6 | 100650 | 87438.2 | 0 | 0 | 87336.7 | 680.249 | 0 | 0 | 0 | 4.5186 | 87332.2 | 681.079 | 84344.6 | 82657.6797
129 | 1998-01-06 08:00 | 255 | 677 | 80 | 2.11 | 5.43 | 0 | 15.0087 | 131.673 | 59.5953 | 0 | 255 | 342.008 | 108.59 | 2.3891 | 229.989 | 101.623 | 0.012471 | 218.767 | 97.8617 | 0.0093968 | 307.139 | 307.126 | 689666 | 8.8439 | 651290 | 693889 | 596273 | 0 | 0 | 593611 | 755.922 | 0 | 0 | 0 | 0 | 593611 | 755.922 | 582425 | 570776.375
130 | 1998-01-06 09:00 | 327 | 472 | 140 | 2.62 | 2.69 | 0 | 23.3653 | 143.387 | 47.8678 | 0 | 327 | 316.315 | 176.748 | 3.0637 | 306.027 | 165.407 | 0.015992 | 298.519 | 159.286 | 0.01205 | 444.082 | 444.077 | 997290 | 14.2739 | 958635 | 1002310 | 930237 | 0 | 0 | 924210 | 755.653 | 0 | 0 | 0 | 0 | 924210 | 755.653 | 907841 | 889684.375
131 | 1998-01-06 10:00 | 397 | 434 | 184 | 3.12 | 2.69 | 0 | 29.5023 | 157.275 | 38.2251 | 0 | 397 | 339.784 | 229.342 | 3.7196 | 339.784 | 214.627 | 0.019415 | 335.147 | 206.684 | 0.01463 | 525.59 | 525.578 | 1180320 | 16.9128 | 1145900 | 1185350 | 1151780 | 0 | 0 | 1142650 | 753.123 | 0 | 0 | 0 | 0 | 1142650 | 753.123 | 1122210 | 1099770.25
132 | 1998-01-06 11:00 | 376 | 235 | 250 | 4.08 | 2.69 | 0 | 32.6863 | 173.038 | 32.5937 | 0 | 376 | 196.572 | 279.819 | 3.5228 | 196.572 | 261.865 | 0.018388 | 194.735 | 252.174 | 0.013856 | 433.514 | 433.504 | 973541 | 15.4565 | 933873 | 972449 | 944053 | 0 | 0 | 937866 | 751.249 | 0 | 0 | 0 | 0 | 937866 | 751.249 | 921442 | 903013.375
133 | 1998-01-06 12:00 | 529 | 586 | 216 | 5.04 | 0.4 | 0 | 32.4178 | 189.488 | 33.0979 | 0 | 529 | 489.121 | 266.97 | 4.9563 | 489.121 | 249.84 | 0.02587 | 484.384 | 240.594 | 0.019494 | 703.248 | 703.238 | 1579290 | 26.5579 | 1560010 | 1549360 | 1507000 | 0 | 0 | 1490450 | 730.308 | 0 | 0 | 0 | 0 | 1490450 | 730.308 | 1464020 | 1434741
134 | 1998-01-06 13:00 | 115 | 0 | 115 | 6 | 0.4 | 0 | 28.7427 | 205.022 | 39.503 | 0 | 115 | 0 | 108.008 | 1.0775 | 0 | 101.078 | 0.005624 | 0 | 97.337 | 0.0042378 | 94.421 | 94.4123 | 212026 | 8.8889 | 181349 | 195863 | 190020 | 0 | 0 | 189739 | 713.131 | 0 | 0 | 0 | 0 | 189739 | 713.131 | 183801 | 180124.9531
135 | 1998-01-06 14:00 | 242 | 219 | 159 | 6.6 | 0.4 | 0 | 22.22 | 218.582 | 49.5662 | 0 | 242 | 142.349 | 187.974 | 2.2673 | 136.838 | 175.913 | 0.011835 | 133.131 | 169.402 | 0.0089178 | 293.466 | 293.449 | 659013 | 15.5791 | 616274 | 642293 | 622028 | 0 | 0 | 619222 | 736.481 | 0 | 0 | 0 | 0 | 619222 | 736.481 | 608804 | 596627.875
136 | 1998-01-06 15:00 | 222 | 477 | 110 | 7.2 | 2.86 | 0 | 13.5885 | 229.988 | 61.5071 | 0 | 222 | 227.411 | 139.535 | 2.08 | 192.416 | 130.582 | 0.010857 | 181.869 | 125.749 | 0.0081808 | 298.398 | 298.32 | 669956 | 14.941 | 628057 | 655378 | 612971 | 0 | 0 | 610225 | 739.54 | 0 | 0 | 0 | 0 | 610225 | 739.54 | 599864 | 587866.875
137 | 1998-01-06 16:00 | 31 | 203 | 15 | 7.8 | 2.86 | 0 | 3.4962 | 239.602 | 74.4121 | 0 | 31 | 49.419 | 26.4788 | 0.29045 | 19.6138 | 24.7799 | 0.001516 | 16.9449 | 23.8628 | 0.0011424 | 39.5846 | 39.5648 | 88856.3 | 8.8267 | 69745.1 | 75532.1 | 64545.3 | 0 | 0 | 64504.3 | 667.876 | 0 | 0 | 0 | 0 | 64504.3 | 667.876 | 62255 | 61009.9141
138 | 1998-01-06 17:00 | 0 | 0 | 0 | 7.45 | 2.86 | 0
139 | 1998-01-06 18:00 | 0 | 0 | 0 | 7.11 | 5.12 | 0
140 | 1998-01-06 19:00 | 0 | 0 | 0 | 6.77 | 5.12 | 0
141 | 1998-01-06 20:00 | 0 | 0 | 0 | 6.55 | 5.12 | 0
142 | 1998-01-06 21:00 | 0 | 0 | 0 | 6.32 | 5.24 | 0
143 | 1998-01-06 22:00 | 0 | 0 | 0 | 6.1 | 5.24 | 0
144 | 1998-01-06 23:00 | 0 | 0 | 0 | 5.7 | 5.24 | 0
145 | 1998-01-07 | 0 | 0 | 0 | 5.29 | 8.39 | 0
146 | 1998-01-07 01:00 | 0 | 0 | 0 | 4.88 | 8.39 | 0
147 | 1998-01-07 02:00 | 0 | 0 | 0 | 4.81 | 8.39 | 0
148 | 1998-01-07 03:00 | 0 | 0 | 0 | 4.73 | 11.1 | 0
149 | 1998-01-07 04:00 | 0 | 0 | 0 | 4.66 | 11.1 | 0
150 | 1998-01-07 05:00 | 0 | 0 | 0 | 4.42 | 11.1 | 0
151 | 1998-01-07 06:00 | 0 | 3 | 0 | 4.19 | 10.08 | 0
152 | 1998-01-07 07:00 | 71 | 529 | 22 | 3.96 | 10.08 | 0 | 5.1096 | 121.663 | 72.4416 | 0 | 71 | 165.979 | 37.5579 | 0.66522 | 19.2283 | 35.1481 | 0.0034722 | 17.0028 | 33.8473 | 0.0026164 | 49.3271 | 49.3014 | 110720 | 4.7662 | 90487.2 | 99346.3 | 86487.7 | 0 | 0 | 86388.4 | 684.878 | 0 | 0 | 0 | 0 | 86388.4 | 684.878 | 83397.9 | 81729.9688
153 | 1998-01-07 08:00 | 250 | 803 | 42 | 4.62 | 10.08 | 0 | 15.0358 | 131.509 | 59.6282 | 0 | 250 | 405.389 | 59.0007 | 2.3423 | 272.855 | 55.2151 | 0.012226 | 259.515 | 53.1716 | 0.0092126 | 303.315 | 303.29 | 681044 | 9.5798 | 644860 | 684614 | 572538 | 0 | 0 | 569884 | 743.003 | 0 | 0 | 0 | 1389.64 | 568494 | 747.754 | 558022 | 546861.875
154 | 1998-01-07 09:00 | 417 | 915 | 54 | 5.29 | 7.71 | 0 | 23.4187 | 143.222 | 47.8692 | 0 | 417 | 612.683 | 72.8138 | 3.907 | 592.992 | 68.142 | 0.020393 | 578.443 | 65.6201 | 0.015367 | 624.756 | 624.745 | 1403030 | 17.1294 | 1377970 | 1421720 | 1293930 | 0 | 0 | 1282140 | 755.878 | 0 | 0 | 0 | 0 | 1282140 | 755.878 | 1258620 | 1233442.75
155 | 1998-01-07 10:00 | 533 | 962 | 59 | 5.96 | 7.71 | 0 | 29.5864 | 157.117 | 38.1804 | 0 | 533 | 754.647 | 78.4128 | 4.9938 | 754.647 | 73.3817 | 0.026066 | 744.378 | 70.6658 | 0.019641 | 790.611 | 790.608 | 1775500 | 20.9426 | 1765330 | 1794810 | 1744490 | 0 | 0 | 1723520 | 750.093 | 0 | 0 | 0 | 0 | 1723520 | 750.093 | 1689320 | 1655534.875
156 | 1998-01-07 11:00 | 592 | 980 | 63 | 7.49 | 7.71 | 0 | 32.8013 | 172.904 | 32.4901 | 0 | 592 | 823.667 | 83.1413 | 5.5466 | 823.667 | 77.8068 | 0.028951 | 816.025 | 74.9272 | 0.021815 | 864.245 | 864.243 | 1940870 | 23.868 | 1938940 | 1947690 | 1893840 | 0 | 0 | 1868780 | 743.872 | 0 | 0 | 0 | 0 | 1868780 | 743.872 | 1830630 | 1794019.25
157 | 1998-01-07 12:00 | 587 | 979 | 62 | 9.02 | 5.31 | 0 | 32.558 | 189.393 | 32.9486 | 0 | 587 | 818.65 | 81.9042 | 5.4997 | 818.65 | 76.6491 | 0.028707 | 810.804 | 73.8124 | 0.021631 | 858.099 | 858.094 | 1927060 | 27.9809 | 1924430 | 1900180 | 1847000 | 0 | 0 | 1822320 | 730.351 | 0 | 0 | 0 | 0 | 1822320 | 730.351 | 1786150 | 1750422.375
158 | 1998-01-07 13:00 | 513 | 951 | 55 | 10.54 | 5.31 | 0 | 28.8982 | 204.972 | 39.3413 | 0 | 513 | 732.967 | 73.4118 | 4.8064 | 732.967 | 68.7015 | 0.025088 | 722.228 | 66.1589 | 0.018904 | 764.754 | 764.752 | 1717450 | 27.4383 | 1704490 | 1686750 | 1638570 | 0 | 0 | 1619110 | 731.627 | 0 | 0 | 0 | 0 | 1619110 | 731.627 | 1589070 | 1557289.625
159 | 1998-01-07 14:00 | 391 | 901 | 49 | 11.08 | 5.31 | 0 | 22.3815 | 218.569 | 49.4106 | 0 | 391 | 584.384 | 66.5704 | 3.6634 | 561.761 | 62.2992 | 0.019121 | 546.678 | 59.9935 | 0.014408 | 588.486 | 588.488 | 1321600 | 24.0835 | 1292060 | 1296580 | 1254660 | 0 | 0 | 1243170 | 731.437 | 0 | 0 | 0 | 0 | 1243170 | 731.437 | 1221840 | 1197401.375
160 | 1998-01-07 15:00 | 209 | 702 | 42 | 11.62 | 3.02 | 0 | 13.75 | 230.003 | 61.3623 | 0 | 209 | 336.738 | 62.5673 | 1.9582 | 284.92 | 58.5528 | 0.010221 | 269.442 | 56.3858 | 0.0077017 | 316.06 | 316.059 | 709792 | 19.7347 | 668819 | 682623 | 628087 | 0 | 0 | 625028 | 723.477 | 0 | 0 | 0 | 0 | 625028 | 723.477 | 614919 | 602620.5
161 | 1998-01-07 16:00 | 31 | 303 | 6 | 12.16 | 3.02 | 0 | 3.6547 | 239.637 | 74.2786 | 0 | 31 | 77.862 | 10.5453 | 0.29045 | 33.9525 | 9.8687 | 0.001516 | 29.3849 | 9.5035 | 0.0011424 | 37.7228 | 37.7083 | 84686.5 | 13.1282 | 67323.9 | 71193.2 | 54500.4 | 0 | 0 | 54458.4 | 615.266 | 0 | 0 | 0 | 905.337 | 53553.1 | 660 | 51692.1 | 50658.3047
162 | 1998-01-07 17:00 | 0 | 0 | 0 | 11.63 | 3.02 | 0
163 | 1998-01-07 18:00 | 0 | 0 | 0 | 11.1 | 4.86 | 0
164 | 1998-01-07 19:00 | 0 | 0 | 0 | 10.57 | 4.86 | 0
165 | 1998-01-07 20:00 | 0 | 0 | 0 | 9.94 | 4.86 | 0
166 | 1998-01-07 21:00 | 0 | 0 | 0 | 9.31 | 2.86 | 0
167 | 1998-01-07 22:00 | 0 | 0 | 0 | 8.67 | 2.86 | 0
168 | 1998-01-07 23:00 | 0 | 0 | 0 | 8.09 | 2.86 | 0
169 | 1998-01-08 | 0 | 0 | 0 | 7.51 | 3.61 | 0
170 | 1998-01-08 01:00 | 0 | 0 | 0 | 6.93 | 3.61 | 0
171 | 1998-01-08 02:00 | 0 | 0 | 0 | 6.32 | 3.61 | 0
172 | 1998-01-08 03:00 | 0 | 0 | 0 | 5.71 | 1.3 | 0
173 | 1998-01-08 04:00 | 0 | 0 | 0 | 5.1 | 1.3 | 0
174 | 1998-01-08 05:00 | 0 | 0 | 0 | 4.9 | 1.3 | 0
175 | 1998-01-08 06:00 | 0 | 0 | 0 | 4.7 | 0.53 | 0
176 | 1998-01-08 07:00 | 31 | 22 | 29 | 4.5 | 0.53 | 0 | 5.1216 | 121.498 | 72.4927 | 0 | 31 | 6.7398 | 23.7535 | 0.29045 | 0.77492 | 22.2294 | 0.001516 | 0.68487 | 21.4067 | 0.0011424 | 21.4299 | 21.4301 | 48126.8 | 5.15 | 34097.1 | 37686 | 36495.1 | 0 | 0 | 36482.6 | 649.539 | 0 | 0 | 0 | 70.8465 | 36411.7 | 660 | 35107.8 | 34405.625
177 | 1998-01-08 08:00 | 141 | 122 | 109 | 5.04 | 0.53 | 0 | 15.0693 | 131.341 | 59.6565 | 0 | 141 | 62.1795 | 123.797 | 1.3211 | 41.8963 | 115.854 | 0.0068955 | 39.8444 | 111.566 | 0.0051959 | 146.873 | 146.847 | 329769 | 9.4939 | 293373 | 314845 | 294575 | 0 | 0 | 293933 | 730.464 | 0 | 0 | 0 | 0 | 293933 | 730.464 | 286309 | 280582.875
178 | 1998-01-08 09:00 | 324 | 448 | 146 | 5.58 | 2.82 | 0 | 23.4791 | 143.054 | 47.8652 | 0 | 324 | 299.729 | 183.334 | 3.0356 | 290.219 | 171.571 | 0.015845 | 283.1 | 165.221 | 0.01194 | 434.883 | 434.872 | 976616 | 16.8943 | 937474 | 969769 | 902065 | 0 | 0 | 896258 | 746.103 | 0 | 0 | 0 | 0 | 896258 | 746.103 | 880773 | 863157.125
179 | 1998-01-08 10:00 | 393 | 377 | 207 | 6.12 | 2.82 | 0 | 29.6777 | 156.958 | 38.1294 | 0 | 393 | 295.506 | 242.751 | 3.6821 | 295.506 | 227.176 | 0.019219 | 291.498 | 218.768 | 0.014482 | 494.972 | 494.964 | 1111570 | 18.9977 | 1075170 | 1102810 | 1071450 | 0 | 0 | 1063390 | 746.029 | 0 | 0 | 0 | 0 | 1063390 | 746.029 | 1044880 | 1023986.5
180 | 1998-01-08 11:00 | 590 | 817 | 147 | 7.48 | 2.82 | 0 | 32.9236 | 172.77 | 32.3795 | 0 | 590 | 688.332 | 194.563 | 5.5278 | 688.332 | 182.079 | 0.028854 | 681.996 | 175.341 | 0.021742 | 831.638 | 831.623 | 1867620 | 29.1168 | 1861980 | 1829570 | 1780800 | 0 | 0 | 1757580 | 726.24 | 0 | 0 | 0 | 0 | 1757580 | 726.24 | 1723520 | 1689053.25
181 | 1998-01-08 12:00 | 590 | 980 | 62 | 8.85 | 3.21 | 0 | 32.705 | 189.301 | 32.7929 | 0 | 590 | 821.475 | 81.8395 | 5.5278 | 821.475 | 76.5885 | 0.028854 | 813.689 | 73.754 | 0.021742 | 860.84 | 860.836 | 1933220 | 30.6756 | 1930900 | 1884780 | 1834980 | 0 | 0 | 1810010 | 721.937 | 0 | 0 | 0 | 0 | 1810010 | 721.937 | 1774370 | 1738881.625
182 | 1998-01-08 13:00 | 522 | 958 | 58 | 10.21 | 3.21 | 0 | 29.0597 | 204.926 | 39.175 | 0 | 522 | 740.554 | 77.1461 | 4.8907 | 740.554 | 72.1962 | 0.025528 | 729.818 | 69.5243 | 0.019236 | 775.38 | 775.376 | 1741300 | 29.8689 | 1729480 | 1693760 | 1650080 | 0 | 0 | 1629740 | 720.22 | 0 | 0 | 0 | 0 | 1629740 | 720.22 | 1599730 | 1567733.5
183 | 1998-01-08 14:00 | 395 | 757 | 105 | 10.5 | 3.21 | 0 | 22.548 | 218.562 | 49.2522 | 0 | 395 | 493.646 | 140.894 | 3.7008 | 474.535 | 131.854 | 0.019317 | 461.912 | 126.974 | 0.014556 | 571.234 | 571.196 | 1282760 | 24.9821 | 1251820 | 1251390 | 1211090 | 0 | 0 | 1200340 | 729.441 | 0 | 0 | 0 | 0 | 1200340 | 729.441 | 1179960 | 1156360.5
184 | 1998-01-08 15:00 | 152 | 215 | 100 | 10.79 | 5.06 | 0 | 13.9155 | 230.024 | 61.2161 | 0 | 152 | 104.113 | 121.446 | 1.4241 | 88.0921 | 113.654 | 0.0074334 | 83.3492 | 109.448 | 0.0056013 | 187.018 | 187 | 419956 | 14.9896 | 380605 | 398265 | 377098 | 0 | 0 | 376010 | 721.419 | 0 | 0 | 0 | 0 | 376010 | 721.419 | 368440 | 361071.4062
185 | 1998-01-08 16:00 | 23 | 94 | 15 | 11.08 | 5.06 | 0 | 3.8165 | 239.679 | 74.1446 | 0 | 23 | 25.1228 | 24.3675 | 0.21549 | 10.9556 | 22.804 | 0.0011248 | 9.4984 | 21.9601 | 0.00084756 | 30.5156 | 30.5076 | 68513.3 | 11.7651 | 51640.2 | 55249.3 | 49835.9 | 0 | 0 | 49811 | 644.486 | 0 | 0 | 0 | 59.1089 | 49751.9 | 660 | 48010.1 | 47049.875
186 | 1998-01-08 17:00 | 0 | 0 | 0 | 10.64 | 5.06 | 0
187 | 1998-01-08 18:00 | 0 | 0 | 0 | 10.2 | 5.85 | 0
188 | 1998-01-08 19:00 | 0 | 0 | 0 | 9.77 | 5.85 | 0
189 | 1998-01-08 20:00 | 0 | 0 | 0 | 9.59 | 5.85 | 0
190 | 1998-01-08 21:00 | 0 | 0 | 0 | 9.41 | 4.23 | 0
191 | 1998-01-08 22:00 | 0 | 0 | 0 | 9.24 | 4.23 | 0
192 | 1998-01-08 23:00 | 0 | 0 | 0 | 8.59 | 4.23 | 0
193 | 1998-01-09 | 0 | 0 | 0 | 7.94 | 4.04 | 0
194 | 1998-01-09 01:00 | 0 | 0 | 0 | 7.29 | 4.04 | 0
195 | 1998-01-09 02:00 | 0 | 0 | 0 | 7.15 | 4.04 | 0
196 | 1998-01-09 03:00 | 0 | 0 | 0 | 7.02 | 5.6 | 0
197 | 1998-01-09 04:00 | 0 | 0 | 0 | 6.88 | 5.6 | 0
198 | 1998-01-09 05:00 | 0 | 0 | 0 | 5.99 | 5.6 | 0
199 | 1998-01-09 06:00 | 0 | 0 | 0 | 5.1 | 5.42 | 0
200 | 1998-01-09 07:00 | 14 | 0 | 14 | 4.22 | 5.42 | 0 | 5.1396 | 121.328 | 72.54 | 0 | 14 | 0 | 11.465 | 0.13117 | 0 | 10.7294 | 0.00068466 | 0 | 10.3323 | 0.0005159 | 10.0228 | 10.0219 | 22506.6 | 4.4399 | 13354.8 | 14675 | 14338.8 | 0 | 0 | 14336.6 | 607.166 | 0 | 0 | 0 | 1202.57 | 13134 | 660 | 12645.3 | 12392.3809
201 | 1998-01-09 08:00 | 61 | 0 | 61 | 5.12 | 5.42 | 0 | 15.1093 | 131.169 | 59.6802 | 0 | 61 | 0 | 56.5782 | 0.57152 | 0 | 52.9481 | 0.0029831 | 0 | 50.9885 | 0.0022479 | 49.461 | 49.4602 | 111075 | 6.2051 | 88802.8 | 97482.5 | 94741.5 | 0 | 0 | 94666.8 | 690.179 | 0 | 0 | 0 | 0 | 94666.8 | 690.179 | 91338.5 | 89511.7266
202 | 1998-01-09 09:00 | 106 | 0 | 106 | 6.03 | 7.71 | 0 | 23.5463 | 142.883 | 47.8558 | 0 | 106 | 0 | 100.11 | 0.99314 | 0 | 93.687 | 0.0051838 | 0 | 90.2197 | 0.0039061 | 87.5169 | 87.5103 | 196526 | 7.6884 | 166898 | 181332 | 176029 | 0 | 0 | 175788 | 713.73 | 0 | 0 | 0 | 0 | 175788 | 713.73 | 170122 | 166719.5781
203 | 1998-01-09 10:00 | 115 | 0 | 115 | 6.93 | 7.71 | 0 | 29.7762 | 156.797 | 38.072 | 0 | 115 | 0 | 107.81 | 1.0775 | 0 | 100.892 | 0.005624 | 0 | 97.1584 | 0.0042378 | 94.2478 | 94.2442 | 211649 | 8.716 | 180996 | 195644 | 190197 | 0 | 0 | 189915 | 712.94 | 0 | 0 | 0 | 0 | 189915 | 712.94 | 183976 | 180296.875
204 | 1998-01-09 11:00 | 367 | 214 | 251 | 7.77 | 7.71 | 0 | 33.0531 | 172.637 | 32.2618 | 0 | 367 | 179.848 | 280.395 | 3.4385 | 179.848 | 262.404 | 0.017948 | 178.206 | 252.693 | 0.013524 | 417.984 | 417.968 | 938651 | 15.6908 | 898319 | 934682 | 908773 | 0 | 0 | 902990 | 748.446 | 0 | 0 | 0 | 0 | 902990 | 748.446 | 887292 | 869546.5625
205 | 1998-01-09 12:00 | 551 | 617 | 217 | 8.61 | 6.55 | 0 | 32.8588 | 189.212 | 32.6309 | 0 | 551 | 518.424 | 267.847 | 5.1624 | 518.424 | 250.662 | 0.026946 | 513.566 | 241.385 | 0.020304 | 732.322 | 732.309 | 1644590 | 23.5496 | 1628240 | 1637860 | 1591840 | 0 | 0 | 1573940 | 741.035 | 0 | 0 | 0 | 0 | 1573940 | 741.035 | 1544810 | 1513913.75
206 | 1998-01-09 13:00 | 125 | 0 | 125 | 9.45 | 6.55 | 0 | 29.2271 | 204.884 | 39.0043 | 0 | 125 | 0 | 118.017 | 1.1711 | 0 | 110.445 | 0.006113 | 0 | 106.357 | 0.0046063 | 103.171 | 103.161 | 231672 | 11.5545 | 199764 | 213042 | 206812 | 0 | 0 | 206474 | 707.039 | 0 | 0 | 0 | 0 | 206474 | 707.039 | 200340 | 196333.2969
207 | 1998-01-09 14:00 | 73 | 0 | 73 | 9.2 | 6.55 | 0 | 22.7194 | 218.56 | 49.0911 | 0 | 73 | 0 | 67.0867 | 0.68395 | 0 | 62.7823 | 0.00357 | 0 | 60.4587 | 0.0026901 | 58.6476 | 58.6458 | 131703 | 10.3964 | 107361 | 115461 | 112203 | 0 | 0 | 112097 | 684.341 | 0 | 0 | 0 | 0 | 112097 | 684.341 | 108337 | 106170.5703
208 | 1998-01-09 15:00 | 38 | 0 | 38 | 8.96 | 5.43 | 0 | 14.0851 | 230.052 | 61.0686 | 0 | 38 | 0 | 33.8841 | 0.35603 | 0 | 31.71 | 0.0018584 | 0 | 30.5364 | 0.0014003 | 29.6217 | 29.6205 | 66519.8 | 9.6094 | 49675.8 | 53759.3 | 52347.3 | 0 | 0 | 52321.7 | 651.646 | 0 | 0 | 0 | 62.6919 | 52259 | 660 | 50437.1 | 49428.3125
209 | 1998-01-09 16:00 | 6 | 0 | 6 | 8.72 | 5.43 | 0 | 3.9815 | 239.727 | 74.0103 | 0 | 6 | 0 | 4.562 | 0.056215 | 0 | 4.2693 | 0.00029342 | 0 | 4.1113 | 0.0002211 | 3.9881 | 3.988 | 8955.91 | 8.8074 | 3487.95 | 3589.73 | 3540.42 | 0 | 0 | 3540.22 | 496.987 | 0 | 0 | 0 | 3540.22 | 0 | 660 | 0 | 0
210 | 1998-01-09 17:00 | 0 | 0 | 0 | 8.84 | 5.43 | 0
211 | 1998-01-09 18:00 | 0 | 0 | 0 | 8.96 | 4.6 | 0
212 | 1998-01-09 19:00 | 0 | 0 | 0 | 9.08 | 4.6 | 0
213 | 1998-01-09 20:00 | 0 | 0 | 0 | 9.02 | 4.6 | 0
214 | 1998-01-09 21:00 | 0 | 0 | 0 | 8.97 | 7.58 | 0
215 | 1998-01-09 22:00 | 0 | 0 | 0 | 8.91 | 7.58 | 0
216 | 1998-01-09 23:00 | 0 | 0 | 0 | 8.7 | 7.58 | 0
217 | 1998-01-10 | 0 | 0 | 0 | 8.49 | 9.74 | 0
218 | 1998-01-10 01:00 | 0 | 0 | 0 | 8.28 | 9.74 | 0
219 | 1998-01-10 02:00 | 0 | 0 | 0 | 8.02 | 9.74 | 0
220 | 1998-01-10 03:00 | 0 | 0 | 0 | 7.76 | 7.85 | 0
221 | 1998-01-10 04:00 | 0 | 0 | 0 | 7.5 | 7.85 | 0
222 | 1998-01-10 05:00 | 0 | 0 | 0 | 7.49 | 7.85 | 0
223 | 1998-01-10 06:00 | 0 | 4 | 0 | 7.47 | 7.29 | 0
224 | 1998-01-10 07:00 | 72 | 532 | 23 | 7.45 | 7.29 | 0 | 5.1636 | 121.154 | 72.5833 | 0 | 72 | 162.962 | 38.7327 | 0.67458 | 18.4061 | 36.2475 | 0.0035211 | 16.2518 | 34.9061 | 0.0026532 | 49.6256 | 49.5876 | 111367 | 8.415 | 90937 | 98179.3 | 86375.5 | 0 | 0 | 86274.2 | 665.279 | 0 | 0 | 0 | 35.2796 | 86239 | 667.519 | 83389.3 | 81721.5469
225 | 1998-01-10 08:00 | 252 | 806 | 41 | 7.96 | 7.29 | 0 | 15.1557 | 130.994 | 59.6994 | 0 | 252 | 407.192 | 57.4901 | 2.361 | 275.141 | 53.8014 | 0.012324 | 261.632 | 51.8102 | 0.0092863 | 304.048 | 304.3 | 683309 | 13.882 | 647157 | 674212 | 565051 | 0 | 0 | 562343 | 726.185 | 0 | 0 | 0 | 270.705 | 562072 | 732.396 | 552108 | 541066.125
226 | 1998-01-10 09:00 | 420 | 916 | 54 | 8.48 | 6.85 | 0 | 23.6204 | 142.709 | 47.8411 | 0 | 420 | 613.104 | 72.6165 | 3.9351 | 594.288 | 67.9573 | 0.02054 | 579.731 | 65.4423 | 0.015477 | 625.833 | 625.849 | 1405510 | 21.0054 | 1380480 | 1401800 | 1276870 | 0 | 0 | 1264940 | 741.72 | 0 | 0 | 0 | 0 | 1264940 | 741.72 | 1242580 | 1217731.625
227 | 1998-01-10 10:00 | 522 | 943 | 54 | 8.99 | 6.85 | 0 | 29.8818 | 156.636 | 38.0083 | 0 | 522 | 740.139 | 71.8929 | 4.8907 | 740.139 | 67.2801 | 0.025528 | 730.179 | 64.7901 | 0.019236 | 771.138 | 771.133 | 1731770 | 24.423 | 1719500 | 1723360 | 1676530 | 0 | 0 | 1656550 | 738.457 | 0 | 0 | 0 | 0 | 1656550 | 738.457 | 1625220 | 1592715.75
228 | 1998-01-10 11:00 | 580 | 744 | 174 | 9.71 | 6.85 | 0 | 33.1897 | 172.505 | 32.1372 | 0 | 580 | 628.029 | 223.581 | 5.4341 | 628.029 | 209.236 | 0.028364 | 622.347 | 201.492 | 0.021373 | 799.145 | 799.133 | 1794650 | 25.7034 | 1785400 | 1779850 | 1729320 | 0 | 0 | 1708000 | 736.632 | 0 | 0 | 0 | 0 | 1708000 | 736.632 | 1675210 | 1641706.125
229 | 1998-01-10 12:00 | 195 | 21 | 184 | 10.44 | 8.66 | 0 | 33.0193 | 189.126 | 32.4627 | 0 | 195 | 17.0321 | 178.075 | 1.827 | 17.0321 | 166.649 | 0.0095363 | 16.8744 | 160.482 | 0.0071858 | 172.042 | 172.033 | 386342 | 13.5114 | 347623 | 366494 | 355879 | 0 | 0 | 354921 | 723.142 | 0 | 0 | 0 | 0 | 354921 | 723.142 | 347249 | 340304.4375
230 | 1998-01-10 13:00 | 290 | 139 | 222 | 11.17 | 8.66 | 0 | 29.4004 | 204.848 | 38.8292 | 0 | 290 | 107.908 | 247.669 | 2.7171 | 107.908 | 231.778 | 0.014182 | 106.378 | 223.2 | 0.010687 | 319.701 | 319.689 | 717942 | 16.8777 | 675212 | 699689 | 680811 | 0 | 0 | 677429 | 734.093 | 0 | 0 | 0 | 0 | 677429 | 734.093 | 666113 | 652790.5625
231 | 1998-01-10 14:00 | 384 | 648 | 132 | 11.12 | 8.66 | 0 | 22.8957 | 218.565 | 48.9275 | 0 | 384 | 425.563 | 168.96 | 3.5978 | 425.563 | 158.119 | 0.018779 | 414.455 | 152.267 | 0.01415 | 549.734 | 549.73 | 1234550 | 20.9348 | 1201850 | 1222620 | 1189010 | 0 | 0 | 1178960 | 741.209 | 0 | 0 | 0 | 0 | 1178960 | 741.209 | 1158430 | 1135264.25
232 | 1998-01-10 15:00 | 232 | 788 | 38 | 11.06 | 7.13 | 0 | 14.2585 | 230.086 | 60.9198 | 0 | 232 | 382.833 | 53.7855 | 2.1737 | 323.922 | 50.3345 | 0.011346 | 306.795 | 48.4717 | 0.0085493 | 344.617 | 344.532 | 773736 | 17.8335 | 733406 | 754808 | 692039 | 0 | 0 | 688418 | 733.988 | 0 | 0 | 0 | 0 | 688418 | 733.988 | 676922 | 663383.0625
233 | 1998-01-10 16:00 | 36 | 358 | 6 | 11.01 | 7.13 | 0 | 4.1495 | 239.782 | 73.8757 | 0 | 36 | 95.7661 | 10.7418 | 0.33729 | 45.4207 | 10.0525 | 0.0017606 | 39.5144 | 9.6805 | 0.0013266 | 47.7203 | 47.657 | 107027 | 11.9469 | 87660.2 | 93160.4 | 71893.7 | 0 | 0 | 71825.4 | 639.026 | 0 | 0 | 0 | 272.473 | 71552.9 | 660 | 69143.9 | 67761.0547
234 | 1998-01-10 17:00 | 0 | 0 | 0 | 10.42 | 7.13 | 0
235 | 1998-01-10 18:00 | 0 | 0 | 0 | 9.82 | 7.62 | 0
236 | 1998-01-10 19:00 | 0 | 0 | 0 | 9.22 | 7.62 | 0
237 | 1998-01-10 20:00 | 0 | 0 | 0 | 8.65 | 7.62 | 0
238 | 1998-01-10 21:00 | 0 | 0 | 0 | 8.08 | 8.62 | 0
239 | 1998-01-10 22:00 | 0 | 0 | 0 | 7.5 | 8.62 | 0
240 | 1998-01-10 23:00 | 0 | 0 | 0 | 7.09 | 8.62 | 0
241 | 1998-01-11 | 0 | 0 | 0 | 6.68 | 9.9 | 0
242 | 1998-01-11 01:00 | 0 | 0 | 0 | 6.26 | 9.9 | 0
243 | 1998-01-11 02:00 | 0 | 0 | 0 | 6.03 | 9.9 | 0
244 | 1998-01-11 03:00 | 0 | 0 | 0 | 5.79 | 10.37 | 0
245 | 1998-01-11 04:00 | 0 | 0 | 0 | 5.55 | 10.37 | 0
246 | 1998-01-11 05:00 | 0 | 0 | 0 | 5.2 | 10.37 | 0
247 | 1998-01-11 06:00 | 0 | 1 | 0 | 4.85 | 6.76 | 0
248 | 1998-01-11 07:00 | 44 | 99 | 35 | 4.5 | 6.76 | 0 | 5.1938 | 120.976 | 72.6227 | 0 | 44 | 29.6933 | 48.7048 | 0.41225 | 3.328 | 45.5798 | 0.0021518 | 2.9372 | 43.893 | 0.0016214 | 45.4268 | 45.4209 | 102005 | 5.4143 | 80827.4 | 89060.9 | 85178.9 | 0 | 0 | 85117.5 | 689.23 | 0 | 0 | 0 | 0 | 85117.5 | 689.23 | 82084.3 | 80442.6016
249 | 1998-01-11 08:00 | 167 | 250 | 101 | 5.53 | 6.76 | 0 | 15.2085 | 130.816 | 59.714 | 0 | 167 | 126.88 | 121.226 | 1.5647 | 85.8962 | 113.448 | 0.008167 | 81.6749 | 109.249 | 0.006154 | 185.202 | 185.214 | 415921 | 9.2581 | 377357 | 404469 | 366926 | 0 | 0 | 365942 | 741.456 | 0 | 0 | 0 | 0 | 365942 | 741.456 | 357946 | 350786.625
250 | 1998-01-11 09:00 | 411 | 753 | 109 | 6.56 | 5.48 | 0 | 23.7013 | 142.533 | 47.8209 | 0 | 411 | 504.463 | 145.669 | 3.8508 | 489.273 | 136.322 | 0.0201 | 477.303 | 131.277 | 0.015145 | 590.337 | 590.296 | 1325670 | 19.4607 | 1297100 | 1326080 | 1214900 | 0 | 0 | 1204370 | 747.842 | 0 | 0 | 0 | 0 | 1204370 | 747.842 | 1182910 | 1159247.75
251 | 1998-01-11 10:00 | 540 | 964 | 59 | 7.6 | 5.48 | 0 | 29.9946 | 156.473 | 37.9384 | 0 | 540 | 758.827 | 78.15 | 5.0594 | 758.827 | 73.1357 | 0.026408 | 748.66 | 70.429 | 0.019899 | 794.536 | 794.531 | 1784320 | 24.9641 | 1774570 | 1774520 | 1725730 | 0 | 0 | 1704600 | 739.515 | 0 | 0 | 0 | 0 | 1704600 | 739.515 | 1671780 | 1638345.75
252 | 1998-01-11 11:00 | 601 | 983 | 63 | 8.59 | 5.48 | 0 | 33.3334 | 172.374 | 32.0058 | 0 | 601 | 830.232 | 82.8703 | 5.6309 | 830.232 | 77.5531 | 0.029391 | 822.791 | 74.683 | 0.022147 | 870.571 | 870.569 | 1955080 | 27.6159 | 1953890 | 1932270 | 1877950 | 0 | 0 | 1852580 | 732.836 | 0 | 0 | 0 | 0 | 1852580 | 732.836 | 1815410 | 1779103
253 | 1998-01-11 12:00 | 598 | 983 | 62 | 9.6 | 5.44 | 0 | 33.1865 | 189.043 | 32.2882 | 0 | 598 | 827.818 | 81.6265 | 5.6028 | 827.818 | 76.3892 | 0.029245 | 820.247 | 73.5621 | 0.022037 | 867.016 | 867.015 | 1947100 | 28.5973 | 1945490 | 1916020 | 1863520 | 0 | 0 | 1838160 | 727.832 | 0 | 0 | 0 | 0 | 1838160 | 727.832 | 1801520 | 1765493.125
254 | 1998-01-11 13:00 | 532 | 961 | 59 | 10.6 | 5.44 | 0 | 29.5795 | 204.817 | 38.6498 | 0 | 532 | 748.339 | 78.1827 | 4.9844 | 748.339 | 73.1663 | 0.026017 | 737.845 | 70.4585 | 0.019604 | 784.074 | 784.069 | 1760820 | 27.7799 | 1749930 | 1729250 | 1680920 | 0 | 0 | 1660330 | 729.244 | 0 | 0 | 0 | 0 | 1660330 | 729.244 | 1629150 | 1596569.625
255 | 1998-01-11 14:00 | 409 | 911 | 53 | 10.92 | 5.44 | 0 | 23.0767 | 218.576 | 48.7615 | 0 | 409 | 598.713 | 71.3463 | 3.832 | 598.713 | 66.7686 | 0.020002 | 583.236 | 64.2975 | 0.015072 | 628.122 | 628.119 | 1410600 | 24.6829 | 1384250 | 1385910 | 1349160 | 0 | 0 | 1335980 | 733.406 | 0 | 0 | 0 | 0 | 1335980 | 733.406 | 1312660 | 1286405.125
256 | 1998-01-11 15:00 | 238 | 795 | 40 | 11.24 | 6.19 | 0 | 14.4356 | 230.127 | 60.77 | 0 | 238 | 387.845 | 56.2939 | 2.2299 | 328.163 | 52.682 | 0.011639 | 310.969 | 50.7322 | 0.0087704 | 350.859 | 350.795 | 787804 | 18.5635 | 747606 | 766806 | 703765 | 0 | 0 | 700002 | 731.899 | 0 | 0 | 0 | 0 | 700002 | 731.899 | 688386 | 674618
257 | 1998-01-11 16:00 | 38 | 367 | 6 | 11.56 | 6.19 | 0 | 4.3204 | 239.844 | 73.7411 | 0 | 38 | 102.981 | 10.8073 | 0.35603 | 48.947 | 10.1139 | 0.0018584 | 42.6532 | 9.7396 | 0.0014003 | 50.8223 | 50.7541 | 113984 | 12.6196 | 94085.4 | 99619.5 | 76578.1 | 0 | 0 | 76500.6 | 640.084 | 0 | 0 | 0 | 293.259 | 76207.3 | 662.359 | 73645.9 | 72172.9688
258 | 1998-01-11 17:00 | 0 | 0 | 0 | 10.76 | 6.19 | 0
259 | 1998-01-11 18:00 | 0 | 0 | 0 | 9.96 | 9.09 | 0
260 | 1998-01-11 19:00 | 0 | 0 | 0 | 9.16 | 9.09 | 0
261 | 1998-01-11 20:00 | 0 | 0 | 0 | 8.67 | 9.09 | 0
262 | 1998-01-11 21:00 | 0 | 0 | 0 | 8.18 | 9.26 | 0
263 | 1998-01-11 22:00 | 0 | 0 | 0 | 7.69 | 9.26 | 0
264 | 1998-01-11 23:00 | 0 | 0 | 0 | 7.52 | 9.26 | 0
265 | 1998-01-12 | 0 | 0 | 0 | 7.34 | 9.67 | 0
266 | 1998-01-12 01:00 | 0 | 0 | 0 | 7.17 | 9.67 | 0
267 | 1998-01-12 02:00 | 0 | 0 | 0 | 7.05 | 9.67 | 0
268 | 1998-01-12 03:00 | 0 | 0 | 0 | 6.94 | 11.29 | 0
269 | 1998-01-12 04:00 | 0 | 0 | 0 | 6.82 | 11.29 | 0
270 | 1998-01-12 05:00 | 0 | 0 | 0 | 6.52 | 11.29 | 0
271 | 1998-01-12 06:00 | 0 | 5 | 0 | 6.21 | 9.33 | 0
272 | 1998-01-12 07:00 | 73 | 535 | 23 | 5.9 | 9.33 | 0 | 5.23 | 120.794 | 72.6581 | 0 | 73 | 163.5 | 38.472 | 0.68395 | 18.1825 | 36.0036 | 0.00357 | 16.0416 | 34.6711 | 0.0026901 | 49.194 | 49.1617 | 110409 | 6.7419 | 90072.3 | 98037.6 | 86646 | 0 | 0 | 86547.4 | 678.236 | 0 | 0 | 0 | 0 | 86547.4 | 678.236 | 83603.3 | 81931.2031
273 | 1998-01-12 08:00 | 254 | 731 | 62 | 6.97 | 9.33 | 0 | 15.2679 | 130.634 | 59.7239 | 0 | 254 | 367.598 | 85.2234 | 2.3798 | 249.418 | 79.7553 | 0.012422 | 237.153 | 76.8036 | 0.00936 | 304.547 | 304.443 | 683631 | 12.1838 | 645981 | 679224 | 578460 | 0 | 0 | 575785 | 736.514 | 0 | 0 | 0 | 70.5648 | 575715 | 737.255 | 565468 | 554158.9375
274 | 1998-01-12 09:00 | 369 | 684 | 94 | 8.03 | 8.62 | 0 | 23.789 | 142.355 | 47.7954 | 0 | 369 | 457.99 | 128.564 | 3.4572 | 444.488 | 120.315 | 0.018046 | 433.63 | 115.862 | 0.013598 | 533.02 | 532.99 | 1196970 | 17.5697 | 1163960 | 1199890 | 1099300 | 0 | 0 | 1090750 | 751.315 | 0 | 0 | 0 | 0 | 1090750 | 751.315 | 1071350 | 1049922
275 | 1998-01-12 10:00 | 491 | 772 | 105 | 9.1 | 8.62 | 0 | 30.1144 | 156.31 | 37.8622 | 0 | 491 | 607.386 | 143.848 | 4.6003 | 607.386 | 134.619 | 0.024012 | 599.288 | 129.636 | 0.018093 | 707.074 | 707.069 | 1587900 | 21.7554 | 1568990 | 1590130 | 1545400 | 0 | 0 | 1528790 | 747.268 | 0 | 0 | 0 | 0 | 1528790 | 747.268 | 1500490 | 1470483.5
276 | 1998-01-12 11:00 | 586 | 914 | 83 | 10.42 | 8.62 | 0 | 33.4842 | 172.244 | 31.8675 | 0 | 586 | 774.294 | 107.434 | 5.4904 | 774.294 | 100.541 | 0.028658 | 767.423 | 96.8202 | 0.021594 | 838.337 | 838.333 | 1882680 | 25.4248 | 1877800 | 1874180 | 1822620 | 0 | 0 | 1799010 | 737.971 | 0 | 0 | 0 | 0 | 1799010 | 737.971 | 1763420 | 1728153.625
277 | 1998-01-12 12:00 | 600 | 820 | 151 | 11.74 | 8.2 | 0 | 33.3602 | 188.964 | 32.1076 | 0 | 600 | 691.627 | 198.636 | 5.6215 | 691.627 | 185.891 | 0.029343 | 685.382 | 179.012 | 0.02211 | 838.484 | 838.468 | 1882980 | 27.147 | 1878120 | 1861020 | 1809260 | 0 | 0 | 1785730 | 733.19 | 0 | 0 | 0 | 0 | 1785730 | 733.19 | 1750660 | 1715646.75
278 | 1998-01-12 13:00 | 329 | 213 | 224 | 13.06 | 8.2 | 0 | 29.7642 | 204.791 | 38.4663 | 0 | 329 | 165.606 | 249.528 | 3.0825 | 165.606 | 233.518 | 0.016089 | 163.311 | 224.876 | 0.012124 | 376.553 | 376.549 | 845635 | 19.9792 | 803895 | 821654 | 798580 | 0 | 0 | 793911 | 731.796 | 0 | 0 | 0 | 0 | 793911 | 731.796 | 780740 | 765125.1875
279 | 1998-01-12 14:00 | 304 | 437 | 132 | 12.99 | 8.2 | 0 | 23.2624 | 218.593 | 48.5931 | 0 | 304 | 288.045 | 166.625 | 2.8482 | 288.045 | 155.934 | 0.014867 | 280.672 | 150.163 | 0.011203 | 417.92 | 417.909 | 938518 | 20.6692 | 898174 | 915134 | 889983 | 0 | 0 | 884193 | 732.787 | 0 | 0 | 0 | 0 | 884193 | 732.787 | 869480 | 852090.875
280 | 1998-01-12 15:00 | 206 | 460 | 90 | 12.92 | 6.99 | 0 | 14.6164 | 230.174 | 60.6193 | 0 | 206 | 225.527 | 116.744 | 1.9301 | 190.822 | 109.254 | 0.010074 | 180.916 | 105.21 | 0.0075912 | 277.55 | 277.472 | 623135 | 18.4239 | 581401 | 597976 | 558564 | 0 | 0 | 556181 | 724.587 | 0 | 0 | 0 | 0 | 556181 | 724.587 | 546839 | 535901.9375
281 | 1998-01-12 16:00 | 34 | 216 | 15 | 12.85 | 6.99 | 0 | 4.4942 | 239.912 | 73.6064 | 0 | 34 | 61.6373 | 28.7067 | 0.31855 | 29.2979 | 26.8648 | 0.0016627 | 25.5724 | 25.8706 | 0.0012529 | 49.9009 | 49.8649 | 111986 | 13.8391 | 90517.1 | 95623.4 | 82161 | 0 | 0 | 82092.7 | 662.216 | 0 | 0 | 0 | 11.3244 | 82081.4 | 662.851 | 79345.5 | 77758.5547
282 | 1998-01-12 17:00 | 0 | 0 | 0 | 12.25 | 6.99 | 0
283 | 1998-01-12 18:00 | 0 | 0 | 0 | 11.65 | 10.15 | 0
284 | 1998-01-12 19:00 | 0 | 0 | 0 | 11.05 | 10.15 | 0
285 | 1998-01-12 20:00 | 0 | 0 | 0 | 10.54 | 10.15 | 0
286 | 1998-01-12 21:00 | 0 | 0 | 0 | 10.02 | 9.82 | 0
287 | 1998-01-12 22:00 | 0 | 0 | 0 | 9.51 | 9.82 | 0
288 | 1998-01-12 23:00 | 0 | 0 | 0 | 9.13 | 9.82 | 0
289 | 1998-01-13 | 0 | 0 | 0 | 8.75 | 10.12 | 0
290 | 1998-01-13 01:00 | 0 | 0 | 0 | 8.38 | 10.12 | 0
291 | 1998-01-13 02:00 | 0 | 0 | 0 | 7.68 | 10.12 | 0
292 | 1998-01-13 03:00 | 0 | 0 | 0 | 6.98 | 10.4 | 0
293 | 1998-01-13 04:00 | 0 | 0 | 0 | 6.28 | 10.4 | 0
294 | 1998-01-13 05:00 | 0 | 0 | 0 | 6.13 | 10.4 | 0
295 | 1998-01-13 06:00 | 0 | 6 | 0 | 5.98 | 8.1 | 0
296 | 1998-01-13 07:00 | 73 | 536 | 22 | 5.83 | 8.1 | 0 | 5.2723 | 120.608 | 72.6894 | 0 | 73 | 165.146 | 36.8643 | 0.68395 | 18.1979 | 34.499 | 0.00357 | 16.0498 | 33.2223 | 0.0026901 | 47.7965 | 47.7725 | 107291 | 6.7134 | 87350.3 | 95049 | 83506.5 | 0 | 0 | 83408.8 | 666.394 | 0 | 0 | 0 | 113.613 | 83295.2 | 670.608 | 80505.8 | 78895.7031
297 | 1998-01-13 08:00 | 260 | 813 | 45 | 6.77 | 8.1 | 0 | 15.3336 | 130.449 | 59.7292 | 0 | 260 | 409.845 | 62.4048 | 2.436 | 278.667 | 58.4008 | 0.012715 | 264.96 | 56.2394 | 0.0095811 | 311.573 | 311.348 | 699121 | 12.5271 | 662766 | 694679 | 584105 | 0 | 0 | 581308 | 735.139 | 0 | 0 | 0 | 651.425 | 580657 | 737.365 | 570278 | 558872.8125
298 | 1998-01-13 09:00 | 425 | 918 | 54 | 7.71 | 6.66 | 0 | 23.8835 | 142.175 | 47.7645 | 0 | 425 | 615.934 | 72.387 | 3.9819 | 598.237 | 67.7425 | 0.020784 | 583.649 | 65.2354 | 0.015661 | 629.433 | 629.42 | 1413530 | 20.4606 | 1388740 | 1413420 | 1281250 | 0 | 0 | 1269440 | 747.668 | 0 | 0 | 0 | 0 | 1269440 | 747.668 | 1246640 | 1221712
299 | 1998-01-13 10:00 | 544 | 966 | 59 | 8.65 | 6.66 | 0 | 30.2413 | 156.145 | 37.7799 | 0 | 544 | 761.115 | 77.9992 | 5.0969 | 761.115 | 72.9946 | 0.026604 | 751.021 | 70.2931 | 0.020047 | 796.695 | 796.692 | 1789160 | 24.7891 | 1779650 | 1780910 | 1731290 | 0 | 0 | 1710030 | 739.091 | 0 | 0 | 0 | 0 | 1710030 | 739.091 | 1677070 | 1643531.75
300 | 1998-01-13 11:00 | 606 | 985 | 62 | 9.78 | 6.66 | 0 | 33.642 | 172.116 | 31.7223 | 0 | 606 | 835.25 | 81.4641 | 5.6777 | 835.25 | 76.2372 | 0.029636 | 827.915 | 73.4157 | 0.022331 | 874.313 | 874.31 | 1963470 | 27.4915 | 1962710 | 1942050 | 1889290 | 0 | 0 | 1863500 | 731.427 | 0 | 0 | 0 | 0 | 1863500 | 731.427 | 1826000 | 1789480.375
301 | 1998-01-13 12:00 | 604 | 983 | 63 | 10.92 | 7.43 | 0 | 33.5404 | 188.889 | 31.921 | 0 | 604 | 831.074 | 82.7214 | 5.659 | 831.074 | 77.4139 | 0.029538 | 823.67 | 74.5488 | 0.022258 | 871.294 | 871.288 | 1956690 | 27.7265 | 1955580 | 1933100 | 1881350 | 0 | 0 | 1855800 | 731.552 | 0 | 0 | 0 | 0 | 1855800 | 731.552 | 1818550 | 1782178.875
302 | 1998-01-13 13:00 | 539 | 963 | 60 | 12.05 | 7.43 | 0 | 29.9545 | 204.771 | 38.2787 | 0 | 539 | 753.071 | 79.2737 | 5.05 | 753.071 | 74.1873 | 0.026359 | 742.759 | 71.4417 | 0.019862 | 789.794 | 789.795 | 1773670 | 27.2845 | 1763410 | 1746270 | 1696490 | 0 | 0 | 1675630 | 731.313 | 0 | 0 | 0 | 0 | 1675630 | 731.313 | 1643940 | 1611059.25
303 | 1998-01-13 14:00 | 413 | 912 | 51 | 12.33 | 7.43 | 0 | 23.4526 | 218.617 | 48.4227 | 0 | 413 | 603.619 | 68.6245 | 3.8695 | 603.619 | 64.2214 | 0.020197 | 588.321 | 61.8446 | 0.015219 | 630.676 | 630.671 | 1416330 | 24.4952 | 1390200 | 1393010 | 1358230 | 0 | 0 | 1344780 | 730.817 | 0 | 0 | 0 | 0 | 1344780 | 730.817 | 1321400 | 1294971
304 | 1998-01-13 15:00 | 236 | 789 | 34 | 12.62 | 4.16 | 0 | 14.8007 | 230.228 | 60.4677 | 0 | 236 | 389.765 | 48.1511 | 2.2111 | 329.787 | 45.0616 | 0.011541 | 312.823 | 43.3939 | 0.0086967 | 345.539 | 345.427 | 775750 | 20.8469 | 735510 | 746679 | 685184 | 0 | 0 | 681520 | 722.771 | 0 | 0 | 0 | 0 | 681520 | 722.771 | 670521 | 657110.8125
305 | 1998-01-13 16:00 | 39 | 376 | 5 | 12.91 | 4.16 | 0 | 4.6707 | 239.988 | 73.4719 | 0 | 39 | 111.178 | 9.167 | 0.3654 | 57.091 | 8.5788 | 0.0019073 | 49.9114 | 8.2614 | 0.0014372 | 56.429 | 56.3635 | 126579 | 14.2524 | 105990 | 111192 | 86398 | 0 | 0 | 86298.3 | 640.699 | 0 | 0 | 0 | 373.725 | 85924.6 | 662.532 | 83085.1 | 81423.3906
306 | 1998-01-13 17:00 | 0 | 0 | 0 | 12.19 | 4.16 | 0
307 | 1998-01-13 18:00 | 0 | 0 | 0 | 11.47 | 6.32 | 0
308 | 1998-01-13 19:00 | 0 | 0 | 0 | 10.74 | 6.32 | 0
309 | 1998-01-13 20:00 | 0 | 0 | 0 | 10.24 | 6.32 | 0
310 | 1998-01-13 21:00 | 0 | 0 | 0 | 9.73 | 8.52 | 0
311 | 1998-01-13 22:00 | 0 | 0 | 0 | 9.22 | 8.52 | 0
312 | 1998-01-13 23:00 | 0 | 0 | 0 | 8.8 | 8.52 | 0
313 | 1998-01-14 | 0 | 0 | 0 | 8.38 | 8.52 | 0
314 | 1998-01-14 01:00 | 0 | 0 | 0 | 7.96 | 8.52 | 0
315 | 1998-01-14 02:00 | 0 | 0 | 0 | 7.7 | 8.52 | 0
316 | 1998-01-14 03:00 | 0 | 0 | 0 | 7.45 | 10.38 | 0
317 | 1998-01-14 04:00 | 0 | 0 | 0 | 7.19 | 10.38 | 0
318 | 1998-01-14 05:00 | 0 | 0 | 0 | 6.95 | 10.38 | 0
319 | 1998-01-14 06:00 | 0 | 6 | 0 | 6.71 | 8.57 | 0
320 | 1998-01-14 07:00 | 71 | 521 | 21 | 6.46 | 8.57 | 0 | 5.3207 | 120.418 | 72.7167 | 0 | 71 | 160.194 | 35.2356 | 0.66522 | 17.5206 | 32.9748 | 0.0034722 | 15.448 | 31.7544 | 0.0026164 | 45.7889 | 45.7471 | 102742 | 7.2814 | 83249.6 | 90368.1 | 79649.3 | 0 | 0 | 79558.6 | 663.137 | 0 | 0 | 0 | 145.419 | 79413.2 | 668.328 | 76751.9 | 75216.8438
321 | 1998-01-14 08:00 | 262 | 815 | 46 | 7.25 | 8.57 | 0 | 15.4058 | 130.261 | 59.7298 | 0 | 262 | 409.86 | 63.5862 | 2.4547 | 279.351 | 59.5064 | 0.012813 | 265.61 | 57.3041 | 0.0096548 | 313.236 | 313.126 | 703115 | 12.872 | 666731 | 698001 | 587844 | 0 | 0 | 585011 | 735.258 | 0 | 0 | 0 | 85.071 | 584926 | 735.884 | 574528 | 563037.25
322 | 1998-01-14 09:00 | 407 | 885 | 48 | 8.04 | 2.26 | 0 | 23.9848 | 141.992 | 47.7283 | 0 | 407 | 594.055 | 64.6749 | 3.8133 | 577.432 | 60.5253 | 0.019904 | 563.381 | 58.2853 | 0.014998 | 603.031 | 602.977 | 1354150 | 24.3233 | 1327030 | 1328480 | 1204070 | 0 | 0 | 1193230 | 733.457 | 0 | 0 | 0 | 0 | 1193230 | 733.457 | 1172670 | 1149218.625
323 | 1998-01-14 10:00 | 541 | 960 | 57 | 8.83 | 2.26 | 0 | 30.3751 | 155.98 | 37.6914 | 0 | 541 | 757.421 | 75.4024 | 5.0687 | 757.421 | 70.5644 | 0.026457 | 747.434 | 67.9529 | 0.019936 | 790.945 | 790.943 | 1776260 | 30.1893 | 1766120 | 1727290 | 1681040 | 0 | 0 | 1660010 | 721.149 | 0 | 0 | 0 | 0 | 1660010 | 721.149 | 1629070 | 1596486.875
324 | 1998-01-14 11:00 | 609 | 985 | 63 | 9.89 | 2.26 | 0 | 33.8066 | 171.988 | 31.5705 | 0 | 609 | 836.084 | 82.6343 | 5.7059 | 836.084 | 77.3323 | 0.029783 | 828.822 | 74.4703 | 0.022442 | 876.215 | 876.21 | 1967740 | 33.5519 | 1967200 | 1896490 | 1846640 | 0 | 0 | 1820700 | 712.895 | 0 | 0 | 0 | 0 | 1820700 | 712.895 | 1784870 | 1749170.125
325 | 1998-01-14 12:00 | 591 | 967 | 56 | 10.94 | 1.67 | 0 | 33.727 | 188.816 | 31.7284 | 0 | 591 | 819.551 | 73.8405 | 5.5372 | 819.551 | 69.1028 | 0.028902 | 812.351 | 66.5453 | 0.021778 | 852.55 | 852.548 | 1914610 | 34.8888 | 1911340 | 1831730 | 1786590 | 0 | 0 | 1761840 | 705.878 | 0 | 0 | 0 | 0 | 1761840 | 705.878 | 1728070 | 1693510.125
326 | 1998-01-14 13:00 | 543 | 964 | 60 | 12 | 1.67 | 0 | 30.1504 | 204.755 | 38.0873 | 0 | 543 | 756.873 | 79.1862 | 5.0875 | 756.873 | 74.1055 | 0.026555 | 746.635 | 71.3629 | 0.02001 | 793.478 | 793.473 | 1781940 | 34.2894 | 1772080 | 1702390 | 1660030 | 0 | 0 | 1638660 | 706.458 | 0 | 0 | 0 | 0 | 1638660 | 706.458 | 1608790 | 1576614.125
327 | 1998-01-14 14:00 | 420 | 915 | 54 | 12.41 | 1.67 | 0 | 23.6472 | 218.646 | 48.2502 | 0 | 420 | 607.603 | 72.3308 | 3.9351 | 607.603 | 67.6899 | 0.02054 | 592.359 | 65.1848 | 0.015477 | 637.833 | 637.829 | 1432410 | 30.3272 | 1406930 | 1374690 | 1338230 | 0 | 0 | 1324550 | 713.815 | 0 | 0 | 0 | 0 | 1324550 | 713.815 | 1302350 | 1276301
328 | 1998-01-14 15:00 | 250 | 805 | 42 | 12.82 | 2.58 | 0 | 14.9885 | 230.289 | 60.3154 | 0 | 250 | 398.286 | 58.53 | 2.3423 | 336.996 | 54.7746 | 0.012226 | 319.822 | 52.7475 | 0.0092126 | 361.401 | 361.306 | 811404 | 22.3713 | 771479 | 777644 | 713834 | 0 | 0 | 709835 | 719.534 | 0 | 0 | 0 | 0 | 709835 | 719.534 | 698494 | 684524.5
329 | 1998-01-14 16:00 | 43 | 390 | 8 | 13.24 | 2.58 | 0 | 4.8498 | 240.07 | 73.3376 | 0 | 43 | 115.352 | 14.5094 | 0.40288 | 63.6439 | 13.5785 | 0.0021029 | 55.728 | 13.076 | 0.0015846 | 66.7413 | 66.692 | 149772 | 15.003 | 126995 | 132647 | 105318 | 0 | 0 | 105184 | 658.567 | 0 | 0 | 0 | 103.952 | 105080 | 663.966 | 101714 | 99679.8438
330 | 1998-01-14 17:00 | 0 | 0 | 0 | 12.78 | 2.58 | 0
331 | 1998-01-14 18:00 | 0 | 0 | 0 | 12.33 | 5.38 | 0
332 | 1998-01-14 19:00 | 0 | 0 | 0 | 11.88 | 5.38 | 0
333 | 1998-01-14 20:00 | 0 | 0 | 0 | 11.55 | 5.38 | 0
334 | 1998-01-14 21:00 | 0 | 0 | 0 | 11.22 | 6.64 | 0
335 | 1998-01-14 22:00 | 0 | 0 | 0 | 10.89 | 6.64 | 0
336 | 1998-01-14 23:00 | 0 | 0 | 0 | 10.59 | 6.64 | 0
337 | 1998-01-15 | 0 | 0 | 0 | 10.3 | 7.93 | 0
338 | 1998-01-15 01:00 | 0 | 0 | 0 | 10 | 7.93 | 0
339 | 1998-01-15 02:00 | 0 | 0 | 0 | 9.8 | 7.93 | 0
340 | 1998-01-15 03:00 | 0 | 0 | 0 | 9.59 | 11.31 | 0
341 | 1998-01-15 04:00 | 0 | 0 | 0 | 9.39 | 11.31 | 0
342 | 1998-01-15 05:00 | 0 | 0 | 0 | 9.29 | 11.31 | 0
343 | 1998-01-15 06:00 | 0 | 7 | 0 | 9.18 | 11.02 | 0
344 | 1998-01-15 07:00 | 73 | 530 | 22 | 9.08 | 11.02 | 0 | 5.3752 | 120.225 | 72.7399 | 0 | 73 | 161.535 | 36.5506 | 0.68395 | 17.4721 | 34.2055 | 0.00357 | 15.4014 | 32.9396 | 0.0026901 | 46.8933 | 46.9005 | 105335 | 9.8043 | 85535.2 | 91827.1 | 81119.3 | 0 | 0 | 81028.1 | 667.896 | 0 | 0 | 0 | 9.2434 | 81018.8 | 669.537 | 78301.3 | 76735.3047
345 | 1998-01-15 08:00 | 256 | 807 | 41 | 10.03 | 11.02 | 0 | 15.4844 | 130.07 | 59.7258 | 0 | 256 | 405.991 | 57.0612 | 2.3985 | 289.792 | 53.4 | 0.012519 | 275.54 | 51.4237 | 0.0094337 | 317.164 | 317.162 | 712181 | 14.9283 | 675289 | 701974 | 598548 | 0 | 0 | 595618 | 731.863 | 0 | 0 | 0 | 483.721 | 595134 | 734.419 | 584596 | 572903.625
346 | 1998-01-15 09:00 | 405 | 838 | 64 | 10.98 | 10.01 | 0 | 24.0928 | 141.807 | 47.6868 | 0 | 405 | 562.338 | 89.7968 | 3.7945 | 547.118 | 84.0353 | 0.019806 | 533.838 | 80.9252 | 0.014924 | 596.334 | 596.309 | 1339180 | 20.7735 | 1311280 | 1333540 | 1212410 | 0 | 0 | 1201770 | 744.802 | 0 | 0 | 0 | 0 | 1201770 | 744.802 | 1180500 | 1156890.875
347 | 1998-01-15 10:00 | 542 | 801 | 136 | 11.92 | 10.01 | 0 | 30.5159 | 155.814 | 37.5968 | 0 | 542 | 633.513 | 179.414 | 5.0781 | 633.513 | 167.902 | 0.026506 | 625.211 | 161.688 | 0.019973 | 763.312 | 763.315 | 1714210 | 24.4563 | 1701100 | 1704720 | 1655380 | 0 | 0 | 1635970 | 740.252 | 0 | 0 | 0 | 0 | 1635970 | 740.252 | 1605110 | 1573011.125
348 | 1998-01-15 11:00 | 501 | 563 | 187 | 12.8 | 10.01 | 0 | 33.9782 | 171.862 | 31.412 | 0 | 501 | 479.499 | 233.301 | 4.694 | 479.499 | 218.332 | 0.024501 | 475.382 | 210.252 | 0.018462 | 665.082 | 665.067 | 1493570 | 23.7227 | 1470600 | 1478350 | 1440960 | 0 | 0 | 1426040 | 735.837 | 0 | 0 | 0 | 0 | 1426040 | 735.837 | 1400750 | 1372734.25
349 | 1998-01-15 12:00 | 516 | 560 | 205 | 13.67 | 8.9 | 0 | 33.9199 | 188.748 | 31.5299 | 0 | 516 | 475.036 | 253.753 | 4.8345 | 475.036 | 237.472 | 0.025234 | 470.922 | 228.683 | 0.019015 | 678.635 | 678.617 | 1524010 | 25.6061 | 1502320 | 1498270 | 1457830 | 0 | 0 | 1442450 | 732.792 | 0 | 0 | 0 | 0 | 1442450 | 732.792 | 1416940 | 1388605.125
350 | 1998-01-15 13:00 | 216 | 29 | 201 | 14.54 | 8.9 | 0 | 30.3516 | 204.745 | 37.8921 | 0 | 216 | 23.4265 | 208.984 | 2.0238 | 23.4265 | 195.576 | 0.010563 | 23.1136 | 188.337 | 0.0079597 | 205.115 | 205.104 | 460611 | 18.1475 | 419978 | 433396 | 420855 | 0 | 0 | 419491 | 715.457 | 0 | 0 | 0 | 0 | 419491 | 715.457 | 411972 | 403732.125
351 | 1998-01-15 14:00 | 135 | 0 | 135 | 14.16 | 8.9 | 0 | 23.8461 | 218.682 | 48.0759 | 0 | 135 | 0 | 130.318 | 1.2648 | 0 | 121.957 | 0.0066021 | 0 | 117.443 | 0.0049748 | 113.925 | 113.918 | 255830 | 16.1637 | 222542 | 232220 | 225688 | 0 | 0 | 225271 | 695.048 | 0 | 0 | 0 | 0 | 225271 | 695.048 | 219078 | 214696.0625
352 | 1998-01-15 15:00 | 124 | 77 | 104 | 13.77 | 9.69 | 0 | 15.1796 | 230.356 | 60.1626 | 0 | 124 | 38.0026 | 105.202 | 1.1618 | 32.1547 | 98.4521 | 0.0060641 | 30.531 | 94.8084 | 0.0045694 | 121.584 | 121.571 | 273019 | 15.8063 | 238916 | 249628 | 240068 | 0 | 0 | 239600 | 698.425 | 0 | 0 | 0 | 0 | 239600 | 698.425 | 233157 | 228493.7969
353 | 1998-01-15 16:00 | 22 | 38 | 18 | 13.39 | 9.69 | 0 | 5.0314 | 240.159 | 73.2037 | 0 | 22 | 13.1796 | 24.2116 | 0.20612 | 7.2717 | 22.6582 | 0.0010759 | 6.3771 | 21.8196 | 0.00081071 | 27.3516 | 27.3458 | 61411.6 | 13.848 | 45417.1 | 48129 | 44931.4 | 0 | 0 | 44910.8 | 631.927 | 0 | 0 | 0 | 811.65 | 44099.2 | 660 | 42540.1 | 41689.3398
354 | 1998-01-15 17:00 | 0 | 0 | 0 | 12.68 | 9.69 | 0
355 | 1998-01-15 18:00 | 0 | 0 | 0 | 11.98 | 10.6 | 0
356 | 1998-01-15 19:00 | 0 | 0 | 0 | 11.28 | 10.6 | 0
357 | 1998-01-15 20:00 | 0 | 0 | 0 | 11.36 | 10.6 | 0
358 | 1998-01-15 21:00 | 0 | 0 | 0 | 11.44 | 10.96 | 0
359 | 1998-01-15 22:00 | 0 | 0 | 0 | 11.51 | 10.96 | 0
360 | 1998-01-15 23:00 | 0 | 0 | 0 | 11.23 | 10.96 | 0
361 | 1998-01-16 | 0 | 0 | 0 | 10.96 | 10.33 | 0
362 | 1998-01-16 01:00 | 0 | 0 | 0 | 10.68 | 10.33 | 0
363 | 1998-01-16 02:00 | 0 | 0 | 0 | 10.31 | 10.33 | 0
364 | 1998-01-16 03:00 | 0 | 0 | 0 | 9.95 | 12.92 | 0
365 | 1998-01-16 04:00 | 0 | 0 | 0 | 9.59 | 12.92 | 0
366 | 1998-01-16 05:00 | 0 | 0 | 0 | 9.32 | 12.92 | 0
367 | 1998-01-16 06:00 | 0 | 2 | 0 | 9.05 | 9.28 | 0
368 | 1998-01-16 07:00 | 45 | 114 | 34 | 8.78 | 9.28 | 0 | 5.4358 | 120.028 | 72.7589 | 0 | 45 | 34.4166 | 46.1894 | 0.42162 | 3.7176 | 43.2258 | 0.0022007 | 3.2763 | 41.626 | 0.0016583 | 43.5569 | 43.5441 | 97790.9 | 9.528 | 77120 | 83362 | 79617.4 | 0 | 0 | 79560.3 | 671.204 | 0 | 0 | 0 | 0 | 79560.3 | 671.204 | 76834.5 | 75297.8047
369 | 1998-01-16 08:00 | 207 | 442 | 88 | 9.72 | 9.28 | 0 | 15.5694 | 129.876 | 59.7172 | 0 | 207 | 223.572 | 113.877 | 1.9394 | 160.054 | 106.571 | 0.010123 | 152.186 | 102.627 | 0.007628 | 247.176 | 247.155 | 555002 | 13.9659 | 514933 | 539582 | 478568 | 0 | 0 | 476802 | 730.034 | 0 | 0 | 0 | 0 | 476802 | 730.034 | 467969 | 458609.4375
370 | 1998-01-16 09:00 | 341 | 541 | 120 | 10.67 | 9.13 | 0 | 24.2075 | 141.62 | 47.64 | 0 | 341 | 363.15 | 152.239 | 3.1949 | 353.663 | 142.471 | 0.016676 | 345.102 | 137.198 | 0.012566 | 467.844 | 467.821 | 1050620 | 18.7817 | 1013200 | 1039870 | 958188 | 0 | 0 | 951592 | 744.246 | 0 | 0 | 0 | 0 | 951592 | 744.246 | 935209 | 916505
371 | 1998-01-16 10:00 | 458 | 582 | 162 | 11.61 | 9.13 | 0 | 30.6635 | 155.647 | 37.4961 | 0 | 458 | 460.484 | 202.893 | 4.2911 | 460.484 | 189.875 | 0.022398 | 454.488 | 182.848 | 0.016877 | 618.233 | 618.221 | 1388370 | 22.3295 | 1361170 | 1376420 | 1337440 | 0 | 0 | 1324730 | 740.558 | 0 | 0 | 0 | 0 | 1324730 | 740.558 | 1301300 | 1275274.75
372 | 1998-01-16 11:00 | 403 | 255 | 260 | 12.74 | 9.13 | 0 | 34.1565 | 171.737 | 31.2468 | 0 | 403 | 217.749 | 289.355 | 3.7758 | 217.749 | 270.789 | 0.019708 | 215.902 | 260.767 | 0.014851 | 462.384 | 462.368 | 1038360 | 20.7571 | 1000100 | 1018430 | 989910 | 0 | 0 | 982850 | 737.459 | 0 | 0 | 0 | 0 | 982850 | 737.459 | 966266 | 946940.75
373 | 1998-01-16 12:00 | 613 | 823 | 153 | 13.87 | 8.54 | 0 | 34.1191 | 188.683 | 31.3256 | 0 | 613 | 700.541 | 200.587 | 5.7433 | 700.541 | 187.717 | 0.029978 | 694.564 | 180.77 | 0.022589 | 849.096 | 849.09 | 1906850 | 29.1435 | 1903190 | 1870020 | 1818240 | 0 | 0 | 1794090 | 727.315 | 0 | 0 | 0 | 0 | 1794090 | 727.315 | 1758870 | 1723690
374 | 1998-01-16 13:00 | 515 | 874 | 72 | 15 | 8.54 | 0 | 30.558 | 204.741 | 37.6933 | 0 | 515 | 689.489 | 93.8689 | 4.8251 | 689.489 | 87.8461 | 0.025186 | 680.396 | 84.5949 | 0.018978 | 742.06 | 742.057 | 1666470 | 28.3482 | 1651130 | 1627650 | 1582610 | 0 | 0 | 1564210 | 726.592 | 0 | 0 | 0 | 0 | 1564210 | 726.592 | 1535910 | 1505189
375 | 1998-01-16 14:00 | 425 | 917 | 52 | 15.25 | 8.54 | 0 | 24.0491 | 218.725 | 47.8998 | 0 | 425 | 613.639 | 69.6042 | 3.9819 | 613.639 | 65.1383 | 0.020784 | 598.556 | 62.7275 | 0.015661 | 641.46 | 641.456 | 1440550 | 26.7886 | 1415400 | 1404470 | 1367330 | 0 | 0 | 1353530 | 726.17 | 0 | 0 | 0 | 0 | 1353530 | 726.17 | 1330170 | 1303568.5
376 | 1998-01-16 15:00 | 255 | 809 | 41 | 15.51 | 7.36 | 0 | 15.3738 | 230.43 | 60.0094 | 0 | 255 | 403.483 | 56.9862 | 2.3891 | 356.916 | 53.3299 | 0.012471 | 339.06 | 51.3562 | 0.0093968 | 378.713 | 378.677 | 850416 | 22.8469 | 809890 | 816381 | 764035 | 0 | 0 | 759566 | 721.907 | 0 | 0 | 0 | 0 | 759566 | 721.907 | 747340 | 732393.625
377 | 1998-01-16 16:00 | 60 | 539 | 9 | 15.76 | 7.36 | 0 | 5.2154 | 240.254 | 73.0702 | 0 | 60 | 163.378 | 16.0688 | 0.56215 | 90.3035 | 15.0378 | 0.0029342 | 79.3133 | 14.4812 | 0.002211 | 90.9829 | 90.9053 | 204149 | 17.5213 | 178654 | 184193 | 144860 | 0 | 0 | 144604 | 663.031 | 0 | 0 | 0 | 34.5455 | 144570 | 665.781 | 140262 | 137457.1406
378 | 1998-01-16 17:00 | 0 | 0 | 0 | 15.06 | 7.36 | 0
379 | 1998-01-16 18:00 | 0 | 0 | 0 | 14.36 | 10.72 | 0
380 | 1998-01-16 19:00 | 0 | 0 | 0 | 13.66 | 10.72 | 0
381 | 1998-01-16 20:00 | 0 | 0 | 0 | 13.04 | 10.72 | 0
382 | 1998-01-16 21:00 | 0 | 0 | 0 | 12.42 | 9.45 | 0
383 | 1998-01-16 22:00 | 0 | 0 | 0 | 11.79 | 9.45 | 0
384 | 1998-01-16 23:00 | 0 | 0 | 0 | 11.38 | 9.45 | 0
385 | 1998-01-17 | 0 | 0 | 0 | 10.97 | 8.88 | 0
386 | 1998-01-17 01:00 | 0 | 0 | 0 | 10.57 | 8.88 | 0
387 | 1998-01-17 02:00 | 0 | 0 | 0 | 10.1 | 8.88 | 0
388 | 1998-01-17 03:00 | 0 | 0 | 0 | 9.63 | 9.92 | 0
389 | 1998-01-17 04:00 | 0 | 0 | 0 | 9.16 | 9.92 | 0
390 | 1998-01-17 05:00 | 0 | 0 | 0 | 9.05 | 9.92 | 0
391 | 1998-01-17 06:00 | 0 | 10 | 0 | 8.94 | 8.69 | 0
392 | 1998-01-17 07:00 | 77 | 546 | 23 | 8.83 | 8.69 | 0 | 5.5026 | 119.828 | 72.7738 | 0 | 77 | 166.772 | 37.6505 | 0.72143 | 17.7645 | 35.2347 | 0.0037656 | 15.6534 | 33.9307 | 0.0028375 | 48.0994 | 48.0422 | 107899 | 9.6861 | 87834.8 | 94299.3 | 83612.1 | 0 | 0 | 83513.5 | 660.585 | 0 | 0 | 0 | 79.2826 | 83434.2 | 664.732 | 80685.9 | 79072.2266
393 | 1998-01-17 08:00 | 266 | 685 | 81 | 10.07 | 8.69 | 0 | 15.6607 | 129.679 | 59.7039 | 0 | 266 | 345.731 | 108.696 | 2.4922 | 248.282 | 101.722 | 0.013008 | 236.088 | 97.9573 | 0.0098022 | 324.034 | 324.098 | 727779 | 15.8456 | 688918 | 714047 | 622026 | 0 | 0 | 619008 | 733.733 | 0 | 0 | 0 | 0 | 619008 | 733.733 | 608224 | 596059.5625
394 | 1998-01-17 09:00 | 325 | 398 | 161 | 11.32 | 3.55 | 0 | 24.3288 | 141.431 | 47.588 | 0 | 325 | 268.491 | 198.805 | 3.045 | 261.743 | 186.05 | 0.015894 | 255.426 | 179.164 | 0.011976 | 421.564 | 421.573 | 946761 | 21.7713 | 906879 | 919208 | 858056 | 0 | 0 | 852604 | 730.806 | 0 | 0 | 0 | 0 | 852604 | 730.806 | 838502 | 821731.4375
395 | 1998-01-17 10:00 | 462 | 572 | 170 | 12.56 | 3.55 | 0 | 30.818 | 155.48 | 37.3895 | 0 | 462 | 452.851 | 211.94 | 4.3286 | 452.851 | 198.342 | 0.022594 | 446.996 | 191.001 | 0.017025 | 618.874 | 618.866 | 1389820 | 27.9024 | 1362670 | 1345550 | 1309250 | 0 | 0 | 1296440 | 721.588 | 0 | 0 | 0 | 0 | 1296440 | 721.588 | 1274470 | 1248977.375
396 | 1998-01-17 11:00 | 618 | 882 | 122 | 14.02 | 3.55 | 0 | 34.3415 | 171.614 | 31.0751 | 0 | 618 | 753.06 | 159.745 | 5.7902 | 753.06 | 149.495 | 0.030223 | 746.751 | 143.962 | 0.022773 | 864.014 | 864.006 | 1940340 | 35.4397 | 1938390 | 1853250 | 1806520 | 0 | 0 | 1781190 | 705.13 | 0 | 0 | 0 | 0 | 1781190 | 705.13 | 1746800 | 1711868
397 | 1998-01-17 12:00 | 609 | 979 | 59 | 15.47 | 5.82 | 0 | 34.3244 | 188.622 | 31.1157 | 0 | 609 | 835.055 | 77.3674 | 5.7059 | 835.055 | 72.4034 | 0.029783 | 828.039 | 69.7238 | 0.022442 | 870.851 | 870.85 | 1955710 | 34.0886 | 1954550 | 1879960 | 1830410 | 0 | 0 | 1804760 | 710.49 | 0 | 0 | 0 | 0 | 1804760 | 710.49 | 1769500 | 1734107.125
398 | 1998-01-17 13:00 | 549 | 964 | 57 | 16.93 | 5.82 | 0 | 30.7697 | 204.742 | 37.491 | 0 | 549 | 763.068 | 75.1465 | 5.1437 | 763.068 | 70.3249 | 0.026848 | 753.136 | 67.7223 | 0.020231 | 796.252 | 796.248 | 1788170 | 33.9537 | 1778610 | 1711310 | 1665590 | 0 | 0 | 1644190 | 708.528 | 0 | 0 | 0 | 0 | 1644190 | 708.528 | 1614090 | 1581811.875
399 | 1998-01-17 14:00 | 424 | 915 | 49 | 17.34 | 5.82 | 0 | 24.2563 | 218.773 | 47.7222 | 0 | 424 | 614.071 | 65.6962 | 3.9726 | 614.071 | 61.481 | 0.020735 | 599.134 | 59.2056 | 0.015624 | 638.605 | 638.603 | 1434140 | 30.9932 | 1408730 | 1372490 | 1337730 | 0 | 0 | 1323960 | 711.175 | 0 | 0 | 0 | 0 | 1323960 | 711.175 | 1301890 | 1275847.375
400 | 1998-01-17 15:00 | 248 | 792 | 35 | 17.75 | 5.71 | 0 | 15.5712 | 230.511 | 59.8558 | 0 | 248 | 398.471 | 49.0209 | 2.3236 | 352.483 | 45.8757 | 0.012128 | 335.012 | 44.1778 | 0.0091389 | 367.823 | 367.773 | 825931 | 25.6689 | 785117 | 781447 | 731507 | 0 | 0 | 727280 | 710.841 | 0 | 0 | 0 | 0 | 727280 | 710.841 | 715977 | 701657.125
401 | 1998-01-17 16:00 | 60 | 528 | 9 | 18.16 | 5.71 | 0 | 5.4017 | 240.356 | 72.9372 | 0 | 60 | 158.961 | 15.879 | 0.56215 | 88.0198 | 14.8602 | 0.0029342 | 77.4218 | 14.3102 | 0.002211 | 88.9822 | 88.874 | 199589 | 20.0736 | 174290 | 177486 | 139392 | 0 | 0 | 139146 | 647.457 | 0 | 0 | 0 | 411.463 | 138735 | 661.114 | 134611 | 131918.8125
402 | 1998-01-17 17:00 | 0 | 5 | 0 | 17.69 | 5.71 | 0
403 | 1998-01-17 18:00 | 0 | 0 | 0 | 17.21 | 7.57 | 0
404 | 1998-01-17 19:00 | 0 | 0 | 0 | 16.74 | 7.57 | 0
405 | 1998-01-17 20:00 | 0 | 0 | 0 | 16.18 | 7.57 | 0
406 | 1998-01-17 21:00 | 0 | 0 | 0 | 15.62 | 3.18 | 0
407 | 1998-01-17 22:00 | 0 | 0 | 0 | 15.06 | 3.18 | 0
408 | 1998-01-17 23:00 | 0 | 0 | 0 | 14.32 | 3.18 | 0
409 | 1998-01-18 | 0 | 0 | 0 | 13.57 | 2.73 | 0
410 | 1998-01-18 01:00 | 0 | 0 | 0 | 12.83 | 2.73 | 0
411 | 1998-01-18 02:00 | 0 | 0 | 0 | 12.27 | 2.73 | 0
412 | 1998-01-18 03:00 | 0 | 0 | 0 | 11.71 | 0.48 | 0
413 | 1998-01-18 04:00 | 0 | 0 | 0 | 11.15 | 0.48 | 0
414 | 1998-01-18 05:00 | 0 | 0 | 0 | 10.53 | 0.48 | 0
415 | 1998-01-18 06:00 | 0 | 3 | 0 | 9.9 | 1.07 | 0
416 | 1998-01-18 07:00 | 52 | 160 | 36 | 9.28 | 1.07 | 0 | 5.5754 | 119.624 | 72.7845 | 0 | 52 | 48.7412 | 54.5651 | 0.4872 | 5.206 | 51.0641 | 0.002543 | 4.5868 | 49.1742 | 0.0019162 | 52.1501 | 52.1352 | 117085 | 10.8047 | 94398.3 | 101303 | 96417.2 | 0 | 0 | 96334 | 675.825 | 0 | 0 | 0 | 0 | 96334 | 675.825 | 93091.3 | 91229.4922
417 | 1998-01-18 08:00 | 265 | 684 | 79 | 9.69 | 1.07 | 0 | 15.7584 | 129.479 | 59.686 | 0 | 265 | 345.683 | 106.521 | 2.4828 | 249.092 | 99.6864 | 0.01296 | 236.871 | 95.9971 | 0.0097653 | 322.892 | 322.775 | 724810 | 19.1298 | 685908 | 699285 | 611143 | 0 | 0 | 608115 | 719.271 | 0 | 0 | 0 | 0 | 608115 | 719.271 | 597958 | 585999.25
418 | 1998-01-18 09:00 | 434 | 920 | 54 | 10.1 | 4.72 | 0 | 24.4568 | 141.24 | 47.5308 | 0 | 434 | 619.733 | 71.939 | 4.0662 | 604.907 | 67.3232 | 0.021224 | 590.357 | 64.8317 | 0.015993 | 635.549 | 635.517 | 1427240 | 24.6918 | 1402720 | 1402690 | 1277990 | 0 | 0 | 1265560 | 723.661 | 0 | 0 | 0 | 0 | 1265560 | 723.661 | 1244210 | 1219324.375
419 | 1998-01-18 10:00 | 557 | 969 | 60 | 10.51 | 4.72 | 0 | 30.9793 | 155.312 | 37.277 | 0 | 557 | 768.311 | 78.8213 | 5.2187 | 768.311 | 73.7639 | 0.02724 | 758.449 | 71.034 | 0.020526 | 804.618 | 804.616 | 1806960 | 28.9844 | 1798320 | 1768000 | 1720370 | 0 | 0 | 1698600 | 725.341 | 0 | 0 | 0 | 0 | 1698600 | 725.341 | 1666370 | 1633042.75
420 | 1998-01-18 11:00 | 622 | 988 | 64 | 11.98 | 4.72 | 0 | 34.5332 | 171.492 | 30.897 | 0 | 622 | 844.645 | 83.5245 | 5.8277 | 844.645 | 78.1654 | 0.030418 | 837.66 | 75.2726 | 0.022921 | 885.567 | 885.564 | 1988750 | 32.313 | 1989290 | 1928260 | 1877340 | 0 | 0 | 1850870 | 717.116 | 0 | 0 | 0 | 0 | 1850870 | 717.116 | 1813970 | 1777690
421 | 1998-01-18 12:00 | 621 | 988 | 63 | 13.44 | 6.79 | 0 | 34.5358 | 188.564 | 30.9001 | 0 | 621 | 844.562 | 82.2761 | 5.8183 | 844.562 | 76.9971 | 0.03037 | 837.577 | 74.1475 | 0.022884 | 884.395 | 884.388 | 1986110 | 31.2075 | 1986520 | 1934820 | 1882510 | 0 | 0 | 1856100 | 719.494 | 0 | 0 | 0 | 0 | 1856100 | 719.494 | 1819000 | 1782621.625
422 | 1998-01-18 13:00 | 557 | 969 | 60 | 14.9 | 6.79 | 0 | 30.9865 | 204.748 | 37.2853 | 0 | 557 | 768.066 | 78.8107 | 5.2187 | 768.066 | 73.7541 | 0.02724 | 758.202 | 71.0245 | 0.020526 | 804.369 | 804.368 | 1806410 | 31.0599 | 1797740 | 1751770 | 1705260 | 0 | 0 | 1683480 | 718.573 | 0 | 0 | 0 | 0 | 1683480 | 718.573 | 1651890 | 1618852.625
423 | 1998-01-18 14:00 | 435 | 922 | 54 | 15.93 | 6.79 | 0 | 24.4675 | 218.828 | 47.543 | 0 | 435 | 620.964 | 71.9207 | 4.0756 | 620.964 | 67.3062 | 0.021273 | 606.018 | 64.8152 | 0.01603 | 650.724 | 650.719 | 1461350 | 29.0031 | 1437040 | 1412370 | 1374750 | 0 | 0 | 1360550 | 720.078 | 0 | 0 | 0 | 0 | 1360550 | 720.078 | 1337300 | 1310555.625
424 | 1998-01-18 15:00 | 262 | 815 | 41 | 16.96 | 10.36 | 0 | 15.7715 | 230.598 | 59.7021 | 0 | 262 | 410.202 | 56.7311 | 2.4547 | 362.86 | 53.0911 | 0.012813 | 345.04 | 51.1262 | 0.0096548 | 384.291 | 384.188 | 862793 | 23.1361 | 822443 | 828169 | 775921 | 0 | 0 | 771290 | 720.207 | 0 | 0 | 0 | 0 | 771290 | 720.207 | 758941 | 743762.5
425 | 1998-01-18 16:00 | 64 | 543 | 10 | 17.98 | 10.36 | 0 | 5.5902 | 240.465 | 72.805 | 0 | 64 | 163.877 | 17.358 | 0.59963 | 90.7419 | 16.2443 | 0.0031299 | 79.9316 | 15.6431 | 0.0023584 | 92.7097 | 92.6114 | 207982 | 19.4688 | 182168 | 186263 | 146826 | 0 | 0 | 146559 | 651.969 | 0 | 0 | 0 | 233.345 | 146325 | 663.196 | 142015 | 139174.9375
426 | 1998-01-18 17:00 | 0 | 9 | 0 | 17.01 | 10.36 | 0
427 | 1998-01-18 18:00 | 0 | 0 | 0 | 16.03 | 12.63 | 0
428 | 1998-01-18 19:00 | 0 | 0 | 0 | 15.05 | 12.63 | 0
429 | 1998-01-18 20:00 | 0 | 0 | 0 | 14.15 | 12.63 | 0
430 | 1998-01-18 21:00 | 0 | 0 | 0 | 13.25 | 13.03 | 0
431 | 1998-01-18 22:00 | 0 | 0 | 0 | 12.35 | 13.03 | 0
432 | 1998-01-18 23:00 | 0 | 0 | 0 | 11.74 | 13.03 | 0
433 | 1998-01-19 | 0 | 0 | 0 | 11.13 | 14.31 | 0
434 | 1998-01-19 01:00 | 0 | 0 | 0 | 10.52 | 14.31 | 0
435 | 1998-01-19 02:00 | 0 | 0 | 0 | 9.86 | 14.31 | 0
436 | 1998-01-19 03:00 | 0 | 0 | 0 | 9.2 | 12.84 | 0
437 | 1998-01-19 04:00 | 0 | 0 | 0 | 8.54 | 12.84 | 0
438 | 1998-01-19 05:00 | 0 | 0 | 0 | 8.17 | 12.84 | 0
439 | 1998-01-19 06:00 | 0 | 10 | 0 | 7.79 | 9.87 | 0
440 | 1998-01-19 07:00 | 77 | 421 | 34 | 7.42 | 9.87 | 0 | 5.6543 | 119.417 | 72.7911 | 0 | 77 | 129.123 | 52.334 | 0.72143 | 14.4094 | 48.9762 | 0.0037656 | 12.6947 | 47.1636 | 0.0028375 | 58.0653 | 58.0459 | 130364 | 8.3815 | 107187 | 116054 | 106174 | 0 | 0 | 106057 | 681.118 | 0 | 0 | 0 | 0 | 106057 | 681.118 | 102522 | 100471.2969
441 | 1998-01-19 08:00 | 215 | 462 | 89 | 7.72 | 9.87 | 0 | 15.8624 | 129.277 | 59.6635 | 0 | 215 | 232.833 | 114.524 | 2.0144 | 175.466 | 107.176 | 0.010514 | 166.869 | 103.21 | 0.0079228 | 261.984 | 261.929 | 588187 | 12.0589 | 547732 | 578601 | 517558 | 0 | 0 | 515542 | 737.74 | 0 | 0 | 0 | 0 | 515542 | 737.74 | 506137 | 496014.625
442 | 1998-01-19 09:00 | 290 | 262 | 181 | 8.02 | 10.2 | 0 | 24.5913 | 141.047 | 47.4684 | 0 | 290 | 177.064 | 211.134 | 2.7171 | 173.033 | 197.587 | 0.014182 | 168.886 | 190.275 | 0.010687 | 348.396 | 348.383 | 782388 | 13.6755 | 740152 | 777065 | 731658 | 0 | 0 | 727901 | 749.854 | 0 | 0 | 0 | 0 | 727901 | 749.854 | 715200 | 700896.375
443 | 1998-01-19 10:00 | 273 | 70 | 237 | 8.32 | 10.2 | 0 | 31.1472 | 155.144 | 37.1585 | 0 | 273 | 55.4692 | 253.433 | 2.5578 | 55.4692 | 237.172 | 0.013351 | 54.7626 | 228.394 | 0.01006 | 274.672 | 274.666 | 616830 | 12.7788 | 574203 | 605885 | 588253 | 0 | 0 | 585792 | 743.653 | 0 | 0 | 0 | 0 | 585792 | 743.653 | 575611 | 564098.8125
444 | 1998-01-19 11:00 | 343 | 126 | 271 | 8.71 | 10.2 | 0 | 34.7315 | 171.372 | 30.7124 | 0 | 343 | 108.65 | 301.544 | 3.2136 | 108.65 | 282.196 | 0.016774 | 107.764 | 271.753 | 0.01264 | 368.143 | 368.127 | 826719 | 14.686 | 784768 | 820360 | 796335 | 0 | 0 | 791886 | 748.104 | 0 | 0 | 0 | 0 | 791886 | 748.104 | 778132 | 762569.25
445 | 1998-01-19 12:00 | 327 | 81 | 281 | 9.09 | 9.57 | 0 | 34.7531 | 188.511 | 30.679 | 0 | 327 | 69.4016 | 306.059 | 3.0637 | 69.4016 | 286.422 | 0.015992 | 68.8369 | 275.821 | 0.01205 | 334.33 | 334.311 | 750775 | 14.7311 | 708197 | 740466 | 719190 | 0 | 0 | 715515 | 743.995 | 0 | 0 | 0 | 0 | 715515 | 743.995 | 703221 | 689156.5
446 | 1998-01-19 13:00 | 359 | 186 | 263 | 9.48 | 9.57 | 0 | 31.2082 | 204.761 | 37.0763 | 0 | 359 | 147.818 | 294.156 | 3.3636 | 147.818 | 275.282 | 0.017557 | 145.946 | 265.094 | 0.013229 | 398.722 | 398.708 | 895397 | 16.2077 | 854347 | 887168 | 861375 | 0 | 0 | 856152 | 746.253 | 0 | 0 | 0 | 0 | 856152 | 746.253 | 841355 | 824527.5
447 | 1998-01-19 14:00 | 288 | 299 | 163 | 9.39 | 9.57 | 0 | 24.6825 | 218.89 | 47.3626 | 0 | 288 | 202.758 | 189.766 | 2.6983 | 202.758 | 177.591 | 0.014084 | 197.929 | 171.018 | 0.010613 | 357.889 | 357.878 | 803705 | 15.4288 | 761508 | 793670 | 770708 | 0 | 0 | 766508 | 745.217 | 0 | 0 | 0 | 0 | 766508 | 745.217 | 753296 | 738230.125
448 | 1998-01-19 15:00 | 147 | 123 | 113 | 9.3 | 8.57 | 0 | 15.9747 | 230.692 | 59.5483 | 0 | 147 | 62.612 | 126.366 | 1.3773 | 57.7945 | 118.258 | 0.0071889 | 54.9824 | 113.881 | 0.005417 | 163.803 | 163.791 | 367834 | 12.2408 | 329753 | 349686 | 337782 | 0 | 0 | 336925 | 725.903 | 0 | 0 | 0 | 0 | 336925 | 725.903 | 329181 | 322597.375
449 | 1998-01-19 16:00 | 37 | 82 | 29 | 9.21 | 8.57 | 0 | 5.7808 | 240.581 | 72.6735 | 0 | 37 | 23.6545 | 38.2259 | 0.34666 | 13.9777 | 35.7733 | 0.0018094 | 12.3299 | 34.4493 | 0.0013635 | 45.3772 | 45.3649 | 101878 | 10.0245 | 80787.2 | 87100.5 | 80526.1 | 0 | 0 | 80467.5 | 671.837 | 0 | 0 | 0 | 0 | 80467.5 | 671.837 | 77708.1 | 76153.9688
450 | 1998-01-19 17:00 | 0 | 2 | 0 | 8.6 | 8.57 | 0
451 | 1998-01-19 18:00 | 0 | 0 | 0 | 7.99 | 8.9 | 0
452 | 1998-01-19 19:00 | 0 | 0 | 0 | 7.38 | 8.9 | 0
453 | 1998-01-19 20:00 | 0 | 0 | 0 | 7.09 | 8.9 | 0
454 | 1998-01-19 21:00 | 0 | 0 | 0 | 6.81 | 7.94 | 0
455 | 1998-01-19 22:00 | 0 | 0 | 0 | 6.52 | 7.94 | 0
456 | 1998-01-19 23:00 | 0 | 0 | 0 | 6.21 | 7.94 | 0
457 | 1998-01-20 | 0 | 0 | 0 | 5.9 | 6.87 | 0
458 | 1998-01-20 01:00 | 0 | 0 | 0 | 5.59 | 6.87 | 0
459 | 1998-01-20 02:00 | 0 | 0 | 0 | 5.15 | 6.87 | 0
460 | 1998-01-20 03:00 | 0 | 0 | 0 | 4.71 | 6 | 0
461 | 1998-01-20 04:00 | 0 | 0 | 0 | 4.27 | 6 | 0
462 | 1998-01-20 05:00 | 0 | 0 | 0 | 4.12 | 6 | 0
463 | 1998-01-20 06:00 | 0 | 0 | 0 | 3.96 | 5.36 | 0
464 | 1998-01-20 07:00 | 33 | 5 | 32 | 3.81 | 5.36 | 0 | 5.7392 | 119.206 | 72.7934 | 0 | 33 | 2.9582 | 27.2639 | 0.30918 | 0.33197 | 25.5146 | 0.0016138 | 0.29246 | 24.5703 | 0.0012161 | 24.1181 | 24.1166 | 54159.9 | 4.3412 | 39150.8 | 43445.5 | 42239.3 | 0 | 0 | 42223 | 659.076 | 0 | 0 | 0 | 0.81217 | 42222.2 | 660.255 | 40723.7 | 39909.2656
465 | 1998-01-20 08:00 | 151 | 120 | 118 | 4.65 | 5.36 | 0 | 15.9727 | 129.072 | 59.6364 | 0 | 151 | 60.6188 | 132.466 | 1.4147 | 45.8559 | 123.966 | 0.0073845 | 43.6129 | 119.379 | 0.0055644 | 158.107 | 158.087 | 355015 | 8.1319 | 317571 | 342812 | 323223 | 0 | 0 | 322467 | 738.198 | 0 | 0 | 0 | 0 | 322467 | 738.198 | 314506 | 308216.1562
466 | 1998-01-20 09:00 | 170 | 17 | 163 | 5.48 | 3.53 | 0 | 24.7323 | 140.852 | 47.4009 | 0 | 170 | 11.3248 | 159.858 | 1.5928 | 11.0807 | 149.601 | 0.0083137 | 10.8162 | 144.064 | 0.0062645 | 150.24 | 150.234 | 337388 | 9.2094 | 300360 | 322965 | 313128 | 0 | 0 | 312405 | 732.249 | 0 | 0 | 0 | 0 | 312405 | 732.249 | 304574 | 298482.625
467 | 1998-01-20 10:00 | 238 | 21 | 227 | 6.32 | 3.53 | 0 | 31.3219 | 154.975 | 37.0343 | 0 | 238 | 16.8916 | 225.126 | 2.2299 | 16.8916 | 210.682 | 0.011639 | 16.6782 | 202.884 | 0.0087704 | 212.984 | 212.978 | 478293 | 11.6069 | 437307 | 464360 | 450674 | 0 | 0 | 449201 | 737.665 | 0 | 0 | 0 | 0 | 449201 | 737.665 | 440621 | 431808.25
468 | 1998-01-20 11:00 | 340 | 128 | 267 | 7.2 | 3.53 | 0 | 34.9362 | 171.254 | 30.5214 | 0 | 340 | 109.811 | 296.438 | 3.1855 | 109.811 | 277.418 | 0.016627 | 108.928 | 267.151 | 0.012529 | 364.809 | 364.791 | 819226 | 16.2555 | 777195 | 807101 | 783063 | 0 | 0 | 778705 | 742.854 | 0 | 0 | 0 | 0 | 778705 | 742.854 | 765366 | 750058.625
469 | 1998-01-20 12:00 | 258 | 25 | 244 | 8.08 | 1.84 | 0 | 34.9764 | 188.461 | 30.4525 | 0 | 258 | 21.0535 | 241.154 | 2.4173 | 21.0535 | 225.681 | 0.012617 | 20.8851 | 217.329 | 0.0095074 | 231.077 | 231.071 | 518928 | 14.4975 | 477262 | 500278 | 484803 | 0 | 0 | 483079 | 733.007 | 0 | 0 | 0 | 0 | 483079 | 733.007 | 474238 | 464752.9688
470 | 1998-01-20 13:00 | 346 | 209 | 237 | 8.96 | 1.84 | 0 | 31.4348 | 204.779 | 36.8643 | 0 | 346 | 167.213 | 262.558 | 3.2418 | 167.213 | 245.711 | 0.016921 | 165.124 | 236.618 | 0.01275 | 389.702 | 389.7 | 875167 | 19.7831 | 833816 | 852852 | 829960 | 0 | 0 | 824926 | 732.858 | 0 | 0 | 0 | 0 | 824926 | 732.858 | 811197 | 794973.0625
471 | 1998-01-20 14:00 | 155 | 4 | 153 | 9.26 | 1.84 | 0 | 24.9012 | 218.958 | 47.181 | 0 | 155 | 3.2285 | 148.842 | 1.4522 | 3.2285 | 139.292 | 0.0075801 | 3.1524 | 134.137 | 0.0057118 | 133.177 | 133.171 | 299068 | 12.9586 | 263636 | 278987 | 270836 | 0 | 0 | 270270 | 715.106 | 0 | 0 | 0 | 0 | 270270 | 715.106 | 263145 | 257882.1875
472 | 1998-01-20 15:00 | 195 | 258 | 123 | 9.55 | 2.3 | 0 | 16.1806 | 230.793 | 59.3946 | 0 | 195 | 131.544 | 145.936 | 1.827 | 121.423 | 136.572 | 0.0095363 | 115.569 | 131.518 | 0.0071858 | 239.681 | 239.66 | 538217 | 16.0047 | 496388 | 516736 | 497874 | 0 | 0 | 496026 | 727.413 | 0 | 0 | 0 | 0 | 496026 | 727.413 | 487214 | 477469.3438
473 | 1998-01-20 16:00 | 50 | 172 | 32 | 9.85 | 2.3 | 0 | 5.9733 | 240.703 | 72.5429 | 0 | 50 | 51.8897 | 48.5589 | 0.46846 | 32.5919 | 45.4433 | 0.0024452 | 28.7893 | 43.7615 | 0.0018425 | 70.3761 | 70.3718 | 158038 | 11.7453 | 131801 | 140560 | 128050 | 0 | 0 | 127907 | 687.845 | 0 | 0 | 0 | 0 | 127907 | 687.845 | 123701 | 121227.3828
474 | 1998-01-20 17:00 | 0 | 6 | 0 | 9.54 | 2.3 | 0
475 | 1998-01-20 18:00 | 0 | 0 | 0 | 9.23 | 5.42 | 0
476 | 1998-01-20 19:00 | 0 | 0 | 0 | 8.93 | 5.42 | 0
477 | 1998-01-20 20:00 | 0 | 0 | 0 | 8.37 | 5.42 | 0
478 | 1998-01-20 21:00 | 0 | 0 | 0 | 7.82 | 4.8 | 0
479 | 1998-01-20 22:00 | 0 | 0 | 0 | 7.27 | 4.8 | 0
480 | 1998-01-20 23:00 | 0 | 0 | 0 | 6.64 | 4.8 | 0
481 | 1998-01-21 | 0 | 0 | 0 | 6.01 | 4.78 | 0
482 | 1998-01-21 01:00 | 0 | 0 | 0 | 5.38 | 4.78 | 0
483 | 1998-01-21 02:00 | 0 | 0 | 0 | 4.84 | 4.78 | 0
484 | 1998-01-21 03:00 | 0 | 0 | 0 | 4.3 | 5.09 | 0
485 | 1998-01-21 04:00 | 0 | 0 | 0 | 3.75 | 5.09 | 0
486 | 1998-01-21 05:00 | 0 | 0 | 0 | 3.34 | 5.09 | 0
487 | 1998-01-21 06:00 | 0 | 17 | 0 | 2.92 | 5.74 | 0
488 | 1998-01-21 07:00 | 83 | 558 | 25 | 2.5 | 5.74 | 0 | 5.8301 | 118.993 | 72.7916 | 0 | 83 | 168.923 | 39.6751 | 0.77765 | 19.9489 | 37.1295 | 0.004059 | 17.5749 | 35.7554 | 0.0030586 | 51.7333 | 51.7034 | 116118 | 3.6111 | 95200.2 | 104980 | 92987.4 | 0 | 0 | 92879.5 | 691.33 | 0 | 0 | 0 | 0 | 92879.5 | 691.33 | 89650.3 | 87857.2812
489 | 1998-01-21 08:00 | 274 | 825 | 45 | 3.59 | 5.74 | 0 | 16.0892 | 128.864 | 59.6047 | 0 | 274 | 418.085 | 61.5368 | 2.5672 | 317.418 | 57.5884 | 0.0134 | 301.921 | 55.4571 | 0.010097 | 346.667 | 346.725 | 778596 | 11.0413 | 741472 | 782341 | 678792 | 0 | 0 | 675178 | 739.417 | 0 | 0 | 0 | 482.378 | 674696 | 743.952 | 662673 | 649419.3125
490 | 1998-01-21 09:00 | 444 | 926 | 55 | 4.67 | 4.72 | 0 | 24.8798 | 140.656 | 47.3283 | 0 | 444 | 626.701 | 72.8882 | 4.1599 | 614.026 | 68.2116 | 0.021713 | 599.431 | 65.6871 | 0.016362 | 645.18 | 645.136 | 1448840 | 19.4827 | 1425030 | 1456510 | 1358640 | 0 | 0 | 1345050 | 730.69 | 0 | 0 | 0 | 1018.01 | 1344030 | 731.626 | 1320670 | 1294253.5
491 | 1998-01-21 10:00 | 565 | 970 | 60 | 5.75 | 4.72 | 0 | 31.503 | 154.806 | 36.9044 | 0 | 565 | 772.792 | 78.5279 | 5.2936 | 772.792 | 73.4894 | 0.027631 | 763.11 | 70.7696 | 0.02082 | 808.883 | 808.877 | 1816540 | 24.3222 | 1808360 | 1813110 | 1763400 | 0 | 0 | 1741480 | 741.063 | 0 | 0 | 0 | 0 | 1741480 | 741.063 | 1707480 | 1673333.25
492 | 1998-01-21 11:00 | 616 | 971 | 59 | 6.99 | 4.72 | 0 | 35.1474 | 171.137 | 30.3242 | 0 | 616 | 835.171 | 77.0011 | 5.7714 | 835.171 | 72.0605 | 0.030125 | 828.552 | 69.3936 | 0.0227 | 871.029 | 871.025 | 1956100 | 26.9892 | 1954950 | 1938410 | 1885850 | 0 | 0 | 1860410 | 734.87 | 0 | 0 | 0 | 0 | 1860410 | 734.87 | 1822970 | 1786509.25
493 | 1998-01-21 12:00 | 626 | 985 | 60 | 8.22 | 2.54 | 0 | 35.2054 | 188.416 | 30.2206 | 0 | 626 | 848.342 | 78.2425 | 5.8651 | 848.342 | 73.2223 | 0.030614 | 841.671 | 70.5124 | 0.023068 | 884.84 | 884.836 | 1987120 | 31.6735 | 1987580 | 1931860 | 1882350 | 0 | 0 | 1855780 | 717.543 | 0 | 0 | 0 | 0 | 1855780 | 717.543 | 1818720 | 1782343
494 | 1998-01-21 13:00 | 569 | 972 | 60 | 9.46 | 2.54 | 0 | 31.6661 | 204.802 | 36.6493 | 0 | 569 | 777.9 | 78.5042 | 5.3311 | 777.9 | 73.4673 | 0.027827 | 768.316 | 70.7483 | 0.020968 | 813.912 | 813.908 | 1827830 | 31.0334 | 1820220 | 1773820 | 1727250 | 0 | 0 | 1704950 | 718.914 | 0 | 0 | 0 | 0 | 1704950 | 718.914 | 1672690 | 1639241
495 | 1998-01-21 14:00 | 447 | 927 | 54 | 10.01 | 2.54 | 0 | 25.1235 | 219.033 | 46.9985 | 0 | 447 | 631.303 | 71.591 | 4.188 | 631.303 | 66.9976 | 0.02186 | 616.586 | 64.5181 | 0.016472 | 660.687 | 660.684 | 1483730 | 27.5221 | 1460340 | 1444450 | 1405430 | 0 | 0 | 1390820 | 724.977 | 0 | 0 | 0 | 0 | 1390820 | 724.977 | 1366720 | 1339388
496 | 1998-01-21 15:00 | 271 | 819 | 40 | 10.57 | 2.45 | 0 | 16.3891 | 230.9 | 59.2411 | 0 | 271 | 418.698 | 55.0514 | 2.5391 | 386.482 | 51.5192 | 0.013253 | 368.022 | 49.6125 | 0.0099864 | 405.115 | 405.104 | 909763 | 21.3722 | 869436 | 882401 | 840430 | 0 | 0 | 835182 | 728.901 | 0 | 0 | 0 | 0 | 835182 | 728.901 | 821447 | 805018.3125
497 | 1998-01-21 16:00 | 70 | 546 | 10 | 11.12 | 2.45 | 0 | 6.1676 | 240.832 | 72.4133 | 0 | 70 | 168.74 | 16.8179 | 0.65585 | 105.986 | 15.7388 | 0.0034233 | 93.7462 | 15.1563 | 0.0025795 | 105.638 | 105.528 | 236988 | 13.9339 | 207969 | 218052 | 179432 | 0 | 0 | 179109 | 685.565 | 0 | 0 | 0 | 0 | 179109 | 685.565 | 173827 | 170350.8281
498 | 1998-01-21 17:00 | 0 | 23 | 0 | 10.81 | 2.45 | 0
499 | 1998-01-21 18:00 | 0 | 0 | 0 | 10.51 | 1.91 | 0
500 | 1998-01-21 19:00 | 0 | 0 | 0 | 10.2 | 1.91 | 0
501 | 1998-01-21 20:00 | 0 | 0 | 0 | 9.87 | 1.91 | 0
502 | 1998-01-21 21:00 | 0 | 0 | 0 | 9.54 | 2.64 | 0
503 | 1998-01-21 22:00 | 0 | 0 | 0 | 9.2 | 2.64 | 0
504 | 1998-01-21 23:00 | 0 | 0 | 0 | 8.61 | 2.64 | 0
505 | 1998-01-22 | 0 | 0 | 0 | 8.01 | 1.9 | 0
506 | 1998-01-22 01:00 | 0 | 0 | 0 | 7.41 | 1.9 | 0
507 | 1998-01-22 02:00 | 0 | 0 | 0 | 6.9 | 1.9 | 0
508 | 1998-01-22 03:00 | 0 | 0 | 0 | 6.39 | 2.08 | 0
509 | 1998-01-22 04:00 | 0 | 0 | 0 | 5.88 | 2.08 | 0
510 | 1998-01-22 05:00 | 0 | 0 | 0 | 5.44 | 2.08 | 0
511 | 1998-01-22 06:00 | 0 | 19 | 0 | 4.99 | 1.78 | 0
512 | 1998-01-22 07:00 | 84 | 561 | 25 | 4.54 | 1.78 | 0 | 5.9271 | 118.777 | 72.7856 | 0 | 84 | 169.091 | 39.4584 | 0.78702 | 20.1363 | 36.9267 | 0.0041079 | 17.7411 | 35.56 | 0.0030954 | 51.7051 | 51.696 | 116104 | 5.9815 | 95211.2 | 103750 | 91467.8 | 0 | 0 | 91359.3 | 680.685 | 0 | 0 | 0 | 0 | 91359.3 | 680.685 | 88263.5 | 86498.2734
513 | 1998-01-22 08:00 | 273 | 823 | 43 | 5.23 | 1.78 | 0 | 16.2119 | 128.654 | 59.5685 | 0 | 273 | 417.266 | 58.8703 | 2.5578 | 318.047 | 55.0931 | 0.013351 | 302.553 | 53.0541 | 0.01006 | 344.949 | 344.73 | 774118 | 14.8427 | 736904 | 764268 | 663871 | 0 | 0 | 660307 | 727.734 | 0 | 0 | 0 | 1193.38 | 659114 | 735.083 | 647606 | 634654.1875
514 | 1998-01-22 09:00 | 443 | 924 | 53 | 5.92 | 0.26 | 0 | 25.0336 | 140.457 | 47.2507 | 0 | 443 | 625.615 | 70.2743 | 4.1506 | 613.747 | 65.7654 | 0.021664 | 599.225 | 63.3315 | 0.016325 | 642.696 | 642.687 | 1443350 | 25.7724 | 1419250 | 1412510 | 1325840 | 0 | 0 | 1312300 | 713.489 | 0 | 0 | 0 | 90.1184 | 1312210 | 714.039 | 1290400 | 1264590.125
515 | 1998-01-22 10:00 | 570 | 973 | 60 | 6.6 | 0.26 | 0 | 31.6907 | 154.637 | 36.7688 | 0 | 570 | 777.675 | 78.4251 | 5.3405 | 777.675 | 73.3932 | 0.027875 | 768.018 | 70.677 | 0.021005 | 813.555 | 813.55 | 1827030 | 31.7303 | 1819370 | 1767590 | 1722660 | 0 | 0 | 1700250 | 716.004 | 0 | 0 | 0 | 0 | 1700250 | 716.004 | 1668210 | 1634849
516 | 1998-01-22 11:00 | 629 | 986 | 60 | 7.99 | 0.26 | 0 | 35.3649 | 171.022 | 30.1207 | 0 | 629 | 850.351 | 78.151 | 5.8932 | 850.351 | 73.1367 | 0.030761 | 843.714 | 70.4299 | 0.023179 | 886.742 | 886.738 | 1991400 | 35.381 | 1992080 | 1905110 | 1855360 | 0 | 0 | 1828760 | 706.417 | 0 | 0 | 0 | 0 | 1828760 | 706.417 | 1792760 | 1756905
517 | 1998-01-22 12:00 | 633 | 988 | 62 | 9.38 | 2.06 | 0 | 35.4401 | 188.375 | 29.9836 | 0 | 633 | 852.947 | 80.6322 | 5.9307 | 852.947 | 75.4586 | 0.030956 | 846.358 | 72.666 | 0.023326 | 891.476 | 891.469 | 2002010 | 33.7774 | 2003240 | 1929410 | 1878540 | 0 | 0 | 1851730 | 712.876 | 0 | 0 | 0 | 0 | 1851730 | 712.876 | 1814860 | 1778562.875
518 | 1998-01-22 13:00 | 573 | 973 | 60 | 10.76 | 2.06 | 0 | 31.9021 | 204.832 | 36.4315 | 0 | 573 | 781.016 | 78.3978 | 5.3686 | 781.016 | 73.3676 | 0.028022 | 771.53 | 70.6523 | 0.021115 | 816.938 | 816.936 | 1834620 | 33.1176 | 1827340 | 1764700 | 1716540 | 0 | 0 | 1694110 | 712.885 | 0 | 0 | 0 | 0 | 1694110 | 712.885 | 1662340 | 1629097.5
519 | 1998-01-22 14:00 | 451 | 929 | 54 | 11.45 | 2.06 | 0 | 25.3494 | 219.114 | 46.815 | 0 | 451 | 634.585 | 71.4774 | 4.2255 | 634.585 | 66.8912 | 0.022056 | 619.951 | 64.4156 | 0.016619 | 663.851 | 663.849 | 1490830 | 29.618 | 1467740 | 1438660 | 1399980 | 0 | 0 | 1385260 | 719.573 | 0 | 0 | 0 | 0 | 1385260 | 719.573 | 1361510 | 1334282
520 | 1998-01-22 15:00 | 275 | 824 | 40 | 12.14 | 0.76 | 0 | 16.6002 | 231.015 | 59.0879 | 0 | 275 | 422.57 | 54.9209 | 2.5765 | 390.057 | 51.397 | 0.013449 | 371.596 | 49.4949 | 0.010134 | 408.468 | 408.422 | 917211 | 24.3368 | 877009 | 878574 | 837465 | 0 | 0 | 832125 | 719.661 | 0 | 0 | 0 | 0 | 832125 | 719.661 | 818825 | 802448.3125
521 | 1998-01-22 16:00 | 73 | 549 | 11 | 12.82 | 0.76 | 0 | 6.3637 | 240.968 | 72.2847 | 0 | 73 | 170.209 | 18.2415 | 0.68395 | 106.908 | 17.0711 | 0.00357 | 94.6864 | 16.4393 | 0.0026901 | 107.795 | 107.694 | 241855 | 16.0361 | 212527 | 220570 | 182314 | 0 | 0 | 181975 | 679.643 | 0 | 0 | 0 | 0 | 181975 | 679.643 | 176736 | 173201.3125
522 | 1998-01-22 17:00 | 0 | 27 | 0 | 12.44 | 0.76 | 0
523 | 1998-01-22 18:00 | 0 | 0 | 0 | 12.05 | 1.82 | 0
524 | 1998-01-22 19:00 | 0 | 0 | 0 | 11.67 | 1.82 | 0
525 | 1998-01-22 20:00 | 0 | 0 | 0 | 11.42 | 1.82 | 0
526 | 1998-01-22 21:00 | 0 | 0 | 0 | 11.17 | 1.62 | 0
527 | 1998-01-22 22:00 | 0 | 0 | 0 | 10.92 | 1.62 | 0
528 | 1998-01-22 23:00 | 0 | 0 | 0 | 10.37 | 1.62 | 0
529 | 1998-01-23 | 0 | 0 | 0 | 9.83 | 4.33 | 0
530 | 1998-01-23 01:00 | 0 | 0 | 0 | 9.28 | 4.33 | 0
531 | 1998-01-23 02:00 | 0 | 0 | 0 | 8.78 | 4.33 | 0
532 | 1998-01-23 03:00 | 0 | 0 | 0 | 8.27 | 3.89 | 0
533 | 1998-01-23 04:00 | 0 | 0 | 0 | 7.76 | 3.89 | 0
534 | 1998-01-23 05:00 | 0 | 0 | 0 | 7.37 | 3.89 | 0
535 | 1998-01-23 06:00 | 0 | 22 | 0 | 6.97 | 4.3 | 0
536 | 1998-01-23 07:00 | 86 | 565 | 25 | 6.58 | 4.3 | 0 | 6.0301 | 118.558 | 72.7753 | 0 | 86 | 171.948 | 39.238 | 0.80575 | 20.7424 | 36.7204 | 0.0042058 | 18.2772 | 35.3614 | 0.0031691 | 52.0326 | 52.0338 | 116863 | 7.808 | 95965.9 | 103766 | 90789.4 | 0 | 0 | 90675.9 | 663.625 | 0 | 0 | 0 | 23.9808 | 90651.9 | 666.531 | 87697.9 | 85943.9375
537 | 1998-01-23 08:00 | 276 | 825 | 44 | 7.06 | 4.3 | 0 | 16.3408 | 128.441 | 59.5277 | 0 | 276 | 418.171 | 60.0197 | 2.5859 | 320.019 | 56.1687 | 0.013498 | 304.468 | 54.0899 | 0.010171 | 347.811 | 347.706 | 780800 | 15.2656 | 743592 | 770715 | 669696 | 0 | 0 | 666111 | 733.463 | 0 | 0 | 0 | 0 | 666111 | 733.463 | 654531 | 641440.5
538 | 1998-01-23 09:00 | 449 | 928 | 55 | 7.54 | 1.78 | 0 | 25.1938 | 140.258 | 47.1681 | 0 | 449 | 629.251 | 72.67 | 4.2068 | 618.211 | 68.0074 | 0.021958 | 603.655 | 65.4904 | 0.016546 | 649.087 | 649.052 | 1457640 | 25.6387 | 1434040 | 1428360 | 1345480 | 0 | 0 | 1331490 | 712.116 | 0 | 0 | 0 | 855.768 | 1330630 | 714.688 | 1308390 | 1282220.875
539 | 1998-01-23 10:00 | 573 | 973 | 60 | 8.03 | 1.78 | 0 | 31.8849 | 154.468 | 36.6276 | 0 | 573 | 779.414 | 78.32 | 5.3686 | 779.414 | 73.2948 | 0.028022 | 769.825 | 70.5823 | 0.021115 | 815.216 | 815.212 | 1830750 | 30.762 | 1823280 | 1778870 | 1729880 | 0 | 0 | 1707550 | 719.954 | 0 | 0 | 0 | 0 | 1707550 | 719.954 | 1675190 | 1641688.75
540 | 1998-01-23 11:00 | 639 | 888 | 124 | 9.52 | 1.78 | 0 | 35.5887 | 170.909 | 29.9112 | 0 | 639 | 767.063 | 161.407 | 5.9869 | 767.063 | 151.05 | 0.03125 | 761.169 | 145.46 | 0.023547 | 879.453 | 879.446 | 1975010 | 34.0431 | 1974850 | 1899780 | 1850100 | 0 | 0 | 1823990 | 710.984 | 0 | 0 | 0 | 0 | 1823990 | 710.984 | 1788080 | 1752318.25
541 | 1998-01-23 12:00 | 549 | 638 | 178 | 11.01 | 1.9 | 0 | 35.6804 | 188.337 | 29.7414 | 0 | 549 | 552.288 | 227.141 | 5.1437 | 552.288 | 212.567 | 0.026848 | 548.099 | 204.7 | 0.020231 | 730.235 | 730.221 | 1639900 | 31.2092 | 1623340 | 1580400 | 1537600 | 0 | 0 | 1519720 | 716.189 | 0 | 0 | 0 | 0 | 1519720 | 716.189 | 1493050 | 1463191.875
542 | 1998-01-23 13:00 | 562 | 851 | 111 | 12.49 | 1.9 | 0 | 32.1426 | 204.867 | 36.2111 | 0 | 562 | 683.962 | 145.436 | 5.2655 | 683.962 | 136.104 | 0.027484 | 675.776 | 131.067 | 0.02071 | 782.657 | 782.649 | 1757630 | 34.1395 | 1746590 | 1678960 | 1635580 | 0 | 0 | 1614800 | 706.63 | 0 | 0 | 0 | 0 | 1614800 | 706.63 | 1585660 | 1553946.875
543 | 1998-01-23 14:00 | 448 | 924 | 50 | 13.19 | 1.9 | 0 | 25.5787 | 219.202 | 46.6308 | 0 | 448 | 633.018 | 66.3344 | 4.1974 | 633.018 | 62.0783 | 0.021909 | 618.577 | 59.7808 | 0.016509 | 658.023 | 658.021 | 1477750 | 31.3921 | 1454120 | 1414250 | 1376000 | 0 | 0 | 1361520 | 712.826 | 0 | 0 | 0 | 0 | 1361520 | 712.826 | 1338570 | 1311796
544 | 1998-01-23 15:00 | 263 | 779 | 38 | 13.89 | 3.23 | 0 | 16.8136 | 231.135 | 58.9352 | 0 | 263 | 401.375 | 52.2075 | 2.4641 | 370.493 | 48.8578 | 0.012862 | 353.117 | 47.0496 | 0.0096916 | 388.171 | 388.148 | 871687 | 23.7181 | 830766 | 834705 | 794910 | 0 | 0 | 790110 | 720.455 | 0 | 0 | 0 | 0 | 790110 | 720.455 | 777450 | 761901.375
545 | 1998-01-23 16:00 | 71 | 519 | 11 | 14.59 | 3.23 | 0 | 6.5614 | 241.11 | 72.1574 | 0 | 71 | 160.886 | 18.0708 | 0.66522 | 101.052 | 16.9114 | 0.0034722 | 89.615 | 16.2855 | 0.0026164 | 102.726 | 102.637 | 230496 | 17.1888 | 201655 | 208427 | 172437 | 0 | 0 | 172125 | 670.117 | 0 | 0 | 0 | -35.7691 | 172161 | 671.266 | 167229 | 163884.875
546 | 1998-01-23 17:00 | 1 | 30 | 1 | 14.21 | 3.23 | 0 | -4.6632 | 249.742 | 85.8617 | 0 | 1 | 0 | 0.92493 | 0.0093692 | 0 | 0.86559 | 0 | 0 | 0.83355 | 0 | 0.80854 | 0.80851 | 1815.7 | 14.2305 | 159.765 | 157.731 | 156.963 | 0 | 0 | 156.956 | 120.631 | 0 | 0 | 0 | 156.956 | 0 | 660 | 0 | 0
547 | 1998-01-23 18:00 | 0 | 0 | 0 | 13.83 | 7.1 | 0
548 | 1998-01-23 19:00 | 0 | 0 | 0 | 13.45 | 7.1 | 0
549 | 1998-01-23 20:00 | 0 | 0 | 0 | 12.73 | 7.1 | 0
550 | 1998-01-23 21:00 | 0 | 0 | 0 | 12.02 | 6.9 | 0
551 | 1998-01-23 22:00 | 0 | 0 | 0 | 11.31 | 6.9 | 0
552 | 1998-01-23 23:00 | 0 | 0 | 0 | 10.58 | 6.9 | 0
553 | 1998-01-24 | 0 | 0 | 0 | 9.85 | 9.17 | 0
554 | 1998-01-24 01:00 | 0 | 0 | 0 | 9.12 | 9.17 | 0
555 | 1998-01-24 02:00 | 0 | 0 | 0 | 9 | 9.17 | 0
556 | 1998-01-24 03:00 | 0 | 0 | 0 | 8.88 | 8.63 | 0
557 | 1998-01-24 04:00 | 0 | 0 | 0 | 8.76 | 8.63 | 0
558 | 1998-01-24 05:00 | 0 | 0 | 0 | 8.09 | 8.63 | 0
559 | 1998-01-24 06:00 | 0 | 24 | 0 | 7.42 | 7.82 | 0
560 | 1998-01-24 07:00 | 88 | 570 | 26 | 6.74 | 7.82 | 0 | 6.139 | 118.336 | 72.7609 | 0 | 88 | 171.817 | 40.387 | 0.82449 | 20.98 | 37.7957 | 0.0043036 | 18.4893 | 36.3969 | 0.0032428 | 53.2428 | 53.2575 | 119608 | 7.7423 | 98415.9 | 106539 | 92377.8 | 0 | 0 | 92266.7 | 674.257 | 0 | 0 | 0 | 70.3634 | 92196.3 | 676.532 | 89110.8 | 87328.5391
561 | 1998-01-24 08:00 | 278 | 827 | 44 | 7.93 | 7.82 | 0 | 16.4758 | 128.226 | 59.4824 | 0 | 278 | 418.977 | 59.8927 | 2.6046 | 321.912 | 56.0499 | 0.013595 | 306.311 | 53.9755 | 0.010244 | 349.488 | 349.427 | 784670 | 14.5061 | 747442 | 778142 | 676072 | 0 | 0 | 672477 | 737.707 | 0 | 0 | 0 | 0 | 672477 | 737.707 | 660718 | 647503.75
562 | 1998-01-24 09:00 | 446 | 922 | 52 | 9.12 | 5.63 | 0 | 25.3603 | 140.057 | 47.0807 | 0 | 446 | 626.42 | 68.8028 | 4.1787 | 616.233 | 64.3883 | 0.021811 | 601.797 | 62.0054 | 0.016435 | 643.905 | 643.925 | 1446120 | 23.0569 | 1421990 | 1432400 | 1351280 | 0 | 0 | 1337440 | 718.542 | 0 | 0 | 0 | 402.365 | 1337040 | 719.933 | 1314430 | 1288143.625
563 | 1998-01-24 10:00 | 557 | 946 | 56 | 10.31 | 5.63 | 0 | 32.0854 | 154.298 | 36.481 | 0 | 557 | 758.367 | 73.2268 | 5.2187 | 758.367 | 68.5284 | 0.02724 | 749.127 | 65.9922 | 0.020526 | 790.685 | 790.685 | 1775680 | 27.4233 | 1765510 | 1747300 | 1702390 | 0 | 0 | 1681260 | 728.745 | 0 | 0 | 0 | 0 | 1681260 | 728.745 | 1649470 | 1616481.25
564 | 1998-01-24 11:00 | 623 | 966 | 59 | 11.81 | 5.63 | 0 | 35.8186 | 170.798 | 29.6956 | 0 | 623 | 837.171 | 76.7011 | 5.837 | 837.171 | 71.7798 | 0.030467 | 830.842 | 69.1233 | 0.022958 | 872.989 | 872.986 | 1960500 | 30.7046 | 1959590 | 1912650 | 1861280 | 0 | 0 | 1835610 | 721.769 | 0 | 0 | 0 | 0 | 1835610 | 721.769 | 1799150 | 1763165.875
565 | 1998-01-24 12:00 | 645 | 993 | 64 | 13.31 | 4.04 | 0 | 35.9262 | 188.305 | 29.4942 | 0 | 645 | 861.887 | 82.8978 | 6.0431 | 861.887 | 77.5789 | 0.031543 | 855.471 | 74.7077 | 0.023768 | 902.296 | 902.292 | 2026320 | 34.9694 | 2028820 | 1944010 | 1894780 | 0 | 0 | 1867150 | 707.729 | 0 | 0 | 0 | 0 | 1867150 | 707.729 | 1829830 | 1793234.625
566 | 1998-01-24 13:00 | 578 | 973 | 58 | 14.81 | 4.04 | 0 | 32.3876 | 204.909 | 35.9881 | 0 | 578 | 785.507 | 75.6899 | 5.4154 | 785.507 | 70.8335 | 0.028267 | 776.243 | 68.212 | 0.021299 | 819.142 | 819.141 | 1839580 | 34.4734 | 1832550 | 1759300 | 1713120 | 0 | 0 | 1690440 | 707.649 | 0 | 0 | 0 | 0 | 1690440 | 707.649 | 1658930 | 1625750.875
567 | 1998-01-24 14:00 | 459 | 932 | 54 | 15.57 | 4.04 | 0 | 25.8112 | 219.297 | 46.4461 | 0 | 459 | 640.918 | 71.245 | 4.3005 | 640.918 | 66.6738 | 0.022447 | 626.456 | 64.2062 | 0.016914 | 669.959 | 669.955 | 1504540 | 31.6522 | 1482030 | 1439840 | 1401050 | 0 | 0 | 1385960 | 711.123 | 0 | 0 | 0 | 0 | 1385960 | 711.123 | 1362560 | 1335306.875
568 | 1998-01-24 15:00 | 273 | 804 | 38 | 16.33 | 0.13 | 0 | 17.0293 | 231.263 | 58.7831 | 0 | 273 | 415.882 | 52.0795 | 2.5578 | 383.883 | 48.738 | 0.013351 | 366.043 | 46.9343 | 0.01006 | 400.598 | 400.559 | 899558 | 28.8126 | 859064 | 843521 | 805056 | 0 | 0 | 799879 | 702.469 | 0 | 0 | 0 | 0 | 799879 | 702.469 | 787782 | 772026.0625
569 | 1998-01-24 16:00 | 69 | 0 | 69 | 17.09 | 0.13 | 0 | 6.7607 | 241.259 | 72.0313 | 0 | 69 | 0 | 79.0433 | 0.64648 | 0 | 73.9718 | 0.0033744 | 0 | 71.2341 | 0.0025427 | 69.0996 | 69.0969 | 155174 | 19.2433 | 128728 | 132541 | 129014 | 0 | 0 | 128863 | 660.639 | 0 | 0 | 0 | -5.9784 | 128869 | 661.221 | 124954 | 122454.8203
570 | 1998-01-24 17:00 | 1 | 0 | 1 | 16.24 | 0.13 | 0 | -4.4778 | 249.908 | 85.7573 | 0 | 1 | 0 | 0.92297 | 0.0093692 | 0 | 0.86375 | 0 | 0 | 0.83178 | 0 | 0.80683 | 0.80676 | 1811.79 | 16.2651 | 159.064 | 157.423 | 156.669 | 0 | 0 | 156.662 | 120.509 | 0 | 0 | 0 | 156.662 | 0 | 660 | 0 | 0
571 | 1998-01-24 18:00 | 0 | 0 | 0 | 15.39 | 5.11 | 0
572 | 1998-01-24 19:00 | 0 | 0 | 0 | 14.54 | 5.11 | 0
573 | 1998-01-24 20:00 | 0 | 0 | 0 | 13.71 | 5.11 | 0
574 | 1998-01-24 21:00 | 0 | 0 | 0 | 12.88 | 6.39 | 0
575 | 1998-01-24 22:00 | 0 | 0 | 0 | 12.04 | 6.39 | 0
576 | 1998-01-24 23:00 | 0 | 0 | 0 | 11.25 | 6.39 | 0
577 | 1998-01-25 | 0 | 0 | 0 | 10.46 | 4.67 | 0
578 | 1998-01-25 01:00 | 0 | 0 | 0 | 9.67 | 4.67 | 0
579 | 1998-01-25 02:00 | 0 | 0 | 0 | 9.11 | 4.67 | 0
580 | 1998-01-25 03:00 | 0 | 0 | 0 | 8.54 | 3.55 | 0
581 | 1998-01-25 04:00 | 0 | 0 | 0 | 7.98 | 3.55 | 0
582 | 1998-01-25 05:00 | 0 | 0 | 0 | 7.72 | 3.55 | 0
583 | 1998-01-25 06:00 | 0 | 27 | 0 | 7.45 | 2.91 | 0
584 | 1998-01-25 07:00 | 90 | 574 | 26 | 7.19 | 2.91 | 0 | 6.2538 | 118.111 | 72.7423 | 0 | 90 | 174.298 | 40.1578 | 0.84323 | 21.662 | 37.5812 | 0.0044014 | 19.0942 | 36.1904 | 0.0033165 | 53.6293 | 53.5976 | 120369 | 8.5762 | 99161.1 | 106783 | 92265.4 | 0 | 0 | 92144.5 | 647.718 | 0 | 0 | 0 | 525.787 | 91618.7 | 661.298 | 88678.7 | 86905.1016
585 | 1998-01-25 08:00 | 279 | 826 | 43 | 8.11 | 2.91 | 0 | 16.6168 | 128.009 | 59.4327 | 0 | 279 | 419.689 | 58.495 | 2.614 | 323.818 | 54.7419 | 0.013644 | 308.172 | 52.7159 | 0.010281 | 350.071 | 349.922 | 785785 | 17.1599 | 748466 | 769293 | 672205 | 0 | 0 | 668521 | 723.92 | 0 | 0 | 0 | 653.668 | 667867 | 725.825 | 656563 | 643431.4375
586 | 1998-01-25 09:00 | 445 | 917 | 51 | 9.03 | 1.06 | 0 | 25.533 | 139.854 | 46.9883 | 0 | 445 | 623.543 | 67.4371 | 4.1693 | 614.366 | 63.1103 | 0.021762 | 600.053 | 60.7746 | 0.016398 | 641.019 | 640.992 | 1439520 | 27.7889 | 1415040 | 1396690 | 1324690 | 0 | 0 | 1310900 | 704.546 | 0 | 0 | 0 | 3675.33 | 1307220 | 708.641 | 1285710 | 1260000
587 | 1998-01-25 10:00 | 576 | 971 | 59 | 9.95 | 1.06 | 0 | 32.2922 | 154.128 | 36.3289 | 0 | 576 | 779.637 | 76.8609 | 5.3967 | 779.637 | 71.9294 | 0.028169 | 770.232 | 69.2673 | 0.021226 | 814.335 | 814.332 | 1828780 | 33.7818 | 1821220 | 1753620 | 1707800 | 0 | 0 | 1685390 | 709.287 | 0 | 0 | 0 | 0 | 1685390 | 709.287 | 1653990 | 1620914
588 | 1998-01-25 11:00 | 646 | 994 | 63 | 11.78 | 1.06 | 0 | 36.0546 | 170.688 | 29.474 | 0 | 646 | 862.361 | 81.5613 | 6.0525 | 862.361 | 76.3282 | 0.031592 | 855.951 | 73.5034 | 0.023805 | 901.594 | 901.591 | 2024740 | 38.1655 | 2027160 | 1914950 | 1866240 | 0 | 0 | 1838510 | 696.12 | 0 | 0 | 0 | 0 | 1838510 | 696.12 | 1802340 | 1766292
589 | 1998-01-25 12:00 | 649 | 994 | 64 | 13.6 | 1.48 | 0 | 36.1774 | 188.276 | 29.242 | 0 | 649 | 864.749 | 82.7861 | 6.0806 | 864.749 | 77.4744 | 0.031739 | 858.434 | 74.6071 | 0.023916 | 905.073 | 905.066 | 2032550 | 39.35 | 2035370 | 1912540 | 1863250 | 0 | 0 | 1835550 | 694.843 | 0 | 0 | 0 | 0 | 1835550 | 694.843 | 1799490 | 1763504.625
590 | 1998-01-25 13:00 | 585 | 976 | 60 | 15.43 | 1.48 | 0 | 32.6368 | 204.956 | 35.7628 | 0 | 585 | 789.909 | 78.0664 | 5.481 | 789.909 | 73.0575 | 0.028609 | 780.731 | 70.3537 | 0.021557 | 825.573 | 825.572 | 1854030 | 38.9184 | 1847710 | 1738890 | 1694720 | 0 | 0 | 1671630 | 692.588 | 0 | 0 | 0 | 0 | 1671630 | 692.588 | 1641120 | 1608293.875
591 | 1998-01-25 14:00 | 465 | 933 | 56 | 16.15 | 1.48 | 0 | 26.0468 | 219.398 | 46.2609 | 0 | 465 | 643.974 | 73.6192 | 4.3567 | 643.974 | 68.8957 | 0.02274 | 629.601 | 66.3459 | 0.017135 | 675.085 | 675.08 | 1516060 | 35.3567 | 1494030 | 1427720 | 1391150 | 0 | 0 | 1375720 | 698.355 | 0 | 0 | 0 | 0 | 1375720 | 698.355 | 1353080 | 1326022.875
592 | 1998-01-25 15:00 | 284 | 825 | 39 | 16.87 | 2.67 | 0 | 17.2472 | 231.397 | 58.6316 | 0 | 284 | 430.131 | 53.2403 | 2.6609 | 397.036 | 49.8243 | 0.013889 | 378.751 | 47.9804 | 0.010466 | 413.939 | 413.867 | 929443 | 27.7456 | 889457 | 877770 | 837919 | 0 | 0 | 832396 | 707.87 | 0 | 0 | 0 | 0 | 832396 | 707.87 | 819582 | 803190.75
593 | 1998-01-25 16:00 | 93 | 0 | 93 | 17.59 | 2.67 | 0 | 6.9614 | 241.414 | 71.9066 | 0 | 93 | 0 | 116.984 | 0.87134 | 0 | 109.478 | 0.0045481 | 0 | 105.426 | 0.0034271 | 102.267 | 102.269 | 229669 | 20.2774 | 197882 | 202537 | 196842 | 0 | 0 | 196506 | 675.84 | 0 | 0 | 0 | 0 | 196506 | 675.84 | 191083 | 187261.0938
594 | 1998-01-25 17:00 | 1 | 0 | 1 | 17.07 | 2.67 | 0 | -4.2915 | 250.08 | 85.6547 | 0 | 1 | 0 | 0.92105 | 0.0093692 | 0 | 0.86196 | 0 | 0 | 0.83006 | 0 | 0.80516 | 0.8051 | 1808.04 | 17.0912 | 158.402 | 156.923 | 156.181 | 0 | 0 | 156.174 | 120.257 | 0 | 0 | 0 | 156.174 | 0 | 660 | 0 | 0
595 | 1998-01-25 18:00 | 0 | 0 | 0 | 16.55 | 4.54 | 0
596 | 1998-01-25 19:00 | 0 | 0 | 0 | 16.03 | 4.54 | 0
597 | 1998-01-25 20:00 | 0 | 0 | 0 | 15.44 | 4.54 | 0
598 | 1998-01-25 21:00 | 0 | 0 | 0 | 14.85 | 5.19 | 0
599 | 1998-01-25 22:00 | 0 | 0 | 0 | 14.27 | 5.19 | 0
600 | 1998-01-25 23:00 | 0 | 0 | 0 | 13.71 | 5.19 | 0
601 | 1998-01-26 | 0 | 0 | 0 | 13.15 | 3.99 | 0
602 | 1998-01-26 01:00 | 0 | 0 | 0 | 12.59 | 3.99 | 0
603 | 1998-01-26 02:00 | 0 | 0 | 0 | 11.86 | 3.99 | 0
604 | 1998-01-26 03:00 | 0 | 0 | 0 | 11.12 | 6.29 | 0
605 | 1998-01-26 04:00 | 0 | 0 | 0 | 10.39 | 6.29 | 0
606 | 1998-01-26 05:00 | 0 | 0 | 0 | 9.95 | 6.29 | 0
607 | 1998-01-26 06:00 | 0 | 23 | 0 | 9.52 | 6.32 | 0
608 | 1998-01-26 07:00 | 78 | 438 | 28 | 9.08 | 6.32 | 0 | 6.3745 | 117.883 | 72.7195 | 0 | 78 | 133.774 | 42.8155 | 0.7308 | 16.9844 | 40.0683 | 0.0038145 | 14.9748 | 38.5854 | 0.0028743 | 51.9562 | 51.97 | 116715 | 10.156 | 95208.1 | 102127 | 90168.8 | 0 | 0 | 90072.7 | 661.293 | 0 | 0 | 0 | 106.488 | 89966.3 | 666.624 | 87007.3 | 85267.1875
609 | 1998-01-26 08:00 | 265 | 762 | 45 | 9.75 | 6.32 | 0 | 16.7638 | 127.79 | 59.3786 | 0 | 265 | 388.522 | 60.8944 | 2.4828 | 301.029 | 56.9873 | 0.01296 | 286.531 | 54.8782 | 0.0097653 | 331.176 | 331.001 | 743301 | 16.6028 | 705148 | 727903 | 637092 | 0 | 0 | 633771 | 720.565 | 0 | 0 | 0 | 1461.05 | 632310 | 726.649 | 621519 | 609088.8125
610 | 1998-01-26 09:00 | 432 | 881 | 51 | 10.43 | 7.76 | 0 | 25.7118 | 139.65 | 46.8913 | 0 | 432 | 600.145 | 67.3261 | 4.0475 | 592.198 | 63.0063 | 0.021127 | 578.479 | 60.6745 | 0.015919 | 619.995 | 619.937 | 1392230 | 22.1413 | 1365780 | 1381470 | 1310260 | 0 | 0 | 1297350 | 721.585 | 0 | 0 | 0 | 0 | 1297350 | 721.585 | 1275460 | 1249950.75
611 | 1998-01-26 10:00 | 576 | 967 | 58 | 11.11 | 7.76 | 0 | 32.5051 | 153.958 | 36.1715 | 0 | 576 | 778.148 | 75.5079 | 5.3967 | 778.148 | 70.6632 | 0.028169 | 768.859 | 68.048 | 0.021226 | 811.82 | 811.818 | 1823140 | 26.4461 | 1815300 | 1804060 | 1753170 | 0 | 0 | 1731150 | 735.061 | 0 | 0 | 0 | 0 | 1731150 | 735.061 | 1697700 | 1663749.5
612 | 1998-01-26 11:00 | 652 | 995 | 65 | 12.9 | 7.76 | 0 | 36.2966 | 170.581 | 29.2466 | 0 | 652 | 865.207 | 83.9185 | 6.1087 | 865.207 | 78.5341 | 0.031885 | 858.887 | 75.6276 | 0.024026 | 906.502 | 906.5 | 2035770 | 30.0247 | 2038770 | 1995900 | 1940820 | 0 | 0 | 1913270 | 726.137 | 0 | 0 | 0 | 0 | 1913270 | 726.137 | 1874200 | 1836715.5
613 | 1998-01-26 12:00 | 653 | 995 | 64 | 14.69 | 7.64 | 0 | 36.4339 | 188.252 | 28.9851 | 0 | 653 | 867.536 | 82.6725 | 6.1181 | 867.536 | 77.368 | 0.031934 | 861.325 | 74.5047 | 0.024063 | 907.778 | 907.773 | 2038640 | 31.9692 | 2041780 | 1982280 | 1930790 | 0 | 0 | 1902890 | 717.748 | 0 | 0 | 0 | 0 | 1902890 | 717.748 | 1864240 | 1826959.375
614 | 1998-01-26 13:00 | 590 | 978 | 60 | 16.47 | 7.64 | 0 | 32.8903 | 205.01 | 35.5354 | 0 | 590 | 794.228 | 77.9523 | 5.5278 | 794.228 | 72.9507 | 0.028854 | 785.139 | 70.2508 | 0.021742 | 829.749 | 829.746 | 1863400 | 32.264 | 1857550 | 1800770 | 1753860 | 0 | 0 | 1730580 | 714.863 | 0 | 0 | 0 | 0 | 1730580 | 714.863 | 1697620 | 1663670.875
615 | 1998-01-26 14:00 | 469 | 935 | 56 | 17.29 | 7.64 | 0 | 26.2855 | 219.506 | 46.0755 | 0 | 469 | 646.959 | 73.4963 | 4.3942 | 646.959 | 68.7807 | 0.022936 | 632.677 | 66.2351 | 0.017283 | 677.962 | 677.959 | 1522520 | 30.1948 | 1500770 | 1467480 | 1429050 | 0 | 0 | 1413590 | 716.808 | 0 | 0 | 0 | 0 | 1413590 | 716.808 | 1389350 | 1361563.5
616 | 1998-01-26 15:00 | 276 | 794 | 38 | 18.11 | 9.23 | 0 | 17.4672 | 231.538 | 58.481 | 0 | 276 | 414.519 | 51.8224 | 2.5859 | 382.626 | 48.4974 | 0.013498 | 365.162 | 46.7025 | 0.010171 | 399.518 | 399.458 | 897083 | 24.9935 | 856549 | 856009 | 814931 | 0 | 0 | 809848 | 717.643 | 0 | 0 | 0 | 0 | 809848 | 717.643 | 796986 | 781046.25
617 | 1998-01-26 16:00 | 95 | 0 | 95 | 18.93 | 9.23 | 0 | 7.1635 | 241.576 | 71.7834 | 0 | 95 | 0 | 118.275 | 0.89008 | 0 | 110.687 | 0.0046459 | 0 | 106.59 | 0.0035008 | 103.396 | 103.393 | 232195 | 20.7117 | 200256 | 204533 | 198668 | 0 | 0 | 198326 | 676.111 | 0 | 0 | 0 | 0 | 198326 | 676.111 | 192870 | 189012.6875
618 | 1998-01-26 17:00 | 1 | 0 | 1 | 18.1 | 9.23 | 0 | -4.1044 | 250.258 | 85.554 | 0 | 1 | 0 | 0.91918 | 0.0093692 | 0 | 0.86021 | 0 | 0 | 0.82837 | 0 | 0.80352 | 0.80351 | 1804.48 | 18.1138 | 157.811 | 156.527 | 155.753 | 0 | 0 | 155.746 | 120.129 | 0 | 0 | 0 | 155.746 | 0 | 660 | 0 | 0
619 | 1998-01-26 18:00 | 0 | 0 | 0 | 17.27 | 7.68 | 0
620 | 1998-01-26 19:00 | 0 | 0 | 0 | 16.44 | 7.68 | 0
621 | 1998-01-26 20:00 | 0 | 0 | 0 | 15.66 | 7.68 | 0
622 | 1998-01-26 21:00 | 0 | 0 | 0 | 14.87 | 9.36 | 0
623 | 1998-01-26 22:00 | 0 | 0 | 0 | 14.09 | 9.36 | 0
624 | 1998-01-26 23:00 | 0 | 0 | 0 | 13.23 | 9.36 | 0
625 | 1998-01-27 | 0 | 0 | 0 | 12.37 | 6.59 | 0
626 | 1998-01-27 01:00 | 0 | 0 | 0 | 11.51 | 6.59 | 0
627 | 1998-01-27 02:00 | 0 | 0 | 0 | 11.11 | 6.59 | 0
628 | 1998-01-27 03:00 | 0 | 0 | 0 | 10.72 | 6.29 | 0
629 | 1998-01-27 04:00 | 0 | 0 | 0 | 10.33 | 6.29 | 0
630 | 1998-01-27 05:00 | 0 | 0 | 0 | 10 | 6.29 | 0
631 | 1998-01-27 06:00 | 1 | 33 | 1 | 9.67 | 7 | 0 | -4.8428 | 109.052 | 86.5056 | 0 | 1 | 0 | 0.9371 | 0.0093692 | 0 | 0.87697 | 0 | 0 | 0.84452 | 0 | 0.81918 | 0.81915 | 1839.59 | 9.6862 | 163.997 | 161.027 | 160.15 | 0 | 0 | 160.143 | 123.126 | 0 | 0 | 0 | 160.143 | 0 | 660 | 0 | 0
632 | 1998-01-27 07:00 | 94 | 584 | 27 | 9.34 | 7 | 0 | 6.5011 | 117.654 | 72.6925 | 0 | 94 | 176.049 | 41.7107 | 0.88071 | 23.9173 | 39.0345 | 0.004597 | 21.0934 | 37.5898 | 0.0034639 | 56.9261 | 56.9248 | 127848 | 10.4684 | 106030 | 113279 | 97750.1 | 0 | 0 | 97617.3 | 647.372 | 0 | 0 | 0 | 881.95 | 96735.4 | 662.868 | 93646.8 | 91773.8906
633 | 1998-01-27 08:00 | 287 | 833 | 45 | 9.87 | 7 | 0 | 16.9167 | 127.568 | 59.32 | 0 | 287 | 424.353 | 60.7591 | 2.689 | 330.226 | 56.8606 | 0.014035 | 314.378 | 54.7563 | 0.010576 | 358.07 | 357.87 | 803650 | 16.9641 | 766400 | 789537 | 690920 | 0 | 0 | 687012 | 720.966 | 0 | 0 | 0 | 1791.03 | 685221 | 727.485 | 673648 | 660175.3125
634 | 1998-01-27 09:00 | 459 | 929 | 54 | 10.4 | 3.33 | 0 | 25.8967 | 139.444 | 46.7895 | 0 | 459 | 634.908 | 70.9615 | 4.3005 | 627.39 | 66.4085 | 0.022447 | 612.943 | 63.9508 | 0.016914 | 656.604 | 656.574 | 1474500 | 26.9153 | 1451310 | 1438340 | 1366840 | 0 | 0 | 1352520 | 713.756 | 0 | 0 | 0 | 0 | 1352520 | 713.756 | 1329800 | 1303206.25
635 | 1998-01-27 10:00 | 587 | 977 | 60 | 10.94 | 3.33 | 0 | 32.7242 | 153.788 | 36.0088 | 0 | 587 | 788.581 | 77.8774 | 5.4997 | 788.581 | 72.8807 | 0.028707 | 779.268 | 70.1834 | 0.021631 | 823.989 | 823.986 | 1850460 | 31.6663 | 1843970 | 1792120 | 1746240 | 0 | 0 | 1723250 | 716.189 | 0 | 0 | 0 | 0 | 1723250 | 716.189 | 1690490 | 1656675.625
636 | 1998-01-27 11:00 | 639 | 974 | 61 | 12.64 | 3.33 | 0 | 36.5445 | 170.476 | 29.0133 | 0 | 639 | 848.884 | 78.8631 | 5.9869 | 848.884 | 73.8031 | 0.03125 | 842.793 | 71.0717 | 0.023547 | 886.472 | 886.469 | 1990790 | 34.938 | 1991440 | 1908350 | 1858880 | 0 | 0 | 1832310 | 708.192 | 0 | 0 | 0 | 0 | 1832310 | 708.192 | 1796160 | 1760238.375
637 | 1998-01-27 12:00 | 656 | 995 | 63 | 14.35 | 1.76 | 0 | 36.6955 | 188.232 | 28.7236 | 0 | 656 | 870.253 | 81.3229 | 6.1462 | 870.253 | 76.1051 | 0.032081 | 864.147 | 73.2885 | 0.024174 | 909.336 | 909.33 | 2042130 | 39.7404 | 2045460 | 1918690 | 1871200 | 0 | 0 | 1843040 | 691.772 | 0 | 0 | 0 | 0 | 1843040 | 691.772 | 1806770 | 1770635.75
638 | 1998-01-27 13:00 | 595 | 929 | 88 | 16.06 | 1.76 | 0 | 33.1478 | 205.069 | 35.3058 | 0 | 595 | 756.677 | 111.74 | 5.5747 | 756.677 | 104.57 | 0.029098 | 748.151 | 100.7 | 0.021926 | 823.407 | 823.4 | 1849150 | 39.0511 | 1842590 | 1733010 | 1689970 | 0 | 0 | 1666900 | 691.48 | 0 | 0 | 0 | 0 | 1666900 | 691.48 | 1636570 | 1603839
639 | 1998-01-27 14:00 | 414 | 647 | 126 | 16.49 | 1.76 | 0 | 26.5271 | 219.621 | 45.8899 | 0 | 414 | 448.835 | 162.703 | 3.8789 | 448.835 | 152.263 | 0.020246 | 439.035 | 146.628 | 0.015256 | 568.108 | 568.099 | 1275810 | 32.3525 | 1244490 | 1204790 | 1174660 | 0 | 0 | 1163770 | 702.89 | 0 | 0 | 0 | 0 | 1163770 | 702.89 | 1145410 | 1122497.75
640 | 1998-01-27 15:00 | 221 | 400 | 100 | 16.93 | 2.57 | 0 | 17.689 | 231.686 | 58.3314 | 0 | 221 | 209.069 | 125.616 | 2.0706 | 201.026 | 117.557 | 0.010808 | 191.932 | 113.206 | 0.0081439 | 295.992 | 295.972 | 664679 | 24.7594 | 621944 | 622489 | 603778 | 0 | 0 | 600897 | 705.196 | 0 | 0 | 0 | 0 | 600897 | 705.196 | 591717 | 579883
641 | 1998-01-27 16:00 | 63 | 267 | 28 | 17.36 | 2.57 | 0 | 7.3667 | 241.744 | 71.6617 | 0 | 63 | 85.8835 | 44.5836 | 0.59026 | 60.3313 | 41.7231 | 0.003081 | 53.7602 | 40.1789 | 0.0023216 | 91.1232 | 91.0902 | 204566 | 19.7696 | 175245 | 179571 | 162318 | 0 | 0 | 162074 | 671.63 | 0 | 0 | 0 | 0 | 162074 | 671.63 | 157322 | 154176.0625
642 | 1998-01-27 17:00 | 1 | 25 | 0 | 16.9 | 2.57 | 0 | -3.9164 | 250.443 | 85.4553 | 0 | 1 | 0.91078 | 0 | 0.0093692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.9 | 0 | 0 | 0 | 0 | 0 | 0 | 660 | 0 | 0 | 0 | 0 | 0 | 660 | 0 | 0
643 | 1998-01-27 18:00 | 0 | 0 | 0 | 16.44 | 3.16 | 0
644 | 1998-01-27 19:00 | 0 | 0 | 0 | 15.98 | 3.16 | 0
645 | 1998-01-27 20:00 | 0 | 0 | 0 | 15.23 | 3.16 | 0
646 | 1998-01-27 21:00 | 0 | 0 | 0 | 14.47 | 3.42 | 0
647 | 1998-01-27 22:00 | 0 | 0 | 0 | 13.71 | 3.42 | 0
648 | 1998-01-27 23:00 | 0 | 0 | 0 | 12.95 | 3.42 | 0
649 | 1998-01-28 | 0 | 0 | 0 | 12.18 | 2.02 | 0
650 | 1998-01-28 01:00 | 0 | 0 | 0 | 11.42 | 2.02 | 0
651 | 1998-01-28 02:00 | 0 | 0 | 0 | 10.53 | 2.02 | 0
652 | 1998-01-28 03:00 | 0 | 0 | 0 | 9.64 | 0.14 | 0
653 | 1998-01-28 04:00 | 0 | 0 | 0 | 8.75 | 0.14 | 0
654 | 1998-01-28 05:00 | 0 | 0 | 0 | 8.39 | 0.14 | 0
655 | 1998-01-28 06:00 | 1 | 20 | 1 | 8.02 | 0.63 | 0 | -4.7307 | 108.81 | 86.4995 | 0 | 1 | 0 | 0.93697 | 0.0093692 | 0 | 0.87685 | 0 | 0 | 0.8444 | 0 | 0.81907 | 0.81899 | 1839.25 | 8.0447 | 163.917 | 160.631 | 159.846 | 0 | 0 | 159.839 | 121.927 | 0 | 0 | 0 | 159.839 | 0 | 660 | 0 | 0
656 | 1998-01-28 07:00 | 78 | 319 | 41 | 7.65 | 0.63 | 0 | 6.6334 | 117.421 | 72.6614 | 0 | 78 | 95.4562 | 58.1458 | 0.7308 | 13.3282 | 54.415 | 0.0038145 | 11.7584 | 52.4012 | 0.0028743 | 62.2376 | 62.232 | 139760 | 9.5248 | 115369 | 124228 | 113330 | 0 | 0 | 113210 | 679.987 | 0 | 0 | 0 | 0 | 113210 | 679.987 | 109482 | 107292.5625
657 | 1998-01-28 08:00 | 287 | 749 | 67 | 8.61 | 0.63 | 0 | 17.0755 | 127.345 | 59.2572 | 0 | 287 | 382.999 | 89.2367 | 2.689 | 299.341 | 83.5111 | 0.014035 | 285.029 | 80.4204 | 0.010576 | 354.496 | 354.414 | 795895 | 19.2872 | 757420 | 771779 | 682756 | 0 | 0 | 678908 | 711.331 | 0 | 0 | 0 | 1488.71 | 677420 | 720.041 | 666348 | 653021.5
658 | 1998-01-28 09:00 | 433 | 831 | 68 | 9.56 | 2.9 | 0 | 26.0875 | 139.238 | 46.6831 | 0 | 433 | 569.427 | 93.0591 | 4.0569 | 563.469 | 87.0882 | 0.021175 | 550.575 | 83.8652 | 0.015956 | 615.423 | 615.402 | 1382050 | 25.4865 | 1355030 | 1351320 | 1291900 | 0 | 0 | 1279290 | 718.223 | 0 | 0 | 0 | 0 | 1279290 | 718.223 | 1257880 | 1232721.625
659 | 1998-01-28 10:00 | 591 | 927 | 88 | 10.51 | 2.9 | 0 | 32.9494 | 153.618 | 35.841 | 0 | 591 | 749.689 | 118.289 | 5.5372 | 749.689 | 110.699 | 0.028902 | 740.933 | 106.602 | 0.021778 | 822.13 | 822.126 | 1846280 | 31.7865 | 1839580 | 1786900 | 1740070 | 0 | 0 | 1717240 | 716.125 | 0 | 0 | 0 | 0 | 1717240 | 716.125 | 1684670 | 1650975.75
660 | 1998-01-28 11:00 | 654 | 991 | 62 | 12.16 | 2.9 | 0 | 36.7981 | 170.373 | 28.7744 | 0 | 654 | 866.282 | 79.9864 | 6.1275 | 866.282 | 74.8544 | 0.031983 | 860.181 | 72.0841 | 0.0241 | 904.32 | 904.318 | 2030860 | 35.5636 | 2033600 | 1943480 | 1893550 | 0 | 0 | 1865830 | 706.231 | 0 | 0 | 0 | 0 | 1865830 | 706.231 | 1828570 | 1791999.75
661 | 1998-01-28 12:00 | 652 | 986 | 61 | 13.81 | 1.56 | 0 | 36.9623 | 188.217 | 28.4574 | 0 | 652 | 864.127 | 78.7364 | 6.1087 | 864.127 | 73.6846 | 0.031885 | 858.189 | 70.9575 | 0.024026 | 901.296 | 901.291 | 2024070 | 39.3154 | 2026450 | 1904420 | 1854730 | 0 | 0 | 1827220 | 693.959 | 0 | 0 | 0 | 0 | 1827220 | 693.959 | 1791470 | 1755638.625
662 | 1998-01-28 13:00 | 566 | 888 | 78 | 15.46 | 1.56 | 0 | 33.4093 | 205.135 | 35.0745 | 0 | 566 | 725.336 | 99.6681 | 5.303 | 725.336 | 93.2732 | 0.02768 | 717.289 | 89.8213 | 0.020857 | 782.917 | 782.915 | 1758240 | 37.6155 | 1747230 | 1653670 | 1609540 | 0 | 0 | 1588920 | 697.267 | 0 | 0 | 0 | 0 | 1588920 | 697.267 | 1560870 | 1529651.125
663 | 1998-01-28 14:00 | 459 | 767 | 114 | 15.89 | 1.56 | 0 | 26.7715 | 219.742 | 45.7044 | 0 | 459 | 534.895 | 149.457 | 4.3005 | 534.895 | 139.868 | 0.022447 | 523.343 | 134.691 | 0.016914 | 638.31 | 638.308 | 1433480 | 33.9533 | 1408050 | 1353820 | 1320860 | 0 | 0 | 1307070 | 701.243 | 0 | 0 | 0 | 0 | 1307070 | 701.243 | 1285800 | 1260082.75
664 | 1998-01-28 15:00 | 202 | 254 | 124 | 16.31 | 3.37 | 0 | 17.9127 | 231.84 | 58.1828 | 0 | 202 | 133.702 | 144.299 | 1.8926 | 128.558 | 135.04 | 0.0098786 | 122.794 | 130.042 | 0.0074438 | 245.259 | 245.253 | 550777 | 22.4628 | 508720 | 514592 | 499129 | 0 | 0 | 497160 | 706.01 | 0 | 0 | 0 | 0 | 497160 | 706.01 | 489004 | 479223.9375
665 | 1998-01-28 16:00 | 99 | 264 | 64 | 16.74 | 3.37 | 0 | 7.5712 | 241.919 | 71.5416 | 0 | 99 | 84.1058 | 83.8214 | 0.92755 | 59.0826 | 78.4433 | 0.0048415 | 52.7064 | 75.5402 | 0.0036482 | 124.403 | 124.377 | 279320 | 19.8603 | 245404 | 251305 | 232905 | 0 | 0 | 232437 | 686.168 | 0 | 0 | 0 | 0 | 232437 | 686.168 | 226327 | 221800.7031
666 | 1998-01-28 17:00 | 2 | 26 | 1 | 16.41 | 3.37 | 0 | -3.7277 | 250.634 | 85.3584 | 0 | 2 | 0.93014 | 1.0942 | 0.018738 | 0 | 1.024 | 0 | 0 | 0.98614 | 0 | 0.95656 | 0.95653 | 2148.13 | 16.434 | 223.482 | 221.231 | 220.182 | 0 | 0 | 220.172 | 141.649 | 0 | 0 | 0 | 220.172 | 0 | 660 | 0 | 0
667 | 1998-01-28 18:00 | 0 | 0 | 0 | 16.09 | 5.43 | 0
668 | 1998-01-28 19:00 | 0 | 0 | 0 | 15.76 | 5.43 | 0
669 | 1998-01-28 20:00 | 0 | 0 | 0 | 14.99 | 5.43 | 0
670 | 1998-01-28 21:00 | 0 | 0 | 0 | 14.21 | 7.47 | 0
671 | 1998-01-28 22:00 | 0 | 0 | 0 | 13.44 | 7.47 | 0
672 | 1998-01-28 23:00 | 0 | 0 | 0 | 12.73 | 7.47 | 0
673 | 1998-01-29 | 0 | 0 | 0 | 12.02 | 7.02 | 0
674 | 1998-01-29 01:00 | 0 | 0 | 0 | 11.31 | 7.02 | 0
675 | 1998-01-29 02:00 | 0 | 0 | 0 | 9.86 | 7.02 | 0
676 | 1998-01-29 03:00 | 0 | 0 | 0 | 8.41 | 9.52 | 0
677 | 1998-01-29 04:00 | 0 | 0 | 0 | 6.96 | 9.52 | 0
678 | 1998-01-29 05:00 | 0 | 0 | 0 | 6.17 | 9.52 | 0
679 | 1998-01-29 06:00 | 1 | 20 | 1 | 5.38 | 10.4 | 0 | -4.613 | 108.566 | 86.4894 | 0 | 1 | 0 | 0.93677 | 0.0093692 | 0 | 0.87666 | 0 | 0 | 0.84422 | 0 | 0.81889 | 0.81884 | 1838.9 | 5.3931 | 163.866 | 160.066 | 159.169 | 0 | 0 | 159.163 | 123.125 | 0 | 0 | 0 | 159.163 | 0 | 660 | 0 | 0
680 | 1998-01-29 07:00 | 79 | 303 | 43 | 4.58 | 10.4 | 0 | 6.7714 | 117.187 | 72.6262 | 0 | 79 | 91.1707 | 60.1758 | 0.74017 | 13.7278 | 56.3148 | 0.0038634 | 12.1156 | 54.2306 | 0.0029112 | 64.3586 | 64.3525 | 144520 | 5.612 | 119678 | 131296 | 119931 | 0 | 0 | 119805 | 699.266 | 0 | 0 | 0 | 0 | 119805 | 699.266 | 115695 | 113381.0469
681 | 1998-01-29 08:00 | 279 | 732 | 62 | 5.21 | 10.4 | 0 | 17.2401 | 127.12 | 59.1901 | 0 | 279 | 375.014 | 83.7551 | 2.614 | 306.304 | 78.3812 | 0.013644 | 291.718 | 75.4803 | 0.010281 | 356.193 | 356.113 | 799712 | 10.9208 | 761086 | 805632 | 718868 | 0 | 0 | 715008 | 748.201 | 0 | 0 | 0 | 0 | 715008 | 748.201 | 702490 | 688440.3125
682 | 1998-01-29 09:00 | 469 | 935 | 56 | 5.84 | 8.29 | 0 | 26.2843 | 139.03 | 46.5721 | 0 | 469 | 641.14 | 73.2006 | 4.3942 | 635.066 | 68.5039 | 0.022936 | 620.629 | 65.9686 | 0.017283 | 666.016 | 665.989 | 1495650 | 18.0088 | 1473230 | 1515720 | 1450180 | 0 | 0 | 1435330 | 742.773 | 0 | 0 | 0 | 0 | 1435330 | 742.773 | 1409300 | 1381118.375
683 | 1998-01-29 10:00 | 596 | 979 | 62 | 6.47 | 8.29 | 0 | 33.1805 | 153.448 | 35.6682 | 0 | 596 | 792.697 | 80.1109 | 5.5841 | 792.697 | 74.9709 | 0.029147 | 783.545 | 72.1962 | 0.021963 | 830.09 | 830.085 | 1864160 | 21.6371 | 1858350 | 1883940 | 1831440 | 0 | 0 | 1808380 | 750.477 | 0 | 0 | 0 | 0 | 1808380 | 750.477 | 1771520 | 1736087.5
684 | 1998-01-29 11:00 | 664 | 998 | 64 | 6.95 | 8.29 | 0 | 37.0575 | 170.272 | 28.5298 | 0 | 664 | 874.754 | 82.3344 | 6.2212 | 874.754 | 77.0517 | 0.032472 | 868.709 | 74.2001 | 0.024469 | 914.645 | 914.641 | 2054060 | 23.6621 | 2058010 | 2068990 | 2013090 | 0 | 0 | 1984930 | 745.457 | 0 | 0 | 0 | 0 | 1984930 | 745.457 | 1942840 | 1903979.125
685 | 1998-01-29 12:00 | 666 | 998 | 64 | 7.43 | 10.97 | 0 | 37.234 | 188.207 | 28.1868 | 0 | 666 | 876.937 | 82.32 | 6.2399 | 876.937 | 77.0382 | 0.03257 | 871.038 | 74.187 | 0.024542 | 916.892 | 916.888 | 2059100 | 21.6335 | 2063320 | 2091570 | 2033070 | 0 | 0 | 2004940 | 752.751 | 0 | 0 | 0 | 0 | 2004940 | 752.751 | 1961380 | 1922148.5
686 | 1998-01-29 13:00 | 595 | 973 | 57 | 7.91 | 10.97 | 0 | 33.6747 | 205.207 | 34.8414 | 0 | 595 | 796.349 | 73.8845 | 5.5747 | 796.349 | 69.1439 | 0.029098 | 787.652 | 66.5849 | 0.021926 | 828.631 | 828.628 | 1860890 | 20.7462 | 1854920 | 1887330 | 1833710 | 0 | 0 | 1810800 | 754.004 | 0 | 0 | 0 | 0 | 1810800 | 754.004 | 1773540 | 1738065.625
687 | 1998-01-29 14:00 | 482 | 939 | 56 | 8.75 | 10.97 | 0 | 27.0186 | 219.871 | 45.519 | 0 | 482 | 657.056 | 73.1191 | 4.516 | 657.056 | 68.4277 | 0.023572 | 643.021 | 65.8952 | 0.017762 | 687.666 | 687.663 | 1544310 | 19.4026 | 1523500 | 1559080 | 1515070 | 0 | 0 | 1499270 | 752.032 | 0 | 0 | 0 | 0 | 1499270 | 752.032 | 1471450 | 1442018.625
688 | 1998-01-29 15:00 | 291 | 809 | 39 | 9.58 | 7.56 | 0 | 18.1381 | 232.001 | 58.0354 | 0 | 291 | 428.538 | 52.7154 | 2.7264 | 412.052 | 49.3331 | 0.014231 | 393.737 | 47.5073 | 0.010723 | 428.018 | 427.972 | 961118 | 17.7676 | 921316 | 950118 | 917238 | 0 | 0 | 911277 | 743.894 | 0 | 0 | 0 | 0 | 911277 | 743.894 | 895624 | 877711.25
689 | 1998-01-29 16:00 | 85 | 539 | 11 | 10.42 | 7.56 | 0 | 7.7766 | 242.099 | 71.4233 | 0 | 85 | 174.225 | 17.1758 | 0.79638 | 122.524 | 16.0737 | 0.0041569 | 109.42 | 15.4789 | 0.0031323 | 121.155 | 121.122 | 272008 | 12.7372 | 240821 | 254258 | 217038 | 0 | 0 | 216605 | 701.153 | 0 | 0 | 0 | 0 | 216605 | 701.153 | 210421 | 206213.0156
690 | 1998-01-29 17:00 | 2 | 59 | 1 | 9.59 | 7.56 | 0 | -3.5385 | 250.831 | 85.2637 | 0 | 2 | 0.94908 | 1.1022 | 0.018738 | 0 | 1.0315 | 0 | 0 | 0.9933 | 0 | 0.9635 | 0.96343 | 2163.62 | 9.6084 | 226.694 | 222.582 | 221.545 | 0 | 0 | 221.536 | 142.103 | 0 | 0 | 0 | 221.536 | 0 | 660 | 0 | 0
691 | 1998-01-29 18:00 | 0 | 0 | 0 | 8.77 | 10.26 | 0
692 | 1998-01-29 19:00 | 0 | 0 | 0 | 7.94 | 10.26 | 0
693 | 1998-01-29 20:00 | 0 | 0 | 0 | 7.46 | 10.26 | 0
694 | 1998-01-29 21:00 | 0 | 0 | 0 | 6.97 | 9.84 | 0
695 | 1998-01-29 22:00 | 0 | 0 | 0 | 6.48 | 9.84 | 0
696 | 1998-01-29 23:00 | 0 | 0 | 0 | 6.18 | 9.84 | 0
697 | 1998-01-30 | 0 | 0 | 0 | 5.87 | 8.04 | 0
698 | 1998-01-30 01:00 | 0 | 0 | 0 | 5.57 | 8.04 | 0
699 | 1998-01-30 02:00 | 0 | 0 | 0 | 4.89 | 8.04 | 0
700 | 1998-01-30 03:00 | 0 | 0 | 0 | 4.21 | 4.67 | 0
701 | 1998-01-30 04:00 | 0 | 0 | 0 | 3.53 | 4.67 | 0
702 | 1998-01-30 05:00 | 0 | 0 | 0 | 3.45 | 4.67 | 0
703 | 1998-01-30 06:00 | 1 | 44 | 0 | 3.37 | 6.2 | 0 | -4.4896 | 108.319 | 86.4753 | 0 | 1 | 0.70665 | 0 | 0.0093692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.37 | 0 | 0 | 0 | 0 | 0 | 0 | 660 | 0 | 0 | 0 | 0 | 0 | 660 | 0 | 0
704 | 1998-01-30 07:00 | 101 | 598 | 28 | 3.29 | 6.2 | 0 | 6.9151 | 116.95 | 72.5869 | 0 | 101 | 181.447 | 42.453 | 0.94629 | 28.3865 | 39.7292 | 0.0049393 | 25.063 | 38.2588 | 0.0037219 | 61.4258 | 61.3881 | 137868 | 4.5708 | 115423 | 126473 | 107449 | 0 | 0 | 107298 | 668.474 | 0 | 0 | 0 | 284.175 | 107014 | 674.857 | 103550 | 101479.2734
705 | 1998-01-30 08:00 | 299 | 842 | 47 | 4.56 | 6.2 | 0 | 17.4105 | 126.892 | 59.1187 | 0 | 299 | 432.27 | 62.8405 | 2.8014 | 354.657 | 58.8085 | 0.014622 | 337.841 | 56.632 | 0.011018 | 382.649 | 382.582 | 859151 | 12.542 | 822216 | 862898 | 768593 | 0 | 0 | 763988 | 736.089 | 0 | 0 | 0 | 1787.98 | 762200 | 742.445 | 749098 | 734116.1875
706 | 1998-01-30 09:00 | 473 | 888 | 78 | 5.82 | 5.09 | 0 | 26.4869 | 138.82 | 46.4566 | 0 | 473 | 610.136 | 104.648 | 4.4316 | 605.152 | 97.9335 | 0.023132 | 591.488 | 94.309 | 0.01743 | 665.24 | 665.193 | 1493850 | 20.7298 | 1471240 | 1496920 | 1433760 | 0 | 0 | 1418940 | 735.524 | 0 | 0 | 0 | 0 | 1418940 | 735.524 | 1393720 | 1365842.75
707 | 1998-01-30 10:00 | 558 | 814 | 111 | 7.09 | 5.09 | 0 | 33.4174 | 153.278 | 35.4904 | 0 | 558 | 660.85 | 144.504 | 5.228 | 660.85 | 135.232 | 0.027289 | 653.311 | 130.227 | 0.020563 | 760.052 | 760.048 | 1706870 | 24.1259 | 1693410 | 1699290 | 1650330 | 0 | 0 | 1631060 | 740.654 | 0 | 0 | 0 | 0 | 1631060 | 740.654 | 1600320 | 1568316.625
708 | 1998-01-30 11:00 | 668 | 946 | 96 | 8.76 | 5.09 | 0 | 37.3225 | 170.173 | 28.2797 | 0 | 668 | 830.823 | 120.643 | 6.2586 | 830.823 | 112.902 | 0.032668 | 825.193 | 108.723 | 0.024616 | 905.923 | 905.918 | 2034450 | 29.0654 | 2037380 | 2002600 | 1947840 | 0 | 0 | 1920300 | 728.993 | 0 | 0 | 0 | 0 | 1920300 | 728.993 | 1880980 | 1843355.5
709 | 1998-01-30 12:00 | 671 | 999 | 65 | 10.43 | 2.51 | 0 | 37.5106 | 188.201 | 27.9119 | 0 | 671 | 879.448 | 83.4268 | 6.2867 | 879.448 | 78.074 | 0.032815 | 873.659 | 75.1845 | 0.024727 | 920.402 | 920.399 | 2066980 | 34.8748 | 2071610 | 1985910 | 1934340 | 0 | 0 | 1905660 | 709.274 | 0 | 0 | 0 | 0 | 1905660 | 709.274 | 1867000 | 1829656.625
710 | 1998-01-30 13:00 | 602 | 975 | 59 | 12.1 | 2.51 | 0 | 33.9437 | 205.286 | 34.6067 | 0 | 602 | 800.401 | 76.2439 | 5.6403 | 800.401 | 71.3519 | 0.02944 | 791.799 | 68.7113 | 0.022184 | 834.716 | 834.71 | 1874550 | 34.269 | 1869260 | 1796200 | 1750240 | 0 | 0 | 1726640 | 708.19 | 0 | 0 | 0 | 0 | 1726640 | 708.19 | 1693960 | 1660079.875
711 | 1998-01-30 14:00 | 473 | 928 | 49 | 12.74 | 2.51 | 0 | 27.2682 | 220.006 | 45.334 | 0 | 473 | 650.566 | 64.276 | 4.4316 | 650.566 | 60.1519 | 0.023132 | 636.822 | 57.9258 | 0.01743 | 673.922 | 673.923 | 1513460 | 30.6387 | 1491320 | 1455310 | 1415030 | 0 | 0 | 1399850 | 716.344 | 0 | 0 | 0 | 0 | 1399850 | 716.344 | 1375920 | 1348403.375
712 | 1998-01-30 15:00 | 297 | 817 | 40 | 13.39 | 1.81 | 0 | 18.3651 | 232.169 | 57.8892 | 0 | 297 | 433.585 | 53.8585 | 2.7827 | 433.585 | 50.4028 | 0.014524 | 414.48 | 48.5374 | 0.010944 | 449.137 | 449.134 | 1008640 | 25.8889 | 969689 | 965787 | 942336 | 0 | 0 | 935542 | 715.334 | 0 | 0 | 0 | 0 | 935542 | 715.334 | 920791 | 902375.4375
713 | 1998-01-30 16:00 | 111 | 399 | 55 | 14.03 | 1.81 | 0 | 7.983 | 242.287 | 71.3068 | 0 | 111 | 129.235 | 71.492 | 1.04 | 94.8918 | 66.9049 | 0.0054284 | 84.8327 | 64.4288 | 0.0040904 | 144.788 | 144.727 | 325020 | 18.0576 | 289696 | 298712 | 271529 | 0 | 0 | 270901 | 698.134 | 0 | 0 | 0 | 0 | 270901 | 698.134 | 264154 | 258871
714 | 1998-01-30 17:00 | 2 | 47 | 1 | 13.61 | 1.81 | 0 | -3.3487 | 251.034 | 85.171 | 0 | 2 | 0.96761 | 1.11 | 0.018738 | 0 | 1.0388 | 0 | 0 | 1.0004 | 0 | 0.97034 | 0.97028 | 2179 | 13.637 | 229.917 | 226.844 | 225.79 | 0 | 0 | 225.781 | 143.426 | 0 | 0 | 0 | 225.781 | 0 | 660 | 0 | 0
715 | 1998-01-30 18:00 | 0 | 0 | 0 | 13.18 | 3.45 | 0
716 | 1998-01-30 19:00 | 0 | 0 | 0 | 12.75 | 3.45 | 0
717 | 1998-01-30 20:00 | 0 | 0 | 0 | 12.42 | 3.45 | 0
718 | 1998-01-30 21:00 | 0 | 0 | 0 | 12.08 | 5.58 | 0
719 | 1998-01-30 22:00 | 0 | 0 | 0 | 11.75 | 5.58 | 0
720 | 1998-01-30 23:00 | 0 | 0 | 0 | 11.14 | 5.58 | 0
721 | 1998-01-31 | 0 | 0 | 0 | 10.53 | 6.75 | 0
722 | 1998-01-31 01:00 | 0 | 0 | 0 | 9.92 | 6.75 | 0
723 | 1998-01-31 02:00 | 0 | 0 | 0 | 9.35 | 6.75 | 0
724 | 1998-01-31 03:00 | 0 | 0 | 0 | 8.78 | 3.54 | 0
725 | 1998-01-31 04:00 | 0 | 0 | 0 | 8.22 | 3.54 | 0
726 | 1998-01-31 05:00 | 0 | 0 | 0 | 7.7 | 3.54 | 0
727 | 1998-01-31 06:00 | 1 | 45 | 0 | 7.17 | 2 | 0 | -4.3605 | 108.069 | 86.4572 | 0 | 1 | 0.71028 | 0 | 0.0093692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.17 | 0 | 0 | 0 | 0 | 0 | 0 | 660 | 0 | 0 | 0 | 0 | 0 | 660 | 0 | 0
728 | 1998-01-31 07:00 | 97 | 574 | 25 | 6.65 | 2 | 0 | 7.0644 | 116.711 | 72.5436 | 0 | 97 | 175.62 | 37.4214 | 0.90881 | 28.7481 | 35.0204 | 0.0047437 | 25.3938 | 33.7243 | 0.0035745 | 57.348 | 57.3139 | 128722 | 8.2248 | 107271 | 115429 | 95108.9 | 0 | 0 | 94979.5 | 651.857 | 0 | 0 | 0 | 174.504 | 94805 | 669.557 | 91713.2 | 89878.9453
729 | 1998-01-31 08:00 | 302 | 844 | 47 | 6.83 | 2 | 0 | 17.5865 | 126.663 | 59.0432 | 0 | 302 | 434.129 | 62.6947 | 2.8295 | 357.777 | 58.6721 | 0.014769 | 340.889 | 56.5007 | 0.011129 | 385.479 | 385.388 | 865447 | 17.4195 | 828459 | 850898 | 762018 | 0 | 0 | 757369 | 724.015 | 0 | 0 | 0 | 1388.7 | 755980 | 726.534 | 743541 | 728670.5625
730 | 1998-01-31 09:00 | 476 | 937 | 56 | 7.01 | 3.11 | 0 | 26.6953 | 138.61 | 46.3368 | 0 | 476 | 645.472 | 72.9462 | 4.4597 | 640.901 | 68.2659 | 0.023278 | 626.533 | 65.7394 | 0.017541 | 671.521 | 671.501 | 1508020 | 24.1482 | 1485980 | 1490480 | 1429290 | 0 | 0 | 1414180 | 725.506 | 0 | 0 | 0 | 0 | 1414180 | 725.506 | 1389600 | 1361803.625
731 | 1998-01-31 10:00 | 604 | 981 | 62 | 7.19 | 3.11 | 0 | 33.6601 | 153.108 | 35.3078 | 0 | 604 | 798 | 79.8645 | 5.659 | 798 | 74.7402 | 0.029538 | 789.007 | 71.9741 | 0.022258 | 835.173 | 835.17 | 1875580 | 28.5054 | 1870350 | 1842590 | 1792590 | 0 | 0 | 1769210 | 728.808 | 0 | 0 | 0 | 0 | 1769210 | 728.808 | 1734730 | 1700036.75
732 | 1998-01-31 11:00 | 672 | 946 | 97 | 8.43 | 3.11 | 0 | 37.5931 | 170.077 | 28.0242 | 0 | 672 | 832.033 | 121.652 | 6.2961 | 832.033 | 113.847 | 0.032864 | 826.507 | 109.633 | 0.024763 | 908.08 | 908.073 | 2039310 | 31.6061 | 2042490 | 1985920 | 1931960 | 0 | 0 | 1904230 | 720.537 | 0 | 0 | 0 | 0 | 1904230 | 720.537 | 1865510 | 1828199.5
733 | 1998-01-31 12:00 | 626 | 824 | 123 | 9.67 | 1.19 | 0 | 37.7919 | 188.199 | 27.6328 | 0 | 626 | 727.203 | 159.42 | 5.8651 | 727.203 | 149.192 | 0.030614 | 722.521 | 143.67 | 0.023068 | 840.228 | 840.219 | 1886920 | 34.0453 | 1882260 | 1810460 | 1763470 | 0 | 0 | 1739580 | 709.604 | 0 | 0 | 0 | 0 | 1739580 | 709.604 | 1706460 | 1672326.125
734 | 1998-01-31 13:00 | 613 | 933 | 90 | 10.91 | 1.19 | 0 | 34.2164 | 205.371 | 34.3708 | 0 | 613 | 767.686 | 113.48 | 5.7433 | 767.686 | 106.199 | 0.029978 | 759.567 | 102.269 | 0.022589 | 836.003 | 835.999 | 1877450 | 35.1629 | 1872310 | 1792010 | 1744200 | 0 | 0 | 1720640 | 706.385 | 0 | 0 | 0 | 0 | 1720640 | 706.385 | 1688200 | 1654431.625
735 | 1998-01-31 14:00 | 479 | 932 | 49 | 10.85 | 1.19 | 0 | 27.5202 | 220.148 | 45.1494 | 0 | 479 | 656.324 | 64.158 | 4.4879 | 656.324 | 60.0415 | 0.023425 | 642.61 | 57.8194 | 0.017651 | 679.433 | 679.431 | 1525830 | 30.5607 | 1504220 | 1468400 | 1428410 | 0 | 0 | 1412980 | 716.683 | 0 | 0 | 0 | 0 | 1412980 | 716.683 | 1388760 | 1360981.25
736 | 1998-01-31 15:00 | 311 | 845 | 42 | 10.79 | 1.52 | 0 | 18.5936 | 232.343 | 57.7445 | 0 | 311 | 450.25 | 56.259 | 2.9138 | 450.25 | 52.6493 | 0.015209 | 430.58 | 50.7008 | 0.01146 | 466.854 | 466.85 | 1048430 | 24.0368 | 1010400 | 1014490 | 987663 | 0 | 0 | 980381 | 724.042 | 0 | 0 | 0 | 0 | 980381 | 724.042 | 964497 | 945206.625
737 | 1998-01-31 16:00 | 97 | 282 | 56 | 10.73 | 1.52 | 0 | 8.1902 | 242.48 | 71.1921 | 0 | 97 | 92.7855 | 74.277 | 0.90881 | 71.6508 | 69.5112 | 0.0047437 | 64.1211 | 66.9387 | 0.0035745 | 127.131 | 127.112 | 285461 | 14.3368 | 251447 | 264071 | 242510 | 0 | 0 | 242024 | 704.349 | 0 | 0 | 0 | 0 | 242024 | 704.349 | 235433 | 230724.0781
738 | 1998-01-31 17:00 | 2 | 35 | 1 | 10.49 | 1.52 | 0 | -3.1584 | 251.243 | 85.0805 | 0 | 2 | 0.98571 | 1.1177 | 0.018738 | 0 | 1.046 | 0 | 0 | 1.0073 | 0 | 0.97706 | 0.97702 | 2194.14 | 10.5177 | 233.12 | 229.145 | 228.084 | 0 | 0 | 228.074 | 144.146 | 0 | 0 | 0 | 228.074 | 0 | 660 | 0 | 0
739 | 1998-01-31 18:00 | 0 | 0 | 0 | 10.26 | 3.05 | 0
740 | 1998-01-31 19:00 | 0 | 0 | 0 | 10.02 | 3.05 | 0
741 | 1998-01-31 20:00 | 0 | 0 | 0 | 9.71 | 3.05 | 0
742 | 1998-01-31 21:00 | 0 | 0 | 0 | 11.21 | 4.02 | 0
743 | 1998-01-31 22:00 | 0 | 0 | 0 | 12.22 | 4.5 | 0
744 | 1998-01-31 23:00 | 0 | 0 | 0 | 13.22 | 4.97 | 0
745 | 2003-02-01 | 0 | 0 | 0 | 14.22 | 5.44 | 0
746 | 2003-02-01 01:00 | 0 | 0 | 0 | 15.22 | 5.91 | 0
747 | 2003-02-01 02:00 | 0 | 0 | 0 | 16.23 | 6.39 | 0
748 | 2003-02-01 03:00 | 0 | 0 | 0 | 16.73 | 6.36 | 0
749 | 2003-02-01 04:00 | 0 | 0 | 0 | 16.35 | 6.36 | 0
750 | 2003-02-01 05:00 | 0 | 0 | 0 | 15.98 | 6.36 | 0
751 | 2003-02-01 06:00 | 1 | 39 | 0 | 15.62 | 8.57 | 0 | -4.2543 | 107.875 | 86.4381 | 0 | 1 | 0.7141 | 0 | 0.0093692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.62 | 0 | 0 | 0 | 0 | 0 | 0 | 660 | 0 | 0 | 0 | 0 | 0 | 660 | 0 | 0
752 | 2003-02-01 07:00 | 105 | 470 | 45 | 15.25 | 8.57 | 0 | 7.1863 | 116.524 | 72.5049 | 0 | 105 | 144.19 | 61.6271 | 0.98377 | 24.4846 | 57.673 | 0.0051349 | 21.6366 | 55.5385 | 0.0038693 | 74.8636 | 74.8737 | 168153 | 16.5943 | 142135 | 147766 | 128598 | 0 | 0 | 128421 | 662.758 | 0 | 0 | 0 | 41.6313 | 128379 | 664.909 | 124468 | 121978.9062
753 | 2003-02-01 08:00 | 260 | 541 | 95 | 16.52 | 8.57 | 0 | 17.729 | 126.485 | 58.9794 | 0 | 260 | 279.237 | 121.619 | 2.436 | 239.864 | 113.816 | 0.012715 | 228.585 | 109.604 | 0.0095811 | 328.052 | 328.045 | 736683 | 22.4099 | 696039 | 702657 | 642750 | 0 | 0 | 639335 | 701.455 | 0 | 0 | 0 | 1211.62 | 638123 | 707.616 | 628210 | 615646.125
754 | 2003-02-01 09:00 | 343 | 334 | 192 | 17.79 | 6.47 | 0 | 26.8628 | 138.447 | 46.2386 | 0 | 343 | 231.136 | 220.064 | 3.2136 | 229.729 | 205.944 | 0.016774 | 224.608 | 198.322 | 0.01264 | 410.255 | 410.237 | 921288 | 26.202 | 880700 | 875878 | 843290 | 0 | 0 | 837748 | 709.012 | 0 | 0 | 0 | 0 | 837748 | 709.012 | 824805 | 808308.5625
755 | 2003-02-01 10:00 | 462 | 465 | 204 | 19.05 | 6.47 | 0 | 33.854 | 152.979 | 35.1607 | 0 | 462 | 378.628 | 247.367 | 4.3286 | 378.628 | 231.495 | 0.022594 | 374.402 | 222.928 | 0.017025 | 579.427 | 579.415 | 1301220 | 30.9311 | 1270790 | 1238190 | 1206370 | 0 | 0 | 1195060 | 708.281 | 0 | 0 | 0 | 0 | 1195060 | 708.281 | 1175810 | 1152292.125
756 | 2003-02-01 11:00 | 514 | 452 | 238 | 20.5 | 6.47 | 0 | 37.8079 | 170.006 | 27.8207 | 0 | 514 | 398.192 | 287.582 | 4.8158 | 398.192 | 269.13 | 0.025137 | 395.59 | 259.169 | 0.018941 | 635.135 | 635.129 | 1426340 | 33.5235 | 1400630 | 1349330 | 1313840 | 0 | 0 | 1300230 | 702.644 | 0 | 0 | 0 | 0 | 1300230 | 702.644 | 1279040 | 1253464
757 | 2003-02-01 12:00 | 576 | 646 | 179 | 21.95 | 7.9 | 0 | 38.014 | 188.205 | 27.4132 | 0 | 576 | 572.247 | 227.365 | 5.3967 | 572.247 | 212.776 | 0.028169 | 568.627 | 204.902 | 0.021226 | 750.344 | 750.331 | 1685050 | 36 | 1670570 | 1592530 | 1550670 | 0 | 0 | 1531670 | 700.325 | 0 | 0 | 0 | 0 | 1531670 | 700.325 | 1505240 | 1475130.875
758 | 2003-02-01 13:00 | 496 | 589 | 164 | 23.4 | 7.9 | 0 | 34.4303 | 205.444 | 34.1876 | 0 | 496 | 485.726 | 208.267 | 4.6471 | 485.726 | 194.904 | 0.024257 | 480.652 | 187.691 | 0.018278 | 648.31 | 648.302 | 1455920 | 35.5395 | 1431390 | 1366620 | 1333000 | 0 | 0 | 1318750 | 696.093 | 0 | 0 | 0 | 0 | 1318750 | 696.093 | 1297460 | 1271511.625
759 | 2003-02-01 14:00 | 391 | 566 | 128 | 22.95 | 7.9 | 0 | 27.7168 | 220.265 | 45.008 | 0 | 391 | 399.79 | 164.349 | 3.6634 | 399.79 | 153.804 | 0.019121 | 391.506 | 148.112 | 0.014408 | 523.443 | 523.437 | 1175510 | 32.7514 | 1140940 | 1102390 | 1074140 | 0 | 0 | 1064920 | 699.281 | 0 | 0 | 0 | 0 | 1064920 | 699.281 | 1048710 | 1027735.3125
760 | 2003-02-01 15:00 | 231 | 421 | 96 | 22.5 | 12.76 | 0 | 18.771 | 232.485 | 57.6349 | 0 | 231 | 224.581 | 120.008 | 2.1643 | 224.581 | 112.309 | 0.011297 | 214.833 | 108.152 | 0.0085124 | 313.304 | 313.295 | 703582 | 26.8616 | 660803 | 655197 | 638541 | 0 | 0 | 635275 | 700.305 | 0 | 0 | 0 | 0 | 635275 | 700.305 | 625736 | 613221.4375
761 | 2003-02-01 16:00 | 118 | 322 | 71 | 22.05 | 12.76 | 0 | 8.3504 | 242.636 | 71.1064 | 0 | 118 | 104.796 | 90.4223 | 1.1056 | 80.9253 | 84.6207 | 0.0057707 | 72.4759 | 81.4889 | 0.0043483 | 149.35 | 149.32 | 335335 | 24.1288 | 299219 | 300233 | 277060 | 0 | 0 | 276380 | 678.338 | 0 | 0 | 0 | 0 | 276380 | 678.338 | 270043 | 264642.3438
762 | 2003-02-01 17:00 | 3 | 42 | 2 | 20.59 | 12.76 | 0 | -3.0118 | 251.411 | 85.0137 | 0 | 3 | 0.99906 | 2.1014 | 0.028108 | 0 | 1.9666 | 0 | 0 | 1.8938 | 0 | 1.837 | 1.8369 | 4125.11 | 20.6156 | 819.19 | 815.626 | 811.52 | 0 | 0 | 811.484 | 272.687 | 0 | 0 | 0 | 811.484 | 0 | 660 | 0 | 0
763 | 2003-02-01 18:00 | 0 | 0 | 0 | 19.12 | 10.59 | 0
764 | 2003-02-01 19:00 | 0 | 0 | 0 | 17.66 | 10.59 | 0
765 | 2003-02-01 20:00 | 0 | 0 | 0 | 16.3 | 10.59 | 0
766 | 2003-02-01 21:00 | 0 | 0 | 0 | 14.95 | 10.15 | 0
767 | 2003-02-01 22:00 | 0 | 0 | 0 | 13.59 | 10.15 | 0
768 | 2003-02-01 23:00 | 0 | 0 | 0 | 12.48 | 10.15 | 0
769 | 2003-02-02 | 0 | 0 | 0 | 11.37 | 11.12 | 0
770 | 2003-02-02 01:00 | 0 | 0 | 0 | 10.26 | 11.12 | 0
771 | 2003-02-02 02:00 | 0 | 0 | 0 | 9.18 | 11.12 | 0
772 | 2003-02-02 03:00 | 0 | 0 | 0 | 8.11 | 11.87 | 0
773 | 2003-02-02 04:00 | 0 | 0 | 0 | 7.03 | 11.87 | 0
774 | 2003-02-02 05:00 | 0 | 0 | 0 | 6.46 | 11.87 | 0
775 | 2003-02-02 06:00 | 1 | 51 | 0 | 5.88 | 5.97 | 0 | -4.1153 | 107.621 | 86.4129 | 0 | 1 | 0.71915 | 0 | 0.0093692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.88 | 0 | 0 | 0 | 0 | 0 | 0 | 660 | 0 | 0 | 0 | 0 | 0 | 660 | 0 | 0
776 | 2003-02-02 07:00 | 104 | 575 | 29 | 5.31 | 5.97 | 0 | 7.3454 | 116.282 | 72.4544 | 0 | 104 | 176.845 | 43.2112 | 0.9744 | 31.8418 | 40.4387 | 0.005086 | 28.1527 | 38.942 | 0.0038324 | 65.0856 | 65.0741 | 146146 | 6.6879 | 123071 | 133539 | 109735 | 0 | 0 | 109582 | 665.468 | 0 | 0 | 0 | 602.611 | 108979 | 675.182 | 105455 | 103345.7812
777 | 2003-02-02 08:00 | 290 | 768 | 54 | 6.77 | 5.97 | 0 | 17.915 | 126.253 | 58.8966 | 0 | 290 | 396.332 | 74.177 | 2.7171 | 341.98 | 69.4177 | 0.014182 | 325.979 | 66.8485 | 0.010687 | 381.053 | 380.925 | 855426 | 14.8358 | 817616 | 850648 | 767728 | 0 | 0 | 763072 | 724.846 | 0 | 0 | 0 | 672.857 | 762399 | 727.304 | 749851 | 734854.3125
778 | 2003-02-02 09:00 | 446 | 815 | 76 | 8.24 | 6.27 | 0 | 27.0813 | 138.235 | 46.1111 | 0 | 446 | 563.437 | 101.892 | 4.1787 | 560.66 | 95.3542 | 0.021811 | 548.256 | 91.8252 | 0.016435 | 620.895 | 620.857 | 1394280 | 21.1351 | 1367480 | 1389430 | 1334720 | 0 | 0 | 1322040 | 739.455 | 0 | 0 | 0 | 0 | 1322040 | 739.455 | 1298710 | 1272732.5
779 | 2003-02-02 10:00 | 561 | 831 | 96 | 9.7 | 6.27 | 0 | 34.1068 | 152.809 | 34.9696 | 0 | 561 | 679.546 | 126.992 | 5.2561 | 679.546 | 118.844 | 0.027435 | 672.06 | 114.446 | 0.020673 | 762.93 | 762.929 | 1713340 | 25.5459 | 1700190 | 1696010 | 1649340 | 0 | 0 | 1629850 | 735.336 | 0 | 0 | 0 | 0 | 1629850 | 735.336 | 1599390 | 1567398.75
780 | 2003-02-02 11:00 | 671 | 930 | 99 | 10.52 | 6.27 | 0 | 38.088 | 169.913 | 27.5557 | 0 | 671 | 822.073 | 123.69 | 6.2867 | 822.073 | 115.753 | 0.032815 | 816.814 | 111.469 | 0.024727 | 900.459 | 900.451 | 2022180 | 29.2223 | 2024470 | 1988610 | 1934820 | 0 | 0 | 1907530 | 728.145 | 0 | 0 | 0 | 0 | 1907530 | 728.145 | 1868630 | 1831260.625
781 | 2003-02-02 12:00 | 657 | 953 | 68 | 11.34 | 6.59 | 0 | 38.3036 | 188.212 | 27.1268 | 0 | 657 | 845.733 | 86.7388 | 6.1556 | 845.733 | 81.1735 | 0.03213 | 840.506 | 78.1693 | 0.024211 | 891.139 | 891.136 | 2001260 | 29.4733 | 2002460 | 1964900 | 1914690 | 0 | 0 | 1887810 | 725.414 | 0 | 0 | 0 | 0 | 1887810 | 725.414 | 1849590 | 1812596.125
782 | 2003-02-02 13:00 | 599 | 946 | 62 | 12.16 | 6.59 | 0 | 34.7092 | 205.54 | 33.9496 | 0 | 599 | 782.312 | 79.5914 | 5.6122 | 782.312 | 74.4847 | 0.029294 | 774.274 | 71.7281 | 0.022073 | 820.643 | 820.638 | 1842950 | 28.8587 | 1836080 | 1806180 | 1759600 | 0 | 0 | 1736790 | 724.971 | 0 | 0 | 0 | 0 | 1736790 | 724.971 | 1703400 | 1669332.875
783 | 2003-02-02 14:00 | 484 | 918 | 54 | 12.32 | 6.59 | 0 | 27.9729 | 220.419 | 44.8247 | 0 | 484 | 650.212 | 70.1589 | 4.5347 | 650.212 | 65.6574 | 0.02367 | 636.886 | 63.2275 | 0.017836 | 679.127 | 679.124 | 1525140 | 26.1391 | 1503510 | 1496040 | 1455080 | 0 | 0 | 1439710 | 731.663 | 0 | 0 | 0 | 0 | 1439710 | 731.663 | 1414300 | 1386016.25
784 | 2003-02-02 15:00 | 328 | 847 | 52 | 12.48 | 5.66 | 0 | 19.0019 | 232.671 | 57.493 | 0 | 328 | 455.538 | 68.4375 | 3.0731 | 455.538 | 64.0464 | 0.016041 | 435.932 | 61.6761 | 0.012087 | 482.691 | 482.685 | 1083980 | 22.9068 | 1046840 | 1056220 | 1027300 | 0 | 0 | 1019560 | 730.353 | 0 | 0 | 0 | 0 | 1019560 | 730.353 | 1002670 | 982618.375
785 | 2003-02-02 16:00 | 123 | 556 | 39 | 12.64 | 5.66 | 0 | 8.559 | 242.841 | 70.9953 | 0 | 123 | 183.799 | 53.9647 | 1.1524 | 141.933 | 50.5022 | 0.0060152 | 127.237 | 48.6332 | 0.0045326 | 170.599 | 170.527 | 382958 | 16.3237 | 346692 | 359816 | 319549 | 0 | 0 | 318684 | 710.016 | 0 | 0 | 0 | 0 | 318684 | 710.016 | 311396 | 305168.125
786 | 2003-02-02 17:00 | 4 | 78 | 2 | 12.21 | 5.66 | 0 | -2.8209 | 251.63 | 84.927 | 0 | 4 | 2.0327 | 2.2382 | 0.037477 | 0 | 2.0946 | 0 | 0 | 2.017 | 0 | 1.9565 | 1.9564 | 4393.63 | 12.2523 | 928.079 | 916.223 | 911.611 | 0 | 0 | 911.571 | 289.61 | 0 | 0 | 0 | 911.571 | 0 | 660 | 0 | 0
787 | 2003-02-02 18:00 | 0 | 0 | 0 | 11.78 | 7.24 | 0
788 | 2003-02-02 19:00 | 0 | 0 | 0 | 11.35 | 7.24 | 0
789 | 2003-02-02 20:00 | 0 | 0 | 0 | 10.66 | 7.24 | 0
790 | 2003-02-02 21:00 | 0 | 0 | 0 | 9.98 | 8.19 | 0
791 | 2003-02-02 22:00 | 0 | 0 | 0 | 9.29 | 8.19 | 0
792 | 2003-02-02 23:00 | 0 | 0 | 0 | 8.58 | 8.19 | 0
793 | 2003-02-03 | 0 | 0 | 0 | 7.86 | 11.33 | 0
794 | 2003-02-03 01:00 | 0 | 0 | 0 | 7.14 | 11.33 | 0
795 | 2003-02-03 02:00 | 0 | 0 | 0 | 6.66 | 11.33 | 0
796 | 2003-02-03 03:00 | 0 | 0 | 0 | 6.18 | 7.24 | 0
797 | 2003-02-03 04:00 | 0 | 0 | 0 | 5.7 | 7.24 | 0
798 | 2003-02-03 05:00 | 0 | 0 | 0 | 5.41 | 7.24 | 0
799 | 2003-02-03 06:00 | 2 | 56 | 1 | 5.12 | 7.98 | 0 | -3.9709 | 107.366 | 86.3837 | 0 | 2 | 0.72499 | 1.0078 | 0.018738 | 0 | 0.94311 | 0 | 0 | 0.90821 | 0 | 0.88096 | 0.8809 | 1978.28 | 5.1364 | 189.593 | 185.144 | 184.202 | 0 | 0 | 184.194 | 131.239 | 0 | 0 | 0 | 184.194 | 0 | 660 | 0 | 0
800 | 2003-02-03 07:00 | 109 | 589 | 31 | 4.83 | 7.98 | 0 | 7.51 | 116.037 | 72.3999 | 0 | 109 | 180.451 | 45.2143 | 1.0212 | 35.8443 | 42.3133 | 0.0053305 | 31.7093 | 40.7473 | 0.0040167 | 70.2868 | 70.2937 | 157875 | 6.1396 | 134032 | 145767 | 119865 | 0 | 0 | 119683 | 663.223 | 0 | 0 | 0 | 574.354 | 119108 | 675.054 | 115336 | 113028.9531
801 | 2003-02-03 08:00 | 302 | 822 | 47 | 5.88 | 7.98 | 0 | 18.1064 | 126.019 | 58.8098 | 0 | 302 | 424.927 | 62.2826 | 2.8295 | 368.337 | 58.2865 | 0.014769 | 351.192 | 56.1293 | 0.011129 | 395.113 | 395.067 | 887190 | 13.2405 | 850223 | 890449 | 802761 | 0 | 0 | 797809 | 736.743 | 0 | 0 | 0 | 803.896 | 797005 | 741.47 | 783366 | 767698.625
802 | 2003-02-03 09:00 | 464 | 890 | 56 | 6.93 | 6.1 | 0 | 27.3052 | 138.021 | 45.9795 | 0 | 464 | 618.066 | 72.5821 | 4.3473 | 615.587 | 67.9251 | 0.022691 | 602.074 | 65.4112 | 0.017098 | 647.477 | 647.443 | 1453990 | 20.525 | 1429560 | 1456100 | 1401480 | 0 | 0 | 1387660 | 743.309 | 0 | 0 | 0 | 0 | 1387660 | 743.309 | 1362750 | 1335494
803 | 2003-02-03 10:00 | 584 | 918 | 67 | 7.98 | 6.1 | 0 | 34.3652 | 152.64 | 34.774 | 0 | 584 | 752.337 | 85.6084 | 5.4716 | 752.337 | 80.1156 | 0.02856 | 744.158 | 77.1506 | 0.021521 | 796.69 | 796.685 | 1789160 | 24.7087 | 1779640 | 1781500 | 1733090 | 0 | 0 | 1711830 | 739.886 | 0 | 0 | 0 | 0 | 1711830 | 739.886 | 1678800 | 1645224.5
804 | 2003-02-03 11:00 | 658 | 951 | 69 | 8.85 | 6.1 | 0 | 38.3734 | 169.823 | 27.2855 | 0 | 658 | 843.231 | 87.8369 | 6.165 | 843.231 | 82.2012 | 0.032179 | 837.953 | 79.159 | 0.024248 | 889.622 | 889.618 | 1997850 | 27.5301 | 1998870 | 1977520 | 1923940 | 0 | 0 | 1897310 | 732.594 | 0 | 0 | 0 | 0 | 1897310 | 732.594 | 1858710 | 1821533.625
805 | 2003-02-03 12:00 | 689 | 993 | 71 | 9.72 | 7.16 | 0 | 38.5977 | 188.224 | 26.8367 | 0 | 689 | 883.932 | 90.2475 | 6.4554 | 883.932 | 84.457 | 0.033695 | 878.598 | 81.3314 | 0.02539 | 931.156 | 931.153 | 2091130 | 27.9915 | 2097040 | 2070710 | 2014730 | 0 | 0 | 1985530 | 732.47 | 0 | 0 | 0 | 0 | 1985530 | 732.47 | 1944020 | 1905139.625
806 | 2003-02-03 13:00 | 626 | 977 | 67 | 10.59 | 7.16 | 0 | 34.9913 | 205.642 | 33.7107 | 0 | 626 | 810.887 | 85.5618 | 5.8651 | 810.887 | 80.072 | 0.030614 | 802.692 | 77.1086 | 0.023068 | 853.429 | 853.423 | 1916570 | 27.3363 | 1913400 | 1894480 | 1841390 | 0 | 0 | 1816910 | 731.458 | 0 | 0 | 0 | 0 | 1816910 | 731.458 | 1780900 | 1745278.625
807 | 2003-02-03 14:00 | 489 | 921 | 54 | 11.21 | 7.16 | 0 | 28.2311 | 220.58 | 44.6422 | 0 | 489 | 654.306 | 70.0297 | 4.5816 | 654.306 | 65.5365 | 0.023914 | 641.041 | 63.111 | 0.01802 | 683.045 | 683.043 | 1533950 | 24.613 | 1512690 | 1514930 | 1471090 | 0 | 0 | 1455600 | 736.911 | 0 | 0 | 0 | 0 | 1455600 | 736.911 | 1429650 | 1401053.25
808 | 2003-02-03 15:00 | 317 | 828 | 44 | 11.83 | 1.23 | 0 | 19.2341 | 232.863 | 57.3527 | 0 | 317 | 447.06 | 58.3835 | 2.97 | 447.06 | 54.6375 | 0.015503 | 427.978 | 52.6154 | 0.011681 | 466.187 | 466.186 | 1046940 | 25.318 | 1008870 | 1007320 | 981820 | 0 | 0 | 974526 | 719.257 | 0 | 0 | 0 | 0 | 974526 | 719.257 | 958970 | 939790.4375
809 | 2003-02-03 16:00 | 124 | 551 | 39 | 12.45 | 1.23 | 0 | 8.7681 | 243.051 | 70.8862 | 0 | 124 | 182.587 | 53.967 | 1.1618 | 140.997 | 50.5044 | 0.0060641 | 126.517 | 48.6353 | 0.0045694 | 169.902 | 169.896 | 381542 | 17.3656 | 345310 | 356384 | 317142 | 0 | 0 | 316282 | 706.454 | 0 | 0 | 0 | 0 | 316282 | 706.454 | 309092 | 302910.5938
810 | 2003-02-03 17:00 | 4 | 82 | 1 | 12 | 1.23 | 0 | -2.6297 | 251.855 | 84.8426 | 0 | 4 | 3.0997 | 1.1957 | 0.037477 | 0 | 1.119 | 0 | 0 | 1.0776 | 0 | 1.0453 | 1.0452 | 2347.28 | 12.0302 | 266.692 | 262.633 | 261.433 | 0 | 0 | 261.421 | 154.098 | 0 | 0 | 0 | 261.421 | 0 | 660 | 0 | 0
811 | 2003-02-03 18:00 | 0 | 0 | 0 | 11.54 | 0.29 | 0
812 | 2003-02-03 19:00 | 0 | 0 | 0 | 11.09 | 0.29 | 0
813 | 2003-02-03 20:00 | 0 | 0 | 0 | 10.77 | 0.29 | 0
814 | 2003-02-03 21:00 | 0 | 0 | 0 | 10.44 | 0.84 | 0
815 | 2003-02-03 22:00 | 0 | 0 | 0 | 10.12 | 0.84 | 0
816 | 2003-02-03 23:00 | 0 | 0 | 0 | 9.32 | 0.84 | 0
817 | 2003-02-04 | 0 | 0 | 0 | 8.53 | 2.55 | 0
818 | 2003-02-04 01:00 | 0 | 0 | 0 | 7.73 | 2.55 | 0
819 | 2003-02-04 02:00 | 0 | 0 | 0 | 7.43 | 2.55 | 0
820 | 2003-02-04 03:00 | 0 | 0 | 0 | 7.13 | 2.1 | 0
821 | 2003-02-04 04:00 | 0 | 0 | 0 | 6.83 | 2.1 | 0
822 | 2003-02-04 05:00 | 0 | 0 | 0 | 6.13 | 2.1 | 0
823 | 2003-02-04 06:00 | 2 | 60 | 1 | 5.43 | 3.3 | 0 | -3.821 | 107.108 | 86.3506 | 0 | 2 | 0.73162 | 1.0103 | 0.018738 | 0 | 0.94545 | 0 | 0 | 0.91046 | 0 | 0.88314 | 0.88308 | 1983.16 | 5.4523 | 190.529 | 186.129 | 185.235 | 0 | 0 | 185.227 | 130.643 | 0 | 0 | 0 | 185.227 | 0 | 660 | 0 | 0
824 | 2003-02-04 07:00 | 111 | 591 | 31 | 4.72 | 3.3 | 0 | 7.68 | 115.79 | 72.3416 | 0 | 111 | 181.587 | 45.1171 | 1.04 | 38.5053 | 42.2223 | 0.0054284 | 34.0837 | 40.6597 | 0.0040904 | 72.505 | 72.56 | 162965 | 6.5488 | 138841 | 150430 | 122439 | 0 | 0 | 122254 | 671.063 | 0 | 0 | 0 | 36.8308 | 122217 | 674.759 | 118375 | 116007.4297
825 | 2003-02-04 08:00 | 315 | 838 | 52 | 5.98 | 3.3 | 0 | 18.3031 | 125.784 | 58.7191 | 0 | 315 | 434.839 | 68.2692 | 2.9513 | 378.601 | 63.8889 | 0.015405 | 361.073 | 61.5244 | 0.011608 | 409.931 | 409.852 | 920398 | 16.3098 | 883853 | 912829 | 828708 | 0 | 0 | 823432 | 734.888 | 0 | 0 | 0 | 0 | 823432 | 734.888 | 809570 | 793378.5625
826 | 2003-02-04 09:00 | 469 | 854 | 75 | 7.23 | 3.71 | 0 | 27.5345 | 137.807 | 45.8439 | 0 | 469 | 593.72 | 100.399 | 4.3942 | 591.826 | 93.9574 | 0.022936 | 578.939 | 90.4801 | 0.017283 | 649.353 | 649.325 | 1458210 | 23.1588 | 1433910 | 1444610 | 1397070 | 0 | 0 | 1383030 | 735.318 | 0 | 0 | 0 | 0 | 1383030 | 735.318 | 1358650 | 1331477
827 | 2003-02-04 10:00 | 573 | 843 | 95 | 8.48 | 3.71 | 0 | 34.6289 | 152.471 | 34.5739 | 0 | 573 | 692.612 | 125.502 | 5.3686 | 692.612 | 117.45 | 0.028022 | 685.184 | 113.103 | 0.021115 | 774.359 | 774.348 | 1738980 | 27.4757 | 1727050 | 1708790 | 1662040 | 0 | 0 | 1641910 | 729.581 | 0 | 0 | 0 | 0 | 1641910 | 729.581 | 1611260 | 1579038.5
828 | 2003-02-04 11:00 | 665 | 912 | 97 | 10.28 | 3.71 | 0 | 38.6639 | 169.735 | 27.0102 | 0 | 665 | 809.997 | 121.015 | 6.2305 | 809.997 | 113.25 | 0.032521 | 805.038 | 109.059 | 0.024505 | 886.698 | 886.695 | 1991280 | 32.0317 | 1991960 | 1933180 | 1879920 | 0 | 0 | 1853490 | 718.384 | 0 | 0 | 0 | 0 | 1853490 | 718.384 | 1816490 | 1780156
829 | 2003-02-04 12:00 | 694 | 994 | 72 | 12.08 | 2.68 | 0 | 38.8961 | 188.241 | 26.5428 | 0 | 694 | 886.181 | 91.3175 | 6.5022 | 886.181 | 85.4584 | 0.033939 | 880.961 | 82.2957 | 0.025574 | 934.383 | 934.38 | 2098370 | 36.6173 | 2104670 | 2002270 | 1950310 | 0 | 0 | 1920690 | 703.282 | 0 | 0 | 0 | 0 | 1920690 | 703.282 | 1881550 | 1843917.125
830 | 2003-02-04 13:00 | 631 | 977 | 68 | 13.89 | 2.68 | 0 | 35.2765 | 205.751 | 33.4711 | 0 | 631 | 813.188 | 86.6367 | 5.912 | 813.188 | 81.0779 | 0.030859 | 805.104 | 78.0772 | 0.023252 | 856.709 | 856.706 | 1923940 | 36.3875 | 1921150 | 1828990 | 1782230 | 0 | 0 | 1757360 | 702.278 | 0 | 0 | 0 | 0 | 1757360 | 702.278 | 1723820 | 1689341.875
831 | 2003-02-04 14:00 | 509 | 937 | 63 | 14.8 | 2.68 | 0 | 28.4913 | 220.747 | 44.4608 | 0 | 509 | 667.309 | 80.9095 | 4.7689 | 667.309 | 75.7182 | 0.024892 | 653.926 | 72.9159 | 0.018757 | 705.055 | 705.049 | 1583360 | 33.3149 | 1564250 | 1508760 | 1470270 | 0 | 0 | 1453470 | 706.714 | 0 | 0 | 0 | 0 | 1453470 | 706.714 | 1428760 | 1400188
832 | 2003-02-04 15:00 | 337 | 852 | 53 | 15.71 | 3.56 | 0 | 19.4673 | 233.062 | 57.2143 | 0 | 337 | 461.447 | 69.3443 | 3.1574 | 461.447 | 64.895 | 0.016481 | 441.911 | 62.4933 | 0.012419 | 489.285 | 489.286 | 1098810 | 27.832 | 1062060 | 1048820 | 1019900 | 0 | 0 | 1011930 | 715.087 | 0 | 0 | 0 | 0 | 1011930 | 715.087 | 995952 | 976033.25
833 | 2003-02-04 16:00 | 131 | 569 | 41 | 16.62 | 3.56 | 0 | 8.9778 | 243.267 | 70.7794 | 0 | 131 | 189.865 | 55.8773 | 1.2274 | 146.617 | 52.2921 | 0.0064064 | 131.68 | 50.3568 | 0.0048274 | 176.58 | 176.465 | 396293 | 20.9919 | 359689 | 365244 | 326138 | 0 | 0 | 325195 | 694.13 | 0 | 0 | 0 | 0 | 325195 | 694.13 | 318304 | 311937.625
834 | 2003-02-04 17:00 | 5 | 89 | 2 | 15.87 | 3.56 | 0 | -2.4383 | 252.086 | 84.7605 | 0 | 5 | 3.1489 | 2.2647 | 0.046846 | 0 | 2.1194 | 0 | 0 | 2.041 | 0 | 1.9797 | 1.9796 | 4445.63 | 15.919 | 949.867 | 941.591 | 936.736 | 0 | 0 | 936.696 | 293.429 | 0 | 0 | 0 | 936.696 | 0 | 660 | 0 | 0
835 | 2003-02-04 18:00 | 0 | 0 | 0 | 15.11 | 5.22 | 0
836 | 2003-02-04 19:00 | 0 | 0 | 0 | 14.35 | 5.22 | 0
837 | 2003-02-04 20:00 | 0 | 0 | 0 | 13.36 | 5.22 | 0
838 | 2003-02-04 21:00 | 0 | 0 | 0 | 12.37 | 9.61 | 0
839 | 2003-02-04 22:00 | 0 | 0 | 0 | 11.38 | 9.61 | 0
840 | 2003-02-04 23:00 | 0 | 0 | 0 | 10.27 | 9.61 | 0
841 | 2003-02-05 | 0 | 0 | 0 | 9.16 | 6.65 | 0
842 | 2003-02-05 01:00 | 0 | 0 | 0 | 8.04 | 6.65 | 0
843 | 2003-02-05 02:00 | 0 | 0 | 0 | 7.28 | 6.65 | 0
844 | 2003-02-05 03:00 | 0 | 0 | 0 | 6.51 | 4.93 | 0
845 | 2003-02-05 04:00 | 0 | 0 | 0 | 5.74 | 4.93 | 0
846 | 2003-02-05 05:00 | 0 | 0 | 0 | 4.77 | 4.93 | 0
847 | 2003-02-05 06:00 | 2 | 63 | 1 | 3.79 | 10.28 | 0 | -3.6658 | 106.848 | 86.3136 | 0 | 2 | 0.73903 | 1.0131 | 0.018738 | 0 | 0.9481 | 0 | 0 | 0.91301 | 0 | 0.88562 | 0.88557 | 1988.75 | 3.8043 | 191.6 | 186.802 | 185.856 | 0 | 0 | 185.848 | 131.756 | 0 | 0 | 0 | 185.848 | 0 | 660 | 0 | 0
848 | 2003-02-05 07:00 | 110 | 578 | 30 | 2.82 | 10.28 | 0 | 7.8552 | 115.542 | 72.2794 | 0 | 110 | 178.166 | 43.9328 | 1.0306 | 42.0164 | 41.114 | 0.0053795 | 37.2151 | 39.5924 | 0.0040535 | 74.5072 | 74.4897 | 167301 | 4.0233 | 143057 | 156980 | 125553 | 0 | 0 | 125358 | 665.274 | 0 | 0 | 0 | 477.5 | 124880 | 678.554 | 120936 | 118517.5859
849 | 2003-02-05 08:00 | 308 | 822 | 47 | 3.75 | 10.28 | 0 | 18.5051 | 125.547 | 58.6245 | 0 | 308 | 428.143 | 61.9817 | 2.8857 | 374.436 | 58.0048 | 0.015062 | 357.199 | 55.8581 | 0.01135 | 400.676 | 400.59 | 899612 | 10.2213 | 862699 | 915132 | 831921 | 0 | 0 | 826842 | 751.997 | 0 | 0 | 0 | 0 | 826842 | 751.997 | 812260 | 796014.5625
850 | 2003-02-05 09:00 | 469 | 848 | 75 | 4.68 | 8.97 | 0 | 27.7692 | 137.591 | 45.7043 | 0 | 469 | 590.573 | 100.238 | 4.3942 | 589.118 | 93.8067 | 0.022936 | 576.395 | 90.335 | 0.017283 | 646.745 | 646.721 | 1452350 | 16.0057 | 1427770 | 1481430 | 1432020 | 0 | 0 | 1418180 | 759.339 | 0 | 0 | 0 | 0 | 1418180 | 759.339 | 1391640 | 1363805.125
851 | 2003-02-05 10:00 | 606 | 950 | 64 | 5.61 | 8.97 | 0 | 34.8979 | 152.302 | 34.3696 | 0 | 606 | 781.964 | 81.6874 | 5.6777 | 781.964 | 76.4462 | 0.029636 | 773.694 | 73.617 | 0.022331 | 821.913 | 821.909 | 1845800 | 20.0036 | 1839070 | 1876820 | 1822820 | 0 | 0 | 1800280 | 755.644 | 0 | 0 | 0 | 0 | 1800280 | 755.644 | 1763200 | 1727932.625
852 | 2003-02-05 11:00 | 674 | 965 | 69 | 6.34 | 8.97 | 0 | 38.9594 | 169.65 | 26.73 | 0 | 674 | 859.373 | 87.5632 | 6.3149 | 859.373 | 81.945 | 0.032961 | 854.232 | 78.9123 | 0.024837 | 905.174 | 905.168 | 2032770 | 22.1917 | 2035610 | 2058820 | 2001370 | 0 | 0 | 1973900 | 750.902 | 0 | 0 | 0 | 0 | 1973900 | 750.902 | 1931590 | 1892962.125
853 | 2003-02-05 12:00 | 695 | 992 | 70 | 7.08 | 10.01 | 0 | 39.1987 | 188.263 | 26.2453 | 0 | 695 | 886.958 | 88.7583 | 6.5116 | 886.958 | 83.0634 | 0.033988 | 881.861 | 79.9893 | 0.025611 | 933.019 | 933.017 | 2095320 | 22.4034 | 2101450 | 2123550 | 2062200 | 0 | 0 | 2033170 | 751.938 | 0 | 0 | 0 | 0 | 2033170 | 751.938 | 1988730 | 1948953.625
854 | 2003-02-05 13:00 | 637 | 978 | 70 | 7.81 | 10.01 | 0 | 35.5648 | 205.867 | 33.231 | 0 | 637 | 815.438 | 88.9131 | 5.9682 | 815.438 | 83.2083 | 0.031152 | 807.467 | 80.1288 | 0.023474 | 860.991 | 860.987 | 1933560 | 21.9504 | 1931260 | 1955310 | 1900170 | 0 | 0 | 1875380 | 750.459 | 0 | 0 | 0 | 0 | 1875380 | 750.459 | 1836380 | 1799649.75
855 | 2003-02-05 14:00 | 513 | 939 | 62 | 8.23 | 10.01 | 0 | 28.7533 | 220.922 | 44.2806 | 0 | 513 | 671.221 | 79.5513 | 4.8064 | 671.221 | 74.4471 | 0.025088 | 657.904 | 71.6919 | 0.018904 | 707.727 | 707.722 | 1589370 | 19.8533 | 1570530 | 1604170 | 1557940 | 0 | 0 | 1541290 | 752.643 | 0 | 0 | 0 | 0 | 1541290 | 752.643 | 1512260 | 1482019.5
856 | 2003-02-05 15:00 | 337 | 853 | 50 | 8.65 | 2.19 | 0 | 19.7014 | 233.267 | 57.0778 | 0 | 337 | 462.7 | 65.52 | 3.1574 | 462.7 | 61.3161 | 0.016481 | 443.268 | 59.0468 | 0.012419 | 487.257 | 487.254 | 1094250 | 21.8698 | 1057370 | 1071550 | 1042300 | 0 | 0 | 1034440 | 735.597 | 0 | 0 | 0 | 0 | 1034440 | 735.597 | 1017000 | 996660.5625
857 | 2003-02-05 16:00 | 132 | 576 | 39 | 9.07 | 2.19 | 0 | 9.1878 | 243.49 | 70.6747 | 0 | 132 | 192.749 | 53.9113 | 1.2367 | 156.162 | 50.4522 | 0.0064554 | 140.376 | 48.585 | 0.0048642 | 183.297 | 183.265 | 411567 | 14.0422 | 373647 | 391826 | 355084 | 0 | 0 | 354081 | 721.602 | 0 | 0 | 0 | 0 | 354081 | 721.602 | 346454 | 339524.9375
858 | 2003-02-05 17:00 | 5 | 95 | 2 | 8.52 | 2.19 | 0 | -2.2468 | 252.322 | 84.6808 | 0 | 5 | 3.1967 | 2.2776 | 0.046846 | 0 | 2.1314 | 0 | 0 | 2.0526 | 0 | 1.991 | 1.9909 | 4471.08 | 8.574 | 960.728 | 944.759 | 939.951 | 0 | 0 | 939.91 | 294.224 | 0 | 0 | 0 | 939.91 | 0 | 660 | 0 | 0
859 | 2003-02-05 18:00 | 0 | 0 | 0 | 7.97 | 3.84 | 0
860 | 2003-02-05 19:00 | 0 | 0 | 0 | 7.41 | 3.84 | 0
861 | 2003-02-05 20:00 | 0 | 0 | 0 | 6.92 | 3.84 | 0
862 | 2003-02-05 21:00 | 0 | 0 | 0 | 6.43 | 4.16 | 0
863 | 2003-02-05 22:00 | 0 | 0 | 0 | 5.94 | 4.16 | 0
864 | 2003-02-05 23:00 | 0 | 0 | 0 | 5.22 | 4.16 | 0
865 | 2003-02-06 | 0 | 0 | 0 | 4.51 | 4.65 | 0
866 | 2003-02-06 01:00 | 0 | 0 | 0 | 3.8 | 4.65 | 0
867 | 2003-02-06 02:00 | 0 | 0 | 0 | 3.08 | 4.65 | 0
868 | 2003-02-06 03:00 | 0 | 0 | 0 | 2.36 | 3.64 | 0
869 | 2003-02-06 04:00 | 0 | 0 | 0 | 1.65 | 3.64 | 0
870 | 2003-02-06 05:00 | 0 | 0 | 0 | 1.09 | 3.64 | 0
871 | 2003-02-06 06:00 | 2 | 71 | 0 | 0.52 | 3.75 | 0 | -3.5052 | 106.587 | 86.2727 | 0 | 2 | 1.4944 | 0 | 0.018738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.52 | 0 | 0 | 0 | 0 | 0 | 0 | 660 | 0 | 0 | 0 | 0 | 0 | 660 | 0 | 0
872 | 2003-02-06 07:00 | 120 | 612 | 33 | -0.04 | 3.75 | 0 | 8.0357 | 115.292 | 72.2134 | 0 | 120 | 190.115 | 47.0057 | 1.1243 | 47.8527 | 43.9898 | 0.0058685 | 42.4128 | 42.3617 | 0.004422 | 82.2355 | 82.1794 | 184568 | 1.9707 | 159299 | 175783 | 140993 | 0 | 0 | 140762 | 680.474 | 0 | 0 | 0 | 1396.15 | 139366 | 693.405 | 134909 | 132210.3594
873 | 2003-02-06 08:00 | 304 | 802 | 47 | 1.37 | 3.75 | 0 | 18.7123 | 125.308 | 58.5262 | 0 | 304 | 418.251 | 61.8301 | 2.8482 | 367.392 | 57.863 | 0.014867 | 350.578 | 55.7215 | 0.011203 | 394.121 | 394.1 | 885036 | 11.0123 | 847626 | 895262 | 813155 | 0 | 0 | 808241 | 746.497 | 0 | 0 | 0 | 0 | 808241 | 746.497 | 794208 | 778323.9375
874 | 2003-02-06 09:00 | 488 | 918 | 58 | 2.78 | 5.15 | 0 | 28.009 | 137.374 | 45.5609 | 0 | 488 | 641.094 | 74.6229 | 4.5722 | 639.87 | 69.8349 | 0.023865 | 626.169 | 67.2504 | 0.017983 | 672.634 | 672.615 | 1510510 | 17.7975 | 1488310 | 1532930 | 1480230 | 0 | 0 | 1465220 | 753.067 | 0 | 0 | 0 | 0 | 1465220 | 753.067 | 1438080 | 1409317.5
875 | 2003-02-06 10:00 | 613 | 956 | 64 | 4.18 | 5.15 | 0 | 35.1721 | 152.133 | 34.161 | 0 | 613 | 788.628 | 81.5513 | 5.7433 | 788.628 | 76.3188 | 0.029978 | 780.406 | 73.4943 | 0.022589 | 828.305 | 828.303 | 1860170 | 22.6736 | 1854160 | 1871680 | 1816390 | 0 | 0 | 1793530 | 747.518 | 0 | 0 | 0 | 0 | 1793530 | 747.518 | 1757400 | 1722251.625
876 | 2003-02-06 11:00 | 682 | 972 | 69 | 5.57 | 5.15 | 0 | 39.2598 | 169.567 | 26.4449 | 0 | 682 | 867.295 | 87.4241 | 6.3898 | 867.295 | 81.8148 | 0.033353 | 862.227 | 78.7869 | 0.025132 | 912.808 | 912.808 | 2049940 | 25.9503 | 2053670 | 2045180 | 1991620 | 0 | 0 | 1963580 | 738.831 | 0 | 0 | 0 | 0 | 1963580 | 738.831 | 1922740 | 1884286.625
877 | 2003-02-06 12:00 | 703 | 996 | 71 | 6.96 | 5.4 | 0 | 39.5054 | 188.29 | 25.9445 | 0 | 703 | 893.351 | 89.8255 | 6.5866 | 893.351 | 84.0621 | 0.03438 | 888.345 | 80.951 | 0.025906 | 940.242 | 940.238 | 2111540 | 27.6152 | 2118540 | 2095200 | 2037360 | 0 | 0 | 2007790 | 735.407 | 0 | 0 | 0 | 0 | 2007790 | 735.407 | 1965530 | 1926218.25
878 | 2003-02-06 13:00 | 642 | 980 | 69 | 8.35 | 5.4 | 0 | 35.856 | 205.989 | 32.9905 | 0 | 642 | 820.504 | 87.5617 | 6.015 | 820.504 | 81.9436 | 0.031397 | 812.618 | 78.9109 | 0.023658 | 864.806 | 864.802 | 1942120 | 27.348 | 1940260 | 1920950 | 1869650 | 0 | 0 | 1844490 | 732.686 | 0 | 0 | 0 | 0 | 1844490 | 732.686 | 1807580 | 1771429
879 | 2003-02-06 14:00 | 506 | 929 | 56 | 8.53 | 5.4 | 0 | 29.0171 | 221.103 | 44.1018 | 0 | 506 | 666.186 | 72.0927 | 4.7408 | 666.186 | 67.4671 | 0.024746 | 653.111 | 64.9702 | 0.018646 | 696.557 | 696.555 | 1564290 | 23.8319 | 1544340 | 1551690 | 1508250 | 0 | 0 | 1492040 | 738.682 | 0 | 0 | 0 | 0 | 1492040 | 738.682 | 1465260 | 1435955.875
880 | 2003-02-06 15:00 | 346 | 858 | 54 | 8.7 | 3.04 | 0 | 19.9365 | 233.478 | 56.9433 | 0 | 346 | 467.119 | 70.2403 | 3.2418 | 467.119 | 65.7335 | 0.016921 | 447.657 | 63.3008 | 0.01275 | 495.641 | 495.637 | 1113070 | 21.4086 | 1076710 | 1093250 | 1062180 | 0 | 0 | 1054060 | 737.45 | 0 | 0 | 0 | 0 | 1054060 | 737.45 | 1036160 | 1015433.125
881 | 2003-02-06 16:00 | 136 | 583 | 40 | 8.87 | 3.04 | 0 | 9.3982 | 243.718 | 70.5723 | 0 | 136 | 195.542 | 54.8657 | 1.2742 | 158.425 | 51.3454 | 0.006651 | 142.531 | 49.4451 | 0.0050116 | 186.222 | 186.176 | 418103 | 13.6437 | 380025 | 399203 | 362315 | 0 | 0 | 361275 | 723.434 | 0 | 0 | 0 | 0 | 361275 | 723.434 | 353609 | 346537
882 | 2003-02-06 17:00 | 6 | 101 | 2 | 8.13 | 3.04 | 0 | -2.0552 | 252.564 | 84.6033 | 0 | 6 | 4.3242 | 2.3557 | 0.056215 | 0 | 2.2046 | 0 | 0 | 2.123 | 0 | 2.0593 | 2.0592 | 4624.52 | 8.1828 | 1026.73 | 1009.77 | 1004.63 | 0 | 0 | 1004.59 | 304.374 | 0 | 0 | 0 | 1004.59 | 0 | 660 | 0 | 0
883 | 2003-02-06 18:00 | 0 | 0 | 0 | 7.39 | 5.09 | 0
884 | 2003-02-06 19:00 | 0 | 0 | 0 | 6.65 | 5.09 | 0
885 | 2003-02-06 20:00 | 0 | 0 | 0 | 5.93 | 5.09 | 0
886 | 2003-02-06 21:00 | 0 | 0 | 0 | 5.21 | 7.83 | 0
887 | 2003-02-06 22:00 | 0 | 0 | 0 | 4.48 | 7.83 | 0
888 | 2003-02-06 23:00 | 0 | 0 | 0 | 3.77 | 7.83 | 0
889 | 2003-02-07 | 0 | 0 | 0 | 3.06 | 9.17 | 0
890 | 2003-02-07 01:00 | 0 | 0 | 0 | 2.35 | 9.17 | 0
891 | 2003-02-07 02:00 | 0 | 0 | 0 | 1.6 | 9.17 | 0
892 | 2003-02-07 03:00 | 0 | 0 | 0 | 0.85 | 9.78 | 0
893 | 2003-02-07 04:00 | 0 | 0 | 0 | 0.1 | 9.78 | 0
894 | 2003-02-07 05:00 | 0 | 0 | 0 | 0.01 | 9.78 | 0
895 | 2003-02-07 06:00 | 3 | 76 | 1 | -0.08 | 8.06 | 0 | -3.3395 | 106.324 | 86.2279 | 0 | 3 | 1.5124 | 1.0569 | 0.028108 | 0 | 0.98906 | 0 | 0 | 0.95246 | 0 | 0.92388 | 0.92381 | 2074.64 | -0.062875 | 208.451 | 202.283 | 201.297 | 0 | 0 | 201.288 | 136.869 | 0 | 0 | 0 | 201.288 | 0 | 660 | 0 | 0
896 | 2003-02-07 07:00 | 123 | 617 | 34 | -0.16 | 8.06 | 0 | 8.2212 | 115.04 | 72.1437 | 0 | 123 | 190.847 | 47.9459 | 1.1524 | 51.2605 | 44.8696 | 0.0060152 | 45.4648 | 43.2091 | 0.0045326 | 86.0181 | 85.8885 | 192890 | 1.4322 | 167086 | 185058 | 150732 | 0 | 0 | 150463 | 666.576 | 0 | 0 | 0 | 406.579 | 150056 | 681.793 | 145517 | 142606.3281
897 | 2003-02-07 08:00 | 317 | 831 | 48 | 1.44 | 8.06 | 0 | 18.9246 | 125.068 | 58.4242 | 0 | 317 | 434.305 | 62.9069 | 2.97 | 383.267 | 58.8707 | 0.015503 | 365.833 | 56.6919 | 0.011681 | 409.861 | 409.784 | 920262 | 9.0364 | 883456 | 941328 | 855800 | 0 | 0 | 850500 | 755.222 | 0 | 0 | 0 | 0 | 850500 | 755.222 | 835424 | 818715.4375
898 | 2003-02-07 09:00 | 474 | 843 | 76 | 3.04 | 10.06 | 0 | 28.254 | 137.157 | 45.4138 | 0 | 474 | 590.198 | 101.09 | 4.441 | 589.514 | 94.6036 | 0.023181 | 577 | 91.1024 | 0.017467 | 648.076 | 648.059 | 1455370 | 13.6508 | 1430840 | 1498690 | 1450290 | 0 | 0 | 1436430 | 768.387 | 0 | 0 | 0 | 0 | 1436430 | 768.387 | 1408900 | 1380721.875
899 | 2003-02-07 10:00 | 586 | 871 | 82 | 4.64 | 10.06 | 0 | 35.4515 | 151.965 | 33.9484 | 0 | 586 | 720.826 | 102.977 | 5.4904 | 720.826 | 96.3695 | 0.028658 | 713.42 | 92.8029 | 0.021594 | 782.057 | 782.054 | 1756300 | 17.4447 | 1745190 | 1799600 | 1747630 | 0 | 0 | 1727270 | 762.695 | 0 | 0 | 0 | 0 | 1727270 | 762.695 | 1691880 | 1658045
900 | 2003-02-07 11:00 | 658 | 872 | 104 | 5.59 | 10.06 | 0 | 39.5651 | 169.487 | 26.1551 | 0 | 658 | 780.704 | 136.523 | 6.165 | 780.704 | 127.763 | 0.032179 | 776.251 | 123.035 | 0.024248 | 872.331 | 872.326 | 1959020 | 19.8728 | 1958030 | 1999080 | 1942220 | 0 | 0 | 1916700 | 756.441 | 0 | 0 | 0 | 0 | 1916700 | 756.441 | 1875740 | 1838222
901 | 2003-02-07 12:00 | 708 | 786 | 206 | 6.54 | 7.53 | 0 | 39.8161 | 188.322 | 25.6403 | 0 | 708 | 706.777 | 255.025 | 6.6334 | 706.777 | 238.662 | 0.034624 | 702.917 | 229.829 | 0.02609 | 904.789 | 904.768 | 2031880 | 23.8822 | 2034670 | 2043660 | 1985320 | 0 | 0 | 1957870 | 744.375 | 0 | 0 | 0 | 0 | 1957870 | 744.375 | 1916780 | 1878448.125
902 | 2003-02-07 13:00 | 413 | 234 | 275 | 7.49 | 7.53 | 0 | 36.1499 | 206.118 | 32.7499 | 0 | 413 | 196.751 | 300.072 | 3.8695 | 196.751 | 280.819 | 0.020197 | 194.892 | 270.426 | 0.015219 | 451.373 | 451.369 | 1013660 | 16.1416 | 974842 | 1012130 | 982691 | 0 | 0 | 975958 | 749.168 | 0 | 0 | 0 | 0 | 975958 | 749.168 | 958960 | 939780.4375
903 | 2003-02-07 14:00 | 208 | 29 | 194 | 7.73 | 7.53 | 0 | 29.2824 | 221.291 | 43.9244 | 0 | 208 | 20.616 | 200.636 | 1.9488 | 20.616 | 187.763 | 0.010172 | 20.2156 | 180.814 | 0.0076649 | 195.006 | 194.993 | 437904 | 11.4675 | 397782 | 422869 | 410382 | 0 | 0 | 409152 | 735.29 | 0 | 0 | 0 | 0 | 409152 | 735.29 | 401168 | 393144.9062
904 | 2003-02-07 15:00 | 231 | 257 | 142 | 7.97 | 8.32 | 0 | 20.1723 | 233.696 | 56.8109 | 0 | 231 | 141.279 | 161.888 | 2.1643 | 141.279 | 151.501 | 0.011297 | 135.438 | 145.894 | 0.0085124 | 272.901 | 272.895 | 612853 | 12.9469 | 570233 | 601295 | 585014 | 0 | 0 | 582572 | 742.741 | 0 | 0 | 0 | 0 | 582572 | 742.741 | 572443 | 560993.875
905 | 2003-02-07 16:00 | 140 | 345 | 82 | 8.21 | 8.32 | 0 | 9.6089 | 243.952 | 70.4723 | 0 | 140 | 116.146 | 100.616 | 1.3117 | 98.5087 | 94.1607 | 0.0068466 | 88.6989 | 90.6759 | 0.005159 | 173.999 | 173.964 | 390678 | 11.3826 | 352202 | 374601 | 353174 | 0 | 0 | 352238 | 729.865 | 0 | 0 | 0 | 0 | 352238 | 729.865 | 344380 | 337492.625
906 | 2003-02-07 17:00 | 6 | 63 | 3 | 7.62 | 8.32 | 0 | -1.8637 | 252.811 | 84.5283 | 0 | 6 | 3.2881 | 3.4101 | 0.056215 | 0 | 3.1913 | 0 | 0 | 3.0732 | 0 | 2.981 | 2.9809 | 6694.25 | 7.6744 | 2089.65 | 2091.37 | 2073.26 | 0 | 0 | 2073.17 | 430.091 | 0 | 0 | 0 | 2073.17 | 0 | 660 | 0 | 0
907 | 2003-02-07 18:00 | 0 | 0 | 0 | 7.03 | 8.44 | 0
908 | 2003-02-07 19:00 | 0 | 0 | 0 | 6.44 | 8.44 | 0
909 | 2003-02-07 20:00 | 0 | 0 | 0 | 5.64 | 8.44 | 0
910 | 2003-02-07 21:00 | 0 | 0 | 0 | 4.85 | 7.72 | 0
911 | 2003-02-07 22:00 | 0 | 0 | 0 | 4.05 | 7.72 | 0
912 | 2003-02-07 23:00 | 0 | 0 | 0 | 3.53 | 7.72 | 0
913 | 2003-02-08 | 0 | 0 | 0 | 3.01 | 8.8 | 0
914 | 2003-02-08 01:00 | 0 | 0 | 0 | 2.49 | 8.8 | 0
915 | 2003-02-08 02:00 | 0 | 0 | 0 | 2.18 | 8.8 | 0
916 | 2003-02-08 03:00 | 0 | 0 | 0 | 1.87 | 5.57 | 0
917 | 2003-02-08 04:00 | 0 | 0 | 0 | 1.56 | 5.57 | 0
918 | 2003-02-08 05:00 | 0 | 0 | 0 | 1.57 | 5.57 | 0
919 | 2003-02-08 06:00 | 3 | 82 | 1 | 1.58 | 3.87 | 0 | -3.1686 | 106.059 | 86.1793 | 0 | 3 | 1.5318 | 1.0607 | 0.028108 | 0 | 0.99264 | 0 | 0 | 0.9559 | 0 | 0.92723 | 0.92713 | 2082.1 | 1.6025 | 209.959 | 204.16 | 203.164 | 0 | 0 | 203.155 | 137.299 | 0 | 0 | 0 | 203.155 | 0 | 660 | 0 | 0
920 | 2003-02-08 07:00 | 126 | 625 | 34 | 1.59 | 3.87 | 0 | 8.4118 | 114.786 | 72.0702 | 0 | 126 | 193.608 | 47.8555 | 1.1805 | 55.1695 | 44.785 | 0.0061619 | 48.9676 | 43.1275 | 0.0046431 | 89.3368 | 89.3079 | 200574 | 3.7579 | 174427 | 190872 | 156649 | 0 | 0 | 156373 | 679.815 | 0 | 0 | 0 | 5.2931 | 156368 | 680.355 | 151737 | 148702.4375
921 | 2003-02-08 08:00 | 322 | 836 | 48 | 2.73 | 3.87 | 0 | 19.1419 | 124.826 | 58.3186 | 0 | 322 | 438.852 | 62.7524 | 3.0169 | 389.009 | 58.7261 | 0.015747 | 371.425 | 56.5527 | 0.011866 | 415.15 | 415.066 | 932116 | 12.8055 | 895499 | 938853 | 853324 | 0 | 0 | 847883 | 742.804 | 0 | 0 | 0 | 0 | 847883 | 742.804 | 833349 | 816682.375
922 | 2003-02-08 09:00 | 505 | 933 | 61 | 3.88 | 2.94 | 0 | 28.504 | 136.938 | 45.263 | 0 | 505 | 654.857 | 77.9814 | 4.7315 | 654.477 | 72.978 | 0.024697 | 640.709 | 70.2771 | 0.018609 | 689.674 | 689.667 | 1548810 | 21.6812 | 1528210 | 1549190 | 1503300 | 0 | 0 | 1487450 | 744.77 | 0 | 0 | 0 | 0 | 1487450 | 744.77 | 1460390 | 1431181.25
923 | 2003-02-08 10:00 | 627 | 965 | 65 | 5.02 | 2.94 | 0 | 35.7358 | 151.796 | 33.7318 | 0 | 627 | 800.251 | 82.4869 | 5.8745 | 800.251 | 77.1944 | 0.030663 | 792.151 | 74.3375 | 0.023105 | 840.516 | 840.51 | 1887570 | 26.7146 | 1882940 | 1869090 | 1818630 | 0 | 0 | 1794880 | 733.911 | 0 | 0 | 0 | 0 | 1794880 | 733.911 | 1759510 | 1724315.75
924 | 2003-02-08 11:00 | 698 | 984 | 69 | 6.04 | 2.94 | 0 | 39.875 | 169.409 | 25.8606 | 0 | 698 | 882.854 | 87.1416 | 6.5397 | 882.854 | 81.5504 | 0.034135 | 877.942 | 78.5323 | 0.025722 | 927.805 | 927.806 | 2083610 | 29.9879 | 2089130 | 2045430 | 1987560 | 0 | 0 | 1958700 | 726.664 | 0 | 0 | 0 | 0 | 1958700 | 726.664 | 1918110 | 1879747.125
925 | 2003-02-08 12:00 | 710 | 994 | 71 | 7.06 | 0.88 | 0 | 40.1307 | 188.359 | 25.333 | 0 | 710 | 896.077 | 89.5368 | 6.6521 | 896.077 | 83.792 | 0.034722 | 891.31 | 80.6909 | 0.026164 | 942.867 | 942.861 | 2117420 | 34.9899 | 2124730 | 2035900 | 1987510 | 0 | 0 | 1957100 | 707.238 | 0 | 0 | 0 | 0 | 1957100 | 707.238 | 1916640 | 1878311.75
926 | 2003-02-08 13:00 | 651 | 982 | 69 | 8.08 | 0.88 | 0 | 36.4465 | 206.253 | 32.5094 | 0 | 651 | 826.167 | 87.2705 | 6.0994 | 826.167 | 81.6711 | 0.031837 | 818.492 | 78.6485 | 0.02399 | 870.249 | 870.243 | 1954350 | 33.8587 | 1953120 | 1880310 | 1832070 | 0 | 0 | 1806430 | 710.96 | 0 | 0 | 0 | 0 | 1806430 | 710.96 | 1771100 | 1735674.125
927 | 2003-02-08 14:00 | 527 | 944 | 62 | 8.68 | 0.88 | 0 | 29.5493 | 221.485 | 43.7486 | 0 | 527 | 681.115 | 79.1138 | 4.9376 | 681.115 | 74.0378 | 0.025773 | 668.027 | 71.2977 | 0.01942 | 717.164 | 717.159 | 1610550 | 29.924 | 1592660 | 1559170 | 1516260 | 0 | 0 | 1499020 | 719.214 | 0 | 0 | 0 | 0 | 1499020 | 719.214 | 1472810 | 1443349.75
928 | 2003-02-08 15:00 | 330 | 819 | 45 | 9.28 | 1.86 | 0 | 20.4087 | 233.92 | 56.6807 | 0 | 330 | 448.94 | 58.9106 | 3.0918 | 448.94 | 55.1307 | 0.016138 | 430.522 | 53.0904 | 0.012161 | 469.116 | 469.113 | 1053510 | 22.2913 | 1015600 | 1027400 | 999530 | 0 | 0 | 992196 | 730.646 | 0 | 0 | 0 | 0 | 992196 | 730.646 | 975793 | 956276.6875
929 | 2003-02-08 16:00 | 144 | 594 | 42 | 9.89 | 1.86 | 0 | 9.8197 | 244.191 | 70.3747 | 0 | 144 | 200.874 | 56.7641 | 1.3492 | 170.37 | 53.122 | 0.0070422 | 153.526 | 51.156 | 0.0053064 | 198.547 | 198.505 | 445791 | 15.3957 | 406399 | 423875 | 392566 | 0 | 0 | 391358 | 718.858 | 0 | 0 | 0 | 0 | 391358 | 718.858 | 383939 | 376260.1875
930 | 2003-02-08 17:00 | 7 | 113 | 2 | 9.52 | 1.86 | 0 | -1.6721 | 253.063 | 84.4557 | 0 | 7 | 5.5526 | 2.3951 | 0.065585 | 0 | 2.2414 | 0 | 0 | 2.1585 | 0 | 2.0937 | 2.0937 | 4701.85 | 9.5781 | 1060.86 | 1045.29 | 1039.82 | 0 | 0 | 1039.77 | 309.759 | 0 | 0 | 0 | 1039.77 | 0 | 660 | 0 | 0
931 | 2003-02-08 18:00 | 0 | 0 | 0 | 9.14 | 1.62 | 0
932 | 2003-02-08 19:00 | 0 | 0 | 0 | 8.77 | 1.62 | 0
933 | 2003-02-08 20:00 | 0 | 0 | 0 | 8.21 | 1.62 | 0
934 | 2003-02-08 21:00 | 0 | 0 | 0 | 7.64 | 1.73 | 0
935 | 2003-02-08 22:00 | 0 | 0 | 0 | 7.08 | 1.73 | 0
936 | 2003-02-08 23:00 | 0 | 0 | 0 | 5.99 | 1.73 | 0
937 | 2003-02-09 | 0 | 0 | 0 | 4.9 | 3.33 | 0
938 | 2003-02-09 01:00 | 0 | 0 | 0 | 3.8 | 3.33 | 0
939 | 2003-02-09 02:00 | 0 | 0 | 0 | 3.31 | 3.33 | 0
940 | 2003-02-09 03:00 | 0 | 0 | 0 | 2.81 | 1.95 | 0
941 | 2003-02-09 04:00 | 0 | 0 | 0 | 2.32 | 1.95 | 0
942 | 2003-02-09 05:00 | 0 | 0 | 0 | 1.9 | 1.95 | 0
943 | 2003-02-09 06:00 | 3 | 85 | 1 | 1.49 | 3.31 | 0 | -2.9926 | 105.793 | 86.127 | 0 | 3 | 1.5528 | 1.0649 | 0.028108 | 0 | 0.99654 | 0 | 0 | 0.95966 | 0 | 0.93087 | 0.93081 | 2090.36 | 1.5134 | 211.629 | 205.762 | 204.748 | 0 | 0 | 204.739 | 137.84 | 0 | 0 | 0 | 204.739 | 0 | 660 | 0 | 0
944 | 2003-02-09 07:00 | 127 | 612 | 35 | 1.08 | 3.31 | 0 | 8.6073 | 114.531 | 71.9932 | 0 | 127 | 190.028 | 48.7984 | 1.1899 | 59.8345 | 45.6674 | 0.0062108 | 53.1483 | 43.9773 | 0.00468 | 94.2164 | 94.1696 | 211492 | 3.4518 | 184413 | 202117 | 166453 | 0 | 0 | 166169 | 702.837 | 0 | 0 | 0 | 0 | 166169 | 702.837 | 161045 | 157823.9062
945 | 2003-02-09 08:00 | 315 | 780 | 56 | 2.5 | 3.31 | 0 | 19.3641 | 124.583 | 58.2095 | 0 | 315 | 411.513 | 75.4425 | 2.9513 | 366.336 | 70.602 | 0.015405 | 349.884 | 67.989 | 0.011608 | 405.348 | 405.218 | 910007 | 12.7062 | 872388 | 915491 | 835753 | 0 | 0 | 830554 | 741.021 | 0 | 0 | 0 | 0 | 830554 | 741.021 | 816403 | 800074.9375
946 | 2003-02-09 09:00 | 501 | 922 | 58 | 3.93 | 4.76 | 0 | 28.7589 | 136.719 | 45.1088 | 0 | 501 | 649.838 | 74.1987 | 4.694 | 649.65 | 69.438 | 0.024501 | 636.108 | 66.8682 | 0.018462 | 681.905 | 681.907 | 1531390 | 19.5461 | 1510030 | 1544330 | 1499410 | 0 | 0 | 1483960 | 752.245 | 0 | 0 | 0 | 0 | 1483960 | 752.245 | 1456470 | 1427341.25
947 | 2003-02-09 10:00 | 644 | 980 | 69 | 5.36 | 4.76 | 0 | 36.0249 | 151.628 | 33.5115 | 0 | 644 | 815.151 | 87.1679 | 6.0338 | 815.151 | 81.5751 | 0.031494 | 807.026 | 78.556 | 0.023732 | 859.037 | 859.032 | 1929170 | 25.0324 | 1926650 | 1925990 | 1871490 | 0 | 0 | 1846840 | 741.241 | 0 | 0 | 0 | 0 | 1846840 | 741.241 | 1809610 | 1773417.125
948 | 2003-02-09 11:00 | 714 | 998 | 72 | 6.8 | 4.76 | 0 | 40.1895 | 169.333 | 25.5616 | 0 | 714 | 897.484 | 90.6075 | 6.6896 | 897.484 | 84.794 | 0.034918 | 892.615 | 81.6558 | 0.026311 | 945.068 | 945.063 | 2122370 | 28.4426 | 2129950 | 2099200 | 2042420 | 0 | 0 | 2012270 | 730.757 | 0 | 0 | 0 | 0 | 2012270 | 730.757 | 1969850 | 1930450.25
949 | 2003-02-09 12:00 | 718 | 998 | 72 | 8.24 | 3.55 | 0 | 40.449 | 188.402 | 25.0227 | 0 | 718 | 902.27 | 90.5921 | 6.7271 | 902.27 | 84.7795 | 0.035113 | 897.597 | 81.6419 | 0.026458 | 949.888 | 949.885 | 2133210 | 31.7888 | 2141360 | 2080620 | 2023510 | 0 | 0 | 1993190 | 721.159 | 0 | 0 | 0 | 0 | 1993190 | 721.159 | 1951420 | 1912395
950 | 2003-02-09 13:00 | 656 | 983 | 69 | 9.67 | 3.55 | 0 | 36.7456 | 206.395 | 32.269 | 0 | 656 | 829.632 | 87.1231 | 6.1462 | 829.632 | 81.5331 | 0.032081 | 822.055 | 78.5156 | 0.024174 | 873.577 | 873.574 | 1961830 | 31.3269 | 1960980 | 1908850 | 1856540 | 0 | 0 | 1830940 | 720.855 | 0 | 0 | 0 | 0 | 1830940 | 720.855 | 1794640 | 1758749.125
951 | 2003-02-09 14:00 | 532 | 944 | 63 | 10.07 | 3.55 | 0 | 29.8175 | 221.687 | 43.5746 | 0 | 532 | 683.332 | 80.1728 | 4.9844 | 683.332 | 75.0287 | 0.026017 | 670.338 | 72.252 | 0.019604 | 720.332 | 720.327 | 1617680 | 27.9277 | 1600100 | 1580060 | 1538200 | 0 | 0 | 1520760 | 725.646 | 0 | 0 | 0 | 0 | 1520760 | 725.646 | 1493720 | 1463847.125
952 | 2003-02-09 15:00 | 344 | 849 | 45 | 10.47 | 3.97 | 0 | 20.6457 | 234.15 | 56.5528 | 0 | 344 | 467.398 | 58.7664 | 3.223 | 467.398 | 54.9958 | 0.016823 | 448.367 | 52.9605 | 0.012677 | 486.3 | 486.298 | 1092100 | 22.1973 | 1055170 | 1067840 | 1038850 | 0 | 0 | 1031000 | 733.473 | 0 | 0 | 0 | 0 | 1031000 | 733.473 | 1013730 | 993460
953 | 2003-02-09 16:00 | 147 | 600 | 42 | 10.86 | 3.97 | 0 | 10.0306 | 244.436 | 70.2795 | 0 | 147 | 203.42 | 56.7078 | 1.3773 | 172.53 | 53.0693 | 0.0071889 | 155.592 | 51.1052 | 0.005417 | 200.501 | 200.458 | 450175 | 15.6941 | 410700 | 427863 | 395533 | 0 | 0 | 394313 | 721.102 | 0 | 0 | 0 | 0 | 394313 | 721.102 | 386827 | 379090.9375
954 | 2003-02-09 17:00 | 7 | 119 | 2 | 10.43 | 3.97 | 0 | -1.4808 | 253.321 | 84.3854 | 0 | 7 | 5.6227 | 2.4019 | 0.065585 | 0 | 2.2478 | 0 | 0 | 2.1646 | 0 | 2.0997 | 2.0996 | 4715.07 | 10.4806 | 1066.68 | 1052.11 | 1046.62 | 0 | 0 | 1046.58 | 310.716 | 0 | 0 | 0 | 1046.58 | 0 | 660 | 0 | 0
955 | 2003-02-09 18:00 | 0 | 0 | 0 | 9.99 | 4.25 | 0
956 | 2003-02-09 19:00 | 0 | 0 | 0 | 9.56 | 4.25 | 0
957 | 2003-02-09 20:00 | 0 | 0 | 0 | 9.06 | 4.25 | 0
958 | 2003-02-09 21:00 | 0 | 0 | 0 | 8.57 | 5.65 | 0
959 | 2003-02-09 22:00 | 0 | 0 | 0 | 8.08 | 5.65 | 0
960 | 2003-02-09 23:00 | 0 | 0 | 0 | 7.43 | 5.65 | 0
961 | 2003-02-10 | 0 | 0 | 0 | 6.79 | 5.06 | 0
962 | 2003-02-10 01:00 | 0 | 0 | 0 | 6.14 | 5.06 | 0
963 | 2003-02-10 02:00 | 0 | 0 | 0 | 5.74 | 5.06 | 0
964 | 2003-02-10 03:00 | 0 | 0 | 0 | 5.34 | 6.75 | 0
965 | 2003-02-10 04:00 | 0 | 0 | 0 | 4.93 | 6.75 | 0
966 | 2003-02-10 05:00 | 0 | 0 | 0 | 4.71 | 6.75 | 0
967 | 2003-02-10 06:00 | 2 | 13 | 2 | 4.49 | 4.91 | 0 | -2.8117 | 105.525 | 86.0709 | 0 | 2 | 0 | 1.854 | 0.018738 | 0 | 1.735 | 0 | 0 | 1.6708 | 0 | 1.6207 | 1.6206 | 3639.56 | 4.5267 | 639.033 | 624.253 | 621.314 | 0 | 0 | 621.287 | 237.344 | 0 | 0 | 0 | 621.287 | 0 | 660 | 0 | 0
968 | 2003-02-10 07:00 | 76 | 86 | 63 | 4.26 | 4.91 | 0 | 8.8077 | 114.275 | 71.9126 | 0 | 76 | 26.3592 | 70.4888 | 0.71206 | 9.1132 | 65.9661 | 0.0037167 | 8.1012 | 63.5248 | 0.0028006 | 69.4799 | 69.4781 | 156031 | 5.8356 | 129641 | 142211 | 135308 | 0 | 0 | 135165 | 708.047 | 0 | 0 | 0 | 0 | 135165 | 708.047 | 130536 | 127925.2578
969 | 2003-02-10 08:00 | 219 | 178 | 159 | 5.69 | 4.91 | 0 | 19.591 | 124.339 | 58.0969 | 0 | 219 | 94.568 | 173.622 | 2.0519 | 84.5609 | 162.482 | 0.01071 | 80.7886 | 156.469 | 0.0080702 | 230.148 | 230.115 | 516780 | 10.9086 | 475386 | 505887 | 480183 | 0 | 0 | 478532 | 742.471 | 0 | 0 | 0 | 0 | 478532 | 742.471 | 469498 | 460108.2188
970 | 2003-02-10 09:00 | 290 | 123 | 230 | 7.13 | 2.96 | 0 | 29.0185 | 136.499 | 44.9511 | 0 | 290 | 87.535 | 249.899 | 2.7171 | 87.5181 | 233.865 | 0.014182 | 85.7108 | 225.209 | 0.010687 | 301.603 | 301.589 | 677294 | 14.9041 | 634505 | 663195 | 643760 | 0 | 0 | 640778 | 739.446 | 0 | 0 | 0 | 0 | 640778 | 739.446 | 629903 | 617304.5
971 | 2003-02-10 10:00 | 483 | 370 | 264 | 8.56 | 2.96 | 0 | 36.3189 | 151.461 | 33.2874 | 0 | 483 | 309.091 | 299.403 | 4.5253 | 309.091 | 280.193 | 0.023621 | 306.058 | 269.823 | 0.017799 | 558.622 | 558.612 | 1254510 | 22.9594 | 1222470 | 1232930 | 1197840 | 0 | 0 | 1187500 | 735.717 | 0 | 0 | 0 | 0 | 1187500 | 735.717 | 1167070 | 1143728.625
972 | 2003-02-10 11:00 | 682 | 800 | 164 | 10.33 | 2.96 | 0 | 40.5085 | 169.26 | 25.2581 | 0 | 682 | 721.22 | 209.259 | 6.3898 | 721.22 | 195.832 | 0.033353 | 717.408 | 188.585 | 0.025132 | 878.837 | 878.831 | 1973640 | 32.9837 | 1973400 | 1907210 | 1855380 | 0 | 0 | 1829440 | 715.53 | 0 | 0 | 0 | 0 | 1829440 | 715.53 | 1793280 | 1757412.125
973 | 2003-02-10 12:00 | 723 | 837 | 178 | 12.1 | 3.86 | 0 | 40.771 | 188.449 | 24.7096 | 0 | 723 | 758.149 | 224.863 | 6.774 | 758.149 | 210.436 | 0.035358 | 754.328 | 202.648 | 0.026643 | 928.292 | 928.279 | 2084690 | 34.6482 | 2090260 | 2005870 | 1954710 | 0 | 0 | 1925500 | 709.629 | 0 | 0 | 0 | 0 | 1925500 | 709.629 | 1886140 | 1848416.5
974 | 2003-02-10 13:00 | 437 | 264 | 278 | 13.88 | 3.86 | 0 | 37.0471 | 206.544 | 32.0291 | 0 | 437 | 223.74 | 315.428 | 4.0944 | 223.74 | 295.19 | 0.021371 | 221.731 | 284.265 | 0.016104 | 490.832 | 490.82 | 1102250 | 25.8022 | 1065610 | 1061730 | 1033070 | 0 | 0 | 1025040 | 720.758 | 0 | 0 | 0 | 0 | 1025040 | 720.758 | 1008530 | 988357.125
975 | 2003-02-10 14:00 | 281 | 100 | 231 | 14.96 | 3.86 | 0 | 30.0871 | 221.895 | 43.4025 | 0 | 281 | 72.4638 | 245.499 | 2.6328 | 72.4638 | 229.747 | 0.013742 | 71.1001 | 221.244 | 0.010355 | 283.584 | 283.577 | 636841 | 21.8482 | 594124 | 602570 | 586014 | 0 | 0 | 583361 | 713.996 | 0 | 0 | 0 | 0 | 583361 | 713.996 | 574088 | 562606.6875
976 | 2003-02-10 15:00 | 235 | 279 | 136 | 16.04 | 1.06 | 0 | 20.8832 | 234.387 | 56.4273 | 0 | 235 | 153.582 | 153.93 | 2.2018 | 153.582 | 144.054 | 0.011492 | 147.374 | 138.722 | 0.0086598 | 277.522 | 277.513 | 623222 | 24.1616 | 580550 | 582706 | 566800 | 0 | 0 | 564261 | 705.372 | 0 | 0 | 0 | 0 | 564261 | 705.372 | 555431 | 544322.375
977 | 2003-02-10 16:00 | 151 | 349 | 89 | 17.12 | 1.06 | 0 | 10.2415 | 244.687 | 70.1867 | 0 | 151 | 118.198 | 107.147 | 1.4147 | 100.249 | 100.272 | 0.0073845 | 90.4736 | 96.5613 | 0.0055644 | 181.429 | 181.419 | 407422 | 22.4293 | 368464 | 372632 | 351439 | 0 | 0 | 350420 | 695.545 | 0 | 0 | 0 | 0 | 350420 | 695.545 | 343501 | 336630.9062
978 | 2003-02-10 17:00 | 8 | 72 | 5 | 16.33 | 1.06 | 0 | -1.2895 | 253.583 | 84.3177 | 0 | 8 | 3.4142 | 5.3355 | 0.074954 | 0 | 4.9932 | 0 | 0 | 4.8084 | 0 | 4.6642 | 4.6641 | 10474.4 | 16.4665 | 4499.62 | 4612.35 | 4538.65 | 0 | 0 | 4538.32 | 496.772 | 0 | 0 | 0 | 4538.32 | 0 | 660 | 0 | 0
979 | 2003-02-10 18:00 | 0 | 0 | 0 | 15.54 | 3.91 | 0
980 | 2003-02-10 19:00 | 0 | 0 | 0 | 14.74 | 3.91 | 0
981 | 2003-02-10 20:00 | 0 | 0 | 0 | 14.04 | 3.91 | 0
982 | 2003-02-10 21:00 | 0 | 0 | 0 | 13.33 | 3.92 | 0
983 | 2003-02-10 22:00 | 0 | 0 | 0 | 12.62 | 3.92 | 0
984 | 2003-02-10 23:00 | 0 | 0 | 0 | 11.98 | 3.92 | 0
985 | 2003-02-11 | 0 | 0 | 0 | 11.34 | 6.64 | 0
986 | 2003-02-11 01:00 | 0 | 0 | 0 | 10.69 | 6.64 | 0
987 | 2003-02-11 02:00 | 0 | 0 | 0 | 10.42 | 6.64 | 0
988 | 2003-02-11 03:00 | 0 | 0 | 0 | 10.15 | 8.28 | 0
989 | 2003-02-11 04:00 | 0 | 0 | 0 | 9.87 | 8.28 | 0
990 | 2003-02-11 05:00 | 0 | 0 | 0 | 8.32 | 8.28 | 0
991 | 2003-02-11 06:00 | 2 | 9 | 2 | 6.76 | 7.04 | 0 | -2.6258 | 105.256 | 86.0111 | 0 | 2 | 0 | 1.8521 | 0.018738 | 0 | 1.7333 | 0 | 0 | 1.6692 | 0 | 1.6191 | 1.619 | 3635.91 | 6.792 | 637.733 | 624.665 | 621.75 | 0 | 0 | 621.723 | 237.395 | 0 | 0 | 0 | 621.723 | 0 | 660 | 0 | 0
992 | 2003-02-11 07:00 | 67 | 58 | 58 | 5.2 | 7.04 | 0 | 9.0128 | 114.017 | 71.8284 | 0 | 67 | 17.9168 | 63.845 | 0.62774 | 6.5135 | 59.7486 | 0.0032766 | 5.7949 | 57.5373 | 0.002469 | 61.4346 | 61.427 | 137949 | 6.4146 | 113097 | 123850 | 118294 | 0 | 0 | 118182 | 702.228 | 0 | 0 | 0 | 0 | 118182 | 702.228 | 114070 | 111788.6797
993 | 2003-02-11 08:00 | 93 | 0 | 93 | 4.99 | 7.04 | 0 | 19.8227 | 124.094 | 57.9811 | 0 | 93 | 0 | 87.4877 | 0.87134 | 0 | 81.8743 | 0.0045481 | 0 | 78.8442 | 0.0034271 | 76.4822 | 76.4805 | 171756 | 6.5022 | 143961 | 157395 | 152740 | 0 | 0 | 152557 | 710.677 | 0 | 0 | 0 | 0 | 152557 | 710.677 | 147457 | 144508.0156
994 | 2003-02-11 09:00 | 159 | 2 | 158 | 4.77 | 2.45 | 0 | 29.2829 | 136.278 | 44.7902 | 0 | 159 | 1.4509 | 150.963 | 1.4897 | 1.4508 | 141.277 | 0.0077758 | 1.4211 | 136.048 | 0.0058592 | 133.351 | 133.343 | 299453 | 8.3256 | 264004 | 285200 | 276441 | 0 | 0 | 275876 | 731.033 | 0 | 0 | 0 | 0 | 275876 | 731.033 | 268338 | 262971.2188
995 | 2003-02-11 10:00 | 225 | 10 | 219 | 4.55 | 2.45 | 0 | 36.6175 | 151.293 | 33.0598 | 0 | 225 | 8.4306 | 211.736 | 2.1081 | 8.4306 | 198.151 | 0.011003 | 8.3492 | 190.817 | 0.0082913 | 193.2 | 193.191 | 433859 | 9.7015 | 393835 | 421877 | 409522 | 0 | 0 | 408311 | 739.075 | 0 | 0 | 0 | 0 | 408311 | 739.075 | 400224 | 392219.7812
996 | 2003-02-11 11:00 | 187 | 1 | 186 | 5.36 | 2.45 | 0 | 40.8318 | 169.19 | 24.9504 | 0 | 187 | 1.3867 | 176.905 | 1.752 | 1.3867 | 165.555 | 0.0091451 | 1.3796 | 159.428 | 0.006891 | 155.99 | 155.984 | 350301 | 9.5193 | 312791 | 335791 | 325712 | 0 | 0 | 324934 | 733.823 | 0 | 0 | 0 | 0 | 324934 | 733.823 | 317011 | 310670.3125
997 | 2003-02-11 12:00 | 205 | 1 | 204 | 6.17 | 3.92 | 0 | 41.0964 | 188.502 | 24.3937 | 0 | 205 | 1.3855 | 195.116 | 1.9207 | 1.3855 | 182.597 | 0.010025 | 1.3787 | 175.839 | 0.0075543 | 171.909 | 171.894 | 386032 | 10.3289 | 347325 | 371327 | 360372 | 0 | 0 | 359421 | 733.748 | 0 | 0 | 0 | 0 | 359421 | 733.748 | 351460 | 344430.5625
998 | 2003-02-11 13:00 | 237 | 8 | 232 | 6.98 | 3.92 | 0 | 37.3509 | 206.699 | 31.7898 | 0 | 237 | 7.005 | 225.073 | 2.2205 | 7.005 | 210.632 | 0.01159 | 6.9432 | 202.836 | 0.0087335 | 203.495 | 203.482 | 456969 | 11.9032 | 416417 | 441724 | 428754 | 0 | 0 | 427408 | 733.856 | 0 | 0 | 0 | 0 | 427408 | 733.856 | 419225 | 410840.0938
999 | 2003-02-11 14:00 | 186 | 4 | 184 | 7.89 | 3.92 | 0 | 30.3577 | 222.11 | 43.2325 | 0 | 186 | 2.8832 | 177.546 | 1.7427 | 2.8832 | 166.154 | 0.0090962 | 2.8295 | 160.005 | 0.0068542 | 157.956 | 157.946 | 354708 | 11.7115 | 317039 | 337068 | 327342 | 0 | 0 | 326536 | 724.445 | 0 | 0 | 0 | 0 | 326536 | 724.445 | 318851 | 312474.0625
1000 | 2003-02-11 15:00 | 112 | 0 | 112 | 8.79 | 2.45 | 0 | 21.1211 | 234.629 | 56.3042 | 0 | 112 | 0 | 106.494 | 1.0494 | 0 | 99.6608 | 0.0054773 | 0 | 95.9725 | 0.0041272 | 93.0973 | 93.0915 | 209060 | 11.2723 | 178578 | 190800 | 185404 | 0 | 0 | 185130 | 703.335 | 0 | 0 | 0 | 0 | 185130 | 703.335 | 179442 | 175853.1875
1001 | 2003-02-11 16:00 | 99 | 84 | 84 | 9.69 | 2.45 | 0 | 10.4523 | 244.943 | 70.0966 | 0 | 99 | 28.148 | 93.9315 | 0.92755 | 24.9422 | 87.9047 | 0.0048415 | 22.5261 | 84.6514 | 0.0036482 | 103.966 | 103.959 | 233467 | 12.4621 | 201483 | 213956 | 206693 | 0 | 0 | 206351 | 703.4 | 0 | 0 | 0 | 0 | 206351 | 703.4 | 200284 | 196278.7656
1002 | 2003-02-11 17:00 | 5 | 18 | 4 | 9.48 | 2.45 | 0 | -1.0985 | 253.851 | 84.2523 | 0 | 5 | 1.1511 | 4.0256 | 0.046846 | 0 | 3.7673 | 0 | 0 | 3.6279 | 0 | 3.519 | 3.5189 | 7902.46 | 9.5738 | 2816.15 | 2862.64 | 2828.86 | 0 | 0 | 2828.72 | 471.074 | 0 | 0 | 0 | 2828.72 | 0 | 660 | 0 | 0
1003 | 2003-02-11 18:00 | 0 | 0 | 0 | 9.26 | 4.12 | 0
1004 | 2003-02-11 19:00 | 0 | 0 | 0 | 9.04 | 4.12 | 0
1005 | 2003-02-11 20:00 | 0 | 0 | 0 | 8.29 | 4.12 | 0
1006 | 2003-02-11 21:00 | 0 | 0 | 0 | 7.54 | 4.5 | 0
1007 | 2003-02-11 22:00 | 0 | 0 | 0 | 6.79 | 4.5 | 0
1008 | 2003-02-11 23:00 | 0 | 0 | 0 | 6.54 | 4.5 | 0
1009 | 2003-02-12 | 0 | 0 | 0 | 6.3 | 4.94 | 0
1010 | 2003-02-12 01:00 | 0 | 0 | 0 | 6.05 | 4.94 | 0
1011 | 2003-02-12 02:00 | 0 | 0 | 0 | 6.35 | 4.94 | 0
1012 | 2003-02-12 03:00 | 0 | 0 | 0 | 6.65 | 9.24 | 0
1013 | 2003-02-12 04:00 | 0 | 0 | 0 | 6.95 | 9.24 | 0
1014 | 2003-02-12 05:00 | 0 | 0 | 0 | 6.75 | 9.24 | 0
1015 | 2003-02-12 06:00 | 1 | 0 | 1 | 6.55 | 9.11 | 0 | -2.4351 | 104.985 | 85.9476 | 0 | 1 | 0 | 0.92656 | 0.0093692 | 0 | 0.86711 | 0 | 0 | 0.83502 | 0 | 0.80997 | 0.8099 | 1818.83 | 6.5641 | 160.304 | 156.808 | 156.026 | 0 | 0 | 156.02 | 120.736 | 0 | 0 | 0 | 156.02 | 0 | 660 | 0 | 0
1016 | 2003-02-12 07:00 | 23 | 0 | 23 | 6.35 | 9.11 | 0 | 9.2226 | 113.758 | 71.7409 | 0 | 23 | 0 | 20.2467 | 0.21549 | 0 | 18.9477 | 0.0011248 | 0 | 18.2464 | 0.00084756 | 17.6999 | 17.6996 | 39748.7 | 6.6573 | 27139.6 | 29768.5 | 29036.9 | 0 | 0 | 29028.6 | 633.194 | 0 | 0 | 0 | 484.44 | 28544.1 | 660 | 27508.3 | 26958.1777
1017 | 2003-02-12 08:00 | 58 | 0 | 58 | 6.52 | 9.11 | 0 | 20.0589 | 123.847 | 57.8619 | 0 | 58 | 0 | 52.9047 | 0.54341 | 0 | 49.5102 | 0.0028364 | 0 | 47.6779 | 0.0021373 | 46.2496 | 46.2461 | 103857 | 7.3229 | 82365.9 | 89978.7 | 87477.1 | 0 | 0 | 87412.1 | 683.214 | 0 | 0 | 0 | 0 | 87412.1 | 683.214 | 84357.1 | 82669.9609
1018 | 2003-02-12 09:00 | 89 | 0 | 89 | 6.69 | 12.23 | 0 | 29.5518 | 136.056 | 44.6261 | 0 | 89 | 0 | 82.138 | 0.83386 | 0 | 76.8679 | 0.0043525 | 0 | 74.0231 | 0.0032797 | 71.8056 | 71.8029 | 161251 | 7.7214 | 134298 | 146078 | 142076 | 0 | 0 | 141914 | 703.11 | 0 | 0 | 0 | 0 | 141914 | 703.11 | 137173 | 134429.2188
1019 | 2003-02-12 10:00 | 115 | 0 | 115 | 6.87 | 12.23 | 0 | 36.9206 | 151.126 | 32.8289 | 0 | 115 | 0 | 106.939 | 1.0775 | 0 | 100.077 | 0.005624 | 0 | 96.3734 | 0.0042378 | 93.4863 | 93.48 | 209933 | 8.2128 | 179393 | 194364 | 188876 | 0 | 0 | 188599 | 714.732 | 0 | 0 | 0 | 0 | 188599 | 714.732 | 182656 | 179002.9219
1020 | 2003-02-12 11:00 | 134 | 0 | 134 | 7.18 | 12.23 | 0 | 41.1594 | 169.122 | 24.6384 | 0 | 134 | 0 | 125.257 | 1.2555 | 0 | 117.22 | 0.0065532 | 0 | 112.882 | 0.0049379 | 109.5 | 109.494 | 245897 | 8.7528 | 213159 | 230149 | 223326 | 0 | 0 | 222945 | 720.267 | 0 | 0 | 0 | 0 | 222945 | 720.267 | 216300 | 211973.9219
1021 | 2003-02-12 12:00 | 152 | 0 | 152 | 7.48 | 6.47 | 0 | 41.4253 | 188.56 | 24.0754 | 0 | 152 | 0 | 142.9 | 1.4241 | 0 | 133.731 | 0.0074334 | 0 | 128.782 | 0.0056013 | 124.924 | 124.911 | 280518 | 10.0413 | 245958 | 263813 | 255919 | 0 | 0 | 255422 | 721.954 | 0 | 0 | 0 | 0 | 255422 | 721.954 | 248301 | 243335.2812
1022 | 2003-02-12 13:00 | 134 | 0 | 134 | 7.79 | 6.47 | 0 | 37.6569 | 206.861 | 31.5514 | 0 | 134 | 0 | 125.435 | 1.2555 | 0 | 117.387 | 0.0065532 | 0 | 113.043 | 0.0049379 | 109.656 | 109.653 | 246252 | 10.0385 | 213494 | 229178 | 222342 | 0 | 0 | 221960 | 715.047 | 0 | 0 | 0 | 0 | 221960 | 715.047 | 215430 | 211120.9844
1023 | 2003-02-12 14:00 | 105 | 0 | 105 | 8.04 | 6.47 | 0 | 30.6294 | 222.331 | 43.0646 | 0 | 105 | 0 | 97.5807 | 0.98377 | 0 | 91.3197 | 0.0051349 | 0 | 87.94 | 0.0038693 | 85.3056 | 85.3021 | 191566 | 9.7891 | 162289 | 174673 | 169582 | 0 | 0 | 169353 | 705.631 | 0 | 0 | 0 | 0 | 169353 | 705.631 | 163948 | 160669.1875
1024 | 2003-02-12 15:00 | 117 | 0 | 117 | 8.29 | 3.06 | 0 | 21.3592 | 234.878 | 56.1838 | 0 | 117 | 0 | 111.53 | 1.0962 | 0 | 104.374 | 0.0057218 | 0 | 100.511 | 0.0043115 | 97.4998 | 97.4957 | 218950 | 10.7866 | 187827 | 201080 | 195299 | 0 | 0 | 194997 | 707.204 | 0 | 0 | 0 | 0 | 194997 | 707.204 | 189061 | 185279.75
1025 | 2003-02-12 16:00 | 121 | 163 | 91 | 8.53 | 3.06 | 0 | 10.663 | 245.205 | 70.009 | 0 | 121 | 55.4291 | 102.117 | 1.1337 | 51.2206 | 95.5651 | 0.0059174 | 46.2904 | 92.0283 | 0.0044589 | 134.174 | 134.155 | 301277 | 11.9653 | 265780 | 282489 | 273123 | 0 | 0 | 272549 | 717.422 | 0 | 0 | 0 | 0 | 272549 | 717.422 | 265351 | 260043.7812
1026 | 2003-02-12 17:00 | 7 | 36 | 5 | 8.87 | 3.06 | 0 | -0.90784 | 254.123 | 84.1895 | 0 | 7 | 2.3273 | 5.0371 | 0.065585 | 0 | 4.714 | 0 | 0 | 4.5395 | 0 | 4.4033 | 4.4034 | 9888.86 | 8.9828 | 4104.58 | 4260.47 | 4194.32 | 0 | 0 | 4194.05 | 511.411 | 0 | 0 | 0 | 4107.48 | 86.576 | 660 | 83.2866 | 81.6209
1027 | 2003-02-12 18:00 | 0 | 0 | 0 | 9.21 | 9.35 | 0
1028 | 2003-02-12 19:00 | 0 | 0 | 0 | 9.54 | 9.35 | 0
1029 | 2003-02-12 20:00 | 0 | 0 | 0 | 9.66 | 9.35 | 0
1030 | 2003-02-12 21:00 | 0 | 0 | 0 | 9.77 | 4.83 | 0
1031 | 2003-02-12 22:00 | 0 | 0 | 0 | 9.88 | 4.83 | 0
1032 | 2003-02-12 23:00 | 0 | 0 | 0 | 9.94 | 4.83 | 0
1033 | 2003-02-13 | 0 | 0 | 0 | 10 | 11.39 | 0
1034 | 2003-02-13 01:00 | 0 | 0 | 0 | 10.05 | 11.39 | 0
1035 | 2003-02-13 02:00 | 0 | 0 | 0 | 9.74 | 11.39 | 0
1036 | 2003-02-13 03:00 | 0 | 0 | 0 | 9.42 | 6.89 | 0
1037 | 2003-02-13 04:00 | 0 | 0 | 0 | 9.1 | 6.89 | 0
1038 | 2003-02-13 05:00 | 0 | 0 | 0 | 9.34 | 6.89 | 0
1039 | 2003-02-13 06:00 | 2 | 8 | 2 | 9.59 | 8.11 | 0 | -2.2397 | 104.713 | 85.8806 | 0 | 2 | 0 | 1.8482 | 0.018738 | 0 | 1.7296 | 0 | 0 | 1.6656 | 0 | 1.6157 | 1.6155 | 3628.1 | 9.6198 | 634.957 | 624.026 | 621.15 | 0 | 0 | 621.122 | 237.297 | 0 | 0 | 0 | 621.122 | 0 | 660 | 0 | 0
1040 | 2003-02-13 07:00 | 68 | 47 | 60 | 9.83 | 8.11 | 0 | 9.437 | 113.497 | 71.65 | 0 | 68 | 15.3606 | 58.3306 | 0.63711 | 6.1202 | 54.588 | 0.0033255 | 5.4542 | 52.5677 | 0.0025058 | 56.2837 | 56.283 | 126398 | 10.8701 | 102631 | 110136 | 105392 | 0 | 0 | 105298 | 681.248 | 0 | 0 | 0 | 0 | 105298 | 681.248 | 101755 | 99720.1406
1041 | 2003-02-13 08:00 | 96 | 0 | 96 | 9.91 | 8.11 | 0 | 20.2996 | 123.599 | 57.7397 | 0 | 96 | 0 | 90.3448 | 0.89945 | 0 | 84.5481 | 0.0046948 | 0 | 81.4191 | 0.0035376 | 78.9799 | 78.972 | 177351 | 11.3694 | 149123 | 159401 | 154769 | 0 | 0 | 154572 | 692.979 | 0 | 0 | 0 | 0 | 154572 | 692.979 | 149671 | 146677.75
1042 | 2003-02-13 09:00 | 114 | 0 | 114 | 9.99 | 2.51 | 0 | 29.8252 | 135.833 | 44.459 | 0 | 114 | 0 | 106.473 | 1.0681 | 0 | 99.6418 | 0.0055751 | 0 | 95.9541 | 0.0042009 | 93.0796 | 93.0768 | 209026 | 12.462 | 178547 | 189721 | 184215 | 0 | 0 | 183940 | 697.671 | 0 | 0 | 0 | 0 | 183940 | 697.671 | 178367 | 174799.5625
1043 | 2003-02-13 10:00 | 192 | 4 | 190 | 10.07 | 2.51 | 0 | 37.2282 | 150.959 | 32.5946 | 0 | 192 | 2.7852 | 181.498 | 1.7989 | 2.7852 | 169.853 | 0.0093896 | 2.7591 | 163.567 | 0.0070753 | 161.343 | 161.337 | 362320 | 14.3549 | 324386 | 340804 | 330798 | 0 | 0 | 329957 | 716.955 | 0 | 0 | 0 | 0 | 329957 | 716.955 | 322460 | 316010.7812
1044 | 2003-02-13 11:00 | 237 | 17 | 226 | 10.19 | 2.51 | 0 | 41.4912 | 169.057 | 24.3224 | 0 | 237 | 15.13 | 217.449 | 2.2205 | 15.13 | 203.497 | 0.01159 | 15.0563 | 195.966 | 0.0087335 | 204.7 | 204.692 | 459685 | 15.6264 | 419074 | 437346 | 424706 | 0 | 0 | 423341 | 722.119 | 0 | 0 | 0 | 0 | 423341 | 722.119 | 415568 | 407256.7188
1045 | 2003-02-13 12:00 | 527 | 329 | 309 | 10.32 | 6.3 | 0 | 41.7574 | 188.623 | 23.7546 | 0 | 527 | 299.605 | 350.3 | 4.9376 | 299.605 | 327.824 | 0.025773 | 298.219 | 315.691 | 0.01942 | 595.512 | 595.486 | 1337310 | 22.6644 | 1308190 | 1321000 | 1284690 | 0 | 0 | 1272850 | 737.252 | 0 | 0 | 0 | 0 | 1272850 | 737.252 | 1250640 | 1225629.875
1046 | 2003-02-13 13:00 | 218 | 9 | 212 | 10.44 | 6.3 | 0 | 37.9649 | 207.03 | 31.3139 | 0 | 218 | 8.3325 | 203.883 | 2.0425 | 8.3325 | 190.802 | 0.010661 | 8.2615 | 183.74 | 0.0080334 | 186.25 | 186.237 | 418239 | 14.3007 | 378611 | 397617 | 386832 | 0 | 0 | 385701 | 722.568 | 0 | 0 | 0 | 0 | 385701 | 722.568 | 378140 | 370577.0312
1047 | 2003-02-13 14:00 | 282 | 90 | 236 | 10.67 | 6.3 | 0 | 30.902 | 222.56 | 42.8991 | 0 | 282 | 65.6141 | 250.602 | 2.6421 | 65.6141 | 234.523 | 0.013791 | 64.4164 | 225.843 | 0.010392 | 281.562 | 281.543 | 632277 | 16.5064 | 589577 | 612188 | 594835 | 0 | 0 | 592237 | 731.912 | 0 | 0 | 0 | 0 | 592237 | 731.912 | 582345 | 570698.125
1048 | 2003-02-13 15:00 | 163 | 30 | 152 | 10.91 | 5.17 | 0 | 21.5976 | 235.132 | 56.0659 | 0 | 163 | 16.6826 | 156.652 | 1.5272 | 16.6826 | 146.601 | 0.0079714 | 16.0226 | 141.176 | 0.0060066 | 152.488 | 152.48 | 342430 | 14.31 | 305207 | 320808 | 311446 | 0 | 0 | 310699 | 716.207 | 0 | 0 | 0 | 0 | 310699 | 716.207 | 303278 | 297212.625
1049 | 2003-02-13 16:00 | 27 | 0 | 27 | 11.14 | 5.17 | 0 | 10.8735 | 245.471 | 69.924 | 0 | 27 | 0 | 23.9644 | 0.25297 | 0 | 22.4268 | 0.0013204 | 0 | 21.5968 | 0.00099496 | 20.9498 | 20.9485 | 47045.1 | 11.6071 | 33176.7 | 35559.3 | 34690.6 | 0 | 0 | 34678.4 | 626.481 | 0 | 0 | 0 | 1124.35 | 33554.1 | 660 | 32346.6 | 31699.6816
1050 | 2003-02-13 17:00 | 2 | 0 | 2 | 11.29 | 5.17 | 0 | -0.71746 | 254.401 | 84.1291 | 0 | 2 | 0 | 1.7968 | 0.018738 | 0 | 1.6815 | 0 | 0 | 1.6192 | 0 | 1.5707 | 1.5706 | 3527.12 | 11.325 | 600.284 | 591.068 | 588.379 | 0 | 0 | 588.354 | 230.944 | 0 | 0 | 0 | 588.354 | 0 | 660 | 0 | 0
1051 | 2003-02-13 18:00 | 0 | 0 | 0 | 11.44 | 6.73 | 0
1052 | 2003-02-13 19:00 | 0 | 0 | 0 | 11.59 | 6.73 | 0
1053 | 2003-02-13 20:00 | 0 | 0 | 0 | 11.36 | 6.73 | 0
1054 | 2003-02-13 21:00 | 0 | 0 | 0 | 11.14 | 3.96 | 0
1055 | 2003-02-13 22:00 | 0 | 0 | 0 | 10.92 | 3.96 | 0
1056 | 2003-02-13 23:00 | 0 | 0 | 0 | 10.44 | 3.96 | 0
1057 | 2003-02-14 | 0 | 0 | 0 | 9.95 | 5.6 | 0
1058 | 2003-02-14 01:00 | 0 | 0 | 0 | 9.47 | 5.6 | 0
1059 | 2003-02-14 02:00 | 0 | 0 | 0 | 9.39 | 5.6 | 0
1060 | 2003-02-14 03:00 | 0 | 0 | 0 | 9.31 | 5.23 | 0
1061 | 2003-02-14 04:00 | 0 | 0 | 0 | 9.23 | 5.23 | 0
1062 | 2003-02-14 05:00 | 0 | 0 | 0 | 8.57 | 5.23 | 0
1063 | 2003-02-14 06:00 | 6 | 118 | 2 | 7.91 | 5.24 | 0 | -2.0397 | 104.44 | 85.81 | 0 | 6 | 3.3593 | 2.1651 | 0.056215 | 0 | 2.0262 | 0 | 0 | 1.9512 | 0 | 1.8927 | 1.8926 | 4250.34 | 7.952 | 869.25 | 853.631 | 849.543 | 0 | 0 | 849.506 | 278.009 | 0 | 0 | 0 | 849.506 | 0 | 660 | 0 | 0
1064 | 2003-02-14 07:00 | 149 | 661 | 37 | 7.25 | 5.24 | 0 | 9.6558 | 113.235 | 71.5559 | 0 | 149 | 211.26 | 50.3804 | 1.396 | 91.3308 | 47.1479 | 0.0072867 | 81.4636 | 45.403 | 0.0054907 | 123.066 | 123.024 | 276277 | 9.9808 | 246007 | 261911 | 212343 | 0 | 0 | 211889 | 702.439 | 0 | 0 | 0 | 34.4265 | 211855 | 703.427 | 206089 | 201967.0156
1065 | 2003-02-14 08:00 | 356 | 862 | 54 | 8.2 | 5.24 | 0 | 20.5447 | 123.35 | 57.6144 | 0 | 356 | 460.923 | 69.0462 | 3.3354 | 418.977 | 64.616 | 0.01741 | 400.814 | 62.2246 | 0.013119 | 449.16 | 449.051 | 1008460 | 18.1676 | 972740 | 998248 | 920885 | 0 | 0 | 914446 | 731.452 | 0 | 0 | 0 | 0 | 914446 | 731.452 | 899250 | 881265.0625
1066 | 2003-02-14 09:00 | 536 | 945 | 63 | 9.14 | 3.58 | 0 | 30.1029 | 135.609 | 44.289 | 0 | 536 | 675.073 | 79.4804 | 5.0219 | 675.073 | 74.3808 | 0.026213 | 661.673 | 71.628 | 0.019752 | 711.321 | 711.319 | 1597440 | 26.7396 | 1578960 | 1567090 | 1523420 | 0 | 0 | 1506520 | 730.029 | 0 | 0 | 0 | 0 | 1506520 | 730.029 | 1479710 | 1450119.75
1067 | 2003-02-14 10:00 | 668 | 984 | 70 | 10.09 | 3.58 | 0 | 37.5401 | 150.792 | 32.3573 | 0 | 668 | 829.038 | 87.6048 | 6.2586 | 829.038 | 81.9839 | 0.032668 | 821.419 | 78.9498 | 0.024616 | 873.382 | 873.381 | 1961390 | 31.6994 | 1960520 | 1905340 | 1854560 | 0 | 0 | 1828900 | 719.344 | 0 | 0 | 0 | 0 | 1828900 | 719.344 | 1792700 | 1756842.125
1068 | 2003-02-14 11:00 | 739 | 802 | 206 | 11.29 | 3.58 | 0 | 41.8269 | 168.994 | 24.0024 | 0 | 739 | 730.129 | 253.78 | 6.9238 | 730.129 | 237.497 | 0.03614 | 726.673 | 228.707 | 0.027232 | 926.746 | 926.736 | 2081210 | 34.2195 | 2086600 | 2006090 | 1954140 | 0 | 0 | 1925020 | 711.459 | 0 | 0 | 0 | 0 | 1925020 | 711.459 | 1885670 | 1847955
1069 | 2003-02-14 12:00 | 459 | 217 | 314 | 12.48 | 3.72 | 0 | 42.0927 | 188.691 | 23.4317 | 0 | 459 | 198.472 | 341.051 | 4.3005 | 198.472 | 319.168 | 0.022447 | 197.581 | 307.356 | 0.016914 | 489.805 | 489.794 | 1099950 | 24.4873 | 1063250 | 1065430 | 1036790 | 0 | 0 | 1028790 | 725.242 | 0 | 0 | 0 | 0 | 1028790 | 725.242 | 1011980 | 991739.75
1070 | 2003-02-14 13:00 | 303 | 71 | 259 | 13.68 | 3.72 | 0 | 38.2748 | 207.206 | 31.0776 | 0 | 303 | 60.8372 | 272.386 | 2.8389 | 60.8372 | 254.909 | 0.014818 | 60.3275 | 245.475 | 0.011166 | 296.639 | 296.635 | 666166 | 20.952 | 623390 | 634724 | 616663 | 0 | 0 | 613773 | 718.925 | 0 | 0 | 0 | 0 | 613773 | 718.925 | 603985 | 591905.75
1071 | 2003-02-14 14:00 | 556 | 718 | 185 | 14.15 | 3.72 | 0 | 31.1754 | 222.795 | 42.7359 | 0 | 556 | 526.399 | 220.936 | 5.2093 | 526.399 | 206.76 | 0.027191 | 516.885 | 199.108 | 0.020489 | 694.533 | 694.523 | 1559720 | 31.1763 | 1539570 | 1498970 | 1459260 | 0 | 0 | 1443050 | 714.192 | 0 | 0 | 0 | 0 | 1443050 | 714.192 | 1418280 | 1389913
1072 | 2003-02-14 15:00 | 381 | 876 | 55 | 14.62 | 2.95 | 0 | 21.836 | 235.393 | 55.9507 | 0 | 381 | 490.735 | 70.1486 | 3.5697 | 490.735 | 65.6478 | 0.018632 | 471.449 | 63.2182 | 0.01404 | 518.641 | 518.64 | 1164740 | 27.9979 | 1129840 | 1115010 | 1084280 | 0 | 0 | 1075330 | 716.194 | 0 | 0 | 0 | 0 | 1075330 | 716.194 | 1058070 | 1036908.75
1073 | 2003-02-14 16:00 | 165 | 608 | 48 | 15.08 | 2.95 | 0 | 11.0838 | 245.743 | 69.8416 | 0 | 165 | 209.734 | 64.3372 | 1.5459 | 193.81 | 60.2092 | 0.0080692 | 175.381 | 57.9809 | 0.0060803 | 226.367 | 226.353 | 508332 | 20.9186 | 467022 | 475642 | 455013 | 0 | 0 | 453384 | 709.692 | 0 | 0 | 0 | 0 | 453384 | 709.692 | 445618 | 436705.9062
1074 | 2003-02-14 17:00 | 10 | 145 | 3 | 14.76 | 2.95 | 0 | -0.52744 | 254.683 | 84.0711 | 0 | 10 | 8.311 | 3.5947 | 0.093692 | 0 | 3.3641 | 0 | 0 | 3.2396 | 0 | 3.1424 | 3.1421 | 7056.41 | 14.841 | 2301.28 | 2315.28 | 2291.74 | 0 | 0 | 2291.62 | 433.943 | 0 | 0 | 0 | 2291.62 | 0 | 660 | 0 | 0
1075 | 2003-02-14 18:00 | 0 | 0 | 0 | 14.43 | 7.17 | 0
1076 | 2003-02-14 19:00 | 0 | 0 | 0 | 14.11 | 7.17 | 0
1077 | 2003-02-14 20:00 | 0 | 0 | 0 | 13.81 | 7.17 | 0
1078 | 2003-02-14 21:00 | 0 | 0 | 0 | 13.51 | 5.9 | 0
1079 | 2003-02-14 22:00 | 0 | 0 | 0 | 13.21 | 5.9 | 0
1080 | 2003-02-14 23:00 | 0 | 0 | 0 | 12.41 | 5.9 | 0
1081 | 2003-02-15 | 0 | 0 | 0 | 11.61 | 7.72 | 0
1082 | 2003-02-15 01:00 | 0 | 0 | 0 | 10.8 | 7.72 | 0
1083 | 2003-02-15 02:00 | 0 | 0 | 0 | 10.14 | 7.72 | 0
1084 | 2003-02-15 03:00 | 0 | 0 | 0 | 9.47 | 5.3 | 0
1085 | 2003-02-15 04:00 | 0 | 0 | 0 | 8.81 | 5.3 | 0
1086 | 2003-02-15 05:00 | 0 | 0 | 0 | 8.53 | 5.3 | 0
1087 | 2003-02-15 06:00 | 6 | 125 | 1 | 8.26 | 3.8 | 0 | -1.8352 | 104.166 | 85.736 | 0 | 6 | 4.2732 | 1.1466 | 0.056215 | 0 | 1.073 | 0 | 0 | 1.0333 | 0 | 1.0023 | 1.0022 | 2250.68 | 8.2844 | 245.219 | 240.395 | 239.304 | 0 | 0 | 239.293 | 147.916 | 0 | 0 | 0 | 239.293 | 0 | 660 | 0 | 0
1088 | 2003-02-15 07:00 | 153 | 667 | 38 | 7.98 | 3.8 | 0 | 9.879 | 112.973 | 71.4585 | 0 | 153 | 213.146 | 51.327 | 1.4335 | 95.9265 | 48.0338 | 0.0074823 | 85.6396 | 46.2561 | 0.0056381 | 127.944 | 128.01 | 287477 | 11.1017 | 256667 | 271736 | 221707 | 0 | 0 | 221198 | 684.572 | 0 | 0 | 0 | 0 | 221198 | 684.572 | 215676 | 211362.5938
1089 | 2003-02-15 08:00 | 350 | 850 | 48 | 9.31 | 3.8 | 0 | 20.7941 | 123.099 | 57.4861 | 0 | 350 | 457.244 | 61.6671 | 3.2792 | 417.4 | 57.7104 | 0.017116 | 399.442 | 55.5746 | 0.012898 | 441.379 | 441.281 | 991018 | 20.0712 | 954802 | 971871 | 897701 | 0 | 0 | 891505 | 727.203 | 0 | 0 | 0 | 0 | 891505 | 727.203 | 876904 | 859366.25
1090 | 2003-02-15 09:00 | 541 | 946 | 63 | 10.64 | 4.44 | 0 | 30.3849 | 135.384 | 44.1163 | 0 | 541 | 678.462 | 79.3252 | 5.0687 | 678.462 | 74.2356 | 0.026457 | 665.133 | 71.4882 | 0.019936 | 714.542 | 714.538 | 1604670 | 27.3488 | 1586510 | 1570530 | 1528320 | 0 | 0 | 1511170 | 727.612 | 0 | 0 | 0 | 0 | 1511170 | 727.612 | 1484320 | 1454632.5
1091 | 2003-02-15 10:00 | 649 | 947 | 69 | 11.96 | 4.44 | 0 | 37.8562 | 150.626 | 32.117 | 0 | 649 | 800.479 | 86.2576 | 6.0806 | 800.479 | 80.7231 | 0.031739 | 793.247 | 77.7356 | 0.023916 | 844.877 | 844.874 | 1897380 | 31.7166 | 1893240 | 1839720 | 1789500 | 0 | 0 | 1765540 | 718.6 | 0 | 0 | 0 | 0 | 1765540 | 718.6 | 1731390 | 1696759.875
1092 | 2003-02-15 11:00 | 744 | 1003 | 73 | 13.1 | 4.44 | 0 | 42.1666 | 168.934 | 23.6786 | 0 | 744 | 915.419 | 90.8839 | 6.9707 | 915.419 | 85.0526 | 0.036385 | 911.211 | 81.9049 | 0.027417 | 963.349 | 963.347 | 2163440 | 35.627 | 2173220 | 2076800 | 2021500 | 0 | 0 | 1990140 | 707.864 | 0 | 0 | 0 | 0 | 1990140 | 707.864 | 1948490 | 1909522.25
1093 | 2003-02-15 12:00 | 749 | 1003 | 74 | 14.23 | 3.61 | 0 | 42.4311 | 188.765 | 23.1067 | 0 | 749 | 920.18 | 92.0585 | 7.0175 | 920.18 | 86.1519 | 0.036629 | 916.167 | 82.9634 | 0.027601 | 969.184 | 969.178 | 2176540 | 38.1622 | 2187020 | 2066710 | 2015050 | 0 | 0 | 1983100 | 699.049 | 0 | 0 | 0 | 0 | 1983100 | 699.049 | 1941730 | 1902893.125
1094 | 2003-02-15 13:00 | 685 | 826 | 171 | 15.36 | 3.61 | 0 | 38.5865 | 207.388 | 30.8427 | 0 | 685 | 707.571 | 213.486 | 6.4179 | 707.571 | 199.788 | 0.033499 | 701.744 | 192.394 | 0.025243 | 867.339 | 867.331 | 1947800 | 36.7773 | 1946230 | 1849760 | 1802840 | 0 | 0 | 1777310 | 700.953 | 0 | 0 | 0 | 0 | 1777310 | 700.953 | 1743140 | 1708273.375
1095 | 2003-02-15 14:00 | 435 | 430 | 211 | 15.94 | 3.61 | 0 | 31.4495 | 223.036 | 42.5754 | 0 | 435 | 316.151 | 247.212 | 4.0756 | 316.151 | 231.351 | 0.021273 | 310.493 | 222.789 | 0.01603 | 517.298 | 517.291 | 1161700 | 28.7136 | 1126730 | 1108420 | 1079260 | 0 | 0 | 1070280 | 712.052 | 0 | 0 | 0 | 0 | 1070280 | 712.052 | 1053330 | 1032263.1875
1096 | 2003-02-15 15:00 | 385 | 645 | 143 | 16.51 | 3.69 | 0 | 22.0744 | 235.659 | 55.8383 | 0 | 385 | 361.593 | 168.636 | 3.6071 | 361.593 | 157.816 | 0.018828 | 347.476 | 151.975 | 0.014187 | 484.481 | 484.471 | 1088000 | 28.4103 | 1050960 | 1035200 | 1007070 | 0 | 0 | 999235 | 711.05 | 0 | 0 | 0 | 0 | 999235 | 711.05 | 983689 | 964014.8125
1097 | 2003-02-15 16:00 | 129 | 311 | 68 | 17.09 | 3.69 | 0 | 11.2937 | 246.02 | 69.7619 | 0 | 129 | 107.749 | 83.6638 | 1.2086 | 99.5675 | 78.2958 | 0.0063086 | 90.1543 | 75.3981 | 0.0047537 | 160.59 | 160.585 | 360634 | 21.0345 | 322844 | 328903 | 316125 | 0 | 0 | 315305 | 695.003 | 0 | 0 | 0 | 0 | 315305 | 695.003 | 308403 | 302235.1875
1098 | 2003-02-15 17:00 | 9 | 77 | 5 | 16.77 | 3.69 | 0 | -0.33784 | 254.969 | 84.0156 | 0 | 9 | 4.7934 | 5.7014 | 0.084323 | 0 | 5.3356 | 0 | 0 | 5.1381 | 0 | 4.984 | 4.984 | 11192.7 | 16.8924 | 4991.73 | 5123.31 | 5037.4 | 0 | 0 | 5037.01 | 503.753 | 0 | 0 | 0 | 5037.01 | 0 | 660 | 0 | 0
1099 | 2003-02-15 18:00 | 0 | 0 | 0 | 16.45 | 10.31 | 0
1100 | 2003-02-15 19:00 | 0 | 0 | 0 | 16.12 | 10.31 | 0
1101 | 2003-02-15 20:00 | 0 | 0 | 0 | 15.1 | 10.31 | 0
1102 | 2003-02-15 21:00 | 0 | 0 | 0 | 14.07 | 8.97 | 0
1103 | 2003-02-15 22:00 | 0 | 0 | 0 | 13.04 | 8.97 | 0
1104 | 2003-02-15 23:00 | 0 | 0 | 0 | 12.55 | 8.97 | 0
1105 | 2003-02-16 | 0 | 0 | 0 | 12.06 | 8.96 | 0
1106 | 2003-02-16 01:00 | 0 | 0 | 0 | 11.57 | 8.96 | 0
1107 | 2003-02-16 02:00 | 0 | 0 | 0 | 11.35 | 8.96 | 0
1108 | 2003-02-16 03:00 | 0 | 0 | 0 | 11.14 | 10.79 | 0
1109 | 2003-02-16 04:00 | 0 | 0 | 0 | 10.92 | 10.79 | 0
1110 | 2003-02-16 05:00 | 0 | 0 | 0 | 10.64 | 10.79 | 0
1111 | 2003-02-16 06:00 | 7 | 132 | 2 | 10.37 | 7.91 | 0 | -1.6262 | 103.891 | 85.6585 | 0 | 7 | 4.3506 | 2.2698 | 0.065585 | 0 | 2.1241 | 0 | 0 | 2.0455 | 0 | 1.9842 | 1.9841 | 4455.72 | 10.4071 | 954.206 | 940.247 | 935.463 | 0 | 0 | 935.422 | 293.464 | 0 | 0 | 0 | 935.422 | 0 | 660 | 0 | 0
1112 | 2003-02-16 07:00 | 157 | 673 | 38 | 10.09 | 7.91 | 0 | 10.1064 | 112.708 | 71.3581 | 0 | 157 | 216.773 | 51.2113 | 1.471 | 105.233 | 47.9255 | 0.007678 | 94.0343 | 46.1518 | 0.0057855 | 135.986 | 135.98 | 305370 | 12.6346 | 273846 | 288344 | 239303 | 0 | 0 | 238734 | 698.741 | 0 | 0 | 0 | 0 | 238734 | 698.741 | 232836 | 228179.0625
1113 | 2003-02-16 08:00 | 366 | 867 | 55 | 10.89 | 7.91 | 0 | 21.0475 | 122.848 | 57.355 | 0 | 366 | 467.122 | 69.9039 | 3.4291 | 428.257 | 65.4188 | 0.017899 | 409.975 | 62.9977 | 0.013487 | 458.796 | 458.7 | 1030130 | 19.4738 | 994695 | 1015820 | 939180 | 0 | 0 | 932465 | 730.264 | 0 | 0 | 0 | 0 | 932465 | 730.264 | 917010 | 898670.1875
1114 | 2003-02-16 09:00 | 546 | 948 | 63 | 11.69 | 9.06 | 0 | 30.6709 | 135.159 | 43.9409 | 0 | 546 | 681.793 | 79.1695 | 5.1156 | 681.793 | 74.0899 | 0.026702 | 668.54 | 71.3479 | 0.02012 | 717.711 | 717.706 | 1611780 | 24.1887 | 1593940 | 1599160 | 1553670 | 0 | 0 | 1536510 | 739.169 | 0 | 0 | 0 | 0 | 1536510 | 739.169 | 1508530 | 1478358.75
1115 | 2003-02-16 10:00 | 678 | 986 | 70 | 12.49 | 9.06 | 0 | 38.1764 | 150.459 | 31.8738 | 0 | 678 | 835.358 | 87.2923 | 6.3523 | 835.358 | 81.6915 | 0.033157 | 827.941 | 78.6681 | 0.024984 | 879.435 | 879.432 | 1974980 | 27.8051 | 1974810 | 1951510 | 1900110 | 0 | 0 | 1874090 | 732.234 | 0 | 0 | 0 | 0 | 1874090 | 732.234 | 1836240 | 1799519.125
1116 | 2003-02-16 11:00 | 750 | 1004 | 74 | 13.27 | 9.06 | 0 | 42.51 | 168.876 | 23.351 | 0 | 750 | 918.475 | 91.9131 | 7.0269 | 918.475 | 86.0158 | 0.036678 | 914.378 | 82.8324 | 0.027638 | 967.321 | 967.318 | 2172360 | 30.1156 | 2182610 | 2136130 | 2078840 | 0 | 0 | 2047330 | 726.705 | 5777.23 | 0 | 0 | 0 | 2041350 | 734.541 | 1997920 | 1957957.5
1117 | 2003-02-16 12:00 | 725 | 916 | 105 | 14.05 | 5.51 | 0 | 42.7724 | 188.845 | 22.7799 | 0 | 725 | 841.776 | 127.954 | 6.7927 | 841.776 | 119.744 | 0.035456 | 838.216 | 115.313 | 0.026717 | 924.948 | 924.939 | 2077180 | 34.2249 | 2082360 | 2002020 | 1950650 | 0 | 0 | 1921680 | 710.98 | 0 | 0 | 0 | 0 | 1921680 | 710.98 | 1882440 | 1844793.25
1118 | 2003-02-16 13:00 | 643 | 871 | 97 | 14.82 | 5.51 | 0 | 38.8999 | 207.578 | 30.6094 | 0 | 643 | 748.326 | 125.79 | 6.0244 | 748.326 | 117.719 | 0.031445 | 742.268 | 113.362 | 0.023695 | 829.984 | 829.977 | 1863920 | 32.9236 | 1858100 | 1796080 | 1749630 | 0 | 0 | 1726330 | 712.511 | 0 | 0 | 0 | 0 | 1726330 | 712.511 | 1693560 | 1659684.75
1119 | 2003-02-16 14:00 | 498 | 663 | 150 | 15.15 | 5.51 | 0 | 31.7242 | 223.284 | 42.4175 | 0 | 498 | 488.581 | 185.438 | 4.6659 | 488.581 | 173.54 | 0.024354 | 479.919 | 167.118 | 0.018351 | 627.644 | 627.634 | 1409510 | 28.8401 | 1383130 | 1360260 | 1325220 | 0 | 0 | 1311940 | 717.524 | 0 | 0 | 0 | 0 | 1311940 | 717.524 | 1289830 | 1264038
1120 | 2003-02-16 15:00 | 266 | 286 | 157 | 15.47 | 5.97 | 0 | 22.3127 | 235.931 | 55.7287 | 0 | 266 | 161.668 | 175.654 | 2.4922 | 161.668 | 164.384 | 0.013008 | 155.397 | 158.3 | 0.0098022 | 304.296 | 304.286 | 683350 | 21.913 | 640551 | 649426 | 632068 | 0 | 0 | 629013 | 716.551 | 0 | 0 | 0 | 0 | 629013 | 716.551 | 619057 | 606676.125
1121 | 2003-02-16 16:00 | 149 | 253 | 98 | 15.79 | 5.97 | 0 | 11.5032 | 246.302 | 69.6849 | 0 | 149 | 88.7881 | 112.571 | 1.396 | 82.0467 | 105.349 | 0.0072867 | 74.333 | 101.45 | 0.0054907 | 170.514 | 170.504 | 382909 | 19.4003 | 344361 | 353481 | 341218 | 0 | 0 | 340281 | 701.085 | 0 | 0 | 0 | 0 | 340281 | 701.085 | 333198 | 326534.5
1122 | 2003-02-16 17:00 | 10 | 64 | 7 | 15.36 | 5.97 | 0 | -0.1487 | 255.26 | 83.9626 | 0 | 10 | 3.6268 | 7.4873 | 0.093692 | 0 | 7.0069 | 0 | 0 | 6.7476 | 0 | 6.5452 | 6.5449 | 14698.1 | 15.4986 | 7481.6 | 7777.62 | 7627.24 | 0 | 0 | 7626.44 | 536.783 | 0 | 0 | 0 | 6687.97 | 938.468 | 660 | 902.86 | 884.8029
1123 | 2003-02-16 18:00 | 0 | 0 | 0 | 14.93 | 6.56 | 0
1124 | 2003-02-16 19:00 | 0 | 0 | 0 | 14.5 | 6.56 | 0
1125 | 2003-02-16 20:00 | 0 | 0 | 0 | 13.83 | 6.56 | 0
1126 | 2003-02-16 21:00 | 0 | 0 | 0 | 13.16 | 9.25 | 0
1127 | 2003-02-16 22:00 | 0 | 0 | 0 | 12.48 | 9.25 | 0
1128 | 2003-02-16 23:00 | 0 | 0 | 0 | 11.76 | 9.25 | 0
1129 | 2003-02-17 | 0 | 0 | 0 | 11.04 | 6.78 | 0
1130 | 2003-02-17 01:00 | 0 | 0 | 0 | 10.31 | 6.78 | 0
1131 | 2003-02-17 02:00 | 0 | 0 | 0 | 10.06 | 6.78 | 0
1132 | 2003-02-17 03:00 | 0 | 0 | 0 | 9.81 | 7.68 | 0
1133 | 2003-02-17 04:00 | 0 | 0 | 0 | 9.55 | 7.68 | 0
1134 | 2003-02-17 05:00 | 0 | 0 | 0 | 9.11 | 7.68 | 0
1135 | 2003-02-17 06:00 | 4 | 20 | 3 | 8.66 | 8.17 | 0 | -1.4128 | 103.615 | 85.5777 | 0 | 4 | 0.88629 | 2.9307 | 0.037477 | 0 | 2.7426 | 0 | 0 | 2.6411 | 0 | 2.5619 | 2.5617 | 5752.84 | 8.7072 | 1570.62 | 1556.58 | 1546.66 | 0 | 0 | 1546.59 | 377.624 | 0 | 0 | 0 | 1546.59 | 0 | 660 | 0 | 0
1136 | 2003-02-17 07:00 | 92 | 96 | 75 | 8.21 | 8.17 | 0 | 10.338 | 112.443 | 71.2546 | 0 | 92 | 30.4433 | 81.8016 | 0.86197 | 15.3122 | 76.5531 | 0.0044992 | 13.6954 | 73.7199 | 0.0033902 | 84.7961 | 84.8034 | 190444 | 9.7712 | 161400 | 173685 | 164663 | 0 | 0 | 164448 | 704.078 | 0 | 0 | 0 | 0 | 164448 | 704.078 | 159185 | 156001.75
1137 | 2003-02-17 08:00 | 243 | 221 | 163 | 9.53 | 8.17 | 0 | 21.305 | 122.595 | 57.2212 | 0 | 243 | 119.207 | 174.87 | 2.2767 | 109.695 | 163.65 | 0.011884 | 105.049 | 157.594 | 0.0089546 | 254.772 | 254.714 | 572024 | 14.2192 | 529996 | 555816 | 528022 | 0 | 0 | 525986 | 735.648 | 0 | 0 | 0 | 0 | 525986 | 735.648 | 516629 | 506296.0938
1138 | 2003-02-17 09:00 | 462 | 566 | 171 | 10.86 | 7.92 | 0 | 30.961 | 134.932 | 43.7629 | 0 | 462 | 408.515 | 202.859 | 4.3286 | 408.515 | 189.843 | 0.022594 | 400.659 | 182.817 | 0.017025 | 565.988 | 565.981 | 1271050 | 21.4447 | 1239570 | 1258240 | 1225060 | 0 | 0 | 1214340 | 739.401 | 0 | 0 | 0 | 0 | 1214340 | 739.401 | 1193200 | 1169339.5
1139 | 2003-02-17 10:00 | 551 | 533 | 220 | 12.18 | 7.92 | 0 | 38.5005 | 150.293 | 31.6281 | 0 | 551 | 452.734 | 260.887 | 5.1624 | 452.734 | 244.148 | 0.026946 | 448.785 | 235.112 | 0.020304 | 663.4 | 663.385 | 1489800 | 24.5863 | 1466670 | 1469020 | 1430110 | 0 | 0 | 1415360 | 734.682 | 0 | 0 | 0 | 0 | 1415360 | 734.682 | 1390340 | 1362535.75
1140 | 2003-02-17 11:00 | 474 | 217 | 327 | 13.08 | 7.92 | 0 | 42.8572 | 168.821 | 23.0199 | 0 | 474 | 198.912 | 354.536 | 4.441 | 198.912 | 331.789 | 0.023181 | 198.051 | 319.509 | 0.017467 | 502.051 | 502.033 | 1127440 | 22.4688 | 1091500 | 1103280 | 1072060 | 0 | 0 | 1063720 | 733.918 | 0 | 0 | 0 | 0 | 1063720 | 733.918 | 1045800 | 1024888.625
1141 | 2003-02-17 12:00 | 521 | 294 | 321 | 13.98 | 3.62 | 0 | 43.1164 | 188.93 | 22.4514 | 0 | 521 | 270.44 | 362.15 | 4.8814 | 270.44 | 338.913 | 0.025479 | 269.331 | 326.37 | 0.019199 | 577.849 | 577.817 | 1297630 | 28.2388 | 1267080 | 1249230 | 1214930 | 0 | 0 | 1203820 | 719.55 | 0 | 0 | 0 | 0 | 1203820 | 719.55 | 1183840 | 1160163.375
1142 | 2003-02-17 13:00 | 678 | 637 | 276 | 14.88 | 3.62 | 0 | 39.2148 | 207.774 | 30.3779 | 0 | 678 | 548.55 | 321.564 | 6.3523 | 548.55 | 300.932 | 0.033157 | 544.185 | 289.794 | 0.024984 | 808.984 | 808.976 | 1816750 | 34.8432 | 1808590 | 1733340 | 1686610 | 0 | 0 | 1664580 | 706.437 | 0 | 0 | 0 | 0 | 1664580 | 706.437 | 1633910 | 1601230.125
1143 | 2003-02-17 14:00 | 267 | 70 | 230 | 15.58 | 3.62 | 0 | 31.9993 | 223.538 | 42.2625 | 0 | 267 | 51.6743 | 241.674 | 2.5016 | 51.6743 | 226.168 | 0.013057 | 50.7668 | 217.798 | 0.009839 | 260.517 | 260.509 | 585034 | 22.0086 | 542618 | 549997 | 534601 | 0 | 0 | 532369 | 710.122 | 0 | 0 | 0 | 0 | 532369 | 710.122 | 523709 | 513234.5625
1144 | 2003-02-17 15:00 | 196 | 94 | 160 | 16.28 | 7.87 | 0 | 22.5508 | 236.208 | 55.622 | 0 | 196 | 53.0045 | 165.278 | 1.8364 | 53.0045 | 154.674 | 0.0095852 | 50.9612 | 148.949 | 0.0072227 | 193.92 | 193.914 | 435481 | 19.9179 | 395410 | 404843 | 393779 | 0 | 0 | 392550 | 705.845 | 0 | 0 | 0 | 0 | 392550 | 705.845 | 385522 | 377811.5625
1145 | 2003-02-17 16:00 | 142 | 216 | 98 | 16.98 | 7.87 | 0 | 11.7122 | 246.589 | 69.6107 | 0 | 142 | 75.5164 | 112.06 | 1.3304 | 72.6496 | 104.87 | 0.0069444 | 65.8558 | 100.988 | 0.0052327 | 161.844 | 161.828 | 363424 | 20.016 | 325460 | 333203 | 323650 | 0 | 0 | 322798 | 696.963 | 0 | 0 | 0 | 0 | 322798 | 696.963 | 315832 | 309515.375
1146 | 2003-02-17 17:00 | 10 | 57 | 7 | 16.02 | 7.87 | 0 | 0.039943 | 255.555 | 83.9121 | 0 | 10 | 3.6571 | 7.5129 | 0.093692 | 0.68295 | 7.0309 | 0.00048904 | 0.39512 | 6.7707 | 0.0003685 | 6.9512 | 6.9525 | 15613.8 | 16.1504 | 8163.49 | 8476.92 | 8139.66 | 0 | 0 | 8138.71 | 531.923 | 0 | 0 | 0 | 6771.03 | 1367.67 | 660 | 1315.83 | 1289.5166
1147 | 2003-02-17 18:00 | 0 | 0 | 0 | 15.06 | 6.08 | 0
1148 | 2003-02-17 19:00 | 0 | 0 | 0 | 14.09 | 6.08 | 0
1149 | 2003-02-17 20:00 | 0 | 0 | 0 | 13.54 | 6.08 | 0
1150 | 2003-02-17 21:00 | 0 | 0 | 0 | 12.98 | 8.9 | 0
1151 | 2003-02-17 22:00 | 0 | 0 | 0 | 12.43 | 8.9 | 0
1152 | 2003-02-17 23:00 | 0 | 0 | 0 | 11.54 | 8.9 | 0
1153 | 2003-02-18 | 0 | 0 | 0 | 10.65 | 7.84 | 0
1154 | 2003-02-18 01:00 | 0 | 0 | 0 | 9.76 | 7.84 | 0
1155 | 2003-02-18 02:00 | 0 | 0 | 0 | 9.88 | 7.84 | 0
1156 | 2003-02-18 03:00 | 0 | 0 | 0 | 9.99 | 9.47 | 0
1157 | 2003-02-18 04:00 | 0 | 0 | 0 | 10.11 | 9.47 | 0
1158 | 2003-02-18 05:00 | 0 | 0 | 0 | 9.11 | 9.47 | 0
1159 | 2003-02-18 06:00 | 7 | 97 | 3 | 8.12 | 5.82 | 0 | -1.1953 | 103.338 | 85.4936 | 0 | 7 | 3.6124 | 3.1948 | 0.065585 | 0 | 2.9898 | 0 | 0 | 2.8791 | 0 | 2.7928 | 2.7926 | 6271.38 | 8.1797 | 1850.24 | 1842.69 | 1829.06 | 0 | 0 | 1828.98 | 408.217 | 0 | 0 | 0 | 1828.98 | 0 | 660 | 0 | 0
1160 | 2003-02-18 07:00 | 132 | 451 | 49 | 7.12 | 5.82 | 0 | 10.5735 | 112.177 | 71.1482 | 0 | 132 | 146.155 | 64.217 | 1.2367 | 75.9631 | 60.0967 | 0.0064554 | 68.0067 | 57.8726 | 0.0048642 | 122.108 | 122.03 | 274033 | 9.729 | 241910 | 258855 | 223789 | 0 | 0 | 223367 | 720.453 | 0 | 0 | 0 | 0 | 223367 | 720.453 | 217009 | 212669.0625
1161 | 2003-02-18 08:00 | 300 | 463 | 130 | 8.81 | 5.82 | 0 | 21.5664 | 122.341 | 57.0848 | 0 | 300 | 251.313 | 153.371 | 2.8108 | 232.237 | 143.531 | 0.014671 | 222.48 | 138.219 | 0.011055 | 349.889 | 349.8 | 785565 | 16.2887 | 744106 | 771933 | 723687 | 0 | 0 | 719874 | 739.584 | 0 | 0 | 0 | 0 | 719874 | 739.584 | 707600 | 693448.4375
1162 | 2003-02-18 09:00 | 543 | 781 | 138 | 10.5 | 10.09 | 0 | 31.2549 | 134.705 | 43.5827 | 0 | 543 | 565.436 | 171.608 | 5.0875 | 565.436 | 160.597 | 0.026555 | 554.679 | 154.654 | 0.02001 | 688.072 | 688.062 | 1545210 | 21.7451 | 1524440 | 1545100 | 1502150 | 0 | 0 | 1486340 | 745.277 | 0 | 0 | 0 | 0 | 1486340 | 745.277 | 1459270 | 1430087.375
1163 | 2003-02-18 10:00 | 689 | 989 | 70 | 12.19 | 10.09 | 0 | 38.8285 | 150.127 | 31.3798 | 0 | 689 | 842.854 | 86.9766 | 6.4554 | 842.854 | 81.396 | 0.033695 | 835.634 | 78.3836 | 0.02539 | 886.621 | 886.617 | 1991120 | 26.6801 | 1991780 | 1977620 | 1926470 | 0 | 0 | 1899940 | 734.883 | 0 | 0 | 0 | 0 | 1899940 | 734.883 | 1861230 | 1824001.375
1164 | 2003-02-18 11:00 | 760 | 1005 | 74 | 13.3 | 10.09 | 0 | 43.2078 | 168.769 | 22.6852 | 0 | 760 | 924.461 | 91.5914 | 7.1206 | 924.461 | 85.7148 | 0.037167 | 920.585 | 82.5425 | 0.028006 | 973.061 | 973.059 | 2185240 | 29.2029 | 2196200 | 2157760 | 2100210 | 0 | 0 | 2068290 | 729.281 | 24382.5 | 0 | 0 | 0 | 2043840 | 747.353 | 1999550 | 1959557.5
1165 | 2003-02-18 12:00 | 765 | 1006 | 75 | 14.41 | 5.82 | 0 | 43.4631 | 189.02 | 22.1213 | 0 | 765 | 929.233 | 92.7604 | 7.1674 | 929.233 | 86.8087 | 0.037412 | 925.541 | 83.596 | 0.028191 | 978.89 | 978.885 | 2198320 | 35.3384 | 2209980 | 2114750 | 2059270 | 0 | 0 | 2026800 | 708.863 | 0 | 0 | 0 | 0 | 2026800 | 708.863 | 1983830 | 1944148.875
1166 | 2003-02-18 13:00 | 701 | 991 | 72 | 15.52 | 5.82 | 0 | 39.5311 | 207.976 | 30.1483 | 0 | 701 | 854.543 | 89.3084 | 6.5678 | 854.543 | 83.5782 | 0.034282 | 847.859 | 80.485 | 0.025832 | 900.519 | 900.513 | 2022320 | 34.7728 | 2024610 | 1941700 | 1891930 | 0 | 0 | 1864410 | 708.629 | 0 | 0 | 0 | 0 | 1864410 | 708.629 | 1827170 | 1790628.125
1167 | 2003-02-18 14:00 | 575 | 956 | 65 | 16.09 | 5.82 | 0 | 32.2748 | 223.799 | 42.1103 | 0 | 575 | 708.538 | 81.1775 | 5.3873 | 708.538 | 75.969 | 0.02812 | 696.211 | 73.1575 | 0.021189 | 746.308 | 746.305 | 1676010 | 32.0459 | 1661110 | 1611450 | 1568170 | 0 | 0 | 1549460 | 713.689 | 0 | 0 | 0 | 0 | 1549460 | 713.689 | 1522030 | 1491588
1168 | 2003-02-18 15:00 | 387 | 876 | 48 | 16.65 | 4.85 | 0 | 22.7887 | 236.491 | 55.5183 | 0 | 387 | 495.496 | 61.1146 | 3.6259 | 495.496 | 57.1934 | 0.018926 | 476.51 | 55.0767 | 0.014261 | 515.653 | 515.653 | 1158030 | 28.3898 | 1122940 | 1106300 | 1077070 | 0 | 0 | 1068200 | 714.847 | 0 | 0 | 0 | 0 | 1068200 | 714.847 | 1051150 | 1030128.125
1169 | 2003-02-18 16:00 | 181 | 641 | 48 | 17.22 | 4.85 | 0 | 11.9207 | 246.88 | 69.5391 | 0 | 181 | 225.083 | 62.0308 | 1.6958 | 225.083 | 58.0508 | 0.0088517 | 204.142 | 55.9023 | 0.0066699 | 252.25 | 252.247 | 566482 | 22.9629 | 524211 | 529092 | 515417 | 0 | 0 | 513307 | 705.113 | 0 | 0 | 0 | 0 | 513307 | 705.113 | 505002 | 494901.9688
1170 | 2003-02-18 17:00 | 14 | 173 | 4 | 16.51 | 4.85 | 0 | 0.22806 | 255.854 | 83.864 | 0 | 14 | 12.2862 | 4.7858 | 0.13117 | 2.7255 | 4.4787 | 0.00068466 | 1.5869 | 4.3129 | 0.0005159 | 5.7233 | 5.7282 | 12865.3 | 16.6404 | 6315.5 | 6516.59 | 5427.43 | 0 | 0 | 5426.83 | 494.093 | 0 | 0 | 0 | 4407.12 | 1019.71 | 660 | 981.059 | 961.438
1171 | 2003-02-18 18:00 | 0 | 0 | 0 | 15.79 | 5.63 | 0
1172 | 2003-02-18 19:00 | 0 | 0 | 0 | 15.08 | 5.63 | 0
1173 | 2003-02-18 20:00 | 0 | 0 | 0 | 14.13 | 5.63 | 0
1174 | 2003-02-18 21:00 | 0 | 0 | 0 | 13.17 | 4.21 | 0
1175 | 2003-02-18 22:00 | 0 | 0 | 0 | 12.22 | 4.21 | 0
1176 | 2003-02-18 23:00 | 0 | 0 | 0 | 11.15 | 4.21 | 0
1177 | 2003-02-19 | 0 | 0 | 0 | 10.09 | 4.82 | 0
1178 | 2003-02-19 01:00 | 0 | 0 | 0 | 9.02 | 4.82 | 0
1179 | 2003-02-19 02:00 | 0 | 0 | 0 | 8.64 | 4.82 | 0
1180 | 2003-02-19 03:00 | 0 | 0 | 0 | 8.25 | 4.47 | 0
1181 | 2003-02-19 04:00 | 0 | 0 | 0 | 7.87 | 4.47 | 0
1182 | 2003-02-19 05:00 | 0 | 0 | 0 | 7.39 | 4.47 | 0
1183 | 2003-02-19 06:00 | 9 | 154 | 2 | 6.91 | 3.16 | 0 | -0.97362 | 103.061 | 85.4063 | 0 | 9 | 6.444 | 2.2933 | 0.084323 | 0 | 2.1462 | 0 | 0 | 2.0667 | 0 | 2.0048 | 2.0046 | 4501.92 | 6.961 | 973.772 | 955.92 | 951.157 | 0 | 0 | 951.116 | 295.985 | 0 | 0 | 0 | 951.116 | 0 | 660 | 0 | 0
1184 | 2003-02-19 07:00 | 170 | 691 | 40 | 6.43 | 3.16 | 0 | 10.813 | 111.91 | 71.0389 | 0 | 170 | 225.156 | 52.982 | 1.5928 | 125.413 | 49.5826 | 0.0083137 | 112.385 | 47.7476 | 0.0062645 | 155.335 | 155.268 | 348676 | 10.3797 | 315477 | 334820 | 282238 | 0 | 0 | 281500 | 716.345 | 0 | 0 | 0 | 0 | 281500 | 716.345 | 275041 | 269540.375
1185 | 2003-02-19 08:00 | 381 | 875 | 56 | 7.93 | 3.16 | 0 | 21.8316 | 122.086 | 56.9459 | 0 | 381 | 476.672 | 70.5847 | 3.5697 | 442.265 | 66.0558 | 0.018632 | 423.836 | 63.6111 | 0.01404 | 472.837 | 472.678 | 1061540 | 19.954 | 1026530 | 1045610 | 968102 | 0 | 0 | 961022 | 732.338 | 0 | 0 | 0 | 0 | 961022 | 732.338 | 944972 | 926072.25
1186 | 2003-02-19 09:00 | 557 | 947 | 62 | 9.42 | 6.35 | 0 | 31.5525 | 134.477 | 43.4001 | 0 | 557 | 687.306 | 77.512 | 5.2187 | 687.306 | 72.5387 | 0.02724 | 674.374 | 69.8541 | 0.020526 | 721.921 | 721.919 | 1621250 | 24.3374 | 1603840 | 1608040 | 1562370 | 0 | 0 | 1545000 | 738.817 | 0 | 0 | 0 | 0 | 1545000 | 738.817 | 1516810 | 1486472
1187 | 2003-02-19 10:00 | 688 | 984 | 68 | 10.91 | 6.35 | 0 | 39.1602 | 149.962 | 31.1292 | 0 | 688 | 840.429 | 84.4469 | 6.446 | 840.429 | 79.0286 | 0.033646 | 833.36 | 76.1038 | 0.025353 | 882.204 | 882.202 | 1981200 | 29.1395 | 1981360 | 1946910 | 1892820 | 0 | 0 | 1866770 | 728.754 | 0 | 0 | 0 | 0 | 1866770 | 728.754 | 1829200 | 1792614.5
1188 | 2003-02-19 11:00 | 765 | 1006 | 74 | 11.83 | 6.35 | 0 | 43.562 | 168.719 | 22.3472 | 0 | 765 | 927.395 | 91.4292 | 7.1674 | 927.395 | 85.563 | 0.037412 | 923.629 | 82.3963 | 0.028191 | 975.872 | 975.867 | 2191560 | 31.9949 | 2202850 | 2138690 | 2082950 | 0 | 0 | 2050690 | 719.316 | 7597.45 | 0 | 0 | 0 | 2042770 | 729.328 | 1999300 | 1959311.25
1189 | 2003-02-19 12:00 | 770 | 843 | 188 | 12.75 | 5.75 | 0 | 43.8124 | 189.115 | 21.79 | 0 | 770 | 780.611 | 233.813 | 7.2143 | 780.611 | 218.811 | 0.037656 | 777.607 | 210.713 | 0.028375 | 958.698 | 958.689 | 2152970 | 33.3394 | 2162190 | 2086970 | 2032640 | 0 | 0 | 2001510 | 714.784 | 0 | 0 | 0 | 0 | 2001510 | 714.784 | 1959460 | 1920267.375
1190 | 2003-02-19 13:00 | 545 | 460 | 251 | 13.68 | 5.75 | 0 | 39.8487 | 208.186 | 29.921 | 0 | 545 | 397.673 | 294.354 | 5.1062 | 397.673 | 275.468 | 0.026653 | 394.615 | 265.273 | 0.020083 | 640.111 | 640.102 | 1437500 | 27.4272 | 1412240 | 1397430 | 1359830 | 0 | 0 | 1346110 | 724.397 | 0 | 0 | 0 | 0 | 1346110 | 724.397 | 1322980 | 1296519
1191 | 2003-02-19 14:00 | 489 | 647 | 141 | 13.78 | 5.75 | 0 | 32.5506 | 224.067 | 41.9612 | 0 | 489 | 480.949 | 175.212 | 4.5816 | 480.949 | 163.97 | 0.023914 | 472.657 | 157.902 | 0.01802 | 611.659 | 611.649 | 1373600 | 26.9161 | 1345840 | 1334630 | 1297630 | 0 | 0 | 1285140 | 724.256 | 0 | 0 | 0 | 0 | 1285140 | 724.256 | 1263280 | 1238017.5
1192 | 2003-02-19 15:00 | 339 | 656 | 83 | 13.89 | 11.77 | 0 | 23.0262 | 236.78 | 55.4176 | 0 | 339 | 371.475 | 106.314 | 3.1762 | 371.475 | 99.4931 | 0.016578 | 357.325 | 95.8109 | 0.012492 | 439.554 | 439.551 | 987124 | 20.3793 | 947720 | 966741 | 938704 | 0 | 0 | 932366 | 738.199 | 0 | 0 | 0 | 0 | 932366 | 738.199 | 916600 | 898268.25
1193 | 2003-02-19 16:00 | 184 | 469 | 85 | 14 | 11.77 | 0 | 12.1286 | 247.177 | 69.4704 | 0 | 184 | 165.242 | 100.907 | 1.7239 | 165.242 | 94.4323 | 0.0089984 | 149.945 | 90.9374 | 0.0067805 | 233.662 | 233.662 | 524745 | 17.4497 | 482974 | 499772 | 486804 | 0 | 0 | 485015 | 722.682 | 0 | 0 | 0 | 0 | 485015 | 722.682 | 476474 | 466944.625
1194 | 2003-02-19 17:00 | 14 | 131 | 6 | 12.83 | 11.77 | 0 | 0.4156 | 256.158 | 83.8183 | 0 | 14 | 9.9018 | 6.9133 | 0.13117 | 2.577 | 6.4698 | 0.00068466 | 1.5093 | 6.2303 | 0.0005159 | 7.5079 | 7.5099 | 16866.6 | 12.9409 | 9150.61 | 9640.32 | 8607.62 | 0 | 0 | 8606.52 | 539.984 | 0 | 0 | 0 | 4569.54 | 4036.98 | 660 | 3884.61 | 3806.9214
1195 | 2003-02-19 18:00 | 0 | 0 | 0 | 11.65 | 10.94 | 0
1196 | 2003-02-19 19:00 | 0 | 0 | 0 | 10.48 | 10.94 | 0
1197 | 2003-02-19 20:00 | 0 | 0 | 0 | 9.56 | 10.94 | 0
1198 | 2003-02-19 21:00 | 0 | 0 | 0 | 8.65 | 6.25 | 0
1199 | 2003-02-19 22:00 | 0 | 0 | 0 | 7.73 | 6.25 | 0
1200 | 2003-02-19 23:00 | 0 | 0 | 0 | 7.11 | 6.25 | 0
1201 | 2003-02-20 | 0 | 0 | 0 | 6.49 | 8.86 | 0
1202 | 2003-02-20 01:00 | 0 | 0 | 0 | 5.86 | 8.86 | 0
1203 | 2003-02-20 02:00 | 0 | 0 | 0 | 5.41 | 8.86 | 0
1204 | 2003-02-20 03:00 | 0 | 0 | 0 | 4.95 | 10.26 | 0
1205 | 2003-02-20 04:00 | 0 | 0 | 0 | 4.5 | 10.26 | 0
1206 | 2003-02-20 05:00 | 0 | 0 | 0 | 4.3 | 10.26 | 0
1207 | 2003-02-20 06:00 | 3 | 0 | 3 | 4.1 | 9.77 | 0 | -0.74794 | 102.782 | 85.3159 | 0 | 3 | 0 | 2.7493 | 0.028108 | 0 | 2.5729 | 0 | 0 | 2.4777 | 0 | 2.4034 | 2.4033 | 5397.11 | 4.1401 | 1388.83 | 1365.96 | 1358.47 | 0 | 0 | 1358.41 | 354.832 | 0 | 0 | 0 | 1358.41 | 0 | 660 | 0 | 0
1208 | 2003-02-20 07:00 | 54 | 0 | 54 | 3.9 | 9.77 | 0 | 11.0563 | 111.641 | 70.9269 | 0 | 54 | 0 | 50.6275 | 0.50594 | 0 | 47.3791 | 0.0026408 | 0 | 45.6257 | 0.0019899 | 44.2588 | 44.2558 | 99387.5 | 4.6376 | 78396.5 | 86736.9 | 84393.8 | 0 | 0 | 84334.5 | 689.972 | 0 | 0 | 0 | 0 | 84334.5 | 689.972 | 81317.1 | 79690.7812
1209 | 2003-02-20 08:00 | 104 | 0 | 104 | 4.96 | 9.77 | 0 | 22.1005 | 121.83 | 56.8046 | 0 | 104 | 0 | 97.7501 | 0.9744 | 0 | 91.4783 | 0.005086 | 0 | 88.0927 | 0.0038324 | 85.4537 | 85.4489 | 191897 | 6.3842 | 162596 | 177728 | 172472 | 0 | 0 | 172242 | 715.188 | 0 | 0 | 0 | 0 | 172242 | 715.188 | 166629 | 163296.1406
1210 | 2003-02-20 09:00 | 156 | 3 | 154 | 6.03 | 8.76 | 0 | 31.8538 | 134.248 | 43.2155 | 0 | 156 | 2.7618 | 145.801 | 1.4616 | 2.7618 | 136.446 | 0.0076291 | 2.7104 | 131.397 | 0.0057487 | 130.089 | 130.077 | 292118 | 8.3379 | 257004 | 277677 | 269283 | 0 | 0 | 268745 | 729.91 | 0 | 0 | 0 | 0 | 268745 | 729.91 | 261304 | 256077.6562
1211 | 2003-02-20 10:00 | 699 | 792 | 196 | 7.09 | 8.76 | 0 | 39.4954 | 149.796 | 30.8764 | 0 | 699 | 678.776 | 238.302 | 6.5491 | 678.776 | 223.012 | 0.034184 | 673.172 | 214.759 | 0.025758 | 861.318 | 861.311 | 1934280 | 22.3721 | 1932020 | 1952680 | 1895650 | 0 | 0 | 1870930 | 749.883 | 0 | 0 | 0 | 0 | 1870930 | 749.883 | 1832130 | 1795485
1212 | 2003-02-20 11:00 | 772 | 1007 | 75 | 8.86 | 8.76 | 0 | 43.9194 | 168.672 | 22.006 | 0 | 772 | 931.628 | 92.4449 | 7.233 | 931.628 | 86.5134 | 0.037754 | 927.967 | 83.3116 | 0.028448 | 980.968 | 980.964 | 2203000 | 26.2651 | 2214910 | 2202990 | 2142120 | 0 | 0 | 2109890 | 740.238 | 66343.6 | 0 | 0 | 0 | 2044460 | 769.16 | 1997680 | 1957725.5
1213 | 2003-02-20 12:00 | 775 | 1007 | 75 | 10.63 | 6.65 | 0 | 44.1642 | 189.217 | 21.4575 | 0 | 775 | 935.075 | 92.4323 | 7.2611 | 935.075 | 86.5017 | 0.037901 | 931.594 | 83.3003 | 0.028559 | 984.475 | 984.469 | 2210880 | 30.5858 | 2223220 | 2171500 | 2112090 | 0 | 0 | 2079460 | 725.451 | 34995.7 | 0 | 0 | 0 | 2044010 | 747.606 | 1999690 | 1959691.5
1214 | 2003-02-20 13:00 | 711 | 993 | 72 | 12.4 | 6.65 | 0 | 40.1675 | 208.402 | 29.696 | 0 | 711 | 860.553 | 88.9849 | 6.6615 | 860.553 | 83.2755 | 0.034771 | 854.047 | 80.1935 | 0.026201 | 906.239 | 906.234 | 2035170 | 30.7699 | 2038140 | 1988920 | 1936150 | 0 | 0 | 1908410 | 722.574 | 0 | 0 | 0 | 0 | 1908410 | 722.574 | 1869530 | 1832139
1215 | 2003-02-20 14:00 | 584 | 959 | 65 | 12.97 | 6.65 | 0 | 32.8266 | 224.34 | 41.8153 | 0 | 584 | 713.543 | 80.8606 | 5.4716 | 713.543 | 75.6724 | 0.02856 | 701.35 | 72.8718 | 0.021521 | 751.016 | 751.014 | 1686590 | 28.1935 | 1672180 | 1649480 | 1603670 | 0 | 0 | 1584820 | 727.116 | 0 | 0 | 0 | 0 | 1584820 | 727.116 | 1555910 | 1524789.125
1216 | 2003-02-20 15:00 | 408 | 889 | 57 | 13.54 | 7.11 | 0 | 23.2634 | 237.074 | 55.3199 | 0 | 408 | 505.666 | 71.5375 | 3.8226 | 505.666 | 66.9475 | 0.019953 | 486.515 | 64.4698 | 0.015035 | 534.469 | 534.467 | 1200280 | 24.0609 | 1166470 | 1171050 | 1138320 | 0 | 0 | 1128860 | 731.552 | 0 | 0 | 0 | 0 | 1128860 | 731.552 | 1109790 | 1087599
1217 | 2003-02-20 16:00 | 187 | 647 | 48 | 14.11 | 7.11 | 0 | 12.3359 | 247.477 | 69.4044 | 0 | 187 | 228.869 | 61.7982 | 1.752 | 228.869 | 57.8332 | 0.0091451 | 207.782 | 55.6928 | 0.006891 | 255.577 | 255.573 | 573954 | 19.1409 | 531612 | 545848 | 531531 | 0 | 0 | 529379 | 719.26 | 0 | 0 | 0 | 0 | 529379 | 719.26 | 520465 | 510055.6562
1218 | 2003-02-20 17:00 | 15 | 185 | 4 | 13.84 | 7.11 | 0 | 0.60254 | 256.465 | 83.775 | 0 | 15 | 13.7099 | 4.8385 | 0.14054 | 4.4749 | 4.528 | 0.00073356 | 2.6352 | 4.3605 | 0.00055276 | 6.7863 | 6.789 | 15248.3 | 13.9736 | 8096.71 | 8475.48 | 6914.33 | 0 | 0 | 6913.44 | 519.328 | 0 | 0 | 0 | 3863.26 | 3050.18 | 660 | 2934.89 | 2876.1934
1219 | 2003-02-20 18:00 | 0 | 0 | 0 | 13.56 | 5.75 | 0
1220 | 2003-02-20 19:00 | 0 | 0 | 0 | 13.29 | 5.75 | 0
1221 | 2003-02-20 20:00 | 0 | 0 | 0 | 12.91 | 5.75 | 0
1222 | 2003-02-20 21:00 | 0 | 0 | 0 | 12.53 | 8.74 | 0
1223 | 2003-02-20 22:00 | 0 | 0 | 0 | 12.16 | 8.74 | 0
1224 | 2003-02-20 23:00 | 0 | 0 | 0 | 11.55 | 8.74 | 0
1225 | 2003-02-21 | 0 | 0 | 0 | 10.93 | 7.82 | 0
1226 | 2003-02-21 01:00 | 0 | 0 | 0 | 10.32 | 7.82 | 0
1227 | 2003-02-21 02:00 | 0 | 0 | 0 | 9.97 | 7.82 | 0
1228 | 2003-02-21 03:00 | 0 | 0 | 0 | 9.61 | 7.68 | 0
1229 | 2003-02-21 04:00 | 0 | 0 | 0 | 9.26 | 7.68 | 0
1230 | 2003-02-21 05:00 | 0 | 0 | 0 | 8.69 | 7.68 | 0
1231 | 2003-02-21 06:00 | 11 | 170 | 3 | 8.12 | 6.44 | 0 | -0.51836 | 102.503 | 85.2224 | 0 | 11 | 7.6587 | 3.4178 | 0.10306 | 0 | 3.1985 | 0 | 0 | 3.0802 | 0 | 2.9878 | 2.9876 | 6709.5 | 8.1814 | 2098.43 | 2101.09 | 2082.9 | 0 | 0 | 2082.8 | 430.334 | 0 | 0 | 0 | 2082.8 | 0 | 660 | 0 | 0
1232 | 2003-02-21 07:00 | 179 | 703 | 41 | 7.55 | 6.44 | 0 | 11.3033 | 111.372 | 70.8123 | 0 | 179 | 231.404 | 53.7996 | 1.6771 | 141.497 | 50.3477 | 0.0087538 | 127.046 | 48.4844 | 0.0065962 | 170.271 | 170.244 | 382287 | 11.0476 | 348074 | 368631 | 314491 | 0 | 0 | 313599 | 719.25 | 0 | 0 | 0 | 452.831 | 313146 | 724.909 | 306246 | 300120.75
1233 | 2003-02-21 08:00 | 390 | 880 | 55 | 8.98 | 6.44 | 0 | 22.3728 | 121.573 | 56.661 | 0 | 390 | 483.703 | 69.0714 | 3.654 | 452.249 | 64.6397 | 0.019073 | 433.717 | 62.2474 | 0.014372 | 481.099 | 481.179 | 1080650 | 18.8657 | 1045890 | 1071050 | 987245 | 0 | 0 | 980096 | 743.166 | 0 | 0 | 0 | 0 | 980096 | 743.166 | 963187 | 943923.125
1234 | 2003-02-21 09:00 | 572 | 954 | 65 | 10.4 | 2.08 | 0 | 32.1586 | 134.018 | 43.0289 | 0 | 572 | 696.311 | 80.7485 | 5.3592 | 696.311 | 75.5675 | 0.027973 | 683.5 | 72.7708 | 0.021078 | 733.603 | 733.603 | 1647490 | 30.4502 | 1631270 | 1593420 | 1553440 | 0 | 0 | 1535200 | 716.503 | 0 | 0 | 0 | 0 | 1535200 | 716.503 | 1508080 | 1477919.875
1235 | 2003-02-21 10:00 | 705 | 991 | 72 | 11.82 | 2.08 | 0 | 39.8342 | 149.63 | 30.6216 | 0 | 705 | 850.383 | 88.8552 | 6.6053 | 850.383 | 83.1541 | 0.034477 | 843.493 | 80.0766 | 0.025979 | 895.887 | 895.884 | 2011930 | 36.3055 | 2013680 | 1918040 | 1868400 | 0 | 0 | 1841250 | 703.916 | 0 | 0 | 0 | 0 | 1841250 | 703.916 | 1804870 | 1768767.875
1236 | 2003-02-21 11:00 | 777 | 1008 | 75 | 13.06 | 2.08 | 0 | 44.28 | 168.627 | 21.6617 | 0 | 777 | 934.483 | 92.2793 | 7.2799 | 934.483 | 86.3585 | 0.037998 | 930.933 | 83.1624 | 0.028633 | 983.7 | 983.696 | 2209130 | 39.9455 | 2221380 | 2082540 | 2031380 | 0 | 0 | 1998360 | 692.923 | 0 | 0 | 0 | 0 | 1998360 | 692.923 | 1956420 | 1917294
1237 | 2003-02-21 12:00 | 780 | 1008 | 75 | 14.29 | 1.47 | 0 | 44.5182 | 189.324 | 21.124 | 0 | 780 | 937.943 | 92.2671 | 7.308 | 937.943 | 86.347 | 0.038145 | 934.565 | 83.1514 | 0.028743 | 987.213 | 987.211 | 2217030 | 42.396 | 2229700 | 2067250 | 2015130 | 0 | 0 | 1982050 | 686.659 | 0 | 0 | 0 | 0 | 1982050 | 686.659 | 1940730 | 1901919.625
1238 | 2003-02-21 13:00 | 675 | 890 | 99 | 15.52 | 1.47 | 0 | 40.4874 | 208.626 | 29.4736 | 0 | 675 | 772.325 | 120.044 | 6.3242 | 772.325 | 112.342 | 0.03301 | 766.584 | 108.184 | 0.024874 | 848.549 | 848.543 | 1905610 | 39.6781 | 1901890 | 1783930 | 1737870 | 0 | 0 | 1713490 | 691.559 | 0 | 0 | 0 | 0 | 1713490 | 691.559 | 1681640 | 1648009.125
1239 | 2003-02-21 14:00 | 559 | 917 | 59 | 16.45 | 1.47 | 0 | 33.1025 | 224.62 | 41.6726 | 0 | 559 | 683.852 | 73.5845 | 5.2374 | 683.852 | 68.8632 | 0.027337 | 672.269 | 66.3146 | 0.020599 | 716.446 | 716.443 | 1608950 | 36.8472 | 1590980 | 1510500 | 1473440 | 0 | 0 | 1456020 | 695.368 | 0 | 0 | 0 | 0 | 1456020 | 695.368 | 1431710 | 1403071.75
1240 | 2003-02-21 15:00 | 405 | 887 | 52 | 17.38 | 3.28 | 0 | 23.5 | 237.373 | 55.2253 | 0 | 405 | 504.914 | 65.4541 | 3.7945 | 504.914 | 61.2544 | 0.019806 | 485.897 | 58.9875 | 0.014924 | 528.552 | 528.55 | 1186990 | 30.719 | 1152770 | 1124040 | 1094880 | 0 | 0 | 1085520 | 707.06 | 0 | 0 | 0 | 0 | 1085520 | 707.06 | 1068520 | 1047148.8125
1241 | 2003-02-21 16:00 | 193 | 653 | 51 | 18.3 | 3.28 | 0 | 12.5425 | 247.783 | 69.3411 | 0 | 193 | 230.693 | 64.7568 | 1.8083 | 230.693 | 60.6019 | 0.0094385 | 209.534 | 58.3591 | 0.0071121 | 259.863 | 259.858 | 583576 | 24.858 | 541151 | 541460 | 527685 | 0 | 0 | 525448 | 700.008 | 0 | 0 | 0 | 0 | 525448 | 700.008 | 517175 | 506831.25
1242 | 2003-02-21 17:00 | 16 | 192 | 4 | 17.88 | 3.28 | 0 | 0.78886 | 256.777 | 83.7341 | 0 | 16 | 15.0541 | 4.8616 | 0.14991 | 4.8856 | 4.5497 | 0.00078247 | 2.8917 | 4.3813 | 0.0005896 | 7.0554 | 7.0524 | 15840.4 | 18.058 | 8553.12 | 8813.08 | 7046.5 | 0 | 0 | 7045.55 | 515.04 | 0 | 0 | 0 | 4700.12 | 2345.42 | 660 | 2256.66 | 2211.5303
1243 | 2003-02-21 18:00 | 0 | 0 | 0 | 17.46 | 7.33 | 0
1244 | 2003-02-21 19:00 | 0 | 0 | 0 | 17.04 | 7.33 | 0
1245 | 2003-02-21 20:00 | 0 | 0 | 0 | 16.08 | 7.33 | 0
1246 | 2003-02-21 21:00 | 0 | 0 | 0 | 15.13 | 7.99 | 0
1247 | 2003-02-21 22:00 | 0 | 0 | 0 | 14.17 | 7.99 | 0
1248 | 2003-02-21 23:00 | 0 | 0 | 0 | 13.2 | 7.99 | 0
1249 | 2003-02-22 | 0 | 0 | 0 | 12.23 | 7.87 | 0
1250 | 2003-02-22 01:00 | 0 | 0 | 0 | 11.26 | 7.87 | 0
1251 | 2003-02-22 02:00 | 0 | 0 | 0 | 10.97 | 7.87 | 0
1252 | 2003-02-22 03:00 | 0 | 0 | 0 | 10.69 | 8.31 | 0
1253 | 2003-02-22 04:00 | 0 | 0 | 0 | 10.4 | 8.31 | 0
1254 | 2003-02-22 05:00 | 0 | 0 | 0 | 9.77 | 8.31 | 0
1255 | 2003-02-22 06:00 | 1 | 361 | 0 | 9.14 | 7.28 | 0 | -0.285 | 102.223 | 85.1259 | 0 | 1 | 0.97662 | 0 | 0.0093692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.14 | 0 | 0 | 0 | 0 | 0 | 0 | 660 | 0 | 0 | 0 | 0 | 0 | 660 | 0 | 0
1256 | 2003-02-22 07:00 | 183 | 709 | 40 | 8.51 | 7.28 | 0 | 11.5538 | 111.102 | 70.6951 | 0 | 183 | 236.036 | 52.5804 | 1.7146 | 148.317 | 49.2067 | 0.0089495 | 133.301 | 47.3856 | 0.0067436 | 175.272 | 175.183 | 393385 | 11.9214 | 358874 | 378702 | 327486 | 0 | 0 | 326505 | 710.351 | 0 | 0 | 0 | 233.943 | 326271 | 712.566 | 319579 | 313187.0625
1257 | 2003-02-22 08:00 | 395 | 881 | 56 | 10.06 | 7.28 | 0 | 22.6486 | 121.315 | 56.5153 | 0 | 395 | 485.695 | 70.0828 | 3.7008 | 455.837 | 65.5861 | 0.019317 | 437.318 | 63.1588 | 0.014556 | 485.476 | 485.526 | 1090410 | 19.5149 | 1055810 | 1078480 | 997009 | 0 | 0 | 989673 | 740.414 | 0 | 0 | 0 | 0 | 989673 | 740.414 | 972715 | 953260.25
1258 | 2003-02-22 09:00 | 578 | 956 | 66 | 11.61 | 1.7 | 0 | 32.4667 | 133.787 | 42.8406 | 0 | 578 | 699.361 | 81.7643 | 5.4154 | 699.361 | 76.5181 | 0.028267 | 686.64 | 73.6862 | 0.021299 | 737.537 | 737.534 | 1656310 | 32.2864 | 1640500 | 1589640 | 1547940 | 0 | 0 | 1529620 | 712.476 | 0 | 0 | 0 | 0 | 1529620 | 712.476 | 1502800 | 1472746.75
1259 | 2003-02-22 10:00 | 708 | 990 | 71 | 13.16 | 1.7 | 0 | 40.1763 | 149.465 | 30.365 | 0 | 708 | 851.934 | 87.5149 | 6.6334 | 851.934 | 81.8998 | 0.034624 | 845.161 | 78.8687 | 0.02609 | 896.334 | 896.327 | 2012920 | 38.2881 | 2014720 | 1902140 | 1852990 | 0 | 0 | 1825780 | 697.124 | 0 | 0 | 0 | 0 | 1825780 | 697.124 | 1790020 | 1754224.25
1260 | 2003-02-22 11:00 | 740 | 897 | 111 | 14.5 | 1.7 | 0 | 44.6438 | 168.585 | 21.3144 | 0 | 740 | 833.896 | 133.463 | 6.9332 | 833.896 | 124.9 | 0.036189 | 830.835 | 120.277 | 0.027269 | 922.605 | 922.603 | 2071930 | 40.3647 | 2076830 | 1942740 | 1893820 | 0 | 0 | 1864910 | 690.669 | 0 | 0 | 0 | 0 | 1864910 | 690.669 | 1827880 | 1791325
1261 | 2003-02-22 12:00 | 777 | 1000 | 73 | 15.83 | 2.16 | 0 | 44.8745 | 189.436 | 20.7898 | 0 | 777 | 932.827 | 89.7492 | 7.2799 | 932.827 | 83.9908 | 0.037998 | 929.579 | 80.8823 | 0.028633 | 980.175 | 980.169 | 2201210 | 42.4764 | 2213030 | 2050970 | 1999910 | 0 | 0 | 1967320 | 686.664 | 0 | 0 | 0 | 0 | 1967320 | 686.664 | 1926560 | 1888028.125
1262 | 2003-02-22 13:00 | 706 | 980 | 67 | 17.16 | 2.16 | 0 | 40.8082 | 208.856 | 29.254 | 0 | 706 | 853.066 | 82.7613 | 6.6147 | 853.066 | 77.4512 | 0.034526 | 846.831 | 74.5848 | 0.026016 | 893.799 | 893.795 | 2007240 | 41.4583 | 2008740 | 1869420 | 1822770 | 0 | 0 | 1795580 | 685.998 | 0 | 0 | 0 | 0 | 1795580 | 685.998 | 1761070 | 1725847.5
1263 | 2003-02-22 14:00 | 588 | 907 | 90 | 17.71 | 2.16 | 0 | 33.3785 | 224.907 | 41.5332 | 0 | 588 | 677.592 | 114.739 | 5.5091 | 677.592 | 107.377 | 0.028756 | 666.212 | 103.403 | 0.021668 | 746.548 | 746.543 | 1676540 | 38.0052 | 1661670 | 1569620 | 1530980 | 0 | 0 | 1512020 | 691.933 | 0 | 0 | 0 | 0 | 1512020 | 691.933 | 1486470 | 1456742.75
1264 | 2003-02-22 15:00 | 374 | 789 | 57 | 18.26 | 5.07 | 0 | 23.736 | 237.678 | 55.1338 | 0 | 374 | 450.202 | 71.207 | 3.5041 | 450.202 | 66.6382 | 0.01829 | 433.335 | 64.172 | 0.013782 | 482.595 | 482.594 | 1083790 | 29.091 | 1046640 | 1027840 | 1000790 | 0 | 0 | 992995 | 709.327 | 0 | 0 | 0 | 0 | 992995 | 709.327 | 977637 | 958084.3125
1265 | 2003-02-22 16:00 | 180 | 541 | 60 | 18.81 | 5.07 | 0 | 12.7483 | 248.092 | 69.2806 | 0 | 180 | 192.392 | 75.6839 | 1.6865 | 192.392 | 70.8279 | 0.0088027 | 174.821 | 68.2066 | 0.0066331 | 235.744 | 235.739 | 529409 | 24.1008 | 487573 | 489574 | 476502 | 0 | 0 | 474677 | 700.365 | 0 | 0 | 0 | 0 | 474677 | 700.365 | 466950 | 457611.375
1266 | 2003-02-22 17:00 | 16 | 163 | 6 | 18.25 | 5.07 | 0 | 0.97451 | 257.092 | 83.6956 | 0 | 16 | 12.6219 | 7.1623 | 0.14991 | 4.9445 | 6.7028 | 0.00078247 | 2.9403 | 6.4547 | 0.0005896 | 9.1138 | 9.1119 | 20465 | 18.4545 | 11945.4 | 12322 | 10547.5 | 0 | 0 | 10545.8 | 547.364 | 0 | 0 | 0 | 6177.09 | 4368.71 | 660 | 4203.9 | 4119.8213
1267 | 2003-02-22 18:00 | 0 | 0 | 0 | 17.7 | 6.01 | 0
1268 | 2003-02-22 19:00 | 0 | 0 | 0 | 17.14 | 6.01 | 0
1269 | 2003-02-22 20:00 | 0 | 0 | 0 | 16.16 | 6.01 | 0
1270 | 2003-02-22 21:00 | 0 | 0 | 0 | 15.18 | 5.08 | 0
1271 | 2003-02-22 22:00 | 0 | 0 | 0 | 14.2 | 5.08 | 0
1272 | 2003-02-22 23:00 | 0 | 0 | 0 | 13.33 | 5.08 | 0
1273 | 2003-02-23 | 0 | 0 | 0 | 12.46 | 3.93 | 0
1274 | 2003-02-23 01:00 | 0 | 0 | 0 | 11.59 | 3.93 | 0
1275 | 2003-02-23 02:00 | 0 | 0 | 0 | 11.12 | 3.93 | 0
1276 | 2003-02-23 03:00 | 0 | 0 | 0 | 10.66 | 3.61 | 0
1277 | 2003-02-23 04:00 | 0 | 0 | 0 | 10.19 | 3.61 | 0
1278 | 2003-02-23 05:00 | 0 | 0 | 0 | 9.75 | 3.61 | 0
1279 | 2003-02-23 06:00 | 2 | 269 | 0 | 9.31 | 3.55 | 0 | -0.047977 | 101.943 | 85.0266 | 0 | 2 | 1.993 | 0 | 0.018738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.31 | 0 | 0 | 0 | 0 | 0 | 0 | 660 | 0 | 0 | 0 | 0 | 0 | 660 | 0 | 0
1280 | 2003-02-23 07:00 | 170 | 528 | 61 | 8.88 | 3.55 | 0 | 11.8078 | 110.831 | 70.5754 | 0 | 170 | 177.149 | 75.8696 | 1.5928 | 114.105 | 71.0017 | 0.0083137 | 102.655 | 68.3739 | 0.0062645 | 165.904 | 165.859 | 372464 | 12.9918 | 336658 | 354268 | 315593 | 0 | 0 | 314757 | 716.202 | 0 | 0 | 0 | 0 | 314757 | 716.202 | 307845 | 301688.1875
1281 | 2003-02-23 08:00 | 298 | 371 | 154 | 10.01 | 3.55 | 0 | 22.9277 | 121.056 | 56.3676 | 0 | 298 | 204.729 | 169.895 | 2.792 | 192.791 | 158.994 | 0.014573 | 185.027 | 153.11 | 0.010981 | 328.003 | 327.982 | 736580 | 18.1411 | 694415 | 715101 | 673641 | 0 | 0 | 670275 | 731.352 | 0 | 0 | 0 | 0 | 670275 | 731.352 | 659102 | 645919.9375
1282 | 2003-02-23 09:00 | 463 | 500 | 193 | 11.14 | 2.59 | 0 | 32.778 | 133.555 | 42.6506 | 0 | 463 | 366.808 | 225.069 | 4.338 | 366.808 | 210.628 | 0.022643 | 360.213 | 202.833 | 0.017062 | 546.171 | 546.159 | 1226540 | 25.5684 | 1193570 | 1190450 | 1159120 | 0 | 0 | 1149110 | 724.18 | 0 | 0 | 0 | 0 | 1149110 | 724.18 | 1130010 | 1107409.125
1283 | 2003-02-23 10:00 | 363 | 96 | 301 | 12.28 | 2.59 | 0 | 40.5216 | 149.299 | 30.1068 | 0 | 363 | 82.5501 | 321.558 | 3.401 | 82.5501 | 300.926 | 0.017752 | 81.9065 | 289.789 | 0.013377 | 360.558 | 360.54 | 809682 | 21.8048 | 767557 | 778339 | 756624 | 0 | 0 | 752341 | 723.949 | 0 | 0 | 0 | 0 | 752341 | 723.949 | 740155 | 725351.5625
1284 | 2003-02-23 11:00 | 542 | 290 | 337 | 13.43 | 2.59 | 0 | 45.0104 | 168.545 | 20.9643 | 0 | 542 | 270.673 | 377.304 | 5.0781 | 270.673 | 353.096 | 0.026506 | 269.714 | 340.028 | 0.019973 | 591.469 | 591.455 | 1328260 | 29.0551 | 1298820 | 1275970 | 1241070 | 0 | 0 | 1229380 | 716.652 | 0 | 0 | 0 | 0 | 1229380 | 716.652 | 1209020 | 1184844.5
1285 | 2003-02-23 12:00 | 566 | 342 | 324 | 14.58 | 0.75 | 0 | 45.2328 | 189.554 | 20.4551 | 0 | 566 | 319.365 | 362.787 | 5.303 | 319.365 | 339.51 | 0.02768 | 318.291 | 326.945 | 0.020857 | 625.898 | 625.885 | 1405580 | 33.2835 | 1379050 | 1329780 | 1295010 | 0 | 0 | 1281820 | 703.593 | 0 | 0 | 0 | 0 | 1281820 | 703.593 | 1260990 | 1235765.75
1286 | 2003-02-23 13:00 | 402 | 139 | 311 | 15.74 | 0.75 | 0 | 41.1298 | 209.092 | 29.0374 | 0 | 402 | 120.957 | 333.723 | 3.7664 | 120.957 | 312.31 | 0.019659 | 120.088 | 300.752 | 0.014814 | 408.229 | 408.202 | 916717 | 27.9384 | 876014 | 864462 | 840441 | 0 | 0 | 834934 | 708.62 | 0 | 0 | 0 | 0 | 834934 | 708.62 | 822050 | 805609.5
1287 | 2003-02-23 14:00 | 275 | 44 | 251 | 16.19 | 0.75 | 0 | 33.6543 | 225.199 | 41.3973 | 0 | 275 | 32.4866 | 265.492 | 2.5765 | 32.4866 | 248.458 | 0.013449 | 31.9455 | 239.263 | 0.010134 | 263.082 | 263.073 | 590795 | 24.0515 | 548337 | 550646 | 536209 | 0 | 0 | 533924 | 703.915 | 0 | 0 | 0 | 0 | 533924 | 703.915 | 525441 | 514932.1875
1288 | 2003-02-23 15:00 | 225 | 131 | 172 | 16.63 | 1.81 | 0 | 23.9714 | 237.987 | 55.0455 | 0 | 225 | 74.7391 | 181.834 | 2.1081 | 74.7391 | 170.167 | 0.011003 | 71.9534 | 163.869 | 0.0082913 | 228.756 | 228.745 | 513705 | 22.9957 | 472104 | 476453 | 464090 | 0 | 0 | 462357 | 700.148 | 0 | 0 | 0 | 0 | 462357 | 700.148 | 454781 | 445685.1562
1289 | 2003-02-23 16:00 | 161 | 226 | 110 | 17.08 | 1.81 | 0 | 12.9534 | 248.406 | 69.2229 | 0 | 161 | 80.7079 | 122.929 | 1.5084 | 80.7079 | 115.041 | 0.0078736 | 73.3675 | 110.784 | 0.0059329 | 178.632 | 178.626 | 401151 | 22.051 | 361982 | 367028 | 357267 | 0 | 0 | 356222 | 694.138 | 0 | 0 | 0 | 0 | 356222 | 694.138 | 349354 | 342366.875
1290 | 2003-02-23 17:00 | 14 | 70 | 9 | 16.79 | 1.81 | 0 | 1.1595 | 257.41 | 83.6595 | 0 | 14 | 6.347 | 9.8622 | 0.13117 | 2.7374 | 9.2294 | 0.00068466 | 1.635 | 8.8878 | 0.0005159 | 10.2076 | 10.2048 | 22918.2 | 17.074 | 13709.3 | 14253.6 | 13389 | 0 | 0 | 13386.6 | 559.149 | 0 | 0 | 0 | 5991.49 | 7395.14 | 660 | 7117.43 | 6975.0791
1291 | 2003-02-23 18:00 | 0 | 0 | 0 | 16.51 | 4.64 | 0
1292 | 2003-02-23 19:00 | 0 | 0 | 0 | 16.22 | 4.64 | 0
1293 | 2003-02-23 20:00 | 0 | 0 | 0 | 15.42 | 4.64 | 0
1294 | 2003-02-23 21:00 | 0 | 0 | 0 | 14.62 | 6.07 | 0
1295 | 2003-02-23 22:00 | 0 | 0 | 0 | 13.83 | 6.07 | 0
1296 | 2003-02-23 23:00 | 0 | 0 | 0 | 12.81 | 6.07 | 0
1297 | 2003-02-24 | 0 | 0 | 0 | 11.79 | 8.16 | 0
1298 | 2003-02-24 01:00 | 0 | 0 | 0 | 10.77 | 8.16 | 0
1299 | 2003-02-24 02:00 | 0 | 0 | 0 | 10.2 | 8.16 | 0
1300 | 2003-02-24 03:00 | 0 | 0 | 0 | 9.62 | 6.86 | 0
1301 | 2003-02-24 04:00 | 0 | 0 | 0 | 9.05 | 6.86 | 0
1302 | 2003-02-24 05:00 | 0 | 0 | 0 | 8.8 | 6.86 | 0
1303 | 2003-02-24 06:00 | 4 | 320 | 0 | 8.55 | 8.03 | 0 | 0.19259 | 101.662 | 84.9244 | 0 | 4 | 4.0676 | 0 | 0.037477 | 0.035386 | 0 | 0.00019562 | 0.017156 | 0 | 0.0001474 | 0.016785 | 0.016753 | 37.6755 | 8.5503 | 7.8384 | 7.7051 | 5.0265 | 0 | 0 | 5.0264 | 283.706 | 0 | 0 | 0 | 5.0264 | 0 | 660 | 0 | 0
1304 | 2003-02-24 07:00 | 181 | 687 | 37 | 8.31 | 8.03 | 0 | 12.065 | 110.559 | 70.4534 | 0 | 181 | 230.496 | 48.9275 | 1.6958 | 151.971 | 45.7882 | 0.0088517 | 136.858 | 44.0936 | 0.0066699 | 175.53 | 175.463 | 394023 | 11.5688 | 359268 | 379948 | 333652 | 0 | 0 | 332662 | 715.128 | 0 | 0 | 0 | 507.274 | 332154 | 721.842 | 325176 | 318671.9688
1305 | 2003-02-24 08:00 | 391 | 822 | 67 | 9.03 | 8.03 | 0 | 23.21 | 120.796 | 56.2179 | 0 | 391 | 457.13 | 85.5179 | 3.6634 | 432.209 | 80.031 | 0.019121 | 414.954 | 77.0691 | 0.014408 | 477.277 | 477.315 | 1071970 | 17.8949 | 1036350 | 1066350 | 983071 | 0 | 0 | 976050 | 745.531 | 0 | 0 | 0 | 0 | 976050 | 745.531 | 959122 | 939939.3125
1306 | 2003-02-24 09:00 | 542 | 825 | 92 | 9.74 | 4.97 | 0 | 33.0925 | 133.322 | 42.459 | 0 | 542 | 608.053 | 116.43 | 5.0781 | 608.053 | 108.96 | 0.026506 | 597.246 | 104.928 | 0.019973 | 681.128 | 681.119 | 1529620 | 25.1263 | 1508170 | 1507120 | 1466600 | 0 | 0 | 1451010 | 732.621 | 0 | 0 | 0 | 0 | 1451010 | 732.621 | 1425330 | 1396823.25
1307 | 2003-02-24 10:00 | 670 | 888 | 90 | 10.46 | 4.97 | 0 | 40.87 | 149.134 | 29.847 | 0 | 670 | 768.81 | 109.204 | 6.2774 | 768.81 | 102.197 | 0.032766 | 762.931 | 98.4147 | 0.02469 | 835.529 | 835.531 | 1876380 | 29.3344 | 1871190 | 1836970 | 1785150 | 0 | 0 | 1761790 | 726.322 | 0 | 0 | 0 | 0 | 1761790 | 726.322 | 1727590 | 1693042.375
1308 | 2003-02-24 11:00 | 757 | 869 | 140 | 11.32 | 4.97 | 0 | 45.38 | 168.508 | 20.6115 | 0 | 757 | 811.353 | 173.815 | 7.0925 | 811.353 | 162.663 | 0.03702 | 808.578 | 156.643 | 0.027896 | 936.291 | 936.28 | 2102640 | 32.4703 | 2109170 | 2043340 | 1994130 | 0 | 0 | 1964230 | 715.685 | 0 | 0 | 0 | 0 | 1964230 | 715.685 | 1923480 | 1885013.5
1309 | 2003-02-24 12:00 | 704 | 727 | 186 | 12.17 | 7.58 | 0 | 45.593 | 189.678 | 20.1201 | 0 | 704 | 680.847 | 230.369 | 6.5959 | 680.847 | 215.588 | 0.034429 | 678.634 | 207.61 | 0.025943 | 859.682 | 859.665 | 1930590 | 28.5956 | 1928150 | 1898960 | 1848500 | 0 | 0 | 1823580 | 727.936 | 0 | 0 | 0 | 0 | 1823580 | 727.936 | 1787410 | 1751663.125
1310 | 2003-02-24 13:00 | 609 | 614 | 203 | 13.03 | 7.58 | 0 | 41.4521 | 209.336 | 28.8239 | 0 | 609 | 537.315 | 245.192 | 5.7059 | 537.315 | 229.46 | 0.029783 | 533.516 | 220.967 | 0.022442 | 731.87 | 731.857 | 1643560 | 27.0136 | 1627170 | 1613130 | 1567900 | 0 | 0 | 1550050 | 730.642 | 0 | 0 | 0 | 0 | 1550050 | 730.642 | 1522010 | 1491570.5
1311 | 2003-02-24 14:00 | 424 | 307 | 253 | 12.68 | 7.58 | 0 | 33.9298 | 225.498 | 41.2649 | 0 | 424 | 230.277 | 279.911 | 3.9726 | 230.277 | 261.951 | 0.020735 | 226.473 | 252.257 | 0.015624 | 464.383 | 464.368 | 1042850 | 21.5527 | 1004700 | 1019630 | 991340 | 0 | 0 | 984169 | 732.633 | 0 | 0 | 0 | 0 | 984169 | 732.633 | 967801 | 948444.6875
1312 | 2003-02-24 15:00 | 108 | 0 | 108 | 12.33 | 7.36 | 0 | 24.2061 | 238.302 | 54.9604 | 0 | 108 | 0 | 101.178 | 1.0119 | 0 | 94.6861 | 0.0052816 | 0 | 91.1819 | 0.0039798 | 88.4503 | 88.4455 | 198626 | 14.0436 | 168851 | 178141 | 173379 | 0 | 0 | 173129 | 689.819 | 0 | 0 | 0 | 0 | 173129 | 689.819 | 167888 | 164530.5781
1313 | 2003-02-24 16:00 | 133 | 105 | 109 | 11.98 | 7.36 | 0 | 13.1576 | 248.724 | 69.168 | 0 | 133 | 37.4953 | 116.964 | 1.2461 | 37.4953 | 109.46 | 0.0065042 | 34.0984 | 105.409 | 0.0049011 | 135.326 | 135.324 | 303902 | 14.6019 | 268248 | 281745 | 273987 | 0 | 0 | 273396 | 708.561 | 0 | 0 | 0 | 0 | 273396 | 708.561 | 266392 | 261063.8594
1314 | 2003-02-24 17:00 | 13 | 33 | 11 | 11.78 | 7.36 | 0 | 1.3437 | 257.733 | 83.6256 | 0 | 13 | 2.5523 | 10.7804 | 0.1218 | 1.1952 | 10.0888 | 0.00063575 | 0.71668 | 9.7154 | 0.00047905 | 10.1196 | 10.1192 | 22725.4 | 11.9761 | 13531.9 | 14402.5 | 13980.8 | 0 | 0 | 13978.4 | 577.78 | 0 | 0 | 0 | 3446.9 | 10531.5 | 660 | 10138 | 9935.2451
1315 | 2003-02-24 18:00 | 0 | 0 | 0 | 11.57 | 12.65 | 0
1316 | 2003-02-24 19:00 | 0 | 0 | 0 | 11.36 | 12.65 | 0
1317 | 2003-02-24 20:00 | 0 | 0 | 0 | 10.5 | 12.65 | 0
1318 | 2003-02-24 21:00 | 0 | 0 | 0 | 9.64 | 7.45 | 0
1319 | 2003-02-24 22:00 | 0 | 0 | 0 | 8.78 | 7.45 | 0
1320 | 2003-02-24 23:00 | 0 | 0 | 0 | 8.61 | 7.45 | 0
1321 | 2003-02-25 | 0 | 0 | 0 | 8.44 | 6.74 | 0
1322 | 2003-02-25 01:00 | 0 | 0 | 0 | 8.27 | 6.74 | 0
1323 | 2003-02-25 02:00 | 0 | 0 | 0 | 7.94 | 6.74 | 0
1324 | 2003-02-25 03:00 | 0 | 0 | 0 | 7.6 | 5.92 | 0
1325 | 2003-02-25 04:00 | 0 | 0 | 0 | 7.27 | 5.92 | 0
1326 | 2003-02-25 05:00 | 0 | 0 | 0 | 6.63 | 5.92 | 0
1327 | 2003-02-25 06:00 | 1 | 0 | 1 | 6 | 3.95 | 0 | 0.43659 | 101.38 | 84.8195 | 0 | 1 | 0 | 0.90625 | 0.0093692 | 0 | 0.8481 | 4.8904e-05 | 0 | 0.81671 | 3.685e-05 | 0.79225 | 0.79219 | 1779.05 | 6.0191 | 153.383 | 149.937 | 149.166 | 0 | 0 | 149.16 | 118.392 | 0 | 0 | 0 | 149.16 | 0 | 660 | 0 | 0
1328 | 2003-02-25 07:00 | 32 | 0 | 32 | 5.36 | 3.95 | 0 | 12.3255 | 110.287 | 70.3291 | 0 | 32 | 0 | 28.7875 | 0.29981 | 0 | 26.9404 | 0.0015649 | 0 | 25.9434 | 0.0011792 | 25.1662 | 25.1654 | 56515.1 | 5.9677 | 41138.6 | 45307.4 | 44116.4 | 0 | 0 | 44098.5 | 656.659 | 0 | 0 | 0 | 11.1375 | 44087.3 | 660 | 42528.6 | 41678.0625
1329 | 2003-02-25 08:00 | 69 | 0 | 69 | 5.93 | 3.95 | 0 | 23.4952 | 120.534 | 56.0664 | 0 | 69 | 0 | 63.3057 | 0.64648 | 0 | 59.2439 | 0.0033744 | 0 | 57.0513 | 0.0025427 | 55.3423 | 55.3417 | 124284 | 7.2664 | 100660 | 109888 | 106807 | 0 | 0 | 106713 | 693.743 | 0 | 0 | 0 | 0 | 106713 | 693.743 | 103006 | 100945.4766
1330 | 2003-02-25 09:00 | 101 | 0 | 101 | 6.5 | 6.45 | 0 | 33.4099 | 133.088 | 42.2661 | 0 | 101 | 0 | 93.4976 | 0.94629 | 0 | 87.4986 | 0.0049393 | 0 | 84.2603 | 0.0037219 | 81.7362 | 81.7327 | 183550 | 8.1781 | 154856 | 167951 | 163078 | 0 | 0 | 162867 | 705.863 | 0 | 0 | 0 | 0 | 162867 | 705.863 | 157599 | 154446.9844
1331 | 2003-02-25 10:00 | 128 | 0 | 128 | 7.06 | 6.45 | 0 | 41.2214 | 148.968 | 29.586 | 0 | 128 | 0 | 119.274 | 1.1993 | 0 | 111.621 | 0.0062597 | 0 | 107.49 | 0.0047168 | 104.27 | 104.266 | 234156 | 9.2008 | 202099 | 217835 | 211589 | 0 | 0 | 211244 | 716.645 | 0 | 0 | 0 | 0 | 211244 | 716.645 | 204856 | 200758.3906
1332 | 2003-02-25 11:00 | 147 | 0 | 147 | 7.72 | 6.45 | 0 | 45.7522 | 168.473 | 20.2561 | 0 | 147 | 0 | 137.593 | 1.3773 | 0 | 128.764 | 0.0071889 | 0 | 123.999 | 0.005417 | 120.284 | 120.278 | 270113 | 10.1895 | 236074 | 253102 | 245619 | 0 | 0 | 245158 | 719.024 | 0 | 0 | 0 | 0 | 245158 | 719.024 | 238224 | 233459.1562
1333 | 2003-02-25 12:00 | 336 | 33 | 312 | 8.38 | 3.01 | 0 | 45.9551 | 189.807 | 19.7849 | 0 | 336 | 31.4182 | 331.165 | 3.1481 | 31.4182 | 309.917 | 0.016432 | 31.3197 | 298.447 | 0.012382 | 319.886 | 319.866 | 718341 | 16.598 | 675629 | 700915 | 679922 | 0 | 0 | 676584 | 737.657 | 0 | 0 | 0 | 0 | 676584 | 737.657 | 665161 | 651857.9375
1334 | 2003-02-25 13:00 | 299 | 48 | 267 | 9.04 | 3.01 | 0 | 41.775 | 209.587 | 28.6137 | 0 | 299 | 42.1667 | 278.965 | 2.8014 | 42.1667 | 261.066 | 0.014622 | 41.8734 | 251.405 | 0.011018 | 284.49 | 284.475 | 638859 | 16.3487 | 596141 | 619387 | 601392 | 0 | 0 | 598748 | 733.85 | 0 | 0 | 0 | 0 | 598748 | 733.85 | 588723 | 576948.0625
1335 | 2003-02-25 14:00 | 567 | 618 | 220 | 9.09 | 3.01 | 0 | 34.205 | 225.802 | 41.1362 | 0 | 567 | 464.894 | 253.692 | 5.3124 | 464.894 | 237.414 | 0.027729 | 457.275 | 228.628 | 0.020894 | 665.346 | 665.338 | 1494180 | 26.1838 | 1471240 | 1463580 | 1422620 | 0 | 0 | 1407790 | 728.454 | 0 | 0 | 0 | 0 | 1407790 | 728.454 | 1383190 | 1355529
1336 | 2003-02-25 15:00 | 289 | 321 | 156 | 9.14 | 3.28 | 0 | 24.44 | 238.621 | 54.8786 | 0 | 289 | 184.938 | 171.282 | 2.7077 | 184.938 | 160.292 | 0.014133 | 178.112 | 154.36 | 0.01065 | 322.509 | 322.504 | 724262 | 17.279 | 681547 | 705011 | 684732 | 0 | 0 | 681316 | 734.415 | 0 | 0 | 0 | 0 | 681316 | 734.415 | 669924 | 656525.3125
1337 | 2003-02-25 16:00 | 139 | 204 | 92 | 9.2 | 3.28 | 0 | 13.361 | 249.046 | 69.1158 | 0 | 139 | 72.5036 | 101.792 | 1.3023 | 72.5036 | 95.2609 | 0.0067977 | 65.9594 | 91.7353 | 0.0051222 | 152.969 | 152.963 | 343517 | 13.0603 | 306243 | 323709 | 314986 | 0 | 0 | 314229 | 719.703 | 0 | 0 | 0 | 0 | 314229 | 719.703 | 306705 | 300571.0625
1338 | 2003-02-25 17:00 | 14 | 66 | 9 | 9.35 | 3.28 | 0 | 1.5273 | 258.058 | 83.594 | 0 | 14 | 6.4122 | 9.9496 | 0.13117 | 3.2379 | 9.3112 | 0.00068466 | 1.9487 | 8.9666 | 0.0005159 | 10.5884 | 10.5878 | 23778.1 | 9.6172 | 14375.8 | 15469.9 | 14601.2 | 0 | 0 | 14598.7 | 588.222 | 0 | 0 | 0 | 2275.94 | 12322.7 | 660 | 11863.6 | 11626.3311
1339 | 2003-02-25 18:00 | 0 | 0 | 0 | 9.5 | 8.1 | 0
1340 | 2003-02-25 19:00 | 0 | 0 | 0 | 9.65 | 8.1 | 0
1341 | 2003-02-25 20:00 | 0 | 0 | 0 | 8.78 | 8.1 | 0
1342 | 2003-02-25 21:00 | 0 | 0 | 0 | 7.91 | 7.12 | 0
1343 | 2003-02-25 22:00 | 0 | 0 | 0 | 7.04 | 7.12 | 0
1344 | 2003-02-25 23:00 | 0 | 0 | 0 | 6.94 | 7.12 | 0
1345 | 2003-02-26 | 0 | 0 | 0 | 6.84 | 9.11 | 0
1346 | 2003-02-26 01:00 | 0 | 0 | 0 | 6.74 | 9.11 | 0
1347 | 2003-02-26 02:00 | 0 | 0 | 0 | 6.57 | 9.11 | 0
1348 | 2003-02-26 03:00 | 0 | 0 | 0 | 6.39 | 7.17 | 0
1349 | 2003-02-26 04:00 | 0 | 0 | 0 | 6.22 | 7.17 | 0
1350 | 2003-02-26 05:00 | 0 | 0 | 0 | 6.23 | 7.17 | 0
1351 | 2003-02-26 06:00 | 5 | 69 | 1 | 6.25 | 3.84 | 0 | 0.68389 | 101.098 | 84.712 | 0 | 5 | 4.2373 | 1.2019 | 0.046846 | 0.026418 | 1.1248 | 0.00024452 | 0.013407 | 1.0832 | 0.00018425 | 1.0638 | 1.0638 | 2388.97 | 6.2759 | 282.534 | 276.749 | 268.423 | 0 | 0 | 268.411 | 160.007 | 0 | 0 | 0 | 268.411 | 0 | 660 | 0 | 0
1352 | 2003-02-26 07:00 | 203 | 538 | 85 | 6.26 | 3.84 | 0 | 12.589 | 110.013 | 70.2027 | 0 | 203 | 183.367 | 98.7449 | 1.902 | 126.259 | 92.4093 | 0.0099275 | 113.933 | 88.9893 | 0.0074806 | 196.842 | 196.843 | 442041 | 11.0477 | 403907 | 428612 | 388544 | 0 | 0 | 387361 | 729.944 | 0 | 0 | 0 | 0 | 387361 | 729.944 | 379498 | 371908.375
1353 | 2003-02-26 08:00 | 384 | 686 | 107 | 7.11 | 3.84 | 0 | 23.7834 | 120.272 | 55.9133 | 0 | 384 | 384.953 | 130.579 | 3.5978 | 366.497 | 122.201 | 0.018779 | 352.125 | 117.678 | 0.01415 | 455.723 | 455.784 | 1023600 | 18.1957 | 986144 | 1013730 | 937614 | 0 | 0 | 931254 | 744.119 | 0 | 0 | 0 | 0 | 931254 | 744.119 | 915235 | 896930.5625
1354 | 2003-02-26 09:00 | 424 | 305 | 255 | 7.96 | 4.36 | 0 | 33.7302 | 132.853 | 42.072 | 0 | 424 | 225.92 | 281.173 | 3.9726 | 225.92 | 263.132 | 0.020735 | 221.998 | 253.394 | 0.015624 | 461.146 | 461.143 | 1035610 | 18.8 | 997291 | 1023950 | 996209 | 0 | 0 | 989160 | 742.515 | 0 | 0 | 0 | 0 | 989160 | 742.515 | 972232 | 952787
1355 | 2003-02-26 10:00 | 731 | 644 | 305 | 8.81 | 4.36 | 0 | 41.5757 | 148.802 | 29.3239 | 0 | 731 | 559.689 | 348.503 | 6.8489 | 559.689 | 326.143 | 0.035749 | 555.577 | 314.072 | 0.026938 | 843.586 | 843.572 | 1894450 | 28.6397 | 1890170 | 1861070 | 1810170 | 0 | 0 | 1786330 | 728.558 | 0 | 0 | 0 | 0 | 1786330 | 728.558 | 1751320 | 1716294
1356 | 2003-02-26 11:00 | 246 | 27 | 227 | 9.38 | 4.36 | 0 | 46.1271 | 168.441 | 19.8983 | 0 | 246 | 24.7832 | 230.825 | 2.3048 | 24.7832 | 216.015 | 0.01203 | 24.7045 | 208.02 | 0.0090652 | 225.752 | 225.741 | 506956 | 14.6864 | 465469 | 487575 | 473528 | 0 | 0 | 471863 | 728.536 | 0 | 0 | 0 | 0 | 471863 | 728.536 | 463291 | 454025.625
1357 | 2003-02-26 12:00 | 161 | 0 | 161 | 9.95 | 7.78 | 0 | 46.3189 | 189.942 | 19.4498 | 0 | 161 | 0 | 151.196 | 1.5084 | 0 | 141.495 | 0.0078736 | 0 | 136.258 | 0.0059329 | 132.176 | 132.173 | 296828 | 12.4437 | 261499 | 277388 | 269161 | 0 | 0 | 268601 | 715.345 | 0 | 0 | 0 | 0 | 268601 | 715.345 | 261487 | 256257
1358 | 2003-02-26 13:00 | 148 | 0 | 148 | 10.53 | 7.78 | 0 | 42.0984 | 209.844 | 28.4071 | 0 | 148 | 0 | 138.641 | 1.3866 | 0 | 129.745 | 0.0072378 | 0 | 124.943 | 0.0054538 | 121.2 | 121.193 | 272167 | 12.8166 | 238023 | 252172 | 244667 | 0 | 0 | 244197 | 710.172 | 0 | 0 | 0 | 0 | 244197 | 710.172 | 237458 | 232709.0156
1359 | 2003-02-26 14:00 | 472 | 318 | 292 | 10.52 | 7.78 | 0 | 34.4797 | 226.113 | 41.0111 | 0 | 472 | 239.924 | 322.116 | 4.4223 | 239.924 | 301.448 | 0.023083 | 236.023 | 290.292 | 0.017393 | 510.542 | 510.529 | 1146520 | 20.1523 | 1111110 | 1134130 | 1102980 | 0 | 0 | 1094280 | 739.409 | 0 | 0 | 0 | 0 | 1094280 | 739.409 | 1075500 | 1053991.375
1360 | 2003-02-26 15:00 | 299 | 298 | 175 | 10.52 | 8.74 | 0 | 24.673 | 238.946 | 54.7999 | 0 | 299 | 171.229 | 191.847 | 2.8014 | 171.229 | 179.538 | 0.014622 | 164.938 | 172.893 | 0.011018 | 327.707 | 327.701 | 735934 | 16.3416 | 693266 | 719994 | 699596 | 0 | 0 | 696084 | 740.085 | 0 | 0 | 0 | 0 | 696084 | 740.085 | 684249 | 670564.25
1361 | 2003-02-26 16:00 | 77 | 0 | 77 | 10.51 | 8.74 | 0 | 13.5635 | 249.372 | 69.0664 | 0 | 77 | 0 | 73.0281 | 0.72143 | 0 | 68.3424 | 0.0037656 | 0 | 65.8131 | 0.0028375 | 63.8415 | 63.8362 | 143360 | 11.644 | 117942 | 126042 | 122583 | 0 | 0 | 122456 | 683.593 | 0 | 0 | 0 | 0 | 122456 | 683.593 | 118436 | 116067.2578
1362 | 2003-02-26 17:00 | 8 | 0 | 8 | 10.14 | 8.74 | 0 | 1.71 | 258.387 | 83.5647 | 0 | 8 | 0 | 7.2533 | 0.074954 | 0 | 6.7879 | 0.00039123 | 0 | 6.5367 | 0.0002948 | 6.3408 | 6.3404 | 14239 | 10.2526 | 7148.63 | 7564.07 | 7418.18 | 0 | 0 | 7417.46 | 550.06 | 0 | 0 | 0 | 4044.73 | 3372.73 | 660 | 3245.25 | 3180.3438
1363 | 2003-02-26 18:00 | 0 | 0 | 0 | 9.77 | 9.5 | 0
1364 | 2003-02-26 19:00 | 0 | 0 | 0 | 9.41 | 9.5 | 0
1365 | 2003-02-26 20:00 | 0 | 0 | 0 | 8.8 | 9.5 | 0
1366 | 2003-02-26 21:00 | 0 | 0 | 0 | 8.19 | 9.73 | 0
1367 | 2003-02-26 22:00 | 0 | 0 | 0 | 7.58 | 9.73 | 0
1368 | 2003-02-26 23:00 | 0 | 0 | 0 | 6.98 | 9.73 | 0
1369 | 2003-02-27 | 0 | 0 | 0 | 6.38 | 11.61 | 0
1370 | 2003-02-27 01:00 | 0 | 0 | 0 | 5.79 | 11.61 | 0
1371 | 2003-02-27 02:00 | 0 | 0 | 0 | 5.53 | 11.61 | 0
1372 | 2003-02-27 03:00 | 0 | 0 | 0 | 5.27 | 10.03 | 0
1373 | 2003-02-27 04:00 | 0 | 0 | 0 | 5.02 | 10.03 | 0
1374 | 2003-02-27 05:00 | 0 | 0 | 0 | 4.79 | 10.03 | 0
1375 | 2003-02-27 06:00 | 5 | 17 | 4 | 4.55 | 7.2 | 0 | 0.93437 | 100.816 | 84.602 | 0 | 5 | 1.0813 | 4.0036 | 0.046846 | 0.0059577 | 3.7467 | 0.00024452 | 0.0030891 | 3.608 | 0.00018425 | 3.503 | 3.5027 | 7866.27 | 4.6186 | 2793.75 | 2842 | 2809.55 | 0 | 0 | 2809.41 | 481.274 | 0 | 0 | 0 | 2803.76 | 5.6524 | 660.234 | 5.4376 | 5.3289
1376 | 2003-02-27 07:00 | 207 | 543 | 86 | 4.32 | 7.2 | 0 | 12.8554 | 109.739 | 70.0742 | 0 | 207 | 185.342 | 99.5382 | 1.9394 | 130.168 | 93.1517 | 0.010123 | 117.579 | 89.7042 | 0.007628 | 201.072 | 201.048 | 451487 | 8.255 | 413099 | 443855 | 402740 | 0 | 0 | 401515 | 742.667 | 0 | 0 | 0 | 0 | 401515 | 742.667 | 393159 | 385295.4375
1377 | 2003-02-27 08:00 | 418 | 890 | 55 | 5.13 | 7.2 | 0 | 24.0743 | 120.008 | 55.7587 | 0 | 418 | 500.717 | 68.0921 | 3.9163 | 478.502 | 63.7232 | 0.020442 | 459.907 | 61.3649 | 0.015403 | 505.649 | 505.685 | 1135670 | 15.0276 | 1101690 | 1146890 | 1049010 | 0 | 0 | 1041260 | 758.021 | 0 | 0 | 0 | 0 | 1041260 | 758.021 | 1022480 | 1002033.75
1378 | 2003-02-27 09:00 | 577 | 776 | 143 | 5.94 | 10.09 | 0 | 34.0531 | 132.617 | 41.8769 | 0 | 577 | 577.09 | 175.015 | 5.406 | 577.09 | 163.786 | 0.028218 | 567.192 | 157.724 | 0.021263 | 703.189 | 703.182 | 1579170 | 17.4322 | 1559870 | 1609000 | 1562980 | 0 | 0 | 1546490 | 759.283 | 0 | 0 | 0 | 0 | 1546490 | 759.283 | 1516840 | 1486501.875
1379 | 2003-02-27 10:00 | 593 | 526 | 242 | 6.76 | 10.09 | 0 | 41.9326 | 148.636 | 29.0608 | 0 | 593 | 459.122 | 281.74 | 5.556 | 459.122 | 263.663 | 0.029 | 455.815 | 253.905 | 0.021852 | 688.45 | 688.427 | 1546030 | 18.0111 | 1525300 | 1569740 | 1523550 | 0 | 0 | 1507860 | 758.389 | 0 | 0 | 0 | 0 | 1507860 | 758.389 | 1479380 | 1449795.125
1380 | 2003-02-27 11:00 | 801 | 845 | 190 | 7.39 | 10.09 | 0 | 46.5045 | 168.411 | 19.5383 | 0 | 801 | 793.763 | 233.792 | 7.5047 | 793.763 | 218.791 | 0.039172 | 791.338 | 210.694 | 0.029517 | 972 | 971.996 | 2182860 | 23.2755 | 2193680 | 2208820 | 2146380 | 0 | 0 | 2114860 | 750.099 | 70233.6 | 0 | 0 | 0 | 2045540 | 779.487 | 1997550 | 1957598.5
1381 | 2003-02-27 12:00 | 741 | 798 | 162 | 8.03 | 10.12 | 0 | 46.6844 | 190.082 | 19.1151 | 0 | 741 | 751.905 | 202.889 | 6.9426 | 751.905 | 189.871 | 0.036238 | 749.711 | 182.844 | 0.027306 | 904.605 | 904.592 | 2031480 | 22.7868 | 2034260 | 2052490 | 1994700 | 0 | 0 | 1967310 | 749.279 | 0 | 0 | 0 | 0 | 1967310 | 749.279 | 1925400 | 1886890.375
1382 | 2003-02-27 13:00 | 734 | 935 | 105 | 8.67 | 10.12 | 0 | 42.4221 | 210.108 | 28.2043 | 0 | 734 | 821.714 | 125.524 | 6.877 | 821.714 | 117.47 | 0.035896 | 816.178 | 113.123 | 0.027048 | 901.448 | 901.444 | 2024410 | 23.3754 | 2026810 | 2040090 | 1985900 | 0 | 0 | 1958480 | 745.559 | 0 | 0 | 0 | 0 | 1958480 | 745.559 | 1917260 | 1878912.75
1383 | 2003-02-27 14:00 | 616 | 859 | 127 | 8.9 | 10.12 | 0 | 34.754 | 226.429 | 40.8898 | 0 | 616 | 648.481 | 157.805 | 5.7714 | 648.481 | 147.679 | 0.030125 | 638.015 | 142.214 | 0.0227 | 756.844 | 756.834 | 1699660 | 21.2464 | 1685860 | 1712030 | 1665840 | 0 | 0 | 1646610 | 748.578 | 0 | 0 | 0 | 0 | 1646610 | 748.578 | 1614840 | 1582546.875
1384 | 2003-02-27 15:00 | 355 | 503 | 143 | 9.12 | 8.84 | 0 | 24.9051 | 239.275 | 54.7246 | 0 | 355 | 290.73 | 165.177 | 3.3261 | 290.73 | 154.579 | 0.017361 | 280.096 | 148.858 | 0.013082 | 416.097 | 416.089 | 934435 | 16.4659 | 894018 | 927240 | 900991 | 0 | 0 | 895269 | 745.77 | 0 | 0 | 0 | 0 | 895269 | 745.77 | 879814 | 862218.1875
1385 | 2003-02-27 16:00 | 207 | 477 | 93 | 9.35 | 8.84 | 0 | 13.765 | 249.701 | 69.0197 | 0 | 207 | 171.545 | 107.088 | 1.9394 | 171.545 | 100.217 | 0.010123 | 156.167 | 96.5079 | 0.007628 | 245.102 | 245.092 | 550414 | 13.677 | 508317 | 534619 | 519554 | 0 | 0 | 517590 | 736.159 | 0 | 0 | 0 | 0 | 517590 | 736.159 | 508271 | 498105.25
1386 | 2003-02-27 17:00 | 21 | 162 | 9 | 8.74 | 8.84 | 0 | 1.892 | 258.719 | 83.5376 | 0 | 21 | 15.5243 | 10.6227 | 0.19675 | 9.4589 | 9.9411 | 0.001027 | 5.7298 | 9.5732 | 0.00077386 | 14.8446 | 14.8424 | 33332.8 | 9.002 | 22064.1 | 23893.8 | 21490.5 | 0 | 0 | 21485.2 | 612.323 | 0 | 0 | 0 | 1214.66 | 20270.6 | 660 | 19525 | 19134.5254
1387 | 2003-02-27 18:00 | 0 | 0 | 0 | 8.13 | 11.32 | 0
1388 | 2003-02-27 19:00 | 0 | 0 | 0 | 7.51 | 11.32 | 0
1389 | 2003-02-27 20:00 | 0 | 0 | 0 | 7.02 | 11.32 | 0
1390 | 2003-02-27 21:00 | 0 | 0 | 0 | 6.54 | 9.14 | 0
1391 | 2003-02-27 22:00 | 0 | 0 | 0 | 6.05 | 9.14 | 0
1392 | 2003-02-27 23:00 | 0 | 0 | 0 | 5.51 | 9.14 | 0
1393 | 2003-02-28 | 0 | 0 | 0 | 4.98 | 10.45 | 0
1394 | 2003-02-28 01:00 | 0 | 0 | 0 | 4.44 | 10.45 | 0
1395 | 2003-02-28 02:00 | 0 | 0 | 0 | 3.96 | 10.45 | 0
1396 | 2003-02-28 03:00 | 0 | 0 | 0 | 3.48 | 10.87 | 0
1397 | 2003-02-28 04:00 | 0 | 0 | 0 | 3 | 10.87 | 0
1398 | 2003-02-28 05:00 | 0 | 0 | 0 | 2.97 | 10.87 | 0
1399 | 2003-02-28 06:00 | 4 | 0 | 4 | 2.95 | 4.33 | 0 | 1.1879 | 100.533 | 84.4895 | 0 | 4 | 0 | 3.6251 | 0.037477 | 0 | 3.3925 | 0.00019562 | 0 | 3.2669 | 0.0001474 | 3.1691 | 3.169 | 7116.63 | 3.0246 | 2337.16 | 2348.12 | 2326.28 | 0 | 0 | 2326.18 | 455.158 | 0 | 0 | 0 | 2326.18 | 0 | 660 | 0 | 0
1400 | 2003-02-28 07:00 | 210 | 545 | 86 | 2.92 | 4.33 | 0 | 13.1247 | 109.464 | 69.9438 | 0 | 210 | 187.275 | 99.0995 | 1.9675 | 134.01 | 92.7411 | 0.01027 | 121.172 | 89.3088 | 0.0077386 | 204.174 | 204.224 | 458626 | 7.7301 | 420068 | 452091 | 409674 | 0 | 0 | 408419 | 747.135 | 0 | 0 | 0 | 0 | 408419 | 747.135 | 399840 | 391843.5625
1401 | 2003-02-28 08:00 | 426 | 896 | 57 | 4.07 | 4.33 | 0 | 24.3678 | 119.744 | 55.6026 | 0 | 426 | 505.241 | 70.2601 | 3.9913 | 484.608 | 65.7521 | 0.020833 | 465.947 | 63.3186 | 0.015698 | 513.403 | 513.353 | 1152880 | 16.161 | 1119290 | 1159550 | 1059670 | 0 | 0 | 1051690 | 753.61 | 0 | 0 | 0 | 0 | 1051690 | 753.61 | 1032920 | 1012264.4375
1402 | 2003-02-28 09:00 | 609 | 913 | 94 | 5.22 | 4.31 | 0 | 34.3787 | 132.38 | 41.6808 | 0 | 609 | 681.178 | 117.875 | 5.7059 | 681.178 | 110.312 | 0.029783 | 669.634 | 106.229 | 0.022442 | 752.609 | 752.611 | 1690170 | 22.9694 | 1675930 | 1689820 | 1640400 | 0 | 0 | 1621530 | 744.26 | 0 | 0 | 0 | 0 | 1621530 | 744.26 | 1590820 | 1559007
1403 | 2003-02-28 10:00 | 670 | 726 | 183 | 6.37 | 4.31 | 0 | 42.2921 | 148.47 | 28.797 | 0 | 670 | 634.22 | 222.872 | 6.2774 | 634.22 | 208.572 | 0.032766 | 629.745 | 200.853 | 0.02469 | 805.704 | 805.689 | 1809370 | 25.3712 | 1800850 | 1797700 | 1752310 | 0 | 0 | 1730340 | 735.698 | 0 | 0 | 0 | 0 | 1730340 | 735.698 | 1696900 | 1662964.375
1404 | 2003-02-28 11:00 | 648 | 512 | 275 | 7.26 | 4.31 | 0 | 46.8842 | 168.384 | 19.1761 | 0 | 648 | 482.625 | 320.296 | 6.0713 | 482.625 | 299.745 | 0.03169 | 481.208 | 288.652 | 0.023879 | 746.787 | 746.763 | 1677050 | 24.8715 | 1662200 | 1662750 | 1617240 | 0 | 0 | 1598610 | 737.789 | 0 | 0 | 0 | 0 | 1598610 | 737.789 | 1568960 | 1537579.375
1405 | 2003-02-28 12:00 | 749 | 768 | 188 | 8.16 | 2.22 | 0 | 47.0512 | 190.229 | 18.781 | 0 | 749 | 725.624 | 231.427 | 7.0175 | 725.624 | 216.578 | 0.036629 | 723.584 | 208.562 | 0.027601 | 904.208 | 904.196 | 2030590 | 32.6429 | 2033320 | 1968120 | 1914400 | 0 | 0 | 1886890 | 716.583 | 0 | 0 | 0 | 0 | 1886890 | 716.583 | 1848800 | 1811822
1406 | 2003-02-28 13:00 | 728 | 924 | 102 | 9.05 | 2.22 | 0 | 42.7461 | 210.378 | 28.0053 | 0 | 728 | 814.287 | 121.948 | 6.8208 | 814.287 | 114.124 | 0.035602 | 808.887 | 109.9 | 0.026827 | 891.25 | 891.243 | 2001510 | 33.1821 | 2002710 | 1933920 | 1883300 | 0 | 0 | 1856380 | 713.232 | 0 | 0 | 0 | 0 | 1856380 | 713.232 | 1819350 | 1782961.125
1407 | 2003-02-28 14:00 | 597 | 938 | 59 | 9.35 | 2.22 | 0 | 35.0276 | 226.752 | 40.7724 | 0 | 597 | 709.849 | 72.5477 | 5.5934 | 709.849 | 67.8929 | 0.029196 | 698.475 | 65.3802 | 0.022 | 740.961 | 740.957 | 1664000 | 29.4129 | 1648540 | 1617560 | 1576730 | 0 | 0 | 1558150 | 720.456 | 0 | 0 | 0 | 0 | 1558150 | 720.456 | 1530230 | 1499629.625
1408 | 2003-02-28 15:00 | 425 | 803 | 84 | 9.65 | 3.76 | 0 | 25.1363 | 239.608 | 54.6525 | 0 | 425 | 464.436 | 103.72 | 3.9819 | 464.436 | 97.0651 | 0.020784 | 447.519 | 93.4727 | 0.015661 | 524.777 | 524.775 | 1178510 | 22.4811 | 1144030 | 1156270 | 1124870 | 0 | 0 | 1115700 | 734.269 | 0 | 0 | 0 | 0 | 1115700 | 734.269 | 1096760 | 1074822.375
1409 | 2003-02-28 16:00 | 176 | 329 | 96 | 9.95 | 3.76 | 0 | 13.9655 | 250.035 | 68.9757 | 0 | 176 | 118.925 | 109.912 | 1.649 | 118.925 | 102.859 | 0.0086071 | 108.297 | 99.0527 | 0.0064856 | 201.136 | 201.13 | 451686 | 14.8678 | 411232 | 430651 | 418701 | 0 | 0 | 417384 | 725.047 | 0 | 0 | 0 | 0 | 417384 | 725.047 | 409600 | 401408
1410 | 2003-02-28 17:00 | 19 | 114 | 11 | 9.82 | 3.76 | 0 | 2.0733 | 259.054 | 83.5127 | 0 | 19 | 10.3893 | 12.1952 | 0.17802 | 6.3844 | 11.4127 | 0.00092918 | 3.8783 | 10.9903 | 0.00070016 | 14.4232 | 14.4212 | 32386.7 | 10.1726 | 21226.5 | 22863.8 | 21221.6 | 0 | 0 | 21216.5 | 607.362 | 0 | 0 | 0 | 1555.8 | 19660.7 | 660 | 18936.9 | 18558.125
1411 | 2003-02-28 18:00 | 0 | 0 | 0 | 9.69 | 6.25 | 0
1412 | 2003-02-28 19:00 | 0 | 0 | 0 | 9.56 | 6.25 | 0
1413 | 2003-02-28 20:00 | 0 | 0 | 0 | 9.24 | 6.25 | 0
1414 | 2003-02-28 21:00 | 0 | 0 | 0 | 10.26 | 6.58 | 0
1415 | 2003-02-28 22:00 | 0 | 0 | 0 | 10.77 | 6.4 | 0
1416 | 2003-02-28 23:00 | 0 | 0 | 0 | 11.29 | 6.23 | 0
1417 | 2008-03-01 | 0 | 0 | 0 | 11.81 | 6.05 | 0
1418 | 2008-03-01 01:00 | 0 | 0 | 0 | 12.33 | 5.88 | 0
1419 | 2008-03-01 02:00 | 0 | 0 | 0 | 12.84 | 5.7 | 0
1420 | 2008-03-01 03:00 | 0 | 0 | 0 | 12.86 | 5.03 | 0
1421 | 2008-03-01 04:00 | 0 | 0 | 0 | 11.67 | 5.03 | 0
1422 | 2008-03-01 05:00 | 0 | 0 | 0 | 11.19 | 5.03 | 0
1423 | 2008-03-01 06:00 | 17 | 191 | 4 | 10.71 | 8.22 | 0 | 1.6488 | 100.026 | 84.2825 | 0 | 17 | 14.8864 | 4.794 | 0.15928 | 0.075543 | 4.4864 | 0.00083137 | 0.041406 | 4.3204 | 0.00062646 | 4.2316 | 4.231 | 9501.87 | 10.7876 | 3854.45 | 3976.78 | 3911.55 | 0 | 0 | 3911.3 | 500.708 | 0 | 0 | 0 | 3868.62 | 42.6846 | 660.046 | 41.0631 | 40.2418
1424 | 2008-03-01 07:00 | 212 | 618 | 66 | 10.23 | 8.22 | 0 | 13.613 | 108.97 | 69.7061 | 0 | 212 | 215.148 | 80.0677 | 1.9863 | 158.889 | 74.9304 | 0.010368 | 143.928 | 72.1573 | 0.0078123 | 209.61 | 209.698 | 470907 | 14.0784 | 432673 | 453177 | 405607 | 0 | 0 | 404288 | 728.836 | 0 | 0 | 0 | 0 | 404288 | 728.836 | 396255 | 388329.9688
1425 | 2008-03-01 08:00 | 386 | 660 | 108 | 11.92 | 8.22 | 0 | 24.8992 | 119.268 | 55.3203 | 0 | 386 | 375.7 | 130.882 | 3.6165 | 362.536 | 122.485 | 0.018877 | 348.805 | 117.952 | 0.014224 | 452.767 | 452.7 | 1016650 | 20.228 | 978680 | 998175 | 921400 | 0 | 0 | 915129 | 735.937 | 0 | 0 | 0 | 0 | 915129 | 735.937 | 899757 | 881762.125
1426 | 2008-03-01 09:00 | 580 | 784 | 131 | 13.62 | 10.38 | 0 | 34.9672 | 131.953 | 41.3283 | 0 | 580 | 588.321 | 161.266 | 5.4341 | 588.321 | 150.918 | 0.028364 | 578.565 | 145.333 | 0.021373 | 702.202 | 702.194 | 1576950 | 24.8945 | 1557560 | 1558060 | 1515170 | 0 | 0 | 1498730 | 736.323 | 0 | 0 | 0 | 0 | 1498730 | 736.323 | 1471880 | 1442441.75
1427 | 2008-03-01 10:00 | 621 | 553 | 245 | 15.31 | 10.38 | 0 | 42.9416 | 148.171 | 28.3237 | 0 | 621 | 485.848 | 284.054 | 5.8183 | 485.848 | 265.828 | 0.03037 | 482.544 | 255.99 | 0.022884 | 716.401 | 716.384 | 1608820 | 26.8123 | 1590860 | 1578500 | 1534500 | 0 | 0 | 1517410 | 731.377 | 0 | 0 | 0 | 0 | 1517410 | 731.377 | 1490250 | 1460447.375
1428 | 2008-03-01 11:00 | 580 | 306 | 355 | 16.28 | 10.38 | 0 | 47.5694 | 168.34 | 18.5229 | 0 | 580 | 289.047 | 394.026 | 5.4341 | 289.047 | 368.745 | 0.028364 | 288.258 | 355.098 | 0.021373 | 624.075 | 624.054 | 1401470 | 26.2999 | 1374780 | 1367000 | 1329430 | 0 | 0 | 1316420 | 727.919 | 0 | 0 | 0 | 0 | 1316420 | 727.919 | 1293750 | 1267879.625
1429 | 2008-03-01 12:00 | 661 | 541 | 262 | 17.26 | 8.15 | 0 | 47.7113 | 190.505 | 18.1851 | 0 | 661 | 512.422 | 305.715 | 6.1931 | 512.422 | 286.1 | 0.032326 | 511.075 | 275.512 | 0.024358 | 763.013 | 763.004 | 1713520 | 31.3244 | 1700380 | 1654840 | 1609790 | 0 | 0 | 1590260 | 716.822 | 0 | 0 | 0 | 0 | 1590260 | 716.822 | 1561530 | 1530297.5
1430 | 2008-03-01 13:00 | 637 | 605 | 223 | 18.23 | 8.15 | 0 | 43.3263 | 210.879 | 27.6594 | 0 | 637 | 534.414 | 260.409 | 5.9682 | 534.414 | 243.701 | 0.031152 | 530.966 | 234.681 | 0.023474 | 742.701 | 742.693 | 1667900 | 31.92 | 1652630 | 1604120 | 1560560 | 0 | 0 | 1542080 | 714.536 | 0 | 0 | 0 | 0 | 1542080 | 714.536 | 1514830 | 1484535.75
1431 | 2008-03-01 14:00 | 567 | 744 | 135 | 17.79 | 8.15 | 0 | 35.5155 | 227.343 | 40.5719 | 0 | 567 | 564.864 | 165.859 | 5.3124 | 564.864 | 155.217 | 0.027729 | 555.925 | 149.473 | 0.020894 | 684.256 | 684.246 | 1536650 | 30.4027 | 1515500 | 1480570 | 1442350 | 0 | 0 | 1426590 | 716.182 | 0 | 0 | 0 | 0 | 1426590 | 716.182 | 1402090 | 1374052.375
1432 | 2008-03-01 15:00 | 377 | 615 | 112 | 17.35 | 10.67 | 0 | 25.5475 | 240.216 | 54.5316 | 0 | 377 | 356.554 | 135.396 | 3.5322 | 356.554 | 126.709 | 0.018437 | 343.658 | 122.019 | 0.013893 | 451.72 | 451.715 | 1014440 | 24.4759 | 975618 | 977770 | 951842 | 0 | 0 | 945030 | 721.67 | 0 | 0 | 0 | 0 | 945030 | 721.67 | 929831 | 911234.25
1433 | 2008-03-01 16:00 | 166 | 316 | 88 | 16.9 | 10.67 | 0 | 14.3219 | 250.64 | 68.9035 | 0 | 166 | 113.495 | 101.079 | 1.5553 | 113.495 | 94.5936 | 0.0081181 | 103.404 | 91.0927 | 0.0061172 | 188.668 | 188.665 | 423692 | 19.8762 | 383907 | 393172 | 382810 | 0 | 0 | 381640 | 703.669 | 0 | 0 | 0 | 0 | 381640 | 703.669 | 374608 | 367116.0938
1434 | 2008-03-01 17:00 | 18 | 114 | 9 | 15.59 | 10.67 | 0 | 2.3958 | 259.661 | 83.4731 | 0 | 18 | 11.7589 | 10.7875 | 0.16865 | 8.0228 | 10.0953 | 0.00088028 | 4.8949 | 9.7217 | 0.00066331 | 14.1788 | 14.1775 | 31838.9 | 15.8137 | 20788.2 | 21792.1 | 20232.4 | 0 | 0 | 20227.5 | 586.538 | 0 | 0 | 0 | 3873.47 | 16354 | 660 | 15748.6 | 15433.6572
1435 | 2008-03-01 18:00 | 0 | 0 | 0 | 14.28 | 9.55 | 0
1436 | 2008-03-01 19:00 | 0 | 0 | 0 | 12.96 | 9.55 | 0
1437 | 2008-03-01 20:00 | 0 | 0 | 0 | 12.21 | 9.55 | 0
1438 | 2008-03-01 21:00 | 0 | 0 | 0 | 11.45 | 10.46 | 0
1439 | 2008-03-01 22:00 | 0 | 0 | 0 | 10.7 | 10.46 | 0
1440 | 2008-03-01 23:00 | 0 | 0 | 0 | 10.02 | 10.46 | 0
1441 | 2008-03-02 | 0 | 0 | 0 | 9.35 | 6.86 | 0
1442 | 2008-03-02 01:00 | 0 | 0 | 0 | 8.67 | 6.86 | 0
1443 | 2008-03-02 02:00 | 0 | 0 | 0 | 7.82 | 6.86 | 0
1444 | 2008-03-02 03:00 | 0 | 0 | 0 | 6.96 | 10.05 | 0
1445 | 2008-03-02 04:00 | 0 | 0 | 0 | 6.1 | 10.05 | 0
1446 | 2008-03-02 05:00 | 0 | 0 | 0 | 5.87 | 10.05 | 0
1447 | 2008-03-02 06:00 | 18 | 164 | 6 | 5.64 | 12.41 | 0 | 1.9101 | 99.7426 | 84.1637 | 0 | 18 | 14.0257 | 7.1278 | 0.16865 | 0.063041 | 6.6705 | 0.00088028 | 0.035195 | 6.4236 | 0.00066331 | 6.2657 | 6.2658 | 14071.4 | 5.729 | 7031.69 | 7544.64 | 7374.6 | 0 | 0 | 7373.91 | 562.807 | 0 | 0 | 0 | 2545.32 | 4828.6 | 660 | 4646.51 | 4553.5801
1448 | 2008-03-02 07:00 | 200 | 599 | 56 | 5.41 | 12.41 | 0 | 13.8893 | 108.693 | 69.571 | 0 | 200 | 209.387 | 69.4107 | 1.8738 | 157.169 | 64.9572 | 0.0097808 | 142.513 | 62.5532 | 0.0073701 | 198.922 | 198.963 | 446789 | 8.2377 | 409051 | 439661 | 388961 | 0 | 0 | 387790 | 744.189 | 0 | 0 | 0 | 0 | 387790 | 744.189 | 379614 | 372022.1875
1449 | 2008-03-02 08:00 | 413 | 777 | 82 | 6.54 | 12.41 | 0 | 25.1994 | 119.001 | 55.1611 | 0 | 413 | 444.116 | 100.863 | 3.8695 | 430.121 | 94.391 | 0.020197 | 413.981 | 90.8977 | 0.015219 | 489.747 | 489.792 | 1099960 | 13.501 | 1064220 | 1115890 | 1019030 | 0 | 0 | 1011850 | 762.608 | 0 | 0 | 0 | 0 | 1011850 | 762.608 | 993470 | 973600.75
1450 | 2008-03-02 09:00 | 574 | 798 | 114 | 7.68 | 12.3 | 0 | 35.2992 | 131.713 | 41.1306 | 0 | 574 | 599.603 | 139.307 | 5.3779 | 599.603 | 130.369 | 0.028071 | 589.78 | 125.544 | 0.021152 | 693.885 | 693.883 | 1558290 | 17.6061 | 1538080 | 1585490 | 1542430 | 0 | 0 | 1526360 | 758.8 | 0 | 0 | 0 | 0 | 1526360 | 758.8 | 1497330 | 1467383.125
1451 | 2008-03-02 10:00 | 672 | 738 | 167 | 8.81 | 12.3 | 0 | 43.3077 | 148.004 | 28.0589 | 0 | 672 | 649.707 | 204.842 | 6.2961 | 649.707 | 191.699 | 0.032864 | 645.38 | 184.605 | 0.024763 | 805.109 | 805.102 | 1808050 | 20.3271 | 1799470 | 1834110 | 1781680 | 0 | 0 | 1760140 | 755.34 | 0 | 0 | 0 | 0 | 1760140 | 755.34 | 1724360 | 1689868.25
1452 | 2008-03-02 11:00 | 753 | 802 | 159 | 9.82 | 12.3 | 0 | 47.9551 | 168.32 | 18.1555 | 0 | 753 | 760.049 | 192.652 | 7.055 | 760.049 | 180.291 | 0.036825 | 758.058 | 173.618 | 0.027748 | 903.753 | 903.744 | 2029580 | 22.7482 | 2032250 | 2050820 | 1994370 | 0 | 0 | 1967040 | 749.664 | 0 | 0 | 0 | 0 | 1967040 | 749.664 | 1925100 | 1886597.75
1453 | 2008-03-02 12:00 | 726 | 682 | 220 | 10.83 | 11.55 | 0 | 48.0816 | 190.667 | 17.8539 | 0 | 726 | 647.27 | 264.732 | 6.8021 | 647.27 | 247.746 | 0.035504 | 645.632 | 238.577 | 0.026753 | 857.709 | 857.704 | 1926190 | 23.6606 | 1923520 | 1933920 | 1879250 | 0 | 0 | 1854560 | 743.813 | 0 | 0 | 0 | 0 | 1854560 | 743.813 | 1816860 | 1780525.375
1454 | 2008-03-02 13:00 | 747 | 862 | 153 | 11.84 | 11.55 | 0 | 43.6504 | 211.169 | 27.4722 | 0 | 747 | 763.51 | 184.309 | 6.9988 | 763.51 | 172.483 | 0.036531 | 758.658 | 166.1 | 0.027527 | 897.041 | 897.031 | 2014500 | 25.2589 | 2016380 | 2013930 | 1956560 | 0 | 0 | 1929650 | 741.278 | 0 | 0 | 0 | 0 | 1929650 | 741.278 | 1889780 | 1851982.25
1455 | 2008-03-02 14:00 | 619 | 926 | 78 | 12.01 | 11.55 | 0 | 35.787 | 227.681 | 40.4656 | 0 | 619 | 703.847 | 94.0979 | 5.7995 | 703.847 | 88.0604 | 0.030272 | 692.782 | 84.8013 | 0.02281 | 754.278 | 754.275 | 1693910 | 23.2934 | 1679840 | 1691620 | 1646150 | 0 | 0 | 1627020 | 741.508 | 0 | 0 | 0 | 0 | 1627020 | 741.508 | 1596350 | 1564421.25
1456 | 2008-03-02 15:00 | 442 | 862 | 67 | 12.18 | 9.02 | 0 | 25.7756 | 240.562 | 54.4687 | 0 | 442 | 501.164 | 81.2301 | 4.1412 | 501.164 | 76.0182 | 0.021616 | 483.104 | 73.2049 | 0.016288 | 539.635 | 539.633 | 1211880 | 21.601 | 1178440 | 1195500 | 1162430 | 0 | 0 | 1152760 | 738.665 | 0 | 0 | 0 | 0 | 1152760 | 738.665 | 1132870 | 1110216.875
1457 | 2008-03-02 16:00 | 229 | 694 | 55 | 12.35 | 9.02 | 0 | 14.5196 | 250.983 | 68.8669 | 0 | 229 | 250.221 | 67.5161 | 2.1456 | 250.221 | 63.1841 | 0.011199 | 228.031 | 60.8457 | 0.0084387 | 280.219 | 280.214 | 629290 | 17.242 | 586583 | 607173 | 590803 | 0 | 0 | 588228 | 730.202 | 0 | 0 | 0 | 0 | 588228 | 730.202 | 578421 | 566852.25
1458 | 2008-03-02 17:00 | 27 | 254 | 7 | 12.05 | 9.02 | 0 | 2.5748 | 260.004 | 83.454 | 0 | 27 | 26.2072 | 8.5916 | 0.25297 | 19.5322 | 8.0403 | 0.0013204 | 11.9422 | 7.7428 | 0.00099496 | 19.0953 | 19.0939 | 42879.4 | 12.3833 | 29942.7 | 31941.6 | 28620.3 | 0 | 0 | 28611.1 | 617.831 | 0 | 0 | 0 | 1473.77 | 27137.3 | 660 | 26150.3 | 25627.3418
1459 | 2008-03-02 18:00 | 0 | 0 | 0 | 11.75 | 10.44 | 0
1460 | 2008-03-02 19:00 | 0 | 0 | 0 | 11.45 | 10.44 | 0
1461 | 2008-03-02 20:00 | 0 | 0 | 0 | 10.88 | 10.44 | 0
1462 | 2008-03-02 21:00 | 0 | 0 | 0 | 10.3 | 11.47 | 0
1463 | 2008-03-02 22:00 | 0 | 0 | 0 | 9.73 | 11.47 | 0
1464 | 2008-03-02 23:00 | 0 | 0 | 0 | 8.98 | 11.47 | 0
1465 | 2008-03-03 | 0 | 0 | 0 | 8.23 | 12.89 | 0
1466 | 2008-03-03 01:00 | 0 | 0 | 0 | 7.48 | 12.89 | 0
1467 | 2008-03-03 02:00 | 0 | 0 | 0 | 6.61 | 12.89 | 0
1468 | 2008-03-03 03:00 | 0 | 0 | 0 | 5.74 | 13.17 | 0
1469 | 2008-03-03 04:00 | 0 | 0 | 0 | 4.88 | 13.17 | 0
1470 | 2008-03-03 05:00 | 0 | 0 | 0 | 4.16 | 13.17 | 0
1471 | 2008-03-03 06:00 | 24 | 236 | 7 | 3.44 | 10 | 0 | 2.174 | 99.4588 | 84.0429 | 0 | 24 | 20.2795 | 8.3301 | 0.22486 | 0.070568 | 7.7956 | 0.0011737 | 0.040099 | 7.5071 | 0.00088441 | 7.3216 | 7.3205 | 16440.4 | 3.5603 | 8764.81 | 9550.92 | 9323.8 | 0 | 0 | 9322.8 | 588.192 | 0 | 0 | 0 | 1686.23 | 7636.57 | 660 | 7349.88 | 7202.8848
1472 | 2008-03-03 07:00 | 229 | 706 | 56 | 2.72 | 10 | 0 | 14.1679 | 108.416 | 69.4344 | 0 | 229 | 248.285 | 68.1909 | 2.1456 | 189.211 | 63.8156 | 0.011199 | 171.74 | 61.4539 | 0.0084387 | 226.206 | 226.207 | 507966 | 6.4374 | 469624 | 507716 | 445273 | 0 | 0 | 443764 | 752.668 | 0 | 0 | 0 | 0 | 443764 | 752.668 | 434744 | 426048.875
1473 | 2008-03-03 08:00 | 443 | 865 | 71 | 4.56 | 10 | 0 | 25.5016 | 118.732 | 55.0009 | 0 | 443 | 495.581 | 88.5875 | 4.1506 | 481.51 | 82.9036 | 0.021664 | 463.61 | 79.8354 | 0.016325 | 527.158 | 527.18 | 1183930 | 13.2234 | 1150670 | 1207350 | 1098840 | 0 | 0 | 1090540 | 764.959 | 0 | 0 | 0 | 0 | 1090540 | 764.959 | 1070450 | 1049045.75
1474 | 2008-03-03 09:00 | 617 | 923 | 80 | 6.4 | 8.27 | 0 | 35.6331 | 131.471 | 40.9326 | 0 | 617 | 696.357 | 96.2159 | 5.7808 | 696.357 | 90.0425 | 0.030174 | 685.088 | 86.7101 | 0.022737 | 748.667 | 748.663 | 1681300 | 20.0965 | 1666650 | 1700470 | 1652360 | 0 | 0 | 1633660 | 752.955 | 0 | 0 | 0 | 0 | 1633660 | 752.955 | 1601930 | 1569889.25
1475 | 2008-03-03 10:00 | 759 | 972 | 89 | 8.24 | 8.27 | 0 | 43.6758 | 147.836 | 27.7942 | 0 | 759 | 858.269 | 106.533 | 7.1112 | 858.269 | 99.6974 | 0.037118 | 852.672 | 96.0077 | 0.027969 | 920.247 | 920.238 | 2066620 | 25.0755 | 2071240 | 2070220 | 2011760 | 0 | 0 | 1983440 | 742.35 | 0 | 0 | 0 | 0 | 1983440 | 742.35 | 1941730 | 1902900.125
1476 | 2008-03-03 11:00 | 830 | 934 | 134 | 9.36 | 8.27 | 0 | 48.3427 | 168.301 | 17.7866 | 0 | 830 | 887.033 | 165.348 | 7.7764 | 887.033 | 154.739 | 0.040591 | 884.807 | 149.012 | 0.030586 | 1002.83 | 1002.83 | 2252110 | 27.7065 | 2266690 | 2241030 | 2179730 | 0 | 0 | 2145820 | 733.811 | 101015 | 0 | 0 | 0 | 2044850 | 771.663 | 1997770 | 1957814.125
1477 | 2008-03-03 12:00 | 789 | 878 | 134 | 10.47 | 2.42 | 0 | 48.4531 | 190.835 | 17.5242 | 0 | 789 | 834.568 | 165.367 | 7.3923 | 834.568 | 154.757 | 0.038585 | 832.537 | 149.029 | 0.029075 | 952.148 | 952.137 | 2138260 | 35.9097 | 2146690 | 2048740 | 1995620 | 0 | 0 | 1964910 | 706.946 | 0 | 0 | 0 | 0 | 1964910 | 706.946 | 1924180 | 1885694.625
1478 | 2008-03-03 13:00 | 764 | 923 | 125 | 11.58 | 2.42 | 0 | 43.9743 | 211.465 | 27.2897 | 0 | 764 | 817.875 | 154.001 | 7.1581 | 817.875 | 144.12 | 0.037363 | 812.753 | 138.786 | 0.028154 | 923.02 | 923.015 | 2072860 | 36.2416 | 2077800 | 1979920 | 1931620 | 0 | 0 | 1902560 | 703.361 | 0 | 0 | 0 | 0 | 1902560 | 703.361 | 1864060 | 1826774.25
1479 | 2008-03-03 14:00 | 632 | 938 | 81 | 12.4 | 2.42 | 0 | 36.0574 | 228.024 | 40.3632 | 0 | 632 | 713.285 | 97.3201 | 5.9214 | 713.285 | 91.0759 | 0.030907 | 702.143 | 87.7052 | 0.023289 | 766.175 | 766.169 | 1720620 | 32.8709 | 1707820 | 1650810 | 1609440 | 0 | 0 | 1589520 | 709.866 | 0 | 0 | 0 | 0 | 1589520 | 709.866 | 1561030 | 1529812.75
1480 | 2008-03-03 15:00 | 452 | 870 | 71 | 13.23 | 1.14 | 0 | 26.0026 | 240.912 | 54.4091 | 0 | 452 | 505.78 | 88.641 | 4.2349 | 505.78 | 82.9536 | 0.022105 | 487.616 | 79.8836 | 0.016656 | 550.491 | 550.487 | 1236260 | 29.2538 | 1203610 | 1181310 | 1150050 | 0 | 0 | 1139880 | 712.451 | 0 | 0 | 0 | 0 | 1139880 | 712.451 | 1121530 | 1099103.75
1481 | 2008-03-03 16:00 | 228 | 682 | 54 | 14.05 | 1.14 | 0 | 14.7161 | 251.329 | 68.833 | 0 | 228 | 247.331 | 66.3162 | 2.1362 | 247.331 | 62.0613 | 0.01115 | 225.45 | 59.7644 | 0.0084019 | 276.666 | 276.66 | 621306 | 22.1031 | 578636 | 586223 | 570590 | 0 | 0 | 568070 | 713.367 | 0 | 0 | 0 | 0 | 568070 | 713.367 | 558958 | 547778.4375
1482 | 2008-03-03 17:00 | 27 | 255 | 6 | 13.87 | 1.14 | 0 | 2.7529 | 260.349 | 83.4368 | 0 | 27 | 27.5894 | 7.4334 | 0.25297 | 20.5624 | 6.9565 | 0.0013204 | 12.5955 | 6.699 | 0.00099496 | 18.7167 | 18.7134 | 42024.9 | 14.4147 | 29274.1 | 30909.7 | 27436 | 0 | 0 | 27426.9 | 602.016 | 0 | 0 | 0 | 2247.4 | 25179.5 | 660 | 24260.8 | 23775.623
1483 | 2008-03-03 18:00 | 0 | 0 | 0 | 13.7 | 1.86 | 0
1484 | 2008-03-03 19:00 | 0 | 0 | 0 | 13.52 | 1.86 | 0
1485 | 2008-03-03 20:00 | 0 | 0 | 0 | 13.22 | 1.86 | 0
1486 | 2008-03-03 21:00 | 0 | 0 | 0 | 12.92 | 3.91 | 0
1487 | 2008-03-03 22:00 | 0 | 0 | 0 | 12.62 | 3.91 | 0
1488 | 2008-03-03 23:00 | 0 | 0 | 0 | 11.98 | 3.91 | 0
1489 | 2008-03-04 | 0 | 0 | 0 | 11.34 | 5.04 | 0
1490 | 2008-03-04 01:00 | 0 | 0 | 0 | 10.7 | 5.04 | 0
1491 | 2008-03-04 02:00 | 0 | 0 | 0 | 10.07 | 5.04 | 0
1492 | 2008-03-04 03:00 | 0 | 0 | 0 | 9.44 | 4.3 | 0
1493 | 2008-03-04 04:00 | 0 | 0 | 0 | 8.81 | 4.3 | 0
1494 | 2008-03-04 05:00 | 0 | 0 | 0 | 8.25 | 4.3 | 0
1495 | 2008-03-04 06:00 | 9 | 0 | 9 | 7.68 | 5.43 | 0 | 2.4404 | 99.1748 | 83.9201 | 0 | 9 | 0 | 8.1674 | 0.084323 | 0 | 7.6434 | 0.00044014 | 0 | 7.3605 | 0.00033165 | 7.14 | 7.1397 | 16033.9 | 7.8365 | 8459.93 | 9072.3 | 8882.73 | 0 | 0 | 8881.77 | 570.256 | 0 | 0 | 0 | 2854.45 | 6027.32 | 660 | 5800.46 | 5684.4536
1496 | 2008-03-04 07:00 | 142 | 156 | 103 | 7.12 | 5.43 | 0 | 14.4487 | 108.137 | 69.2963 | 0 | 142 | 55.2591 | 106.915 | 1.3304 | 42.7402 | 100.055 | 0.0069444 | 38.8326 | 96.352 | 0.0052327 | 131.134 | 131.14 | 294498 | 9.9953 | 259521 | 278203 | 262082 | 0 | 0 | 261563 | 723.087 | 0 | 0 | 0 | 0 | 261563 | 723.087 | 254406 | 249318.1562
1497 | 2008-03-04 08:00 | 341 | 373 | 179 | 8.64 | 5.43 | 0 | 25.8058 | 118.462 | 54.8399 | 0 | 341 | 214.301 | 193.647 | 3.1949 | 208.868 | 181.222 | 0.016676 | 201.176 | 174.515 | 0.012566 | 364.433 | 364.411 | 818385 | 16.6299 | 776552 | 804970 | 753533 | 0 | 0 | 749459 | 742.411 | 0 | 0 | 0 | 0 | 749459 | 742.411 | 736636 | 721903.5
1498 | 2008-03-04 09:00 | 574 | 729 | 146 | 10.17 | 4.48 | 0 | 35.969 | 131.228 | 40.7345 | 0 | 574 | 552.166 | 176.819 | 5.3779 | 552.166 | 165.474 | 0.028071 | 543.339 | 159.35 | 0.021152 | 681.629 | 681.631 | 1530770 | 26.0677 | 1509370 | 1502290 | 1459350 | 0 | 0 | 1443930 | 732.802 | 0 | 0 | 0 | 0 | 1443930 | 732.802 | 1418390 | 1390018.375
1499 | 2008-03-04 10:00 | 712 | 831 | 136 | 11.69 | 4.48 | 0 | 44.0459 | 147.668 | 27.5296 | 0 | 712 | 734.688 | 165.701 | 6.6709 | 734.688 | 155.069 | 0.03482 | 729.998 | 149.33 | 0.026237 | 852.974 | 852.963 | 1915540 | 31.5837 | 1912320 | 1859370 | 1814450 | 0 | 0 | 1789670 | 716.462 | 0 | 0 | 0 | 0 | 1789670 | 716.462 | 1754790 | 1719691.875
1500 | 2008-03-04 11:00 | 796 | 923 | 104 | 13.43 | 4.48 | 0 | 48.7321 | 168.285 | 17.4162 | 0 | 796 | 878.455 | 123.212 | 7.4579 | 878.455 | 115.307 | 0.038928 | 876.344 | 111.039 | 0.029333 | 957.79 | 957.781 | 2150940 | 35.7684 | 2160050 | 2062890 | 2010600 | 0 | 0 | 1979490 | 707.043 | 0 | 0 | 0 | 0 | 1979490 | 707.043 | 1938230 | 1899469.75
1501 | 2008-03-04 12:00 | 796 | 923 | 103 | 15.18 | 1.2 | 0 | 48.8254 | 191.009 | 17.1963 | 0 | 796 | 879.521 | 122.086 | 7.4579 | 879.521 | 114.253 | 0.038928 | 877.463 | 110.024 | 0.029333 | 957.891 | 957.885 | 2151160 | 42.9502 | 2160280 | 1997440 | 1946370 | 0 | 0 | 1915180 | 683.291 | 0 | 0 | 0 | 0 | 1915180 | 683.291 | 1876400 | 1838873.125
1502 | 2008-03-04 13:00 | 768 | 922 | 126 | 16.92 | 1.2 | 0 | 44.2979 | 211.767 | 27.1118 | 0 | 768 | 818.249 | 154.848 | 7.1956 | 818.249 | 144.913 | 0.037558 | 813.199 | 139.55 | 0.028301 | 924.194 | 924.185 | 2075480 | 43.7132 | 2080570 | 1916580 | 1869620 | 0 | 0 | 1840560 | 680.529 | 0 | 0 | 0 | 0 | 1840560 | 680.529 | 1804540 | 1768449.75
1503 | 2008-03-04 14:00 | 622 | 921 | 77 | 17.69 | 1.2 | 0 | 36.3269 | 228.373 | 40.265 | 0 | 622 | 702.018 | 92.5925 | 5.8277 | 702.018 | 86.6516 | 0.030418 | 691.119 | 83.4447 | 0.022921 | 751.349 | 751.345 | 1687330 | 39.4723 | 1672950 | 1569760 | 1531460 | 0 | 0 | 1512230 | 687.124 | 0 | 0 | 0 | 0 | 1512230 | 687.124 | 1486850 | 1457114.5
1504 | 2008-03-04 15:00 | 447 | 861 | 67 | 18.45 | 4.86 | 0 | 26.2282 | 241.266 | 54.3528 | 0 | 447 | 501.102 | 80.8696 | 4.188 | 501.102 | 75.6809 | 0.02186 | 483.166 | 72.88 | 0.016472 | 539.38 | 539.379 | 1211310 | 30.722 | 1177850 | 1148540 | 1118410 | 0 | 0 | 1108650 | 707.583 | 0 | 0 | 0 | 0 | 1108650 | 707.583 | 1091160 | 1069338.25
1505 | 2008-03-04 16:00 | 235 | 713 | 51 | 19.22 | 4.86 | 0 | 14.9114 | 251.678 | 68.8016 | 0 | 235 | 258.56 | 62.9803 | 2.2018 | 258.56 | 58.9394 | 0.011492 | 235.736 | 56.7581 | 0.0086598 | 283.727 | 283.724 | 637170 | 25.6753 | 594434 | 592556 | 576788 | 0 | 0 | 574124 | 701.298 | 0 | 0 | 0 | 0 | 574124 | 701.298 | 565324 | 554017.25
1506 | 2008-03-04 17:00 | 28 | 272 | 6 | 18.59 | 4.86 | 0 | 2.9303 | 260.697 | 83.4216 | 0 | 28 | 28.97 | 7.4501 | 0.26234 | 23.3793 | 6.9721 | 0.0013693 | 14.3446 | 6.714 | 0.0010318 | 20.4278 | 20.4257 | 45869.8 | 19.0547 | 32482.1 | 33507.5 | 30077 | 0 | 0 | 30065.8 | 591.396 | 0 | 0 | 0 | 4217.38 | 25848.4 | 660 | 24906.3 | 24408.2227
1507 | 2008-03-04 18:00 | 0 | 0 | 0 | 17.97 | 8.41 | 0
1508 | 2008-03-04 19:00 | 0 | 0 | 0 | 17.34 | 8.41 | 0
1509 | 2008-03-04 20:00 | 0 | 0 | 0 | 16.23 | 8.41 | 0
1510 | 2008-03-04 21:00 | 0 | 0 | 0 | 15.11 | 10.08 | 0
1511 | 2008-03-04 22:00 | 0 | 0 | 0 | 13.99 | 10.08 | 0
1512 | 2008-03-04 23:00 | 0 | 0 | 0 | 13.11 | 10.08 | 0
1513 | 2008-03-05 | 0 | 0 | 0 | 12.22 | 6.93 | 0
1514 | 2008-03-05 01:00 | 0 | 0 | 0 | 11.33 | 6.93 | 0
1515 | 2008-03-05 02:00 | 0 | 0 | 0 | 10.31 | 6.93 | 0
1516 | 2008-03-05 03:00 | 0 | 0 | 0 | 9.28 | 8.91 | 0
1517 | 2008-03-05 04:00 | 0 | 0 | 0 | 8.25 | 8.91 | 0
1518 | 2008-03-05 05:00 | 0 | 0 | 0 | 7.87 | 8.91 | 0
1519 | 2008-03-05 06:00 | 32 | 286 | 10 | 7.48 | 7.24 | 0 | 2.709 | 98.8906 | 83.7955 | 0 | 32 | 27.3299 | 11.8689 | 0.29981 | 0.019813 | 11.1074 | 0.0015649 | 0.011637 | 10.6963 | 0.0011792 | 10.3878 | 10.3875 | 23327.9 | 7.6828 | 13991.7 | 15180.6 | 14824.1 | 0 | 0 | 14821.7 | 597.315 | 0 | 0 | 0 | 1900.22 | 12921.5 | 660 | 12440.5 | 12191.6758
1520 | 2008-03-05 07:00 | 238 | 716 | 55 | 7.09 | 7.24 | 0 | 14.7315 | 107.859 | 69.157 | 0 | 238 | 256.058 | 66.944 | 2.2299 | 200.833 | 62.6488 | 0.011639 | 182.653 | 60.3302 | 0.0087704 | 235.702 | 235.774 | 529455 | 11.693 | 490715 | 518686 | 456831 | 0 | 0 | 455178 | 737.282 | 0 | 0 | 0 | 0 | 455178 | 737.282 | 446400 | 437471.6875
1521 | 2008-03-05 08:00 | 446 | 859 | 68 | 8.45 | 7.24 | 0 | 26.1118 | 118.192 | 54.6783 | 0 | 446 | 496.557 | 84.833 | 4.1787 | 485.638 | 79.3899 | 0.021811 | 467.921 | 76.4518 | 0.016435 | 528.058 | 528.025 | 1185840 | 18.7586 | 1152390 | 1182250 | 1100030 | 0 | 0 | 1090950 | 724.914 | 0 | 0 | 0 | 6468.34 | 1084480 | 729.239 | 1066410 | 1045082.625
1522 | 2008-03-05 09:00 | 630 | 882 | 109 | 9.82 | 9.95 | 0 | 36.3067 | 130.984 | 40.5364 | 0 | 630 | 668.724 | 133.266 | 5.9026 | 668.724 | 124.715 | 0.03081 | 658.165 | 120.1 | 0.023216 | 754.939 | 754.932 | 1695390 | 22.2643 | 1681390 | 1700380 | 1653030 | 0 | 0 | 1633960 | 746.025 | 0 | 0 | 0 | 0 | 1633960 | 746.025 | 1602760 | 1570703.875
1523 | 2008-03-05 10:00 | 719 | 800 | 160 | 11.19 | 9.95 | 0 | 44.4178 | 147.499 | 27.2655 | 0 | 719 | 709.961 | 196.291 | 6.7365 | 709.961 | 183.697 | 0.035162 | 705.524 | 176.898 | 0.026495 | 855.975 | 855.969 | 1922290 | 25.2998 | 1919420 | 1916740 | 1862360 | 0 | 0 | 1837840 | 739.687 | 0 | 0 | 0 | 0 | 1837840 | 739.687 | 1800980 | 1764961.25
1524 | 2008-03-05 11:00 | 814 | 905 | 132 | 11.74 | 9.95 | 0 | 49.1231 | 168.271 | 17.0446 | 0 | 814 | 862.358 | 162.623 | 7.6265 | 862.358 | 152.189 | 0.039808 | 860.377 | 146.556 | 0.029996 | 976.755 | 976.75 | 2193540 | 27.8408 | 2204940 | 2178770 | 2117610 | 0 | 0 | 2085680 | 735.298 | 42276.5 | 0 | 0 | 0 | 2044030 | 758.345 | 1998490 | 1958517.875
1525 | 2008-03-05 12:00 | 794 | 870 | 137 | 12.29 | 9 | 0 | 49.1985 | 191.188 | 16.8706 | 0 | 794 | 830.572 | 168.156 | 7.4392 | 830.572 | 157.366 | 0.03883 | 828.704 | 151.542 | 0.029259 | 950.867 | 950.857 | 2135390 | 28.9108 | 2143660 | 2108670 | 2052760 | 0 | 0 | 2022290 | 729.997 | 0 | 0 | 0 | 0 | 2022290 | 729.997 | 1979530 | 1939935.5
1526 | 2008-03-05 13:00 | 770 | 920 | 125 | 12.84 | 9 | 0 | 44.6211 | 212.076 | 26.9389 | 0 | 770 | 818.62 | 153.49 | 7.2143 | 818.62 | 143.642 | 0.037656 | 813.638 | 138.326 | 0.028375 | 923.433 | 923.427 | 2073780 | 28.9813 | 2078770 | 2044160 | 1989490 | 0 | 0 | 1960710 | 728.398 | 0 | 0 | 0 | 0 | 1960710 | 728.398 | 1920050 | 1881646.375
1527 | 2008-03-05 14:00 | 611 | 856 | 101 | 12.93 | 9 | 0 | 36.5952 | 228.728 | 40.171 | 0 | 611 | 653.691 | 124.491 | 5.7246 | 653.691 | 116.504 | 0.02988 | 643.601 | 112.192 | 0.022516 | 733.141 | 733.138 | 1646440 | 25.7451 | 1630170 | 1624840 | 1580850 | 0 | 0 | 1562760 | 732.447 | 0 | 0 | 0 | 0 | 1562760 | 732.447 | 1534300 | 1503609.5
1528 | 2008-03-05 15:00 | 460 | 872 | 72 | 13.01 | 7.44 | 0 | 26.4526 | 241.624 | 54.2998 | 0 | 460 | 508.275 | 89.3406 | 4.3098 | 508.275 | 83.6083 | 0.022496 | 490.138 | 80.514 | 0.016951 | 553.549 | 553.544 | 1243120 | 23.6807 | 1210690 | 1217390 | 1183290 | 0 | 0 | 1173100 | 732.246 | 0 | 0 | 0 | 0 | 1173100 | 732.246 | 1153130 | 1130066.75
1529 | 2008-03-05 16:00 | 235 | 693 | 54 | 13.1 | 7.44 | 0 | 15.1057 | 252.029 | 68.7727 | 0 | 235 | 251.475 | 65.9772 | 2.2018 | 251.475 | 61.744 | 0.011492 | 229.321 | 59.4589 | 0.0086598 | 280.125 | 280.123 | 629088 | 18.4999 | 586384 | 603641 | 586397 | 0 | 0 | 583838 | 727.533 | 0 | 0 | 0 | 0 | 583838 | 727.533 | 574150 | 562666.5625
1530 | 2008-03-05 17:00 | 29 | 269 | 7 | 12.74 | 7.44 | 0 | 3.1067 | 261.047 | 83.4082 | 0 | 29 | 29.0285 | 8.6567 | 0.27171 | 23.4644 | 8.1013 | 0.0014182 | 14.4174 | 7.8014 | 0.0010687 | 21.5533 | 21.5585 | 48413.8 | 13.1556 | 34581.7 | 36756.1 | 33159.5 | 0 | 0 | 33147.1 | 615.023 | 0 | 0 | 0 | 1463.84 | 31683.3 | 660 | 30539.6 | 29928.8301
1531 | 2008-03-05 18:00 | 0 | 0 | 0 | 12.39 | 6.86 | 0
1532 | 2008-03-05 19:00 | 0 | 0 | 0 | 12.04 | 6.86 | 0
1533 | 2008-03-05 20:00 | 0 | 0 | 0 | 11.36 | 6.86 | 0
1534 | 2008-03-05 21:00 | 0 | 0 | 0 | 10.68 | 4.24 | 0
1535 | 2008-03-05 22:00 | 0 | 0 | 0 | 10 | 4.24 | 0
1536 | 2008-03-05 23:00 | 0 | 0 | 0 | 9.43 | 4.24 | 0
1537 | 2008-03-06 | 0 | 0 | 0 | 8.85 | 7.45 | 0
1538 | 2008-03-06 01:00 | 0 | 0 | 0 | 8.27 | 7.45 | 0
1539 | 2008-03-06 02:00 | 0 | 0 | 0 | 7.48 | 7.45 | 0
1540 | 2008-03-06 03:00 | 0 | 0 | 0 | 6.69 | 4.26 | 0
1541 | 2008-03-06 04:00 | 0 | 0 | 0 | 5.9 | 4.26 | 0
1542 | 2008-03-06 05:00 | 0 | 0 | 0 | 5.62 | 4.26 | 0
1543 | 2008-03-06 06:00 | 31 | 231 | 13 | 5.34 | 4.74 | 0 | 2.9798 | 98.6063 | 83.6691 | 0 | 31 | 22.8145 | 15.1327 | 0.29045 | 0.0033079 | 14.1618 | 0.001516 | 0.0019734 | 13.6376 | 0.0011424 | 13.2315 | 13.2309 | 29713.3 | 5.6434 | 19015.1 | 20899.1 | 20396.9 | 0 | 0 | 20392.6 | 619.008 | 0 | 0 | 0 | 869.183 | 19523.4 | 660 | 18804.4 | 18428.3242
1544 | 2008-03-06 07:00 | 225 | 653 | 55 | 5.05 | 4.74 | 0 | 15.0162 | 107.579 | 69.0166 | 0 | 225 | 234.962 | 66.8206 | 2.1081 | 186.666 | 62.5333 | 0.011003 | 169.936 | 60.2189 | 0.0082913 | 223.258 | 223.241 | 501312 | 10.169 | 462564 | 492246 | 435476 | 0 | 0 | 433977 | 733.249 | 0 | 0 | 0 | 167.532 | 433809 | 734.319 | 425402 | 416893.7812
1545 | 2008-03-06 08:00 | 420 | 742 | 90 | 6.66 | 4.74 | 0 | 26.4195 | 117.92 | 54.5162 | 0 | 420 | 430.52 | 110.219 | 3.9351 | 422.468 | 103.148 | 0.02054 | 407.201 | 99.3301 | 0.015477 | 491.351 | 491.327 | 1103420 | 17.9264 | 1067330 | 1099080 | 1031440 | 0 | 0 | 1023590 | 730.668 | 0 | 0 | 0 | 0 | 1023590 | 730.668 | 1006590 | 986462.9375
1546 | 2008-03-06 09:00 | 621 | 818 | 133 | 8.27 | 5.27 | 0 | 36.646 | 130.738 | 40.3384 | 0 | 621 | 623.202 | 162.165 | 5.8183 | 623.202 | 151.76 | 0.03037 | 613.482 | 146.143 | 0.022884 | 736.859 | 736.85 | 1654770 | 24.5941 | 1638890 | 1641390 | 1594640 | 0 | 0 | 1576550 | 738.733 | 0 | 0 | 0 | 0 | 1576550 | 738.733 | 1547480 | 1516530.875
1547 | 2008-03-06 10:00 | 718 | 786 | 165 | 9.87 | 5.27 | 0 | 44.7914 | 147.33 | 27.002 | 0 | 718 | 699.359 | 201.506 | 6.7271 | 699.359 | 188.577 | 0.035113 | 695.08 | 181.597 | 0.026458 | 850.403 | 850.395 | 1909770 | 28.7096 | 1906260 | 1876430 | 1827230 | 0 | 0 | 1802900 | 728.491 | 0 | 0 | 0 | 0 | 1802900 | 728.491 | 1767380 | 1732028.375
1548 | 2008-03-06 11:00 | 820 | 907 | 132 | 11.02 | 5.27 | 0 | 49.5158 | 168.259 | 16.6719 | 0 | 820 | 866.542 | 162.365 | 7.6828 | 866.542 | 151.947 | 0.040101 | 864.641 | 146.324 | 0.030217 | 980.665 | 980.66 | 2202320 | 32.7454 | 2214200 | 2142770 | 2086180 | 0 | 0 | 2053710 | 717.965 | 10248.6 | 0 | 0 | 0 | 2043030 | 728.838 | 1999550 | 1959555
1549 | 2008-03-06 12:00 | 801 | 913 | 108 | 12.16 | 2.91 | 0 | 49.5723 | 191.373 | 16.5473 | 0 | 801 | 872.672 | 127.199 | 7.5047 | 872.672 | 119.037 | 0.039172 | 870.787 | 114.632 | 0.029517 | 955.885 | 955.875 | 2146660 | 36.8815 | 2155530 | 2048440 | 1996670 | 0 | 0 | 1965650 | 702.839 | 0 | 0 | 0 | 0 | 1965650 | 702.839 | 1924900 | 1886400.75
1550 | 2008-03-06 13:00 | 732 | 894 | 102 | 13.3 | 2.91 | 0 | 44.9438 | 212.392 | 26.771 | 0 | 732 | 796.238 | 120.462 | 6.8583 | 796.238 | 112.733 | 0.035798 | 791.458 | 108.561 | 0.026974 | 873.044 | 873.037 | 1960620 | 35.8791 | 1959710 | 1870040 | 1822480 | 0 | 0 | 1796640 | 704.197 | 0 | 0 | 0 | 0 | 1796640 | 704.197 | 1761760 | 1726520.25
1551 | 2008-03-06 14:00 | 590 | 800 | 111 | 14 | 2.91 | 0 | 36.8623 | 229.087 | 40.0811 | 0 | 590 | 610.939 | 135.233 | 5.5278 | 610.939 | 126.556 | 0.028854 | 601.562 | 121.873 | 0.021742 | 701.753 | 701.745 | 1575950 | 32.149 | 1556510 | 1509020 | 1470880 | 0 | 0 | 1454210 | 710 | 0 | 0 | 0 | 0 | 1454210 | 710 | 1429360 | 1400772.125
1552 | 2008-03-06 15:00 | 422 | 779 | 72 | 14.7 | 3.24 | 0 | 26.6757 | 241.986 | 54.25 | 0 | 422 | 455.489 | 89.1274 | 3.9538 | 455.489 | 83.4088 | 0.020638 | 439.283 | 80.3219 | 0.015551 | 504.032 | 504.027 | 1131920 | 27.4538 | 1096070 | 1084250 | 1055910 | 0 | 0 | 1047430 | 716.608 | 0 | 0 | 0 | 0 | 1047430 | 716.608 | 1030700 | 1010081.25
1553 | 2008-03-06 16:00 | 211 | 547 | 66 | 15.39 | 3.24 | 0 | 15.2987 | 252.384 | 68.7464 | 0 | 211 | 199.21 | 79.2958 | 1.9769 | 199.21 | 74.208 | 0.010319 | 181.693 | 71.4616 | 0.0077754 | 245.568 | 245.565 | 551477 | 21.6037 | 509367 | 517301 | 503554 | 0 | 0 | 501570 | 709.873 | 0 | 0 | 0 | 0 | 501570 | 709.873 | 493244 | 483379.5938
1554 | 2008-03-06 17:00 | 27 | 216 | 9 | 15.37 | 3.24 | 0 | 3.2824 | 261.399 | 83.3967 | 0 | 27 | 23.7919 | 11.1581 | 0.25297 | 20.6999 | 10.4422 | 0.0013204 | 12.7345 | 10.0557 | 0.00099496 | 22.1075 | 22.1064 | 49644.4 | 15.9294 | 35419.7 | 37146.7 | 34843.1 | 0 | 0 | 34829.9 | 612.766 | 0 | 0 | 0 | 2372.28 | 32457.7 | 660 | 31287.6 | 30661.8027
1555 | 2008-03-06 18:00 | 0 | 0 | 0 | 15.34 | 3.3 | 0
1556 | 2008-03-06 19:00 | 0 | 0 | 0 | 15.31 | 3.3 | 0
1557 | 2008-03-06 20:00 | 0 | 0 | 0 | 14.53 | 3.3 | 0
1558 | 2008-03-06 21:00 | 0 | 0 | 0 | 13.74 | 4.23 | 0
1559 | 2008-03-06 22:00 | 0 | 0 | 0 | 12.95 | 4.23 | 0
1560 | 2008-03-06 23:00 | 0 | 0 | 0 | 12.27 | 4.23 | 0
1561 | 2008-03-07 | 0 | 0 | 0 | 11.59 | 7.68 | 0
1562 | 2008-03-07 01:00 | 0 | 0 | 0 | 10.91 | 7.68 | 0
1563 | 2008-03-07 02:00 | 0 | 0 | 0 | 10.28 | 7.68 | 0
1564 | 2008-03-07 03:00 | 0 | 0 | 0 | 9.65 | 6.35 | 0
1565 | 2008-03-07 04:00 | 0 | 0 | 0 | 9.02 | 6.35 | 0
1566 | 2008-03-07 05:00 | 0 | 0 | 0 | 8.41 | 6.35 | 0
1567 | 2008-03-07 06:00 | 39 | 239 | 19 | 7.8 | 7.91 | 0 | 3.2526 | 98.3218 | 83.5411 | 0 | 39 | 25.8599 | 21.4997 | 0.3654 | 0 | 20.1202 | 0.0019073 | 0 | 19.3756 | 0.0014372 | 18.7957 | 18.794 | 42206.4 | 8.1517 | 29162.3 | 31772.1 | 30977.9 | 0 | 0 | 30968.3 | 631.13 | 0 | 0 | 0 | 605.391 | 30362.9 | 660 | 29264.5 | 28679.1914
1568 | 2008-03-07 07:00 | 221 | 571 | 70 | 7.19 | 7.91 | 0 | 15.3026 | 107.299 | 68.8751 | 0 | 221 | 206.205 | 83.2402 | 2.0706 | 165.808 | 77.8994 | 0.010808 | 151.095 | 75.0163 | 0.0081439 | 219.336 | 219.374 | 492624 | 11.2952 | 453323 | 480817 | 430192 | 0 | 0 | 428765 | 734.73 | 0 | 0 | 0 | 0 | 428765 | 734.73 | 420298 | 411891.9688
1569 | 2008-03-07 08:00 | 411 | 683 | 104 | 8.89 | 7.91 | 0 | 26.7288 | 117.647 | 54.3537 | 0 | 411 | 397.79 | 125.297 | 3.8508 | 391.552 | 117.258 | 0.0201 | 377.536 | 112.918 | 0.015145 | 475.755 | 475.708 | 1068330 | 17.792 | 1031170 | 1062800 | 1004650 | 0 | 0 | 997158 | 727.918 | 0 | 0 | 0 | 0 | 997158 | 727.918 | 980792 | 961176.1875
1570 | 2008-03-07 09:00 | 616 | 801 | 135 | 10.59 | 3.49 | 0 | 36.9868 | 130.491 | 40.1409 | 0 | 616 | 611.182 | 164.092 | 5.7714 | 611.182 | 153.564 | 0.030125 | 601.767 | 147.881 | 0.0227 | 727.18 | 727.174 | 1633050 | 28.689 | 1616170 | 1590740 | 1550230 | 0 | 0 | 1532390 | 722.812 | 0 | 0 | 0 | 0 | 1532390 | 722.812 | 1505120 | 1475018.875
1571 | 2008-03-07 10:00 | 700 | 754 | 166 | 12.29 | 3.49 | 0 | 45.1666 | 147.159 | 26.7394 | 0 | 700 | 672.479 | 202.307 | 6.5584 | 672.479 | 189.327 | 0.034233 | 668.453 | 182.32 | 0.025795 | 825.275 | 825.263 | 1853330 | 32.8303 | 1846990 | 1785990 | 1741020 | 0 | 0 | 1717890 | 711.991 | 0 | 0 | 0 | 0 | 1717890 | 711.991 | 1685400 | 1651690
1572 | 2008-03-07 11:00 | 781 | 816 | 158 | 13.49 | 3.49 | 0 | 49.9098 | 168.249 | 16.2983 | 0 | 781 | 781.619 | 190.323 | 7.3174 | 781.619 | 178.112 | 0.038194 | 779.983 | 171.52 | 0.02878 | 922.986 | 922.977 | 2072780 | 36.4624 | 2077720 | 1977920 | 1926750 | 0 | 0 | 1897860 | 703.429 | 0 | 0 | 0 | 0 | 1897860 | 703.429 | 1859520 | 1822330.875
1573 | 2008-03-07 12:00 | 765 | 769 | 178 | 14.69 | 2.4 | 0 | 49.9467 | 191.564 | 16.2267 | 0 | 765 | 736.324 | 218.031 | 7.1674 | 736.324 | 204.041 | 0.037412 | 734.797 | 196.49 | 0.028191 | 903.375 | 903.356 | 2028700 | 38.8585 | 2031330 | 1912990 | 1864310 | 0 | 0 | 1836540 | 694.535 | 0 | 0 | 0 | 0 | 1836540 | 694.535 | 1800450 | 1764445.5
1574 | 2008-03-07 13:00 | 751 | 844 | 153 | 15.89 | 2.4 | 0 | 45.2659 | 212.714 | 26.6083 | 0 | 751 | 752.646 | 183.041 | 7.0363 | 752.646 | 171.297 | 0.036727 | 748.188 | 164.957 | 0.027675 | 885.778 | 885.773 | 1989210 | 39.5881 | 1989780 | 1867540 | 1818670 | 0 | 0 | 1792090 | 692.468 | 0 | 0 | 0 | 0 | 1792090 | 692.468 | 1757580 | 1722426.75
1575 | 2008-03-07 14:00 | 559 | 599 | 198 | 16.57 | 2.4 | 0 | 37.1282 | 229.452 | 39.9955 | 0 | 559 | 458.184 | 226.516 | 5.2374 | 458.184 | 211.982 | 0.027337 | 451.19 | 204.137 | 0.020599 | 635.686 | 635.678 | 1427570 | 33.577 | 1401900 | 1350170 | 1314970 | 0 | 0 | 1301350 | 702.81 | 0 | 0 | 0 | 0 | 1301350 | 702.81 | 1280130 | 1254527.625
1576 | 2008-03-07 15:00 | 313 | 248 | 201 | 17.26 | 1.48 | 0 | 26.8974 | 242.351 | 54.2034 | 0 | 313 | 144.807 | 216.09 | 2.9326 | 144.807 | 202.226 | 0.015307 | 139.669 | 194.741 | 0.011534 | 324.389 | 324.381 | 728475 | 26.489 | 685779 | 681083 | 663082 | 0 | 0 | 659588 | 703.367 | 0 | 0 | 0 | 0 | 659588 | 703.367 | 649583 | 636591.3125
1577 | 2008-03-07 16:00 | 81 | 0 | 81 | 17.94 | 1.48 | 0 | 15.4906 | 252.742 | 68.7225 | 0 | 81 | 0 | 75.9648 | 0.75891 | 0 | 71.0908 | 0.0039612 | 0 | 68.4598 | 0.0029849 | 66.4089 | 66.4032 | 149125 | 19.8292 | 123198 | 126488 | 123198 | 0 | 0 | 123058 | 656.929 | 0 | 0 | 0 | 21.5594 | 123037 | 660 | 119270 | 116884.1328
1578 | 2008-03-07 17:00 | 10 | 0 | 10 | 17.5 | 1.48 | 0 | 3.4572 | 261.753 | 83.387 | 0 | 10 | 0 | 9.0082 | 0.093692 | 0 | 8.4302 | 0.00048904 | 0 | 8.1182 | 0.0003685 | 7.875 | 7.8751 | 17685.5 | 17.7241 | 9686.94 | 10014.5 | 9808.98 | 0 | 0 | 9807.68 | 543.763 | 0 | 0 | 0 | 7686.27 | 2121.41 | 660 | 2041.07 | 2000.2478
1579 | 2008-03-07 18:00 | 0 | 0 | 0 | 17.05 | 5.61 | 0
1580 | 2008-03-07 19:00 | 0 | 0 | 0 | 16.6 | 5.61 | 0
1581 | 2008-03-07 20:00 | 0 | 0 | 0 | 15.79 | 5.61 | 0
1582 | 2008-03-07 21:00 | 0 | 0 | 0 | 14.99 | 6.82 | 0
1583 | 2008-03-07 22:00 | 0 | 0 | 0 | 14.18 | 6.82 | 0
1584 | 2008-03-07 23:00 | 0 | 0 | 0 | 13.49 | 6.82 | 0
1585 | 2008-03-08 | 0 | 0 | 0 | 12.79 | 8.05 | 0
1586 | 2008-03-08 01:00 | 0 | 0 | 0 | 12.1 | 8.05 | 0
1587 | 2008-03-08 02:00 | 0 | 0 | 0 | 11.45 | 8.05 | 0
1588 | 2008-03-08 03:00 | 0 | 0 | 0 | 10.81 | 9.75 | 0
1589 | 2008-03-08 04:00 | 0 | 0 | 0 | 10.17 | 9.75 | 0
1590 | 2008-03-08 05:00 | 0 | 0 | 0 | 9.87 | 9.75 | 0
1591 | 2008-03-08 06:00 | 41 | 296 | 16 | 9.56 | 9.8 | 0 | 3.5273 | 98.0373 | 83.4115 | 0 | 41 | 32.9705 | 18.7378 | 0.38414 | 0 | 17.5355 | 0.0020051 | 0 | 16.8866 | 0.0015109 | 16.3814 | 16.3802 | 36785.8 | 9.8325 | 24716.5 | 26698.4 | 26094.7 | 0 | 0 | 26087.6 | 617.24 | 0 | 0 | 0 | 1337.87 | 24749.7 | 660 | 23846 | 23369.0566
1592 | 2008-03-08 07:00 | 240 | 675 | 58 | 9.25 | 9.8 | 0 | 15.5906 | 107.018 | 68.7327 | 0 | 240 | 245.626 | 69.6762 | 2.2486 | 199.762 | 65.2056 | 0.011737 | 182.214 | 62.7924 | 0.0088441 | 237.664 | 237.606 | 533571 | 13.203 | 494248 | 519594 | 462696 | 0 | 0 | 460996 | 727.43 | 0 | 0 | 0 | 50.3476 | 460945 | 728.353 | 452374 | 443326.375
1593 | 2008-03-08 08:00 | 470 | 876 | 72 | 11.15 | 9.8 | 0 | 27.0395 | 117.373 | 54.191 | 0 | 470 | 512.235 | 88.7559 | 4.4035 | 505.773 | 83.0612 | 0.022985 | 487.84 | 79.9872 | 0.01732 | 550.809 | 550.757 | 1236870 | 20.3127 | 1204690 | 1228280 | 1163210 | 0 | 0 | 1153220 | 728.232 | 0 | 0 | 0 | 0 | 1153220 | 728.232 | 1133890 | 1111213.125
1594 | 2008-03-08 09:00 | 646 | 934 | 80 | 13.04 | 7.62 | 0 | 37.3289 | 130.243 | 39.9438 | 0 | 646 | 715.609 | 95.2865 | 6.0525 | 715.609 | 89.1727 | 0.031592 | 704.719 | 85.8725 | 0.023805 | 766.897 | 766.892 | 1722240 | 27.656 | 1709510 | 1690210 | 1644680 | 0 | 0 | 1624930 | 728.888 | 0 | 0 | 0 | 0 | 1624930 | 728.888 | 1594800 | 1562908.875
1595 | 2008-03-08 10:00 | 786 | 977 | 90 | 14.94 | 7.62 | 0 | 45.5432 | 146.988 | 26.4778 | 0 | 786 | 872.812 | 106.666 | 7.3642 | 872.812 | 99.8222 | 0.038439 | 867.698 | 96.1278 | 0.028964 | 934.939 | 934.933 | 2099630 | 32.7587 | 2105990 | 2037780 | 1987160 | 0 | 0 | 1957410 | 714.961 | 0 | 0 | 0 | 0 | 1957410 | 714.961 | 1916910 | 1878574.25
1596 | 2008-03-08 11:00 | 855 | 991 | 95 | 16.41 | 7.62 | 0 | 50.3052 | 168.242 | 15.924 | 0 | 855 | 949.807 | 112.275 | 8.0107 | 949.807 | 105.071 | 0.041813 | 947.912 | 101.183 | 0.031507 | 1017.65 | 1017.65 | 2285380 | 35.8051 | 2301780 | 2198420 | 2142400 | 0 | 0 | 2107230 | 707.827 | 61282.9 | 0 | 0 | 0 | 2043530 | 738.216 | 1999980 | 1959977.5
1597 | 2008-03-08 12:00 | 855 | 991 | 94 | 17.87 | 7.79 | 0 | 50.3215 | 191.761 | 15.9091 | 0 | 855 | 950.903 | 111.144 | 8.0107 | 950.903 | 104.013 | 0.041813 | 949.01 | 100.164 | 0.031507 | 1017.73 | 1017.72 | 2285550 | 37.0595 | 2301960 | 2186520 | 2130610 | 0 | 0 | 2095480 | 704.115 | 49938.2 | 0 | 0 | 0 | 2043460 | 731.545 | 1999970 | 1959974.5
1598 | 2008-03-08 13:00 | 787 | 977 | 91 | 19.34 | 7.79 | 0 | 45.5873 | 213.042 | 26.451 | 0 | 787 | 872.357 | 107.764 | 7.3736 | 872.357 | 100.849 | 0.038488 | 867.257 | 97.1171 | 0.029001 | 935.471 | 935.464 | 2100820 | 36.9785 | 2107250 | 2001680 | 1949580 | 0 | 0 | 1919920 | 702.299 | 0 | 0 | 0 | 0 | 1919920 | 702.299 | 1880810 | 1843192.875
1599 | 2008-03-08 14:00 | 631 | 910 | 79 | 19.62 | 7.79 | 0 | 37.3928 | 229.821 | 39.9141 | 0 | 631 | 697.193 | 94.1217 | 5.912 | 697.193 | 88.0826 | 0.030859 | 686.604 | 84.8228 | 0.023252 | 748.306 | 748.301 | 1680490 | 33.7295 | 1665800 | 1604120 | 1562860 | 0 | 0 | 1543880 | 706.729 | 0 | 0 | 0 | 0 | 1543880 | 706.729 | 1516850 | 1486514.875
1600 | 2008-03-08 15:00 | 472 | 844 | 87 | 19.9 | 10.89 | 0 | 27.1177 | 242.72 | 54.1601 | 0 | 472 | 494.551 | 105.105 | 4.4223 | 494.551 | 98.3616 | 0.023083 | 477.047 | 94.7213 | 0.017393 | 554.632 | 554.629 | 1245560 | 28.5334 | 1213220 | 1194630 | 1162220 | 0 | 0 | 1151970 | 716.905 | 0 | 0 | 0 | 0 | 1151970 | 716.905 | 1133160 | 1110497
1601 | 2008-03-08 16:00 | 229 | 606 | 65 | 20.17 | 10.89 | 0 | 15.6812 | 253.102 | 68.701 | 0 | 229 | 220.399 | 77.7794 | 2.1456 | 220.399 | 72.7889 | 0.011199 | 201.08 | 70.0951 | 0.0084387 | 263.048 | 263.046 | 590735 | 24.2646 | 548255 | 550079 | 535375 | 0 | 0 | 533095 | 703.488 | 0 | 0 | 0 | 0 | 533095 | 703.488 | 524633 | 514140.5938
1602 | 2008-03-08 17:00 | 30 | 248 | 9 | 19.44 | 10.89 | 0 | 3.6311 | 262.109 | 83.379 | 0 | 30 | 27.8315 | 11.0718 | 0.28108 | 25.9685 | 10.3615 | 0.0014671 | 16.0059 | 9.978 | 0.0011055 | 25.2054 | 25.2053 | 56604.1 | 19.8323 | 41236.1 | 42392.1 | 40502.3 | 0 | 0 | 40484.4 | 607.11 | 0 | 0 | 0 | 3947.93 | 36536.5 | 660 | 35228.3 | 34523.6953
1603 | 2008-03-08 18:00 | 0 | 0 | 0 | 18.7 | 7.48 | 0
1604 | 2008-03-08 19:00 | 0 | 0 | 0 | 17.96 | 7.48 | 0
1605 | 2008-03-08 20:00 | 0 | 0 | 0 | 16.89 | 7.48 | 0
1606 | 2008-03-08 21:00 | 0 | 0 | 0 | 15.82 | 6.98 | 0
1607 | 2008-03-08 22:00 | 0 | 0 | 0 | 14.75 | 6.98 | 0
1608 | 2008-03-08 23:00 | 0 | 0 | 0 | 13.83 | 6.98 | 0
1609 | 2008-03-09 | 0 | 0 | 0 | 12.9 | 10.46 | 0
1610 | 2008-03-09 01:00 | 0 | 0 | 0 | 11.98 | 10.46 | 0
1611 | 2008-03-09 02:00 | 0 | 0 | 0 | 10.86 | 10.46 | 0
1612 | 2008-03-09 03:00 | 0 | 0 | 0 | 9.73 | 12.63 | 0
1613 | 2008-03-09 04:00 | 0 | 0 | 0 | 8.61 | 12.63 | 0
1614 | 2008-03-09 05:00 | 0 | 0 | 0 | 8.17 | 12.63 | 0
1615 | 2008-03-09 06:00 | 44 | 309 | 17 | 7.73 | 12.5 | 0 | 3.8037 | 97.7527 | 83.2805 | 0 | 44 | 36.3129 | 20.0209 | 0.41225 | 0 | 18.7363 | 0.0021518 | 0 | 18.0429 | 0.0016214 | 17.5031 | 17.5024 | 39305.8 | 7.9774 | 26776.2 | 29187.9 | 28485.3 | 0 | 0 | 28477.2 | 628.171 | 0 | 0 | 0 | 728.751 | 27748.4 | 660 | 26740.2 | 26205.4004
1616 | 2008-03-09 07:00 | 250 | 715 | 54 | 7.29 | 12.5 | 0 | 15.8801 | 106.737 | 68.5894 | 0 | 250 | 261.487 | 65.3649 | 2.3423 | 215.126 | 61.1709 | 0.012226 | 196.416 | 58.907 | 0.0092126 | 247.673 | 247.678 | 556189 | 10.7914 | 516759 | 548845 | 487067 | 0 | 0 | 485242 | 741.235 | 0 | 0 | 0 | 0 | 485242 | 741.235 | 476044 | 466523.5938
1617 | 2008-03-09 08:00 | 461 | 852 | 70 | 8.78 | 12.5 | 0 | 27.3514 | 117.098 | 54.0281 | 0 | 461 | 499.881 | 86.3218 | 4.3192 | 494.832 | 80.7832 | 0.022545 | 477.452 | 77.7935 | 0.016988 | 538.605 | 538.582 | 1209520 | 16.3938 | 1176370 | 1219180 | 1163610 | 0 | 0 | 1153990 | 742.149 | 0 | 0 | 0 | 0 | 1153990 | 742.149 | 1133900 | 1111222
1618 | 2008-03-09 09:00 | 659 | 944 | 83 | 10.27 | 8.02 | 0 | 37.6723 | 129.993 | 39.7474 | 0 | 659 | 724.657 | 98.4675 | 6.1743 | 724.657 | 92.1496 | 0.032228 | 713.765 | 88.7392 | 0.024284 | 778.453 | 778.45 | 1748210 | 24.7368 | 1736720 | 1738350 | 1687760 | 0 | 0 | 1667600 | 740.118 | 0 | 0 | 0 | 0 | 1667600 | 740.118 | 1635860 | 1603141.5
1619 | 2008-03-09 10:00 | 787 | 973 | 90 | 11.76 | 8.02 | 0 | 45.9211 | 146.816 | 26.2175 | 0 | 787 | 870.42 | 106.466 | 7.3736 | 870.42 | 99.6346 | 0.038488 | 865.43 | 95.9472 | 0.029001 | 932.564 | 932.563 | 2094300 | 29.0909 | 2100380 | 2064460 | 2011890 | 0 | 0 | 1982350 | 726.936 | 0 | 0 | 0 | 0 | 1982350 | 726.936 | 1940960 | 1902137.375
1620 | 2008-03-09 11:00 | 860 | 991 | 95 | 12.83 | 8.02 | 0 | 50.7018 | 168.236 | 15.5491 | 0 | 860 | 952.371 | 112.065 | 8.0575 | 952.371 | 104.875 | 0.042058 | 950.562 | 100.993 | 0.031691 | 1020.04 | 1020.03 | 2290740 | 31.7865 | 2307440 | 2242440 | 2182570 | 0 | 0 | 2147440 | 721.527 | 100721 | 0 | 0 | 0 | 2045080 | 759 | 1999430 | 1959439.125
1621 | 2008-03-09 12:00 | 836 | 958 | 97 | 13.89 | 5.22 | 0 | 50.6966 | 191.964 | 15.5949 | 0 | 836 | 919.866 | 114.293 | 7.8327 | 919.866 | 106.96 | 0.040884 | 918.108 | 103.001 | 0.030807 | 990.506 | 990.5 | 2224410 | 35.9047 | 2237490 | 2135830 | 2081970 | 0 | 0 | 2048630 | 706.834 | 5521 | 0 | 0 | 0 | 2042860 | 715.093 | 1999330 | 1959342.5
1622 | 2008-03-09 13:00 | 791 | 977 | 91 | 14.96 | 5.22 | 0 | 45.9079 | 213.377 | 26.2991 | 0 | 791 | 873.748 | 107.561 | 7.4111 | 873.748 | 100.66 | 0.038683 | 868.704 | 96.9346 | 0.029149 | 936.698 | 936.696 | 2103580 | 35.7789 | 2110160 | 2015050 | 1962390 | 0 | 0 | 1932650 | 706.415 | 0 | 0 | 0 | 0 | 1932650 | 706.415 | 1893060 | 1855198.25
1623 | 2008-03-09 14:00 | 646 | 930 | 79 | 15.54 | 5.22 | 0 | 37.6559 | 230.195 | 39.8369 | 0 | 646 | 712.67 | 93.9361 | 6.0525 | 712.67 | 87.909 | 0.031592 | 701.898 | 84.6555 | 0.023805 | 762.98 | 762.975 | 1713440 | 32.4978 | 1700300 | 1646270 | 1601920 | 0 | 0 | 1582300 | 712.044 | 0 | 0 | 0 | 0 | 1582300 | 712.044 | 1553960 | 1522880.375
1624 | 2008-03-09 15:00 | 475 | 878 | 72 | 16.12 | 5.71 | 0 | 27.3365 | 243.092 | 54.12 | 0 | 475 | 514.343 | 88.4817 | 4.4504 | 514.343 | 82.8045 | 0.02323 | 496.181 | 79.74 | 0.017504 | 558.66 | 558.657 | 1254600 | 28.1491 | 1222560 | 1205830 | 1174890 | 0 | 0 | 1164420 | 717.183 | 0 | 0 | 0 | 0 | 1164420 | 717.183 | 1145350 | 1122441.375
1625 | 2008-03-09 16:00 | 246 | 707 | 52 | 16.71 | 5.71 | 0 | 15.8707 | 253.464 | 68.6819 | 0 | 246 | 257.903 | 63.1362 | 2.3048 | 257.903 | 59.0853 | 0.01203 | 235.327 | 56.8986 | 0.0090652 | 283.468 | 283.466 | 636594 | 22.8136 | 593859 | 599728 | 583914 | 0 | 0 | 581264 | 711.761 | 0 | 0 | 0 | 0 | 581264 | 711.761 | 572078 | 560636.75
1626 | 2008-03-09 17:00 | 34 | 294 | 7 | 16.47 | 5.71 | 0 | 3.8042 | 262.467 | 83.3726 | 0 | 34 | 35.8176 | 8.7196 | 0.31855 | 33.4668 | 8.1601 | 0.0016627 | 20.6414 | 7.8581 | 0.0012529 | 27.6457 | 27.6455 | 62084 | 17.0653 | 45904.6 | 47869.1 | 45617.3 | 0 | 0 | 45595.8 | 623.367 | 0 | 0 | 0 | 1953.02 | 43642.8 | 660 | 42098.7 | 41256.7539
1627 | 2008-03-09 18:00 | 0 | 0 | 0 | 16.24 | 7.77 | 0
1628 | 2008-03-09 19:00 | 0 | 0 | 0 | 16.01 | 7.77 | 0
1629 | 2008-03-09 20:00 | 0 | 0 | 0 | 15.28 | 7.77 | 0
1630 | 2008-03-09 21:00 | 0 | 0 | 0 | 14.55 | 8.91 | 0
1631 | 2008-03-09 22:00 | 0 | 0 | 0 | 13.81 | 8.91 | 0
1632 | 2008-03-09 23:00 | 0 | 0 | 0 | 13.25 | 8.91 | 0
1633 | 2008-03-10 | 0 | 0 | 0 | 12.68 | 7.93 | 0
1634 | 2008-03-10 01:00 | 0 | 0 | 0 | 12.12 | 7.93 | 0
1635 | 2008-03-10 02:00 | 0 | 0 | 0 | 11.45 | 7.93 | 0
1636 | 2008-03-10 03:00 | 0 | 0 | 0 | 10.78 | 2.28 | 0
1637 | 2008-03-10 04:00 | 0 | 0 | 0 | 10.11 | 2.28 | 0
1638 | 2008-03-10 05:00 | 0 | 0 | 0 | 9.66 | 2.28 | 0
1639 | 2008-03-10 06:00 | 48 | 331 | 18 | 9.22 | 1.99 | 0 | 4.0818 | 97.468 | 83.1482 | 0 | 48 | 41.1383 | 21.3229 | 0.44972 | 0 | 19.9547 | 0.0023474 | 0 | 19.2162 | 0.0017688 | 18.6415 | 18.6403 | 41861.3 | 9.7325 | 28877.6 | 31225.1 | 30469.9 | 0 | 0 | 30460.5 | 625.222 | 0 | 0 | 0 | 956.664 | 29503.8 | 660 | 28434.9 | 27866.2031
1640 | 2008-03-10 07:00 | 264 | 712 | 65 | 8.77 | 1.99 | 0 | 16.1709 | 106.455 | 68.4455 | 0 | 264 | 262.509 | 77.4815 | 2.4735 | 218.199 | 72.5101 | 0.012911 | 199.413 | 69.8266 | 0.0097285 | 261.171 | 261.116 | 586374 | 15.9496 | 546413 | 566748 | 507513 | 0 | 0 | 505443 | 720.626 | 0 | 0 | 0 | 456.26 | 504986 | 722.152 | 496113 | 486190.9688
1641 | 2008-03-10 08:00 | 453 | 787 | 88 | 10.4 | 1.99 | 0 | 27.6645 | 116.822 | 53.8653 | 0 | 453 | 463.577 | 105.862 | 4.2443 | 459.824 | 99.0697 | 0.022154 | 443.826 | 95.4032 | 0.016693 | 523.069 | 523.038 | 1174620 | 24.7814 | 1140270 | 1140790 | 1094570 | 0 | 0 | 1085420 | 715.229 | 0 | 0 | 0 | 0 | 1085420 | 715.229 | 1068030 | 1046672.9375
1642 | 2008-03-10 09:00 | 638 | 897 | 86 | 12.02 | 3.04 | 0 | 38.0166 | 129.741 | 39.5518 | 0 | 638 | 691.063 | 101.625 | 5.9776 | 691.063 | 95.1042 | 0.031201 | 680.803 | 91.5844 | 0.023511 | 749.239 | 749.235 | 1682590 | 31.231 | 1668000 | 1623850 | 1580880 | 0 | 0 | 1561940 | 715.097 | 0 | 0 | 0 | 0 | 1561940 | 715.097 | 1534100 | 1503417.875
1643 | 2008-03-10 10:00 | 748 | 849 | 136 | 13.65 | 3.04 | 0 | 46.3002 | 146.642 | 25.9588 | 0 | 748 | 761.104 | 164.227 | 7.0082 | 761.104 | 153.69 | 0.03658 | 756.834 | 148.002 | 0.027564 | 877.718 | 877.712 | 1971110 | 36.1553 | 1970740 | 1878290 | 1830070 | 0 | 0 | 1803930 | 703.317 | 0 | 0 | 0 | 0 | 1803930 | 703.317 | 1768820 | 1733444.125
1644 | 2008-03-10 11:00 | 833 | 941 | 103 | 15.08 | 3.04 | 0 | 51.0995 | 168.232 | 15.1738 | 0 | 833 | 905.314 | 120.757 | 7.8046 | 905.314 | 113.009 | 0.040737 | 903.679 | 108.827 | 0.030696 | 982.161 | 982.151 | 2205660 | 40.2632 | 2217720 | 2076140 | 2022980 | 0 | 0 | 1990280 | 693.397 | 0 | 0 | 0 | 0 | 1990280 | 693.397 | 1948650 | 1909673.125
1645 | 2008-03-10 12:00 | 844 | 963 | 97 | 16.52 | 0.85 | 0 | 51.072 | 192.172 | 15.2845 | 0 | 844 | 926.269 | 114.079 | 7.9076 | 926.269 | 106.76 | 0.041275 | 924.571 | 102.809 | 0.031102 | 996.588 | 996.586 | 2238080 | 46.1011 | 2251900 | 2052430 | 2002510 | 0 | 0 | 1968730 | 674.433 | 0 | 0 | 0 | 0 | 1968730 | 674.433 | 1927950 | 1889394.875
1646 | 2008-03-10 13:00 | 795 | 978 | 90 | 17.96 | 0.85 | 0 | 46.2276 | 213.718 | 26.1528 | 0 | 795 | 876.373 | 106.24 | 7.4485 | 876.373 | 99.4232 | 0.038879 | 871.376 | 95.7436 | 0.029296 | 938.134 | 938.127 | 2106800 | 45.8059 | 2113540 | 1928220 | 1881690 | 0 | 0 | 1851630 | 673.203 | 0 | 0 | 0 | 0 | 1851630 | 673.203 | 1815310 | 1779007.125
1647 | 2008-03-10 14:00 | 652 | 934 | 79 | 18.51 | 0.85 | 0 | 37.9176 | 230.575 | 39.764 | 0 | 652 | 716.741 | 93.7508 | 6.1087 | 716.741 | 87.7355 | 0.031885 | 705.957 | 84.4885 | 0.024026 | 766.755 | 766.752 | 1721930 | 41.2691 | 1709180 | 1590700 | 1553410 | 0 | 0 | 1533380 | 682.876 | 0 | 0 | 0 | 0 | 1533380 | 682.876 | 1507520 | 1477365.75
1648 | 2008-03-10 15:00 | 474 | 875 | 69 | 19.07 | 1.14 | 0 | 27.5538 | 243.468 | 54.083 | 0 | 474 | 513.592 | 82.0342 | 4.441 | 513.592 | 76.7707 | 0.023181 | 495.496 | 73.9295 | 0.017467 | 552.36 | 552.354 | 1240450 | 35.1481 | 1207940 | 1154580 | 1126500 | 0 | 0 | 1116220 | 693.932 | 0 | 0 | 0 | 0 | 1116220 | 693.932 | 1099260 | 1077272.625
1649 | 2008-03-10 16:00 | 243 | 668 | 58 | 19.62 | 1.14 | 0 | 16.0588 | 253.829 | 68.6651 | 0 | 243 | 243.313 | 69.2639 | 2.2767 | 243.313 | 64.8198 | 0.011884 | 222.04 | 62.4209 | 0.0089546 | 275.936 | 275.933 | 619677 | 27.6519 | 577015 | 569942 | 555370 | 0 | 0 | 552841 | 692.83 | 0 | 0 | 0 | 0 | 552841 | 692.83 | 544510 | 533619.3125
1650 | 2008-03-10 17:00 | 34 | 283 | 8 | 19.11 | 1.14 | 0 | 3.9764 | 262.827 | 83.3678 | 0 | 34 | 34.5158 | 9.9285 | 0.31855 | 34.3357 | 9.2915 | 0.0016627 | 21.1879 | 8.9476 | 0.0012529 | 29.2327 | 29.2323 | 65647.5 | 19.9609 | 48927.9 | 50262.7 | 48507 | 0 | 0 | 48482.2 | 615.415 | 0 | 0 | 0 | 3384.73 | 45097.4 | 660 | 43505.9 | 42635.75
1651 | 2008-03-10 18:00 | 0 | 0 | 0 | 18.61 | 2.16 | 0
1652 | 2008-03-10 19:00 | 0 | 0 | 0 | 18.1 | 2.16 | 0
1653 | 2008-03-10 20:00 | 0 | 0 | 0 | 17.63 | 2.16 | 0
1654 | 2008-03-10 21:00 | 0 | 0 | 0 | 17.15 | 3.22 | 0
1655 | 2008-03-10 22:00 | 0 | 0 | 0 | 16.68 | 3.22 | 0
1656 | 2008-03-10 23:00 | 0 | 0 | 0 | 16.05 | 3.22 | 0
1657 | 2008-03-11 | 0 | 0 | 0 | 15.41 | 3.38 | 0
1658 | 2008-03-11 01:00 | 0 | 0 | 0 | 14.78 | 3.38 | 0
1659 | 2008-03-11 02:00 | 0 | 0 | 0 | 14.24 | 3.38 | 0
1660 | 2008-03-11 03:00 | 0 | 0 | 0 | 13.71 | 3.67 | 0
1661 | 2008-03-11 04:00 | 0 | 0 | 0 | 13.17 | 3.67 | 0
1662 | 2008-03-11 05:00 | 0 | 0 | 0 | 12.71 | 3.67 | 0
1663 | 2008-03-11 06:00 | 55 | 239 | 33 | 12.25 | 4.04 | 0 | 4.3613 | 97.1833 | 83.0147 | 0 | 55 | 30.7531 | 36.1376 | 0.51531 | 0 | 33.8189 | 0.0026897 | 0 | 32.5673 | 0.0020268 | 31.5922 | 31.5913 | 70945.8 | 13.0083 | 53487.8 | 56922.7 | 55452.5 | 0 | 0 | 55423 | 643.176 | 0 | 0 | 0 | 371.058 | 55051.9 | 660 | 53141.8 | 52079.0078
1664 | 2008-03-11 07:00 | 178 | 215 | 117 | 11.79 | 4.04 | 0 | 16.463 | 106.172 | 68.3011 | 0 | 178 | 79.5831 | 123.86 | 1.6677 | 66.7596 | 115.913 | 0.0087049 | 61.0694 | 111.623 | 0.0065594 | 167.518 | 167.506 | 376167 | 15.811 | 338083 | 352634 | 330801 | 0 | 0 | 329950 | 713.292 | 0 | 0 | 0 | 0 | 329950 | 713.292 | 322655 | 316201.8125
1665 | 2008-03-11 08:00 | 370 | 372 | 196 | 13.51 | 4.04 | 0 | 27.9785 | 116.545 | 53.7026 | 0 | 370 | 219.559 | 209.252 | 3.4666 | 218.222 | 195.826 | 0.018094 | 210.701 | 188.579 | 0.013635 | 387.315 | 387.299 | 869772 | 22.8071 | 828388 | 836260 | 804925 | 0 | 0 | 799994 | 718.486 | 0 | 0 | 0 | 0 | 799994 | 718.486 | 787255 | 771509.625
1666 | 2008-03-11 09:00 | 462 | 274 | 292 | 15.24 | 2.02 | 0 | 38.3619 | 129.488 | 39.3572 | 0 | 462 | 211.794 | 315.095 | 4.3286 | 211.794 | 294.878 | 0.022594 | 208.688 | 283.965 | 0.017025 | 477.889 | 477.866 | 1073170 | 28.353 | 1035760 | 1020430 | 993584 | 0 | 0 | 985934 | 710.385 | 0 | 0 | 0 | 0 | 985934 | 710.385 | 970633 | 951219.9375
1667 | 2008-03-11 10:00 | 740 | 745 | 199 | 16.96 | 2.02 | 0 | 46.6803 | 146.468 | 25.7017 | 0 | 740 | 670.036 | 236.506 | 6.9332 | 670.036 | 221.331 | 0.036189 | 666.358 | 213.14 | 0.027269 | 853.139 | 853.143 | 1915940 | 40.3709 | 1912740 | 1788500 | 1741610 | 0 | 0 | 1716890 | 688.289 | 0 | 0 | 0 | 0 | 1716890 | 688.289 | 1685010 | 1651306.25
1668 | 2008-03-11 11:00 | 851 | 917 | 135 | 18.21 | 2.02 | 0 | 51.4981 | 168.23 | 14.7983 | 0 | 851 | 884.567 | 164.351 | 7.9732 | 884.567 | 153.806 | 0.041617 | 883.049 | 148.114 | 0.03136 | 1000.26 | 1000.25 | 2246300 | 45.6576 | 2260560 | 2064730 | 2019120 | 0 | 0 | 1984630 | 673.601 | 0 | 0 | 0 | 0 | 1984630 | 673.601 | 1943230 | 1904368.75
1669 | 2008-03-11 12:00 | 869 | 992 | 95 | 19.46 | 2.4 | 0 | 51.4474 | 192.386 | 14.9781 | 0 | 869 | 956.097 | 111.636 | 8.1418 | 956.097 | 104.473 | 0.042498 | 954.416 | 100.607 | 0.032023 | 1023.4 | 1023.39 | 2298290 | 46.84 | 2315400 | 2103470 | 2054050 | 0 | 0 | 2018090 | 670.379 | 0 | 0 | 0 | 0 | 2018090 | 670.379 | 1975360 | 1935850.875
1670 | 2008-03-11 13:00 | 782 | 956 | 89 | 20.71 | 2.4 | 0 | 46.5463 | 214.066 | 26.0122 | 0 | 782 | 857.934 | 104.92 | 7.3267 | 857.934 | 98.1885 | 0.038243 | 853.098 | 94.5546 | 0.028817 | 919.251 | 919.246 | 2064390 | 45.3036 | 2068890 | 1891740 | 1844440 | 0 | 0 | 1815720 | 674.966 | 0 | 0 | 0 | 0 | 1815720 | 674.966 | 1780690 | 1745071.625
1671 | 2008-03-11 14:00 | 666 | 946 | 82 | 21.2 | 2.4 | 0 | 38.1777 | 230.958 | 39.6953 | 0 | 666 | 726.998 | 96.9243 | 6.2399 | 726.998 | 90.7054 | 0.03257 | 716.107 | 87.3485 | 0.024542 | 779.376 | 779.37 | 1750270 | 42.0513 | 1738870 | 1612640 | 1573190 | 0 | 0 | 1552490 | 680.225 | 0 | 0 | 0 | 0 | 1552490 | 680.225 | 1526140 | 1495614
1672 | 2008-03-11 15:00 | 467 | 862 | 66 | 21.69 | 1.6 | 0 | 27.7696 | 243.846 | 54.0491 | 0 | 467 | 505.291 | 78.5039 | 4.3754 | 505.291 | 73.4669 | 0.022838 | 487.522 | 70.748 | 0.017209 | 541.539 | 541.535 | 1216150 | 36.9737 | 1182840 | 1121030 | 1094540 | 0 | 0 | 1084610 | 685.933 | 0 | 0 | 0 | 0 | 1084610 | 685.933 | 1068670 | 1047298.625
1673 | 2008-03-11 16:00 | 251 | 711 | 52 | 22.18 | 1.6 | 0 | 16.2458 | 254.195 | 68.6506 | 0 | 251 | 258.963 | 62.7595 | 2.3517 | 258.963 | 58.7328 | 0.012275 | 236.344 | 56.5591 | 0.0092494 | 284.125 | 284.124 | 638070 | 30.1988 | 595331 | 581090 | 566679 | 0 | 0 | 563981 | 684.161 | 0 | 0 | 0 | 0 | 563981 | 684.161 | 555805 | 544689.3125
1674 | 2008-03-11 17:00 | 36 | 306 | 8 | 21.9 | 1.6 | 0 | 4.1478 | 263.188 | 83.3645 | 0 | 36 | 37.1891 | 9.9425 | 0.33729 | 37.092 | 9.3046 | 0.0017606 | 22.8967 | 8.9603 | 0.0013266 | 30.9025 | 30.9023 | 69398.2 | 22.7722 | 52149.3 | 52778.8 | 51393.2 | 0 | 0 | 51364.9 | 608.541 | 0 | 0 | 0 | 5204.93 | 46159.9 | 660 | 44533.7 | 43643.0352
1675 | 2008-03-11 18:00 | 0 | 0 | 0 | 21.62 | 0.89 | 0
1676 | 2008-03-11 19:00 | 0 | 0 | 0 | 21.33 | 0.89 | 0
1677 | 2008-03-11 20:00 | 0 | 0 | 0 | 20.57 | 0.89 | 0
1678 | 2008-03-11 21:00 | 0 | 0 | 0 | 19.8 | 3.62 | 0
1679 | 2008-03-11 22:00 | 0 | 0 | 0 | 19.03 | 3.62 | 0
1680 | 2008-03-11 23:00 | 0 | 0 | 0 | 18.03 | 3.62 | 0
1681 | 2008-03-12 | 0 | 0 | 0 | 17.04 | 3.05 | 0
1682 | 2008-03-12 01:00 | 0 | 0 | 0 | 16.04 | 3.05 | 0
1683 | 2008-03-12 02:00 | 0 | 0 | 0 | 15.03 | 3.05 | 0
1684 | 2008-03-12 03:00 | 0 | 0 | 0 | 14.02 | 3.71 | 0
1685 | 2008-03-12 04:00 | 0 | 0 | 0 | 13.02 | 3.71 | 0
1686 | 2008-03-12 05:00 | 0 | 0 | 0 | 12.45 | 3.71 | 0
1687 | 2008-03-12 06:00 | 57 | 362 | 23 | 11.89 | 3.45 | 0 | 4.6422 | 96.8986 | 82.8801 | 0 | 57 | 48.4387 | 26.9085 | 0.53405 | 0.028093 | 25.182 | 0.0027875 | 0.018165 | 24.25 | 0.0021005 | 23.5422 | 23.5402 | 52865.4 | 12.4775 | 38055.6 | 40617.7 | 39606.9 | 0 | 0 | 39591.3 | 630.57 | 0 | 0 | 0 | 1026.7 | 38564.6 | 660 | 37188.4 | 36444.6016
1688 | 2008-03-12 07:00 | 266 | 545 | 109 | 11.33 | 3.45 | 0 | 16.756 | 105.889 | 68.1562 | 0 | 266 | 202.625 | 119.802 | 2.4922 | 171.606 | 112.115 | 0.013008 | 157.126 | 107.966 | 0.0098022 | 257.148 | 257.05 | 577254 | 17.7447 | 536180 | 552849 | 505055 | 0 | 0 | 503048 | 716.709 | 0 | 0 | 0 | 0 | 503048 | 716.709 | 494430 | 484541.875
1689 | 2008-03-12 08:00 | 246 | 79 | 209 | 13.54 | 3.45 | 0 | 28.2934 | 116.266 | 53.5402 | 0 | 246 | 46.3886 | 217.528 | 2.3048 | 46.1891 | 203.571 | 0.01203 | 44.6123 | 196.037 | 0.0090652 | 233.439 | 233.435 | 524237 | 19.3654 | 482493 | 495004 | 479392 | 0 | 0 | 477625 | 715.591 | 0 | 0 | 0 | 0 | 477625 | 715.591 | 469390 | 460002.5938
1690 | 2008-03-12 09:00 | 157 | 6 | 153 | 15.75 | 1.9 | 0 | 38.708 | 129.233 | 39.1638 | 0 | 157 | 4.9594 | 143.273 | 1.471 | 4.9594 | 134.08 | 0.007678 | 4.8876 | 129.118 | 0.0057855 | 129.991 | 129.984 | 291911 | 19.3456 | 256807 | 263877 | 256487 | 0 | 0 | 255942 | 690.361 | 0 | 0 | 0 | 0 | 255942 | 690.361 | 249494 | 244504.4844
1691 | 2008-03-12 10:00 | 589 | 344 | 338 | 17.97 | 1.9 | 0 | 47.0612 | 146.292 | 25.4467 | 0 | 589 | 309.596 | 367.771 | 5.5185 | 309.596 | 344.174 | 0.028805 | 307.932 | 331.437 | 0.021705 | 620.209 | 620.187 | 1392790 | 35.1255 | 1365770 | 1306080 | 1271500 | 0 | 0 | 1258560 | 697.085 | 0 | 0 | 0 | 0 | 1258560 | 697.085 | 1238520 | 1213744.75
1692 | 2008-03-12 11:00 | 829 | 797 | 204 | 19.62 | 1.9 | 0 | 51.8976 | 168.23 | 14.4229 | 0 | 829 | 769.215 | 244.652 | 7.7671 | 769.215 | 228.955 | 0.040542 | 767.963 | 220.481 | 0.030549 | 958.821 | 958.808 | 2153240 | 46.1423 | 2162470 | 1970090 | 1922790 | 0 | 0 | 1891350 | 672.597 | 0 | 0 | 0 | 0 | 1891350 | 672.597 | 1853550 | 1816483.75
1693 | 2008-03-12 12:00 | 859 | 923 | 135 | 21.27 | 5.94 | 0 | 51.8229 | 192.606 | 14.6762 | 0 | 859 | 890.948 | 155.002 | 8.0482 | 890.948 | 145.056 | 0.042009 | 889.446 | 139.688 | 0.031654 | 998.29 | 998.288 | 2241900 | 42.4489 | 2255930 | 2091340 | 2039130 | 0 | 0 | 2005380 | 687.328 | 0 | 0 | 0 | 0 | 2005380 | 687.328 | 1963180 | 1923911.875
1694 | 2008-03-12 13:00 | 789 | 961 | 89 | 22.92 | 5.94 | 0 | 46.8639 | 214.419 | 25.8774 | 0 | 789 | 863.073 | 104.721 | 7.3923 | 863.073 | 98.0022 | 0.038585 | 858.264 | 94.3752 | 0.029075 | 924.088 | 924.081 | 2075250 | 42.5245 | 2080330 | 1927070 | 1879540 | 0 | 0 | 1850480 | 684.19 | 0 | 0 | 0 | 0 | 1850480 | 684.19 | 1814050 | 1777770.5
1695 | 2008-03-12 14:00 | 671 | 946 | 84 | 23.04 | 5.94 | 0 | 38.4363 | 231.346 | 39.6309 | 0 | 671 | 727.248 | 98.9615 | 6.2867 | 727.248 | 92.612 | 0.032815 | 716.397 | 89.1845 | 0.024727 | 781.438 | 781.435 | 1754900 | 39.6183 | 1743730 | 1635520 | 1596890 | 0 | 0 | 1576030 | 687.686 | 0 | 0 | 0 | 0 | 1576030 | 687.686 | 1548690 | 1517719.875
1696 | 2008-03-12 15:00 | 487 | 882 | 73 | 23.16 | 6.18 | 0 | 27.9838 | 244.228 | 54.0184 | 0 | 487 | 518.381 | 86.1043 | 4.5628 | 518.381 | 80.5797 | 0.023816 | 500.185 | 77.5975 | 0.017946 | 560.466 | 560.461 | 1258650 | 34.8682 | 1226750 | 1174180 | 1145620 | 0 | 0 | 1135040 | 695.333 | 0 | 0 | 0 | 0 | 1135040 | 695.333 | 1117630 | 1095276
1697 | 2008-03-12 16:00 | 253 | 698 | 55 | 23.28 | 6.18 | 0 | 16.4314 | 254.564 | 68.6382 | 0 | 253 | 254.969 | 65.757 | 2.3704 | 254.969 | 61.5379 | 0.012373 | 232.719 | 59.2604 | 0.0093231 | 283.229 | 283.226 | 636056 | 29.1967 | 593325 | 581877 | 567148 | 0 | 0 | 564474 | 687.98 | 0 | 0 | 0 | 0 | 564474 | 687.98 | 556176 | 545052.25
1698 | 2008-03-12 17:00 | 36 | 305 | 8 | 22.37 | 6.18 | 0 | 4.3183 | 263.55 | 83.3627 | 0 | 36 | 37.1992 | 9.9551 | 0.33729 | 37.1021 | 9.3164 | 0.0017606 | 22.9072 | 8.9716 | 0.0013266 | 30.9237 | 30.9239 | 69446.9 | 23.016 | 52191.3 | 52752.8 | 51358.5 | 0 | 0 | 51330.2 | 608.097 | 0 | 0 | 0 | 5405.21 | 45925 | 660 | 44306.4 | 43420.2734
1699 | 2008-03-12 18:00 | 0 | 0 | 0 | 21.46 | 9 | 0
1700 | 2008-03-12 19:00 | 0 | 0 | 0 | 20.55 | 9 | 0
1701 | 2008-03-12 20:00 | 0 | 0 | 0 | 19.54 | 9 | 0
1702 | 2008-03-12 21:00 | 0 | 0 | 0 | 18.52 | 13.78 | 0
1703 | 2008-03-12 22:00 | 0 | 0 | 0 | 17.51 | 13.78 | 0
1704 | 2008-03-12 23:00 | 0 | 0 | 0 | 16.57 | 13.78 | 0
1705 | 2008-03-13 | 0 | 0 | 0 | 15.62 | 8.03 | 0
1706 | 2008-03-13 01:00 | 0 | 0 | 0 | 14.68 | 8.03 | 0
1707 | 2008-03-13 02:00 | 0 | 0 | 0 | 14.06 | 8.03 | 0
1708 | 2008-03-13 03:00 | 0 | 0 | 0 | 13.43 | 11.71 | 0
1709 | 2008-03-13 04:00 | 0 | 0 | 0 | 12.81 | 11.71 | 0
1710 | 2008-03-13 05:00 | 0 | 0 | 0 | 12.73 | 11.71 | 0
1711 | 2008-03-13 06:00 | 41 | 107 | 31 | 12.66 | 13.36 | 0 | 4.9243 | 96.614 | 82.7445 | 0 | 41 | 14.5165 | 32.9229 | 0.38414 | 0.23152 | 30.8105 | 0.0020051 | 0.15144 | 29.6702 | 0.0015109 | 28.9285 | 28.9254 | 64960.3 | 13.0488 | 48341.2 | 51443 | 49965.3 | 0 | 0 | 49941.1 | 638.844 | 0 | 0 | 0 | 575.927 | 49365.1 | 660 | 47635.5 | 46682.7969
1712 | 2008-03-13 07:00 | 255 | 552 | 93 | 12.58 | 13.36 | 0 | 17.05 | 105.606 | 68.011 | 0 | 255 | 206.877 | 105.26 | 2.3891 | 176.782 | 98.5063 | 0.012471 | 162.014 | 94.8607 | 0.0093968 | 249.177 | 249.145 | 559501 | 15.9288 | 518690 | 539550 | 492244 | 0 | 0 | 490345 | 720.253 | 0 | 0 | 0 | 0 | 490345 | 720.253 | 481718 | 472083.75
1713 | 2008-03-13 08:00 | 497 | 840 | 95 | 14.12 | 13.36 | 0 | 28.6089 | 115.986 | 53.3782 | 0 | 497 | 500.816 | 112.724 | 4.6565 | 499.267 | 105.492 | 0.024305 | 482.383 | 101.587 | 0.018315 | 566.469 | 566.447 | 1272090 | 21.7337 | 1240740 | 1257860 | 1217230 | 0 | 0 | 1206580 | 736.448 | 0 | 0 | 0 | 0 | 1206580 | 736.448 | 1185730 | 1162018.875
1714 | 2008-03-13 09:00 | 666 | 925 | 84 | 15.66 | 11.63 | 0 | 39.0547 | 128.976 | 38.9717 | 0 | 666 | 718.151 | 98.823 | 6.2399 | 718.151 | 92.4823 | 0.03257 | 707.872 | 89.0596 | 0.024542 | 773.048 | 773.044 | 1736060 | 27.1689 | 1723980 | 1708110 | 1662220 | 0 | 0 | 1642130 | 730.167 | 0 | 0 | 0 | 0 | 1642130 | 730.167 | 1611460 | 1579233.125
1715 | 2008-03-13 10:00 | 809 | 976 | 92 | 17.21 | 11.63 | 0 | 47.443 | 146.115 | 25.1938 | 0 | 809 | 880.79 | 107.89 | 7.5797 | 880.79 | 100.968 | 0.039564 | 876.161 | 97.2313 | 0.029812 | 944.219 | 944.216 | 2120470 | 31.2672 | 2127940 | 2072390 | 2017760 | 0 | 0 | 1987640 | 721.864 | 0 | 0 | 0 | 0 | 1987640 | 721.864 | 1946070 | 1907145.625
1716 | 2008-03-13 11:00 | 856 | 959 | 99 | 18.31 | 11.63 | 0 | 52.2978 | 168.232 | 14.0477 | 0 | 856 | 928.161 | 115.663 | 8.02 | 928.161 | 108.241 | 0.041862 | 926.731 | 104.235 | 0.031544 | 1000.07 | 1000.06 | 2245880 | 33.1986 | 2260120 | 2183200 | 2124050 | 0 | 0 | 2090240 | 715.799 | 44998.2 | 0 | 0 | 0 | 2043740 | 742.632 | 1999990 | 1959989.75
1717 | 2008-03-13 12:00 | 867 | 926 | 137 | 19.42 | 8.45 | 0 | 52.1983 | 192.832 | 14.3792 | 0 | 867 | 894.949 | 165.956 | 8.1231 | 894.949 | 155.308 | 0.0424 | 893.502 | 149.56 | 0.031949 | 1011.8 | 1011.8 | 2272250 | 37.723 | 2287930 | 2166790 | 2108660 | 0 | 0 | 2074120 | 703.126 | 29377.4 | 0 | 0 | 0 | 2043500 | 723.688 | 1999980 | 1959977.375
1718 | 2008-03-13 13:00 | 750 | 794 | 169 | 20.53 | 8.45 | 0 | 47.1802 | 214.779 | 25.7485 | 0 | 750 | 713.45 | 203.555 | 7.0269 | 713.45 | 190.495 | 0.036678 | 709.518 | 183.445 | 0.027638 | 866.2 | 866.198 | 1945260 | 36.1992 | 1943560 | 1852090 | 1807090 | 0 | 0 | 1781580 | 702.906 | 0 | 0 | 0 | 0 | 1781580 | 702.906 | 1747220 | 1712279.125
1719 | 2008-03-13 14:00 | 675 | 898 | 114 | 20.84 | 8.45 | 0 | 38.6932 | 231.739 | 39.5707 | 0 | 675 | 691.739 | 136.717 | 6.3242 | 691.739 | 127.945 | 0.03301 | 681.457 | 123.21 | 0.024874 | 780.551 | 780.546 | 1752910 | 34.9598 | 1741640 | 1668240 | 1625130 | 0 | 0 | 1604560 | 704.677 | 0 | 0 | 0 | 0 | 1604560 | 704.677 | 1575790 | 1544271.75
1720 | 2008-03-13 15:00 | 491 | 884 | 73 | 21.14 | 7.46 | 0 | 28.1964 | 244.612 | 53.9906 | 0 | 491 | 520.11 | 85.918 | 4.6003 | 520.11 | 80.4054 | 0.024012 | 501.882 | 77.4296 | 0.018093 | 561.95 | 561.946 | 1261990 | 31.9589 | 1230190 | 1193090 | 1163050 | 0 | 0 | 1152410 | 704.111 | 0 | 0 | 0 | 0 | 1152410 | 704.111 | 1134220 | 1111539.375
1721 | 2008-03-13 16:00 | 261 | 725 | 53 | 21.45 | 7.46 | 0 | 16.6158 | 254.935 | 68.628 | 0 | 261 | 265.077 | 63.446 | 2.4454 | 265.077 | 59.3752 | 0.012764 | 241.962 | 57.1777 | 0.0096179 | 290.174 | 290.173 | 651656 | 27.0366 | 608880 | 603187 | 587608 | 0 | 0 | 584804 | 696.486 | 0 | 0 | 0 | 0 | 584804 | 696.486 | 576049 | 564528.1875
1722 | 2008-03-13 17:00 | 38 | 322 | 8 | 20.31 | 7.46 | 0 | 4.488 | 263.914 | 83.3623 | 0 | 38 | 39.8587 | 9.9663 | 0.35603 | 39.8587 | 9.3269 | 0.0018584 | 24.6103 | 8.9817 | 0.0014003 | 32.5856 | 32.585 | 73177.5 | 20.9373 | 55412.5 | 56629.1 | 55321.2 | 0 | 0 | 55289.3 | 617.451 | 0 | 0 | 0 | 3544.26 | 51745.1 | 660 | 49939.4 | 48940.6406
1723 | 2008-03-13 18:00 | 0 | 0 | 0 | 19.17 | 9.6 | 0
1724 | 2008-03-13 19:00 | 0 | 0 | 0 | 18.04 | 9.6 | 0
1725 | 2008-03-13 20:00 | 0 | 0 | 0 | 17.07 | 9.6 | 0
1726 | 2008-03-13 21:00 | 0 | 0 | 0 | 16.1 | 8.8 | 0
1727 | 2008-03-13 22:00 | 0 | 0 | 0 | 15.14 | 8.8 | 0
1728 | 2008-03-13 23:00 | 0 | 0 | 0 | 14.3 | 8.8 | 0
1729 | 2008-03-14 | 0 | 0 | 0 | 13.46 | 9.66 | 0
1730 | 2008-03-14 01:00 | 0 | 0 | 0 | 12.62 | 9.66 | 0
1731 | 2008-03-14 02:00 | 0 | 0 | 0 | 11.93 | 9.66 | 0
1732 | 2008-03-14 03:00 | 0 | 0 | 0 | 11.23 | 11.64 | 0
1733 | 2008-03-14 04:00 | 0 | 0 | 0 | 10.53 | 11.64 | 0
1734 | 2008-03-14 05:00 | 0 | 0 | 0 | 9.89 | 11.64 | 0
1735 | 2008-03-14 06:00 | 65 | 393 | 26 | 9.24 | 9.29 | 0 | 5.2074 | 96.3293 | 82.6081 | 0 | 65 | 55.2833 | 30.234 | 0.609 | 2.5797 | 28.2942 | 0.0031788 | 1.7061 | 27.247 | 0.0023953 | 28.0869 | 28.0845 | 63073.7 | 9.7222 | 46837.9 | 50639.8 | 47311.1 | 0 | 0 | 47289.6 | 647.717 | 0 | 0 | 0 | 161.309 | 47128.3 | 660 | 45471 | 44561.5859
1736 | 2008-03-14 07:00 | 287 | 761 | 60 | 8.6 | 9.29 | 0 | 17.3447 | 105.322 | 67.8655 | 0 | 287 | 286.896 | 70.9494 | 2.689 | 247.157 | 66.3972 | 0.014035 | 226.716 | 63.9399 | 0.010576 | 281.947 | 281.885 | 633020 | 13.4395 | 592740 | 622143 | 564553 | 0 | 0 | 562049 | 725.915 | 0 | 0 | 0 | 1147.3 | 560902 | 729.558 | 551237 | 540211.875
1737 | 2008-03-14 08:00 | 499 | 884 | 72 | 9.94 | 9.29 | 0 | 28.9251 | 115.705 | 53.2168 | 0 | 499 | 528.636 | 84.7351 | 4.6752 | 527.563 | 79.2984 | 0.024403 | 509.889 | 76.3636 | 0.018388 | 568.683 | 568.665 | 1277070 | 19.703 | 1245850 | 1273770 | 1232630 | 0 | 0 | 1221890 | 742.76 | 0 | 0 | 0 | 0 | 1221890 | 742.76 | 1200410 | 1176403.375
1738 | 2008-03-14 09:00 | 684 | 947 | 84 | 11.29 | 9.96 | 0 | 39.4019 | 128.718 | 38.7811 | 0 | 684 | 736.86 | 98.6332 | 6.4085 | 736.86 | 92.3047 | 0.03345 | 726.441 | 88.8885 | 0.025206 | 790.894 | 790.889 | 1776130 | 24.319 | 1765990 | 1770750 | 1722390 | 0 | 0 | 1701390 | 739.944 | 0 | 0 | 0 | 0 | 1701390 | 739.944 | 1668670 | 1635292.25
1739 | 2008-03-14 10:00 | 808 | 916 | 131 | 12.64 | 9.96 | 0 | 47.8253 | 145.937 | 24.9434 | 0 | 808 | 828.298 | 157.775 | 7.5703 | 828.298 | 147.651 | 0.039515 | 824.038 | 142.187 | 0.029775 | 937.267 | 937.258 | 2104850 | 28.0803 | 2111490 | 2084270 | 2029660 | 0 | 0 | 1999850 | 730.015 | 0 | 0 | 0 | 0 | 1999850 | 730.015 | 1957860 | 1918699.125
1740 | 2008-03-14 11:00 | 824 | 808 | 183 | 13.63 | 9.96 | 0 | 52.6986 | 168.236 | 13.673 | 0 | 824 | 782.988 | 221.233 | 7.7202 | 782.988 | 207.038 | 0.040297 | 781.846 | 199.376 | 0.030365 | 951.815 | 951.802 | 2137510 | 29.3099 | 2145890 | 2107330 | 2051270 | 0 | 0 | 2020750 | 728.135 | 0 | 0 | 0 | 0 | 2020750 | 728.135 | 1978030 | 1938473.25
1741 | 2008-03-14 12:00 | 851 | 902 | 137 | 14.63 | 10.88 | 0 | 52.5734 | 193.063 | 14.0874 | 0 | 851 | 872.055 | 165.671 | 7.9732 | 872.055 | 155.041 | 0.041617 | 870.703 | 149.303 | 0.03136 | 989.436 | 989.43 | 2222010 | 30.0409 | 2234960 | 2188150 | 2129370 | 0 | 0 | 2096270 | 725.7 | 51689.1 | 0 | 0 | 0 | 2044240 | 753.864 | 1999200 | 1959217.75
1742 | 2008-03-14 13:00 | 811 | 928 | 128 | 15.62 | 10.88 | 0 | 47.4953 | 215.144 | 25.6256 | 0 | 811 | 835.324 | 154.36 | 7.5984 | 835.324 | 144.456 | 0.039661 | 830.768 | 139.11 | 0.029886 | 940.81 | 940.804 | 2112800 | 30.2736 | 2119870 | 2073260 | 2017860 | 0 | 0 | 1988000 | 725.271 | 0 | 0 | 0 | 0 | 1988000 | 725.271 | 1946410 | 1907485.25
1743 | 2008-03-14 14:00 | 631 | 830 | 110 | 15.53 | 10.88 | 0 | 38.9483 | 232.136 | 39.5148 | 0 | 631 | 639.387 | 132.132 | 5.912 | 639.387 | 123.654 | 0.030859 | 629.916 | 119.078 | 0.023252 | 726.547 | 726.536 | 1631610 | 26.8462 | 1614670 | 1601930 | 1557670 | 0 | 0 | 1540040 | 730.324 | 0 | 0 | 0 | 0 | 1540040 | 730.324 | 1512290 | 1482041.75
1744 | 2008-03-14 15:00 | 453 | 785 | 80 | 15.45 | 7.25 | 0 | 28.4074 | 245 | 53.9658 | 0 | 453 | 461.228 | 96.1987 | 4.2443 | 461.228 | 90.0264 | 0.022154 | 445.087 | 86.6946 | 0.016693 | 515.844 | 515.843 | 1158450 | 25.5144 | 1123370 | 1120750 | 1090630 | 0 | 0 | 1081760 | 723.373 | 0 | 0 | 0 | 0 | 1081760 | 723.373 | 1064020 | 1042736
1745 | 2008-03-14 16:00 | 261 | 655 | 71 | 15.37 | 7.25 | 0 | 16.799 | 255.307 | 68.6199 | 0 | 261 | 239.66 | 82.6077 | 2.4454 | 239.66 | 77.3074 | 0.012764 | 218.773 | 74.4463 | 0.0096179 | 284.432 | 284.426 | 638750 | 20.9193 | 596010 | 607017 | 590778 | 0 | 0 | 588109 | 718.044 | 0 | 0 | 0 | 0 | 588109 | 718.044 | 578670 | 567097.125
1746 | 2008-03-14 17:00 | 39 | 295 | 11 | 14.18 | 7.25 | 0 | 4.6569 | 264.279 | 83.3632 | 0 | 39 | 37.1964 | 13.5328 | 0.3654 | 37.1964 | 12.6645 | 0.0019073 | 22.9643 | 12.1958 | 0.0014372 | 34.1067 | 34.1061 | 76593.6 | 14.8454 | 58375.1 | 61549.1 | 60164 | 0 | 0 | 60129 | 640.417 | 0 | 0 | 0 | 600.989 | 59528 | 660 | 57478.5 | 56328.9531
1747 | 2008-03-14 18:00 | 0 | 0 | 0 | 12.98 | 9.14 | 0
1748 | 2008-03-14 19:00 | 0 | 0 | 0 | 11.79 | 9.14 | 0
1749 | 2008-03-14 20:00 | 0 | 0 | 0 | 10.85 | 9.14 | 0
1750 | 2008-03-14 21:00 | 0 | 0 | 0 | 9.9 | 9.56 | 0
1751 | 2008-03-14 22:00 | 0 | 0 | 0 | 8.96 | 9.56 | 0
1752 | 2008-03-14 23:00 | 0 | 0 | 0 | 8.33 | 9.56 | 0
1753 | 2008-03-15 | 0 | 0 | 0 | 7.71 | 10.82 | 0
1754 | 2008-03-15 01:00 | 0 | 0 | 0 | 7.09 | 10.82 | 0
1755 | 2008-03-15 02:00 | 0 | 0 | 0 | 6.53 | 10.82 | 0
1756 | 2008-03-15 03:00 | 0 | 0 | 0 | 5.96 | 10.13 | 0
1757 | 2008-03-15 04:00 | 0 | 0 | 0 | 5.39 | 10.13 | 0
1758 | 2008-03-15 05:00 | 0 | 0 | 0 | 4.92 | 10.13 | 0
1759 | 2008-03-15 06:00 | 71 | 412 | 29 | 4.46 | 7.71 | 0 | 5.4914 | 96.0447 | 82.4709 | 0 | 71 | 57.5073 | 33.4899 | 0.66522 | 4.5442 | 31.3411 | 0.0034722 | 3.0374 | 30.1812 | 0.0026164 | 32.2246 | 32.2332 | 72394.5 | 5.0708 | 54932.2 | 60682.5 | 55581.9 | 0 | 0 | 55553.7 | 670.151 | 0 | 0 | 0 | 0 | 55553.7 | 670.151 | 53574.2 | 52502.7539
1760 | 2008-03-15 07:00 | 293 | 765 | 61 | 3.99 | 7.71 | 0 | 17.6401 | 105.037 | 67.72 | 0 | 293 | 290.258 | 71.8483 | 2.7452 | 252.108 | 67.2384 | 0.014329 | 231.466 | 64.7499 | 0.010797 | 287.339 | 287.29 | 645162 | 9.4344 | 604739 | 645296 | 585595 | 0 | 0 | 583076 | 749.078 | 0 | 0 | 0 | 0 | 583076 | 749.078 | 572535 | 561084.625
1761 | 2008-03-15 08:00 | 502 | 880 | 72 | 5.41 | 7.71 | 0 | 29.2416 | 115.423 | 53.056 | 0 | 502 | 529.065 | 84.5616 | 4.7034 | 528.503 | 79.136 | 0.02455 | 510.961 | 76.2072 | 0.018499 | 569.572 | 569.561 | 1279090 | 16.2036 | 1247910 | 1294340 | 1252270 | 0 | 0 | 1241570 | 756.358 | 0 | 0 | 0 | 0 | 1241570 | 756.358 | 1218940 | 1194557.375
1762 | 2008-03-15 09:00 | 660 | 854 | 115 | 6.83 | 5.93 | 0 | 39.7494 | 128.458 | 38.5921 | 0 | 660 | 666.179 | 137.527 | 6.1837 | 666.179 | 128.703 | 0.032277 | 656.872 | 123.94 | 0.024321 | 757.411 | 757.403 | 1700940 | 22.9088 | 1687200 | 1701650 | 1654360 | 0 | 0 | 1635150 | 744 | 0 | 0 | 0 | 0 | 1635150 | 744 | 1604070 | 1571985.75
1763 | 2008-03-15 10:00 | 775 | 858 | 137 | 8.25 | 5.93 | 0 | 48.2081 | 145.757 | 24.6956 | 0 | 775 | 777.457 | 164.007 | 7.2611 | 777.457 | 153.484 | 0.037901 | 773.543 | 147.804 | 0.028559 | 893.735 | 893.73 | 2007100 | 27.2229 | 2008590 | 1989690 | 1933690 | 0 | 0 | 1906900 | 733.823 | 0 | 0 | 0 | 0 | 1906900 | 733.823 | 1867970 | 1830613.375
1764 | 2008-03-15 11:00 | 799 | 601 | 320 | 8.9 | 5.93 | 0 | 53.0999 | 168.241 | 13.2989 | 0 | 799 | 582.924 | 361.989 | 7.486 | 582.924 | 338.763 | 0.039074 | 582.121 | 326.226 | 0.029443 | 881.125 | 881.114 | 1978760 | 27.605 | 1978800 | 1956990 | 1901540 | 0 | 0 | 1875630 | 733.967 | 0 | 0 | 0 | 0 | 1875630 | 733.967 | 1837710 | 1800957.625
1765 | 2008-03-15 12:00 | 166 | 1 | 165 | 9.56 | 10.4 | 0 | 52.9482 | 193.301 | 13.8013 | 0 | 166 | 1.2168 | 154.582 | 1.5553 | 1.2168 | 144.664 | 0.0081181 | 1.215 | 139.31 | 0.0061172 | 136.315 | 136.306 | 306110 | 11.7459 | 270364 | 287647 | 279478 | 0 | 0 | 278882 | 719.259 | 0 | 0 | 0 | 0 | 278882 | 719.259 | 271587 | 266155.3125
1766 | 2008-03-15 13:00 | 158 | 0 | 158 | 10.21 | 10.4 | 0 | 47.8091 | 215.516 | 25.5088 | 0 | 158 | 0 | 147.805 | 1.4803 | 0 | 138.322 | 0.0077269 | 0 | 133.203 | 0.0058223 | 129.212 | 129.207 | 290164 | 12.282 | 255143 | 270878 | 263079 | 0 | 0 | 262543 | 714.991 | 0 | 0 | 0 | 0 | 262543 | 714.991 | 255496 | 250386.0469
1767 | 2008-03-15 14:00 | 125 | 0 | 125 | 9.88 | 10.4 | 0 | 39.2017 | 232.537 | 39.463 | 0 | 125 | 0 | 116.197 | 1.1711 | 0 | 108.742 | 0.006113 | 0 | 104.717 | 0.0046063 | 101.58 | 101.577 | 228115 | 11.5089 | 196422 | 209542 | 203559 | 0 | 0 | 203229 | 705.433 | 0 | 0 | 0 | 0 | 203229 | 705.433 | 197179 | 193235.4688
1768 | 2008-03-15 15:00 | 248 | 83 | 208 | 9.55 | 10.58 | 0 | 28.6168 | 245.389 | 53.944 | 0 | 248 | 49.1555 | 215.788 | 2.3236 | 49.1555 | 201.942 | 0.012128 | 47.4375 | 194.469 | 0.0091389 | 234.658 | 234.645 | 526951 | 13.2719 | 485164 | 511258 | 495970 | 0 | 0 | 494182 | 736.108 | 0 | 0 | 0 | 0 | 494182 | 736.108 | 485119 | 475416.3125
1769 | 2008-03-15 16:00 | 224 | 312 | 133 | 9.23 | 10.58 | 0 | 16.9808 | 255.681 | 68.6138 | 0 | 224 | 113.622 | 139.049 | 2.0987 | 113.622 | 130.127 | 0.010955 | 103.724 | 125.311 | 0.0082545 | 222.172 | 222.169 | 498936 | 12.754 | 457568 | 483395 | 468934 | 0 | 0 | 467337 | 737.272 | 0 | 0 | 0 | 0 | 467337 | 737.272 | 458547 | 449376.1875
1770 | 2008-03-15 17:00 | 35 | 143 | 21 | 8.47 | 10.58 | 0 | 4.8249 | 264.644 | 83.3654 | 0 | 35 | 18.5922 | 23.5069 | 0.32792 | 18.5922 | 21.9987 | 0.0017117 | 11.4758 | 21.1845 | 0.0012898 | 31.6818 | 31.6816 | 71148.8 | 8.9725 | 53660.2 | 58242.6 | 56832.6 | 0 | 0 | 56803 | 658.121 | 0 | 0 | 0 | 2.9159 | 56800.1 | 660 | 54835.3 | 53738.5547
1771 | 2008-03-15 18:00 | 0 | 0 | 0 | 7.71 | 7.57 | 0
1772 | 2008-03-15 19:00 | 0 | 0 | 0 | 6.95 | 7.57 | 0
1773 | 2008-03-15 20:00 | 0 | 0 | 0 | 6.44 | 7.57 | 0
1774 | 2008-03-15 21:00 | 0 | 0 | 0 | 5.92 | 6.77 | 0
1775 | 2008-03-15 22:00 | 0 | 0 | 0 | 5.41 | 6.77 | 0
1776 | 2008-03-15 23:00 | 0 | 0 | 0 | 5.29 | 6.77 | 0
1777 | 2008-03-16 | 0 | 0 | 0 | 5.16 | 7.65 | 0
1778 | 2008-03-16 01:00 | 0 | 0 | 0 | 5.04 | 7.65 | 0
1779 | 2008-03-16 02:00 | 0 | 0 | 0 | 4.92 | 7.65 | 0
1780 | 2008-03-16 03:00 | 0 | 0 | 0 | 4.8 | 10.99 | 0
1781 | 2008-03-16 04:00 | 0 | 0 | 0 | 4.68 | 10.99 | 0
1782 | 2008-03-16 05:00 | 0 | 0 | 0 | 4.55 | 10.99 | 0
1783 | 2008-03-16 06:00 | 76 | 432 | 31 | 4.42 | 8.02 | 0 | 5.7763 | 95.7602 | 82.333 | 0 | 76 | 59.6526 | 35.3239 | 0.71206 | 6.5848 | 33.0575 | 0.0037167 | 4.4463 | 31.834 | 0.0028006 | 35.1946 | 35.1785 | 79008.2 | 5.0738 | 60741 | 67067.8 | 60759.7 | 0 | 0 | 60724.7 | 662.299 | 0 | 0 | 0 | -724.284 | 61449 | 664.943 | 59313.4 | 58127.1719
1784 | 2008-03-16 07:00 | 298 | 770 | 60 | 4.3 | 8.02 | 0 | 17.9359 | 104.752 | 67.5746 | 0 | 298 | 294.825 | 70.6592 | 2.792 | 257.935 | 66.1255 | 0.014573 | 237.025 | 63.6783 | 0.010981 | 291.692 | 291.609 | 654870 | 9.7193 | 614422 | 654859 | 597660 | 0 | 0 | 594995 | 742.505 | 0 | 0 | 0 | 0 | 594995 | 742.505 | 584573 | 572881.375
1785 | 2008-03-16 08:00 | 514 | 893 | 74 | 5.05 | 8.02 | 0 | 29.5583 | 115.139 | 52.8961 | 0 | 514 | 538.071 | 86.588 | 4.8158 | 537.863 | 81.0324 | 0.025137 | 520.176 | 78.0334 | 0.018941 | 580.282 | 580.284 | 1303170 | 15.8341 | 1272820 | 1322110 | 1282770 | 0 | 0 | 1271610 | 758.968 | 0 | 0 | 0 | 0 | 1271610 | 758.968 | 1248210 | 1223241.25
1786 | 2008-03-16 09:00 | 690 | 943 | 83 | 5.81 | 4.69 | 0 | 40.0971 | 128.195 | 38.4049 | 0 | 690 | 738.519 | 97.1475 | 6.4648 | 738.519 | 90.9143 | 0.033744 | 728.324 | 87.5496 | 0.025427 | 791.422 | 791.417 | 1777320 | 24.0169 | 1767230 | 1774130 | 1723190 | 0 | 0 | 1702330 | 742.707 | 0 | 0 | 0 | 0 | 1702330 | 742.707 | 1669390 | 1636005.5
1787 | 2008-03-16 10:00 | 805 | 949 | 95 | 6.57 | 4.69 | 0 | 48.5913 | 145.576 | 24.4507 | 0 | 805 | 861.755 | 110.594 | 7.5422 | 861.755 | 103.498 | 0.039368 | 857.51 | 99.6674 | 0.029664 | 928.491 | 928.487 | 2085150 | 27.9303 | 2090740 | 2064960 | 2010320 | 0 | 0 | 1981320 | 733.182 | 0 | 0 | 0 | 0 | 1981320 | 733.182 | 1939940 | 1901143.25
1788 | 2008-03-16 11:00 | 856 | 891 | 142 | 7.37 | 4.69 | 0 | 53.5016 | 168.248 | 12.9257 | 0 | 856 | 865.693 | 170.616 | 8.02 | 865.693 | 159.669 | 0.041862 | 864.568 | 153.76 | 0.031544 | 987.809 | 987.803 | 2218360 | 30.0949 | 2231110 | 2183710 | 2124850 | 0 | 0 | 2092010 | 727.316 | 47544.9 | 0 | 0 | 0 | 2044170 | 752.764 | 1999260 | 1959270.625
1789 | 2008-03-16 12:00 | 818 | 746 | 221 | 8.17 | 4.36 | 0 | 53.3226 | 193.543 | 13.5213 | 0 | 818 | 723.747 | 261.138 | 7.664 | 723.747 | 244.383 | 0.040004 | 722.716 | 235.338 | 0.030144 | 929.341 | 929.322 | 2087030 | 30.0154 | 2092720 | 2048770 | 1994360 | 0 | 0 | 1965270 | 725.389 | 0 | 0 | 0 | 0 | 1965270 | 725.389 | 1924460 | 1885970.5
1790 | 2008-03-16 13:00 | 614 | 381 | 331 | 8.97 | 4.36 | 0 | 48.1213 | 215.893 | 25.3981 | 0 | 614 | 343.354 | 357.987 | 5.7527 | 343.354 | 335.018 | 0.030027 | 341.517 | 322.619 | 0.022626 | 644.234 | 644.215 | 1446740 | 24.1134 | 1421850 | 1426920 | 1387550 | 0 | 0 | 1373700 | 735.573 | 0 | 0 | 0 | 0 | 1373700 | 735.573 | 1349510 | 1322521.5
1791 | 2008-03-16 14:00 | 604 | 594 | 227 | 9.07 | 4.36 | 0 | 39.4533 | 232.942 | 39.4154 | 0 | 604 | 458.347 | 253.639 | 5.659 | 458.347 | 237.365 | 0.029538 | 451.6 | 228.58 | 0.022258 | 659.796 | 659.782 | 1481710 | 24.5794 | 1458240 | 1460570 | 1421530 | 0 | 0 | 1406930 | 734.112 | 0 | 0 | 0 | 0 | 1406930 | 734.112 | 1382110 | 1354471.625
1792 | 2008-03-16 15:00 | 311 | 207 | 211 | 9.16 | 7.9 | 0 | 28.8245 | 245.781 | 53.925 | 0 | 311 | 122.134 | 215.772 | 2.9138 | 122.134 | 201.928 | 0.015209 | 117.87 | 194.455 | 0.01146 | 302.966 | 302.954 | 680359 | 14.8328 | 637564 | 666603 | 647727 | 0 | 0 | 644731 | 741.88 | 0 | 0 | 0 | 0 | 644731 | 741.88 | 633715 | 621041
1793 | 2008-03-16 16:00 | 276 | 490 | 131 | 9.25 | 7.9 | 0 | 17.1614 | 256.057 | 68.6096 | 0 | 276 | 179.231 | 139.972 | 2.5859 | 179.231 | 130.991 | 0.013498 | 163.621 | 126.143 | 0.010171 | 281.081 | 281.076 | 631227 | 14.5132 | 588518 | 616366 | 598908 | 0 | 0 | 596327 | 739.482 | 0 | 0 | 0 | 0 | 596327 | 739.482 | 586169 | 574446
1794 | 2008-03-16 17:00 | 43 | 227 | 20 | 9.17 | 7.9 | 0 | 4.9921 | 265.011 | 83.3687 | 0 | 43 | 30.5223 | 23.661 | 0.40288 | 30.5223 | 22.1429 | 0.0021029 | 18.833 | 21.3234 | 0.0015846 | 38.9532 | 38.9523 | 87476.7 | 9.8994 | 67882.5 | 73306.6 | 71472.7 | 0 | 0 | 71427.1 | 667.212 | 0 | 0 | 0 | 0 | 71427.1 | 667.212 | 68969.8 | 67590.4297
1795 | 2008-03-16 18:00 | 0 | 0 | 0 | 9.08 | 8.79 | 0
1796 | 2008-03-16 19:00 | 0 | 0 | 0 | 9 | 8.79 | 0
1797 | 2008-03-16 20:00 | 0 | 0 | 0 | 8.39 | 8.79 | 0
1798 | 2008-03-16 21:00 | 0 | 0 | 0 | 7.79 | 9.48 | 0
1799 | 2008-03-16 22:00 | 0 | 0 | 0 | 7.18 | 9.48 | 0
1800 | 2008-03-16 23:00 | 0 | 0 | 0 | 6.44 | 9.48 | 0
1801 | 2008-03-17 | 0 | 0 | 0 | 5.69 | 9.44 | 0
1802 | 2008-03-17 01:00 | 0 | 0 | 0 | 4.95 | 9.44 | 0
1803 | 2008-03-17 02:00 | 0 | 0 | 0 | 4.29 | 9.44 | 0
1804 | 2008-03-17 03:00 | 0 | 0 | 0 | 3.63 | 10.67 | 0
1805 | 2008-03-17 04:00 | 0 | 0 | 0 | 2.97 | 10.67 | 0
1806 | 2008-03-17 05:00 | 0 | 4 | 0 | 2.56 | 10.67 | 0
1807 | 2008-03-17 06:00 | 77 | 421 | 31 | 2.16 | 9.83 | 0 | 6.0617 | 95.4757 | 82.1946 | 0 | 77 | 59.1591 | 35.2029 | 0.72143 | 8.3345 | 32.9442 | 0.0037656 | 5.6827 | 31.725 | 0.0028375 | 36.2882 | 36.2738 | 81467.1 | 2.7624 | 62945.1 | 70222.4 | 64746.3 | 0 | 0 | 64708 | 677.702 | 0 | 0 | 0 | -4.6475 | 64712.7 | 677.906 | 62397.9 | 61149.9844
1808 | 2008-03-17 07:00 | 298 | 763 | 59 | 1.76 | 9.83 | 0 | 18.2321 | 104.466 | 67.4292 | 0 | 298 | 293.204 | 69.4587 | 2.792 | 258.337 | 65.0021 | 0.014573 | 237.601 | 62.5964 | 0.010981 | 291.202 | 291.171 | 653890 | 6.5952 | 613302 | 662325 | 603479 | 0 | 0 | 600887 | 760.174 | 0 | 0 | 0 | 0 | 600887 | 760.174 | 589766 | 577970.5625
1809 | 2008-03-17 08:00 | 520 | 894 | 75 | 3.41 | 9.83 | 0 | 29.8752 | 114.855 | 52.7371 | 0 | 520 | 540.912 | 87.5087 | 4.872 | 540.808 | 81.8939 | 0.02543 | 523.188 | 78.8631 | 0.019162 | 584.008 | 584.004 | 1311530 | 13.1079 | 1281470 | 1345700 | 1305570 | 0 | 0 | 1294330 | 769.568 | 0 | 0 | 0 | 0 | 1294330 | 769.568 | 1269820 | 1244427.25
1810 | 2008-03-17 09:00 | 702 | 952 | 85 | 5.06 | 6.16 | 0 | 40.4449 | 127.931 | 38.2197 | 0 | 702 | 747.233 | 99.1707 | 6.5772 | 747.233 | 92.8077 | 0.034331 | 737.04 | 89.373 | 0.025869 | 801.645 | 801.642 | 1800280 | 21.828 | 1791310 | 1814610 | 1766000 | 0 | 0 | 1744440 | 748.544 | 0 | 0 | 0 | 0 | 1744440 | 748.544 | 1709740 | 1675544.5
1811 | 2008-03-17 10:00 | 804 | 937 | 99 | 6.7 | 6.16 | 0 | 48.9747 | 145.392 | 24.2089 | 0 | 804 | 852.31 | 114.78 | 7.5328 | 852.31 | 107.415 | 0.039319 | 848.201 | 103.44 | 0.029628 | 923.12 | 923.113 | 2073080 | 26.0088 | 2078040 | 2068970 | 2014190 | 0 | 0 | 1985400 | 737.84 | 0 | 0 | 0 | 0 | 1985400 | 737.84 | 1943800 | 1904920.25
1812 | 2008-03-17 11:00 | 862 | 894 | 142 | 8.21 | 6.16 | 0 | 53.9035 | 168.256 | 12.5538 | 0 | 862 | 869.757 | 170.329 | 8.0763 | 869.757 | 159.4 | 0.042155 | 868.692 | 153.501 | 0.031765 | 991.558 | 991.55 | 2226780 | 28.9503 | 2239980 | 2203050 | 2142680 | 0 | 0 | 2109720 | 732.076 | 65371.4 | 0 | 0 | 0 | 2044380 | 760.635 | 1998570 | 1958595.375
1813 | 2008-03-17 12:00 | 895 | 995 | 95 | 9.72 | 2.92 | 0 | 53.6964 | 193.792 | 13.2478 | 0 | 895 | 966.273 | 110.37 | 8.3855 | 966.273 | 103.289 | 0.043769 | 964.952 | 99.4662 | 0.032981 | 1032.52 | 1032.51 | 2318740 | 36.4057 | 2336980 | 2226100 | 2168390 | 0 | 0 | 2132200 | 706.226 | 85272.4 | 0 | 0 | 0 | 2043640 | 741.808 | 1999980 | 1959984.25
1814 | 2008-03-17 13:00 | 824 | 981 | 92 | 11.22 | 2.92 | 0 | 48.432 | 216.277 | 25.2937 | 0 | 824 | 884.59 | 107.046 | 7.7202 | 884.59 | 100.178 | 0.040297 | 879.9 | 96.4702 | 0.030365 | 947.109 | 947.106 | 2126950 | 35.6985 | 2134770 | 2039260 | 1984280 | 0 | 0 | 1954010 | 707.645 | 0 | 0 | 0 | 0 | 1954010 | 707.645 | 1913660 | 1875389.875
1815 | 2008-03-17 14:00 | 689 | 950 | 83 | 12.05 | 2.92 | 0 | 39.703 | 233.351 | 39.372 | 0 | 689 | 733.341 | 96.893 | 6.4554 | 733.341 | 90.6761 | 0.033695 | 722.576 | 87.3203 | 0.02539 | 785.624 | 785.62 | 1764300 | 32.3548 | 1753590 | 1699000 | 1654330 | 0 | 0 | 1633520 | 713.188 | 0 | 0 | 0 | 0 | 1633520 | 713.188 | 1603610 | 1571535
1816 | 2008-03-17 15:00 | 504 | 888 | 73 | 12.89 | 6.7 | 0 | 29.0306 | 246.176 | 53.9089 | 0 | 504 | 523.185 | 85.1795 | 4.7221 | 523.185 | 79.7142 | 0.024648 | 504.937 | 76.7641 | 0.018573 | 564.268 | 564.263 | 1267200 | 24.2915 | 1235580 | 1239170 | 1204750 | 0 | 0 | 1194180 | 732.014 | 0 | 0 | 0 | 0 | 1194180 | 732.014 | 1173800 | 1150319.75
1817 | 2008-03-17 16:00 | 276 | 741 | 55 | 13.72 | 6.7 | 0 | 17.3406 | 256.433 | 68.6073 | 0 | 276 | 270.461 | 64.7978 | 2.5859 | 270.461 | 60.6402 | 0.013498 | 246.91 | 58.396 | 0.010171 | 296.157 | 296.153 | 665085 | 19.7041 | 622286 | 637138 | 620086 | 0 | 0 | 617195 | 724.163 | 0 | 0 | 0 | 0 | 617195 | 724.163 | 607191 | 595047.375
1818 | 2008-03-17 17:00 | 44 | 349 | 9 | 13.6 | 6.7 | 0 | 5.1585 | 265.378 | 83.3732 | 0 | 44 | 44.9226 | 11.0922 | 0.41225 | 44.9226 | 10.3805 | 0.0021518 | 27.7053 | 9.9963 | 0.0016214 | 36.5722 | 36.5718 | 82131.3 | 14.339 | 63199.8 | 66795.2 | 65162.7 | 0 | 0 | 65122.5 | 647.514 | 0 | 0 | 0 | 285.462 | 64837 | 660 | 62625.4 | 61372.9219
1819 | 2008-03-17 18:00 | 0 | 0 | 0 | 13.48 | 4.93 | 0
1820 | 2008-03-17 19:00 | 0 | 0 | 0 | 13.36 | 4.93 | 0
1821 | 2008-03-17 20:00 | 0 | 0 | 0 | 13.17 | 4.93 | 0
1822 | 2008-03-17 21:00 | 0 | 0 | 0 | 12.97 | 6.54 | 0
1823 | 2008-03-17 22:00 | 0 | 0 | 0 | 12.77 | 6.54 | 0
1824 | 2008-03-17 23:00 | 0 | 0 | 0 | 12 | 6.54 | 0
1825 | 2008-03-18 | 0 | 0 | 0 | 11.23 | 4.55 | 0
1826 | 2008-03-18 01:00 | 0 | 0 | 0 | 10.46 | 4.55 | 0
1827 | 2008-03-18 02:00 | 0 | 0 | 0 | 9.94 | 4.55 | 0
1828 | 2008-03-18 03:00 | 0 | 0 | 0 | 9.42 | 5.27 | 0
1829 | 2008-03-18 04:00 | 0 | 0 | 0 | 8.9 | 5.27 | 0
1830 | 2008-03-18 05:00 | 0 | 9 | 0 | 8.49 | 5.27 | 0
1831 | 2008-03-18 06:00 | 85 | 456 | 33 | 8.08 | 6.85 | 0 | 6.3477 | 95.1914 | 82.0559 | 0 | 85 | 65.0029 | 37.0447 | 0.79638 | 11.2171 | 34.6678 | 0.0041569 | 7.7199 | 33.3848 | 0.0031323 | 39.8746 | 39.8689 | 89542.8 | 8.8779 | 70129.2 | 75988.2 | 69731.5 | 0 | 0 | 69685.1 | 668.69 | 0 | 0 | 0 | -0.33527 | 69685.5 | 669.156 | 67275.3 | 65929.75
1832 | 2008-03-18 07:00 | 309 | 777 | 62 | 7.66 | 6.85 | 0 | 18.5285 | 104.179 | 67.2842 | 0 | 309 | 300.154 | 72.4528 | 2.8951 | 266.346 | 67.8041 | 0.015111 | 245.177 | 65.2947 | 0.011387 | 301.169 | 301.104 | 676198 | 13.6861 | 635547 | 666216 | 610427 | 0 | 0 | 607563 | 729.66 | 0 | 0 | 0 | 64.3268 | 607498 | 730.461 | 597361 | 585414.25
1833 | 2008-03-18 08:00 | 526 | 896 | 76 | 9.54 | 6.85 | 0 | 30.1921 | 114.569 | 52.5792 | 0 | 526 | 543.743 | 88.4255 | 4.9282 | 543.691 | 82.752 | 0.025724 | 526.139 | 79.6894 | 0.019383 | 587.672 | 587.671 | 1319760 | 21.3013 | 1289990 | 1310130 | 1273240 | 0 | 0 | 1261770 | 742.307 | 0 | 0 | 0 | 0 | 1261770 | 742.307 | 1239530 | 1214736.5
1834 | 2008-03-18 09:00 | 707 | 954 | 85 | 11.43 | 3.64 | 0 | 40.7926 | 127.665 | 38.0366 | 0 | 707 | 749.857 | 98.9812 | 6.624 | 749.857 | 92.6304 | 0.034575 | 739.747 | 89.2022 | 0.026053 | 804.106 | 804.103 | 1805810 | 31.2468 | 1797110 | 1749670 | 1703600 | 0 | 0 | 1681820 | 718.323 | 0 | 0 | 0 | 0 | 1681820 | 718.323 | 1650290 | 1617283.25
1835 | 2008-03-18 10:00 | 838 | 983 | 94 | 13.3 | 3.64 | 0 | 49.3582 | 145.207 | 23.9705 | 0 | 838 | 895.937 | 109.076 | 7.8514 | 895.937 | 102.078 | 0.040982 | 891.709 | 98.2998 | 0.030881 | 960.339 | 960.332 | 2156660 | 36.967 | 2166070 | 2057720 | 2003240 | 0 | 0 | 1972040 | 703.047 | 0 | 0 | 0 | 0 | 1972040 | 703.047 | 1931060 | 1892434.875
1836 | 2008-03-18 11:00 | 904 | 996 | 97 | 14.64 | 3.64 | 0 | 54.3056 | 168.265 | 12.1833 | 0 | 904 | 971.29 | 112.37 | 8.4698 | 971.29 | 105.16 | 0.044209 | 970.171 | 101.268 | 0.033313 | 1039.33 | 1039.33 | 2334070 | 40.2538 | 2353150 | 2203620 | 2145370 | 0 | 0 | 2108840 | 695.187 | 62690.4 | 0 | 0 | 0 | 2043490 | 725.207 | 1999980 | 1959977
1837 | 2008-03-18 12:00 | 901 | 995 | 97 | 15.97 | 0.46 | 0 | 54.0695 | 194.046 | 12.9814 | 0 | 901 | 967.548 | 112.363 | 8.4417 | 967.548 | 105.154 | 0.044063 | 966.279 | 101.262 | 0.033202 | 1035.55 | 1035.55 | 2325580 | 47.5277 | 2344180 | 2122830 | 2074950 | 0 | 0 | 2038120 | 669.084 | 1741.88 | 0 | 0 | 0 | 2036290 | 671.551 | 1992830 | 1952975.875
1838 | 2008-03-18 13:00 | 828 | 981 | 92 | 17.31 | 0.46 | 0 | 48.7411 | 216.666 | 25.1954 | 0 | 828 | 885.918 | 106.842 | 7.7577 | 885.918 | 99.9871 | 0.040493 | 881.26 | 96.2866 | 0.030512 | 948.25 | 948.246 | 2129520 | 46.2072 | 2137480 | 1946500 | 1899350 | 0 | 0 | 1868740 | 672.649 | 0 | 0 | 0 | 0 | 1868740 | 672.649 | 1831800 | 1795159.375
1839 | 2008-03-18 14:00 | 693 | 950 | 84 | 18.08 | 0.46 | 0 | 39.9508 | 233.763 | 39.3326 | 0 | 693 | 733.573 | 97.8053 | 6.4929 | 733.573 | 91.5299 | 0.033891 | 722.831 | 88.1425 | 0.025537 | 786.669 | 786.664 | 1766650 | 42.0531 | 1756040 | 1628590 | 1589460 | 0 | 0 | 1568350 | 680.379 | 0 | 0 | 0 | 0 | 1568350 | 680.379 | 1541500 | 1510666
1840 | 2008-03-18 15:00 | 507 | 889 | 73 | 18.85 | 2.19 | 0 | 29.2349 | 246.572 | 53.8955 | 0 | 507 | 523.634 | 84.9967 | 4.7502 | 523.634 | 79.5432 | 0.024794 | 505.384 | 76.5993 | 0.018683 | 564.542 | 564.541 | 1267820 | 34.1667 | 1236220 | 1187020 | 1156420 | 0 | 0 | 1145710 | 697.821 | 0 | 0 | 0 | 0 | 1145710 | 697.821 | 1127960 | 1105399.5
1841 | 2008-03-18 16:00 | 277 | 736 | 55 | 19.61 | 2.19 | 0 | 17.5186 | 256.811 | 68.6068 | 0 | 277 | 269.015 | 64.6033 | 2.5953 | 269.015 | 60.4583 | 0.013546 | 245.591 | 58.2207 | 0.010207 | 294.707 | 294.704 | 661828 | 27.6057 | 619033 | 611626 | 595530 | 0 | 0 | 592651 | 696.209 | 0 | 0 | 0 | 0 | 592651 | 696.209 | 583832 | 572155.4375
1842 | 2008-03-18 17:00 | 45 | 351 | 9 | 19.38 | 2.19 | 0 | 5.3242 | 265.746 | 83.3786 | 0 | 45 | 44.736 | 10.9964 | 0.42162 | 44.736 | 10.2908 | 0.0022007 | 27.5743 | 9.91 | 0.0016583 | 36.3613 | 36.3609 | 81657.3 | 20.3665 | 62785.6 | 64348.7 | 62915.5 | 0 | 0 | 62875.4 | 625.649 | 0 | 0 | 0 | 2595.12 | 60280.3 | 660 | 58207.6 | 57043.4961
1843 | 2008-03-18 18:00 | 0 | 0 | 0 | 19.13 | 3.14 | 0
1844 | 2008-03-18 19:00 | 0 | 0 | 0 | 18.9 | 3.14 | 0
1845 | 2008-03-18 20:00 | 0 | 0 | 0 | 18.31 | 3.14 | 0
1846 | 2008-03-18 21:00 | 0 | 0 | 0 | 17.72 | 3.21 | 0
1847 | 2008-03-18 22:00 | 0 | 0 | 0 | 17.14 | 3.21 | 0
1848 | 2008-03-18 23:00 | 0 | 0 | 0 | 16.27 | 3.21 | 0
1849 | 2008-03-19 | 0 | 0 | 0 | 15.4 | 2.65 | 0
1850 | 2008-03-19 01:00 | 0 | 0 | 0 | 14.53 | 2.65 | 0
1851 | 2008-03-19 02:00 | 0 | 0 | 0 | 13.47 | 2.65 | 0
1852 | 2008-03-19 03:00 | 0 | 0 | 0 | 12.41 | 7.41 | 0
1853 | 2008-03-19 04:00 | 0 | 0 | 0 | 11.36 | 7.41 | 0
1854 | 2008-03-19 05:00 | 0 | 15 | 0 | 10.86 | 7.41 | 0
1855 | 2008-03-19 06:00 | 91 | 473 | 35 | 10.36 | 6.72 | 0 | 6.634 | 94.9071 | 81.9168 | 0 | 91 | 68.1598 | 38.8821 | 0.8526 | 14.1683 | 36.3874 | 0.0044503 | 9.8386 | 35.0407 | 0.0033534 | 43.5362 | 43.5502 | 97809.8 | 11.2388 | 77514.5 | 83010.7 | 74634.8 | 0 | 0 | 74581 | 665.511 | 0 | 0 | 0 | 12.2831 | 74568.7 | 666.37 | 72032.5 | 70591.8125
1856 | 2008-03-19 07:00 | 314 | 782 | 61 | 9.86 | 6.72 | 0 | 18.8249 | 103.892 | 67.1395 | 0 | 314 | 304.6 | 71.2563 | 2.9419 | 272.065 | 66.6843 | 0.015356 | 250.653 | 64.2164 | 0.011571 | 305.434 | 305.366 | 685771 | 16.0223 | 645050 | 669498 | 615323 | 0 | 0 | 612352 | 720.976 | 0 | 0 | 0 | 259.009 | 612093 | 724.373 | 602068 | 590026.875
1857 | 2008-03-19 08:00 | 527 | 893 | 74 | 11.71 | 6.72 | 0 | 30.5087 | 114.281 | 52.4225 | 0 | 527 | 544.162 | 86.0677 | 4.9376 | 544.162 | 80.5455 | 0.025773 | 526.754 | 77.5645 | 0.01942 | 586.208 | 586.203 | 1316460 | 23.5397 | 1286570 | 1294420 | 1259370 | 0 | 0 | 1247900 | 734.549 | 0 | 0 | 0 | 0 | 1247900 | 734.549 | 1226320 | 1201798.5
1858 | 2008-03-19 09:00 | 704 | 943 | 84 | 13.56 | 3.15 | 0 | 41.14 | 127.397 | 37.8557 | 0 | 704 | 744.073 | 97.6914 | 6.5959 | 744.073 | 91.4233 | 0.034429 | 734.157 | 88.0398 | 0.025943 | 797.556 | 797.551 | 1791100 | 33.8615 | 1781680 | 1714910 | 1671840 | 0 | 0 | 1650250 | 707.82 | 0 | 0 | 0 | 0 | 1650250 | 707.82 | 1619990 | 1587585.875
1859 | 2008-03-19 10:00 | 842 | 929 | 134 | 15.41 | 3.15 | 0 | 49.7416 | 145.02 | 23.7356 | 0 | 842 | 849.273 | 159.696 | 7.8889 | 849.273 | 149.45 | 0.041177 | 845.349 | 143.918 | 0.031028 | 959.619 | 959.61 | 2155040 | 39.8367 | 2164370 | 2029900 | 1979300 | 0 | 0 | 1948000 | 693.269 | 0 | 0 | 0 | 0 | 1948000 | 693.269 | 1907930 | 1869775.5
1860 | 2008-03-19 11:00 | 854 | 831 | 177 | 16.69 | 3.15 | 0 | 54.7078 | 168.276 | 11.8145 | 0 | 854 | 811.866 | 206.797 | 8.0013 | 811.866 | 193.529 | 0.041764 | 810.988 | 186.367 | 0.03147 | 967.464 | 967.457 | 2172660 | 41.3164 | 2182940 | 2033720 | 1982730 | 0 | 0 | 1950920 | 689.302 | 0 | 0 | 0 | 0 | 1950920 | 689.302 | 1910770 | 1872556.75
1861 | 2008-03-19 12:00 | 904 | 940 | 141 | 17.96 | 6.05 | 0 | 54.4419 | 194.306 | 12.7225 | 0 | 904 | 914.865 | 159.355 | 8.4698 | 914.865 | 149.131 | 0.044209 | 913.714 | 143.611 | 0.033313 | 1025.64 | 1025.63 | 2303300 | 39.5655 | 2320690 | 2179900 | 2125070 | 0 | 0 | 2089160 | 694.826 | 43767.6 | 0 | 0 | 0 | 2043500 | 721.814 | 1999980 | 1959977.25
1862 | 2008-03-19 13:00 | 832 | 982 | 92 | 19.24 | 6.05 | 0 | 49.0485 | 217.06 | 25.1035 | 0 | 832 | 887.241 | 106.639 | 7.7952 | 887.241 | 99.7967 | 0.040688 | 882.614 | 96.1033 | 0.030659 | 949.385 | 949.377 | 2132060 | 39.2391 | 2140150 | 2012580 | 1960800 | 0 | 0 | 1930290 | 696.13 | 0 | 0 | 0 | 0 | 1930290 | 696.13 | 1890850 | 1853036
1863 | 2008-03-19 14:00 | 696 | 950 | 84 | 19.49 | 6.05 | 0 | 40.1967 | 234.179 | 39.2973 | 0 | 696 | 733.806 | 97.6142 | 6.521 | 733.806 | 91.3511 | 0.034037 | 723.085 | 87.9702 | 0.025648 | 786.749 | 786.747 | 1766830 | 36.0632 | 1756240 | 1673980 | 1631070 | 0 | 0 | 1610150 | 701.099 | 0 | 0 | 0 | 0 | 1610150 | 701.099 | 1581320 | 1549698.375
1864 | 2008-03-19 15:00 | 512 | 890 | 75 | 19.75 | 7.04 | 0 | 29.4375 | 246.971 | 53.8848 | 0 | 512 | 524.081 | 86.9921 | 4.797 | 524.081 | 81.4106 | 0.025039 | 505.826 | 78.3976 | 0.018867 | 566.716 | 566.71 | 1272690 | 30.9554 | 1241260 | 1209250 | 1177790 | 0 | 0 | 1167000 | 708.74 | 0 | 0 | 0 | 0 | 1167000 | 708.74 | 1148290 | 1125327.625
1865 | 2008-03-19 16:00 | 264 | 667 | 61 | 20.01 | 7.04 | 0 | 17.6954 | 257.19 | 68.6081 | 0 | 264 | 243.599 | 70.6805 | 2.4735 | 243.599 | 66.1455 | 0.012911 | 222.385 | 63.6975 | 0.0097285 | 277.51 | 277.508 | 623212 | 25.4971 | 580532 | 579175 | 564987 | 0 | 0 | 562418 | 699.485 | 0 | 0 | 0 | 0 | 562418 | 699.485 | 553786 | 542710.3125
1866 | 2008-03-19 17:00 | 43 | 323 | 10 | 19.09 | 7.04 | 0 | 5.489 | 266.115 | 83.3851 | 0 | 43 | 39.7418 | 12.0711 | 0.40288 | 39.7418 | 11.2966 | 0.0021029 | 24.4793 | 10.8785 | 0.0015846 | 34.2986 | 34.2979 | 77024.4 | 19.7682 | 58749.5 | 60404.8 | 59069.9 | 0 | 0 | 59034.3 | 623.7 | 0 | 0 | 0 | 2571.99 | 56462.3 | 660 | 54508 | 53417.8672
1867 | 2008-03-19 18:00 | 0 | 0 | 0 | 18.17 | 8.93 | 0
1868 | 2008-03-19 19:00 | 0 | 0 | 0 | 17.25 | 8.93 | 0
1869 | 2008-03-19 20:00 | 0 | 0 | 0 | 16.04 | 8.93 | 0
1870 | 2008-03-19 21:00 | 0 | 0 | 0 | 14.83 | 6.83 | 0
1871 | 2008-03-19 22:00 | 0 | 0 | 0 | 13.62 | 6.83 | 0
1872 | 2008-03-19 23:00 | 0 | 0 | 0 | 12.89 | 6.83 | 0
1873 | 2008-03-20 | 0 | 0 | 0 | 12.17 | 8.16 | 0
1874 | 2008-03-20 01:00 | 0 | 0 | 0 | 11.45 | 8.16 | 0
1875 | 2008-03-20 02:00 | 0 | 0 | 0 | 10.9 | 8.16 | 0
1876 | 2008-03-20 03:00 | 0 | 0 | 0 | 10.35 | 9.94 | 0
1877 | 2008-03-20 04:00 | 0 | 0 | 0 | 9.8 | 9.94 | 0
1878 | 2008-03-20 05:00 | 0 | 14 | 0 | 9.47 | 9.94 | 0
1879 | 2008-03-20 06:00 | 94 | 332 | 53 | 9.14 | 8.54 | 0 | 6.9205 | 94.623 | 81.7775 | 0 | 94 | 48.6648 | 55.3522 | 0.88071 | 12.0551 | 51.8007 | 0.004597 | 8.4433 | 49.8836 | 0.0034639 | 56.5804 | 56.5781 | 127064 | 10.1577 | 103418 | 111304 | 103517 | 0 | 0 | 103424 | 677.756 | 0 | 0 | 0 | 0 | 103424 | 677.756 | 99970.5 | 97971.1016
1880 | 2008-03-20 07:00 | 227 | 263 | 141 | 8.81 | 8.54 | 0 | 19.1213 | 103.605 | 66.9954 | 0 | 227 | 102.602 | 145.88 | 2.1268 | 92.196 | 136.52 | 0.011101 | 85.0102 | 131.467 | 0.008365 | 209.991 | 209.938 | 471466 | 12.5864 | 430895 | 455504 | 430676 | 0 | 0 | 429311 | 733.041 | 0 | 0 | 0 | 0 | 429311 | 733.041 | 420969 | 412549.5
1881 | 2008-03-20 08:00 | 463 | 577 | 167 | 10.82 | 8.54 | 0 | 30.8251 | 113.993 | 52.2672 | 0 | 463 | 353.512 | 183.879 | 4.338 | 353.512 | 172.081 | 0.022643 | 342.305 | 165.712 | 0.017062 | 492.793 | 492.788 | 1106670 | 19.6843 | 1070140 | 1094560 | 1063020 | 0 | 0 | 1055000 | 742.745 | 0 | 0 | 0 | 0 | 1055000 | 742.745 | 1036820 | 1016083.5625
1882 | 2008-03-20 09:00 | 704 | 849 | 142 | 12.83 | 5.28 | 0 | 41.487 | 127.126 | 37.6772 | 0 | 704 | 671.453 | 164.734 | 6.5959 | 671.453 | 154.164 | 0.034429 | 662.607 | 148.459 | 0.025943 | 786.759 | 786.753 | 1766840 | 30.2483 | 1756250 | 1717250 | 1671010 | 0 | 0 | 1650220 | 721.266 | 0 | 0 | 0 | 0 | 1650220 | 721.266 | 1619570 | 1587180
1883 | 2008-03-20 10:00 | 847 | 984 | 93 | 14.84 | 5.28 | 0 | 50.1248 | 144.831 | 23.5046 | 0 | 847 | 900.964 | 107.565 | 7.9357 | 900.964 | 100.664 | 0.041422 | 896.889 | 96.9382 | 0.031212 | 964.042 | 964.038 | 2164980 | 36.1833 | 2174840 | 2073310 | 2020100 | 0 | 0 | 1988560 | 705.683 | 0 | 0 | 0 | 0 | 1988560 | 705.683 | 1946980 | 1908037.125
1884 | 2008-03-20 11:00 | 881 | 904 | 141 | 16.19 | 5.28 | 0 | 55.1098 | 168.289 | 11.4477 | 0 | 881 | 884.217 | 168.371 | 8.2543 | 884.217 | 157.568 | 0.043085 | 883.319 | 151.736 | 0.032465 | 1004.04 | 1004.02 | 2254780 | 38.4186 | 2269510 | 2142570 | 2089060 | 0 | 0 | 2054650 | 697.858 | 10595.2 | 0 | 0 | 0 | 2043570 | 711.039 | 1999990 | 1959994.375
1885 | 2008-03-20 12:00 | 909 | 996 | 97 | 17.55 | 5.78 | 0 | 54.8135 | 194.572 | 12.4715 | 0 | 909 | 970.095 | 111.934 | 8.5166 | 970.095 | 104.752 | 0.044454 | 968.923 | 100.875 | 0.033497 | 1037.74 | 1037.74 | 2330490 | 39.794 | 2349370 | 2204680 | 2146480 | 0 | 0 | 2109980 | 696.125 | 63795 | 0 | 0 | 0 | 2043480 | 726.844 | 1999980 | 1959976.75
1886 | 2008-03-20 13:00 | 828 | 921 | 131 | 18.91 | 5.78 | 0 | 49.354 | 217.46 | 25.0179 | 0 | 828 | 832.429 | 155.912 | 7.7577 | 832.429 | 145.908 | 0.040493 | 828.12 | 140.508 | 0.030512 | 939.599 | 939.589 | 2110070 | 39.0502 | 2116990 | 1992420 | 1946510 | 0 | 0 | 1916280 | 694.247 | 0 | 0 | 0 | 0 | 1916280 | 694.247 | 1877360 | 1839816.75
1887 | 2008-03-20 14:00 | 654 | 789 | 143 | 19.42 | 5.78 | 0 | 40.4405 | 234.598 | 39.266 | 0 | 654 | 609.912 | 168.546 | 6.1275 | 609.912 | 157.732 | 0.031983 | 601.018 | 151.894 | 0.0241 | 730.349 | 730.336 | 1640160 | 35.0748 | 1623600 | 1554000 | 1514880 | 0 | 0 | 1496830 | 702.094 | 0 | 0 | 0 | 0 | 1496830 | 702.094 | 1471320 | 1441889
1888 | 2008-03-20 15:00 | 505 | 842 | 89 | 19.93 | 6.21 | 0 | 29.6384 | 247.371 | 53.8768 | 0 | 505 | 495.914 | 104.494 | 4.7315 | 495.914 | 97.7894 | 0.024697 | 478.649 | 94.1703 | 0.018609 | 555.653 | 555.647 | 1247840 | 31.5153 | 1215570 | 1181210 | 1149710 | 0 | 0 | 1139400 | 706.784 | 0 | 0 | 0 | 0 | 1139400 | 706.784 | 1121340 | 1098911.875
1889 | 2008-03-20 16:00 | 281 | 735 | 55 | 20.44 | 6.21 | 0 | 17.8708 | 257.57 | 68.611 | 0 | 281 | 268.586 | 64.2132 | 2.6328 | 268.586 | 60.0932 | 0.013742 | 245.193 | 57.8692 | 0.010355 | 293.98 | 293.976 | 660196 | 26.5694 | 617403 | 612945 | 597262 | 0 | 0 | 594394 | 699.979 | 0 | 0 | 0 | 0 | 594394 | 699.979 | 585445 | 573736
1890 | 2008-03-20 17:00 | 48 | 360 | 10 | 19.58 | 6.21 | 0 | 5.653 | 266.484 | 83.3924 | 0 | 48 | 44.3905 | 11.9771 | 0.44972 | 44.3905 | 11.2086 | 0.0023474 | 27.3215 | 10.7938 | 0.0017688 | 36.9735 | 36.9729 | 83031.8 | 20.3509 | 63986.7 | 65583.9 | 64157.9 | 0 | 0 | 64116.1 | 625.443 | 0 | 0 | 0 | 2520.78 | 61595.4 | 660 | 59482.4 | 58292.7305
1891 | 2008-03-20 18:00 | 0 | 0 | 0 | 18.71 | 7.74 | 0
1892 | 2008-03-20 19:00 | 0 | 0 | 0 | 17.85 | 7.74 | 0
1893 | 2008-03-20 20:00 | 0 | 0 | 0 | 16.7 | 7.74 | 0
1894 | 2008-03-20 21:00 | 0 | 0 | 0 | 15.55 | 9.9 | 0
1895 | 2008-03-20 22:00 | 0 | 0 | 0 | 14.4 | 9.9 | 0
1896 | 2008-03-20 23:00 | 0 | 0 | 0 | 13.45 | 9.9 | 0
1897 | 2008-03-21 | 0 | 0 | 0 | 12.49 | 7.78 | 0
1898 | 2008-03-21 01:00 | 0 | 0 | 0 | 11.54 | 7.78 | 0
1899 | 2008-03-21 02:00 | 0 | 0 | 0 | 10.89 | 7.78 | 0
1900 | 2008-03-21 03:00 | 0 | 0 | 0 | 10.24 | 6.67 | 0
1901 | 2008-03-21 04:00 | 0 | 0 | 0 | 9.58 | 6.67 | 0
1902 | 2008-03-21 05:00 | 1 | 26 | 1 | 9.12 | 6.67 | 0 | -5.1479 | 85.8106 | 90 | 0 | 1 | 0 | 1.0032 | 0.0093692 | 0 | 0.93882 | 0 | 0 | 0.90408 | 0 | 0.87696 | 0.87697 | 1969.45 | 9.1378 | 187.939 | 184.418 | 183.468 | 0 | 0 | 183.46 | 130.72 | 0 | 0 | 0 | 183.46 | 0 | 660 | 0 | 0
1903 | 2008-03-21 06:00 | 97 | 479 | 36 | 8.65 | 3.42 | 0 | 7.2071 | 94.3391 | 81.6382 | 0 | 97 | 70.7088 | 39.63 | 0.90881 | 20.5504 | 37.0872 | 0.0047437 | 14.5122 | 35.7147 | 0.0035745 | 48.7235 | 48.7209 | 109419 | 9.8682 | 87989.9 | 94744.9 | 83360.9 | 0 | 0 | 83296.3 | 674.79 | 0 | 0 | 0 | 0.16642 | 83296.1 | 675.002 | 80444.1 | 78835.2188
1904 | 2008-03-21 07:00 | 325 | 788 | 63 | 8.18 | 3.42 | 0 | 19.4174 | 103.317 | 66.8519 | 0 | 325 | 309.807 | 73.0439 | 3.045 | 280.145 | 68.3573 | 0.015894 | 258.521 | 65.8274 | 0.011976 | 314.629 | 314.566 | 706438 | 16.0456 | 665581 | 690515 | 636774 | 0 | 0 | 633662 | 727.327 | 0 | 0 | 0 | 0 | 633662 | 727.327 | 623147 | 610684.375
1905 | 2008-03-21 08:00 | 540 | 899 | 75 | 10.59 | 3.42 | 0 | 31.141 | 113.703 | 52.1133 | 0 | 540 | 552.18 | 86.8153 | 5.0594 | 552.18 | 81.245 | 0.026408 | 534.831 | 78.2382 | 0.019899 | 594.696 | 594.692 | 1335520 | 25.4601 | 1306330 | 1303550 | 1267060 | 0 | 0 | 1255290 | 728.917 | 0 | 0 | 0 | 0 | 1255290 | 728.917 | 1233820 | 1209147
1906 | 2008-03-21 09:00 | 717 | 948 | 85 | 13 | 0.98 | 0 | 41.8335 | 126.854 | 37.5014 | 0 | 717 | 751.745 | 98.4162 | 6.7177 | 751.745 | 92.1017 | 0.035064 | 741.954 | 88.693 | 0.026422 | 805.753 | 805.747 | 1809500 | 36.7079 | 1800990 | 1711700 | 1668010 | 0 | 0 | 1646050 | 700.23 | 0 | 0 | 0 | 0 | 1646050 | 700.23 | 1616140 | 1583814.875
1907 | 2008-03-21 10:00 | 813 | 878 | 137 | 15.41 | 0.98 | 0 | 50.5077 | 144.64 | 23.2777 | 0 | 813 | 804.672 | 162.383 | 7.6172 | 804.672 | 151.964 | 0.039759 | 801.107 | 146.34 | 0.029959 | 919.052 | 919.045 | 2063940 | 42.4515 | 2068420 | 1916460 | 1871770 | 0 | 0 | 1842880 | 682.94 | 0 | 0 | 0 | 0 | 1842880 | 682.94 | 1806740 | 1770604.5
1908 | 2008-03-21 11:00 | 915 | 995 | 97 | 17.11 | 0.98 | 0 | 55.5116 | 168.302 | 11.0833 | 0 | 915 | 973.918 | 111.725 | 8.5728 | 973.918 | 104.557 | 0.044747 | 972.992 | 100.687 | 0.033718 | 1041.5 | 1041.5 | 2338940 | 47.7546 | 2358290 | 2133430 | 2082950 | 0 | 0 | 2045960 | 669.886 | 5181.44 | 0 | 0 | 0 | 2040540 | 675.266 | 1996920 | 1956983.5
1909 | 2008-03-21 12:00 | 913 | 996 | 97 | 18.81 | 1.66 | 0 | 55.1841 | 194.843 | 12.2289 | 0 | 913 | 971.368 | 111.72 | 8.5541 | 971.368 | 104.552 | 0.04465 | 970.241 | 100.682 | 0.033644 | 1038.83 | 1038.82 | 2332930 | 48.011 | 2351940 | 2125120 | 2073830 | 0 | 0 | 2036830 | 667.265 | 1949.48 | 0 | 0 | 0 | 2034780 | 670.06 | 1991380 | 1951552.5
1910 | 2008-03-21 13:00 | 840 | 983 | 92 | 20.51 | 1.66 | 0 | 49.6577 | 217.865 | 24.9385 | 0 | 840 | 889.878 | 106.233 | 7.8701 | 889.878 | 99.417 | 0.041079 | 885.303 | 95.7377 | 0.030954 | 951.639 | 951.633 | 2137120 | 47.2601 | 2145480 | 1944250 | 1898340 | 0 | 0 | 1867270 | 667.997 | 0 | 0 | 0 | 0 | 1867270 | 667.997 | 1830430 | 1793823.75
1911 | 2008-03-21 14:00 | 676 | 871 | 109 | 20.93 | 1.66 | 0 | 40.6823 | 235.021 | 39.2387 | 0 | 676 | 673.686 | 129.213 | 6.3336 | 673.686 | 120.922 | 0.033059 | 663.88 | 116.447 | 0.024911 | 756.941 | 756.937 | 1699890 | 42.2073 | 1686100 | 1562280 | 1522920 | 0 | 0 | 1503540 | 680.667 | 0 | 0 | 0 | 0 | 1503540 | 680.667 | 1478650 | 1449074.875
1912 | 2008-03-21 15:00 | 479 | 798 | 82 | 21.36 | 2.64 | 0 | 29.8376 | 247.773 | 53.8713 | 0 | 479 | 470.455 | 96.7662 | 4.4879 | 470.455 | 90.5575 | 0.023425 | 454.082 | 87.206 | 0.017651 | 525.066 | 525.065 | 1179160 | 35.1852 | 1144710 | 1093760 | 1066190 | 0 | 0 | 1056900 | 690.779 | 0 | 0 | 0 | 0 | 1056900 | 690.779 | 1041270 | 1020441.0625
1913 | 2008-03-21 16:00 | 281 | 662 | 76 | 21.79 | 2.64 | 0 | 18.045 | 257.951 | 68.6156 | 0 | 281 | 241.306 | 86.0193 | 2.6328 | 241.306 | 80.5002 | 0.013742 | 220.282 | 77.5209 | 0.010355 | 288.879 | 288.875 | 648738 | 29.3962 | 605969 | 593736 | 578917 | 0 | 0 | 576137 | 689.081 | 0 | 0 | 0 | 0 | 576137 | 689.081 | 567690 | 556336.6875
1914 | 2008-03-21 17:00 | 48 | 329 | 13 | 21.35 | 2.64 | 0 | 5.8163 | 266.853 | 83.4005 | 0 | 48 | 39.6934 | 15.2884 | 0.44972 | 39.6934 | 14.3074 | 0.0023474 | 24.4093 | 13.7779 | 0.0017688 | 37.0433 | 37.0428 | 83188.9 | 22.3254 | 64124.6 | 65047 | 63607.7 | 0 | 0 | 63565.8 | 618.745 | 0 | 0 | 0 | 3814.89 | 59750.9 | 660 | 57694.6 | 56540.6719
1915 | 2008-03-21 18:00 | 0 | 0 | 0 | 20.92 | 3.23 | 0
1916 | 2008-03-21 19:00 | 0 | 0 | 0 | 20.48 | 3.23 | 0
1917 | 2008-03-21 20:00 | 0 | 0 | 0 | 19.39 | 3.23 | 0
1918 | 2008-03-21 21:00 | 0 | 0 | 0 | 18.29 | 2.84 | 0
1919 | 2008-03-21 22:00 | 0 | 0 | 0 | 17.19 | 2.84 | 0
1920 | 2008-03-21 23:00 | 0 | 0 | 0 | 16.16 | 2.84 | 0
1921 | 2008-03-22 | 0 | 0 | 0 | 15.14 | 2.3 | 0
1922 | 2008-03-22 01:00 | 0 | 0 | 0 | 14.11 | 2.3 | 0
1923 | 2008-03-22 02:00 | 0 | 0 | 0 | 13.16 | 2.3 | 0
1924 | 2008-03-22 03:00 | 0 | 0 | 0 | 12.2 | 7.81 | 0
1925 | 2008-03-22 04:00 | 0 | 0 | 0 | 11.25 | 7.81 | 0
1926 | 2008-03-22 05:00 | 1 | 33 | 0 | 10.64 | 7.81 | 0 | -4.8613 | 85.5281 | 90 | 0 | 1 | 0 | 0 | 0.0093692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.64 | 0 | 0 | 0 | 0 | 0 | 0 | 660 | 0 | 0 | 0 | 0 | 0 | 660 | 0 | 0
1927 | 2008-03-22 06:00 | 102 | 493 | 37 | 10.02 | 10.46 | 0 | 7.4937 | 94.0553 | 81.4989 | 0 | 102 | 73.6785 | 40.4917 | 0.95566 | 24.6325 | 37.8936 | 0.0049882 | 17.5327 | 36.4912 | 0.0037587 | 52.4069 | 52.3784 | 117631 | 10.8569 | 95426 | 102284 | 89092.6 | 0 | 0 | 89011.2 | 644.497 | 0 | 0 | 0 | -828.343 | 89839.5 | 666.719 | 86872.7 | 85135.2344
1928 | 2008-03-22 07:00 | 331 | 793 | 63 | 9.4 | 10.46 | 0 | 19.7132 | 103.029 | 66.7091 | 0 | 331 | 314.152 | 72.8902 | 3.1012 | 285.638 | 68.2134 | 0.016187 | 263.8 | 65.6889 | 0.012198 | 319.616 | 319.476 | 717469 | 14.5046 | 676589 | 707116 | 654350 | 0 | 0 | 651131 | 734.334 | 0 | 0 | 0 | 0 | 651131 | 734.334 | 640116 | 627313.6875
1929 | 2008-03-22 08:00 | 547 | 902 | 76 | 11.63 | 10.46 | 0 | 31.4563 | 113.412 | 51.9609 | 0 | 547 | 556.158 | 87.7304 | 5.125 | 556.158 | 82.1015 | 0.026751 | 538.837 | 79.063 | 0.020157 | 599.383 | 599.38 | 1346060 | 21.2069 | 1317250 | 1338340 | 1300070 | 0 | 0 | 1288170 | 744.141 | 0 | 0 | 0 | 0 | 1288170 | 744.141 | 1265290 | 1239979.625
1930 | 2008-03-22 09:00 | 727 | 957 | 85 | 13.86 | 6.05 | 0 | 42.1793 | 126.579 | 37.3282 | 0 | 727 | 760.295 | 98.2292 | 6.8114 | 760.295 | 91.9266 | 0.035553 | 750.503 | 88.5245 | 0.02679 | 813.883 | 813.88 | 1827770 | 31.0048 | 1820160 | 1774070 | 1725600 | 0 | 0 | 1703390 | 720.079 | 0 | 0 | 0 | 0 | 1703390 | 720.079 | 1671150 | 1637731.5
1931 | 2008-03-22 10:00 | 850 | 977 | 93 | 16.09 | 6.05 | 0 | 50.8901 | 144.446 | 23.0551 | 0 | 850 | 897.672 | 107.157 | 7.9638 | 897.672 | 100.282 | 0.041569 | 893.776 | 96.5703 | 0.031323 | 960.666 | 960.659 | 2157400 | 36.3268 | 2166860 | 2064400 | 2012250 | 0 | 0 | 1980860 | 704.437 | 0 | 0 | 0 | 0 | 1980860 | 704.437 | 1939560 | 1900769.625
1932 | 2008-03-22 11:00 | 921 | 997 | 97 | 17.3 | 6.05 | 0 | 55.9132 | 168.316 | 10.7217 | 0 | 921 | 977.573 | 111.511 | 8.629 | 977.573 | 104.356 | 0.045041 | 976.704 | 100.494 | 0.033939 | 1044.91 | 1044.91 | 2346600 | 39.3116 | 2366370 | 2225530 | 2169630 | 0 | 0 | 2132480 | 696.981 | 85421.7 | 0 | 0 | 0 | 2043450 | 732.628 | 1999970 | 1959973.125
1933 | 2008-03-22 12:00 | 900 | 974 | 99 | 18.52 | 5.1 | 0 | 55.5536 | 195.12 | 11.9954 | 0 | 900 | 950.106 | 113.69 | 8.4323 | 950.106 | 106.395 | 0.044014 | 949.045 | 102.458 | 0.033165 | 1019.99 | 1019.99 | 2290630 | 41.3673 | 2307320 | 2149740 | 2096570 | 0 | 0 | 2061080 | 689.506 | 16743.2 | 0 | 0 | 0 | 2043590 | 705.55 | 1999980 | 1959983.5
1934 | 2008-03-22 13:00 | 844 | 983 | 93 | 19.73 | 5.1 | 0 | 49.9595 | 218.276 | 24.8655 | 0 | 844 | 890.007 | 107.125 | 7.9076 | 890.007 | 100.252 | 0.041275 | 885.46 | 96.5417 | 0.031102 | 952.572 | 952.566 | 2139220 | 41.0671 | 2147690 | 2003060 | 1951610 | 0 | 0 | 1920800 | 689.177 | 0 | 0 | 0 | 0 | 1920800 | 689.177 | 1881770 | 1844130.375
1935 | 2008-03-22 14:00 | 708 | 952 | 85 | 20.17 | 5.1 | 0 | 40.922 | 235.446 | 39.2152 | 0 | 708 | 736.891 | 98.1377 | 6.6334 | 736.891 | 91.841 | 0.034624 | 726.18 | 88.442 | 0.02609 | 790.209 | 790.207 | 1774610 | 37.8704 | 1764390 | 1668150 | 1623830 | 0 | 0 | 1602800 | 696.506 | 0 | 0 | 0 | 0 | 1602800 | 696.506 | 1574350 | 1542859.625
1936 | 2008-03-22 15:00 | 519 | 891 | 73 | 20.61 | 4.97 | 0 | 30.035 | 248.177 | 53.8682 | 0 | 519 | 525.406 | 84.2739 | 4.8626 | 525.406 | 78.8668 | 0.025381 | 507.124 | 75.9479 | 0.019125 | 565.598 | 565.598 | 1270190 | 33.3867 | 1238680 | 1193630 | 1164780 | 0 | 0 | 1153960 | 698.996 | 0 | 0 | 0 | 0 | 1153960 | 698.996 | 1135990 | 1113266.875
1937 | 2008-03-22 16:00 | 289 | 743 | 56 | 21.05 | 4.97 | 0 | 18.2179 | 258.332 | 68.6216 | 0 | 289 | 271.676 | 64.8775 | 2.7077 | 271.676 | 60.7148 | 0.014133 | 247.995 | 58.4678 | 0.01065 | 297.28 | 297.277 | 667609 | 27.7654 | 624808 | 616889 | 601043 | 0 | 0 | 598107 | 695.59 | 0 | 0 | 0 | 0 | 598107 | 695.59 | 589254 | 577469.375
1938 | 2008-03-22 17:00 | 66 | 495 | 13 | 20.55 | 4.97 | 0 | 5.9788 | 267.222 | 83.4093 | 0 | 66 | 58.4007 | 15.1837 | 0.61837 | 58.4007 | 14.2095 | 0.0032277 | 35.8794 | 13.6836 | 0.0024321 | 48.0785 | 48.0778 | 107970 | 21.6361 | 86023.3 | 87555.6 | 85542.9 | 0 | 0 | 85471.1 | 636.145 | 0 | 0 | 0 | 1756.53 | 83714.6 | 660 | 80954 | 79334.8828
1939 | 2008-03-22 18:00 | 0 | 2 | 0 | 20.05 | 5.23 | 0
1940 | 2008-03-22 19:00 | 0 | 0 | 0 | 19.55 | 5.23 | 0
1941 | 2008-03-22 20:00 | 0 | 0 | 0 | 18.63 | 5.23 | 0
1942 | 2008-03-22 21:00 | 0 | 0 | 0 | 17.71 | 6.43 | 0
1943 | 2008-03-22 22:00 | 0 | 0 | 0 | 16.79 | 6.43 | 0
1944 | 2008-03-22 23:00 | 0 | 0 | 0 | 15.9 | 6.43 | 0
1945 | 2008-03-23 | 0 | 0 | 0 | 15.01 | 6.23 | 0
1946 | 2008-03-23 01:00 | 0 | 0 | 0 | 14.12 | 6.23 | 0
1947 | 2008-03-23 02:00 | 0 | 0 | 0 | 13.33 | 6.23 | 0
1948 | 2008-03-23 03:00 | 0 | 0 | 0 | 12.55 | 7.71 | 0
1949 | 2008-03-23 04:00 | 0 | 0 | 0 | 11.76 | 7.71 | 0
1950 | 2008-03-23 05:00 | 1 | 38 | 0 | 11.25 | 7.71 | 0 | -4.5746 | 85.2464 | 90 | 0 | 1 | 0 | 0 | 0.0093692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.25 | 0 | 0 | 0 | 0 | 0 | 0 | 660 | 0 | 0 | 0 | 0 | 0 | 660 | 0 | 0
1951 | 2008-03-23 06:00 | 105 | 489 | 38 | 10.74 | 8.06 | 0 | 7.78 | 93.7716 | 81.3597 | 0 | 105 | 74.3552 | 41.353 | 0.98377 | 27.9259 | 38.6997 | 0.0051349 | 20.0278 | 37.2675 | 0.0038693 | 55.5802 | 55.5545 | 124768 | 11.7698 | 101889 | 108692 | 96749.5 | 0 | 0 | 96662.4 | 673.159 | 0 | 0 | 0 | 4.903 | 96657.5 | 673.917 | 93446.4 | 91577.4453
1952 | 2008-03-23 07:00 | 332 | 789 | 62 | 10.24 | 8.06 | 0 | 20.0085 | 102.74 | 66.5672 | 0 | 332 | 313.807 | 71.6866 | 3.1106 | 287.039 | 67.0871 | 0.016236 | 265.301 | 64.6042 | 0.012234 | 320.02 | 320.036 | 718725 | 16.1727 | 677746 | 703238 | 653232 | 0 | 0 | 649983 | 729.505 | 0 | 0 | 0 | 0 | 649983 | 729.505 | 639129 | 626346.625
1953 | 2008-03-23 08:00 | 539 | 840 | 97 | 12.39 | 8.06 | 0 | 31.7708 | 113.119 | 51.8103 | 0 | 539 | 519.017 | 112.882 | 5.05 | 519.017 | 105.639 | 0.026359 | 502.994 | 101.73 | 0.019862 | 586.601 | 586.598 | 1317350 | 23.264 | 1287500 | 1296880 | 1261180 | 0 | 0 | 1249750 | 736.665 | 0 | 0 | 0 | 0 | 1249750 | 736.665 | 1228030 | 1203470.5
1954 | 2008-03-23 09:00 | 698 | 854 | 121 | 14.54 | 4 | 0 | 42.5243 | 126.301 | 37.1579 | 0 | 698 | 680.355 | 142.044 | 6.5397 | 680.355 | 132.93 | 0.034135 | 671.69 | 128.011 | 0.025722 | 775.734 | 775.723 | 1742080 | 33.2101 | 1730290 | 1670130 | 1627260 | 0 | 0 | 1606940 | 709.949 | 0 | 0 | 0 | 0 | 1606940 | 709.949 | 1577930 | 1546373.5
1955 | 2008-03-23 10:00 | 861 | 931 | 136 | 16.69 | 4 | 0 | 51.2719 | 144.25 | 22.837 | 0 | 861 | 856.491 | 160.755 | 8.0669 | 856.491 | 150.44 | 0.042106 | 852.848 | 144.873 | 0.031728 | 967.82 | 967.811 | 2173450 | 39.9833 | 2183770 | 2046850 | 1996130 | 0 | 0 | 1964190 | 692.532 | 0 | 0 | 0 | 0 | 1964190 | 692.532 | 1923530 | 1885062.875
1956 | 2008-03-23 11:00 | 926 | 998 | 98 | 17.92 | 4 | 0 | 56.3143 | 168.331 | 10.3632 | 0 | 926 | 978.85 | 112.387 | 8.6759 | 978.85 | 105.176 | 0.045285 | 978.038 | 101.284 | 0.034123 | 1046.98 | 1046.97 | 2351230 | 43.1184 | 2371260 | 2192030 | 2139540 | 0 | 0 | 2102120 | 684.783 | 56112 | 0 | 0 | 0 | 2043540 | 713.716 | 1999980 | 1959979.75
1957 | 2008-03-23 12:00 | 917 | 992 | 97 | 19.14 | 2.79 | 0 | 55.9219 | 195.402 | 11.7713 | 0 | 917 | 969.19 | 111.292 | 8.5916 | 969.19 | 104.151 | 0.044845 | 968.148 | 100.296 | 0.033792 | 1036.42 | 1036.42 | 2327530 | 46.1588 | 2346250 | 2138510 | 2087550 | 0 | 0 | 2050830 | 673.896 | 8464.7 | 0 | 0 | 0 | 2041970 | 682.555 | 1998330 | 1958358.75
1958 | 2008-03-23 13:00 | 847 | 983 | 93 | 20.37 | 2.79 | 0 | 50.2592 | 218.692 | 24.7988 | 0 | 847 | 890.143 | 106.922 | 7.9357 | 890.143 | 100.061 | 0.041422 | 885.622 | 96.3583 | 0.031212 | 952.551 | 952.548 | 2139180 | 45.2023 | 2147660 | 1965170 | 1917340 | 0 | 0 | 1886430 | 676.282 | 0 | 0 | 0 | 0 | 1886430 | 676.282 | 1848780 | 1811808.625
1959 | 2008-03-23 14:00 | 686 | 876 | 110 | 20.9 | 2.79 | 0 | 41.1596 | 235.875 | 39.1955 | 0 | 686 | 678.251 | 129.762 | 6.4273 | 678.251 | 121.436 | 0.033548 | 668.405 | 116.942 | 0.025279 | 761.811 | 761.806 | 1710820 | 40.7598 | 1697550 | 1583570 | 1544350 | 0 | 0 | 1524620 | 684.004 | 0 | 0 | 0 | 0 | 1524620 | 684.004 | 1498980 | 1468999.375
1960 | 2008-03-23 15:00 | 524 | 894 | 74 | 21.43 | 2.82 | 0 | 30.2307 | 248.581 | 53.8676 | 0 | 524 | 527.017 | 85.1778 | 4.9095 | 527.017 | 79.7127 | 0.025626 | 508.679 | 76.7626 | 0.01931 | 567.897 | 567.89 | 1275340 | 36.2051 | 1244000 | 1183440 | 1153070 | 0 | 0 | 1142240 | 691.596 | 0 | 0 | 0 | 0 | 1142240 | 691.596 | 1124870 | 1102371.75
1961 | 2008-03-23 16:00 | 298 | 762 | 57 | 21.96 | 2.82 | 0 | 18.3896 | 258.714 | 68.6291 | 0 | 298 | 278.378 | 65.7327 | 2.792 | 278.378 | 61.5151 | 0.014573 | 254.1 | 59.2385 | 0.010981 | 303.949 | 303.948 | 682591 | 29.868 | 639785 | 625544 | 609725 | 0 | 0 | 606643 | 688.493 | 0 | 0 | 0 | 0 | 606643 | 688.493 | 597893 | 585934.9375
1962 | 2008-03-23 17:00 | 69 | 508 | 13 | 21.66 | 2.82 | 0 | 6.1406 | 267.591 | 83.4189 | 0 | 69 | 60.0003 | 15.0836 | 0.64648 | 60.0003 | 14.1158 | 0.0033744 | 36.8245 | 13.5934 | 0.0025427 | 48.9079 | 48.9075 | 109834 | 22.9325 | 87687.2 | 88646.8 | 86494.9 | 0 | 0 | 86420.7 | 632.523 | 0 | 0 | 0 | 2347.53 | 84073.2 | 660 | 81302.5 | 79676.4688
1963 | 2008-03-23 18:00 | 0 | 5 | 0 | 21.36 | 2.7 | 0
1964 | 2008-03-23 19:00 | 0 | 0 | 0 | 21.06 | 2.7 | 0
1965 | 2008-03-23 20:00 | 0 | 0 | 0 | 20.27 | 2.7 | 0
1966 | 2008-03-23 21:00 | 0 | 0 | 0 | 19.47 | 0.68 | 0
1967 | 2008-03-23 22:00 | 0 | 0 | 0 | 18.68 | 0.68 | 0
1968 | 2008-03-23 23:00 | 0 | 0 | 0 | 18.16 | 0.68 | 0
1969 | 2008-03-24 | 0 | 0 | 0 | 17.63 | 4.28 | 0
1970 | 2008-03-24 01:00 | 0 | 0 | 0 | 17.11 | 4.28 | 0
1971 | 2008-03-24 02:00 | 0 | 0 | 0 | 16.25 | 4.28 | 0
1972 | 2008-03-24 03:00 | 0 | 0 | 0 | 15.4 | 2.82 | 0
1973 | 2008-03-24 04:00 | 0 | 0 | 0 | 14.54 | 2.82 | 0
1974 | 2008-03-24 05:00 | 1 | 43 | 0 | 13.92 | 2.82 | 0 | -4.2879 | 84.9655 | 90 | 0 | 1 | 0 | 0 | 0.0093692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.92 | 0 | 0 | 0 | 0 | 0 | 0 | 660 | 0 | 0 | 0 | 0 | 0 | 660 | 0 | 0
1975 | 2008-03-24 06:00 | 107 | 481 | 38 | 13.3 | 3.03 | 0 | 8.066 | 93.4882 | 81.2208 | 0 | 107 | 75.0548 | 41.2282 | 1.0025 | 31.0924 | 38.5829 | 0.0052327 | 22.4612 | 37.155 | 0.003943 | 57.8315 | 57.8283 | 129869 | 14.7837 | 106540 | 111954 | 99668.2 | 0 | 0 | 99573.5 | 666.48 | 0 | 0 | 0 | 77.0639 | 99496.4 | 668.779 | 96260.6 | 94335.4297
1976 | 2008-03-24 07:00 | 328 | 772 | 60 | 12.68 | 3.03 | 0 | 20.3031 | 102.45 | 66.4262 | 0 | 328 | 308.892 | 69.4208 | 3.0731 | 283.976 | 64.9666 | 0.016041 | 262.671 | 62.5622 | 0.012087 | 315.488 | 315.452 | 708428 | 20.7738 | 667330 | 678483 | 630137 | 0 | 0 | 626997 | 715.51 | 0 | 0 | 0 | 0 | 626997 | 715.51 | 616968 | 604628.6875
1977 | 2008-03-24 08:00 | 536 | 866 | 76 | 14.8 | 3.03 | 0 | 32.0845 | 112.825 | 51.6614 | 0 | 536 | 537.195 | 87.3892 | 5.0219 | 537.195 | 81.7821 | 0.026213 | 520.754 | 78.7554 | 0.019752 | 581.543 | 581.542 | 1306000 | 29.7211 | 1275730 | 1249660 | 1216430 | 0 | 0 | 1205080 | 713.098 | 0 | 0 | 0 | 0 | 1205080 | 713.098 | 1185380 | 1161677.125
1978 | 2008-03-24 09:00 | 698 | 845 | 124 | 16.91 | 1.64 | 0 | 42.8683 | 126.022 | 36.9905 | 0 | 698 | 673.913 | 144.985 | 6.5397 | 673.913 | 135.682 | 0.034135 | 665.423 | 130.661 | 0.025722 | 772.226 | 772.218 | 1734200 | 38.6459 | 1722040 | 1622140 | 1580150 | 0 | 0 | 1559990 | 692.405 | 0 | 0 | 0 | 0 | 1559990 | 692.405 | 1532980 | 1502321.5
1979 | 2008-03-24 10:00 | 848 | 911 | 135 | 19.03 | 1.64 | 0 | 51.653 | 144.051 | 22.6237 | 0 | 848 | 839.172 | 159.401 | 7.9451 | 839.172 | 149.174 | 0.041471 | 835.674 | 143.653 | 0.031249 | 949.977 | 949.971 | 2133390 | 45.7692 | 2141560 | 1954320 | 1908390 | 0 | 0 | 1877660 | 674.721 | 0 | 0 | 0 | 0 | 1877660 | 674.721 | 1840360 | 1803551.5
1980 | 2008-03-24 11:00 | 930 | 998 | 98 | 20.37 | 1.64 | 0 | 56.7148 | 168.347 | 10.0082 | 0 | 930 | 980.13 | 112.171 | 8.7134 | 980.13 | 104.974 | 0.045481 | 979.373 | 101.089 | 0.034271 | 1048.08 | 1048.08 | 2353720 | 49.8707 | 2373880 | 2126260 | 2076340 | 0 | 0 | 2038870 | 663.318 | 1110.11 | 0 | 0 | 0 | 2037700 | 665.563 | 1994160 | 1954277.25
1981 | 2008-03-24 12:00 | 925 | 997 | 98 | 21.72 | 4.36 | 0 | 56.289 | 195.69 | 11.5571 | 0 | 925 | 974.016 | 112.167 | 8.6665 | 974.016 | 104.97 | 0.045236 | 973.008 | 101.085 | 0.034086 | 1041.9 | 1041.89 | 2339840 | 46.2116 | 2359230 | 2149950 | 2098790 | 0 | 0 | 2061810 | 675.26 | 17349.7 | 0 | 0 | 0 | 2043660 | 690.548 | 1999990 | 1959985.625
1982 | 2008-03-24 13:00 | 851 | 984 | 92 | 23.06 | 4.36 | 0 | 50.5568 | 219.113 | 24.7384 | 0 | 851 | 892.639 | 105.628 | 7.9732 | 892.639 | 98.8506 | 0.041617 | 888.129 | 95.1922 | 0.03136 | 953.852 | 953.846 | 2142090 | 45.4818 | 2150730 | 1965480 | 1918540 | 0 | 0 | 1887530 | 675.239 | 0 | 0 | 0 | 0 | 1887530 | 675.239 | 1849850 | 1812852.125
1983 | 2008-03-24 14:00 | 683 | 866 | 111 | 23.4 | 4.36 | 0 | 41.395 | 236.306 | 39.1796 | 0 | 683 | 670.548 | 130.572 | 6.3992 | 670.548 | 122.194 | 0.033402 | 660.823 | 117.672 | 0.025169 | 755.165 | 755.157 | 1695900 | 41.1513 | 1681920 | 1566120 | 1528480 | 0 | 0 | 1509140 | 683.796 | 0 | 0 | 0 | 0 | 1509140 | 683.796 | 1483980 | 1454299
1984 | 2008-03-24 15:00 | 509 | 870 | 69 | 23.74 | 5.11 | 0 | 30.4246 | 248.988 | 53.8693 | 0 | 509 | 512.312 | 79.5773 | 4.7689 | 512.312 | 74.4714 | 0.024892 | 494.484 | 71.7153 | 0.018757 | 549.232 | 549.227 | 1233430 | 36.0345 | 1200680 | 1143000 | 1114570 | 0 | 0 | 1104410 | 689.565 | 0 | 0 | 0 | 0 | 1104410 | 689.565 | 1087890 | 1066136.25
1985 | 2008-03-24 16:00 | 294 | 743 | 57 | 24.08 | 5.11 | 0 | 18.56 | 259.096 | 68.6379 | 0 | 294 | 271.224 | 65.5367 | 2.7546 | 271.224 | 61.3318 | 0.014378 | 247.556 | 59.0619 | 0.010834 | 297.43 | 297.427 | 667947 | 30.7379 | 625145 | 608719 | 593431 | 0 | 0 | 590475 | 684.464 | 0 | 0 | 0 | 0 | 590475 | 684.464 | 582031 | 570390.125
1986 | 2008-03-24 17:00 | 69 | 495 | 13 | 23.4 | 5.11 | 0 | 6.3017 | 267.96 | 83.429 | 0 | 69 | 58.3835 | 14.9877 | 0.64648 | 58.3835 | 14.0261 | 0.0033744 | 35.7933 | 13.507 | 0.0025427 | 47.8237 | 47.8231 | 107398 | 24.4705 | 85513.2 | 85751.5 | 83802.2 | 0 | 0 | 83730.7 | 624.476 | 0 | 0 | 0 | 3728.27 | 80002.5 | 660 | 77346.4 | 75799.4766
1987 | 2008-03-24 18:00 | 0 | 8 | 0 | 22.73 | 7.29 | 0
1988 | 2008-03-24 19:00 | 0 | 0 | 0 | 22.05 | 7.29 | 0
1989 | 2008-03-24 20:00 | 0 | 0 | 0 | 20.88 | 7.29 | 0
1990 | 2008-03-24 21:00 | 0 | 0 | 0 | 19.7 | 7.71 | 0
1991 | 2008-03-24 22:00 | 0 | 0 | 0 | 18.53 | 7.71 | 0
1992 | 2008-03-24 23:00 | 0 | 0 | 0 | 17.5 | 7.71 | 0
1993 | 2008-03-25 | 0 | 0 | 0 | 16.48 | 9.44 | 0
1994 | 2008-03-25 01:00 | 0 | 0 | 0 | 15.46 | 9.44 | 0
1995 | 2008-03-25 02:00 | 0 | 0 | 0 | 14.63 | 9.44 | 0
1996 | 2008-03-25 03:00 | 0 | 0 | 0 | 13.8 | 7.19 | 0
1997 | 2008-03-25 04:00 | 0 | 0 | 0 | 12.97 | 7.19 | 0
1998 | 2008-03-25 05:00 | 2 | 50 | 1 | 12.59 | 7.19 | 0 | -4.0014 | 84.6854 | 90 | 0 | 2 | 0 | 0.70247 | 0.018738 | 0 | 0.6574 | 0 | 0 | 0.63307 | 0 | 0.61408 | 0.61402 | 1378.93 | 12.602 | 92.2212 | 90.8647 | 90.1452 | 0 | 0 | 90.1416 | 95.1653 | 0 | 0 | 0 | 90.1416 | 0 | 660 | 0 | 0
1999 | 2008-03-25 06:00 | 113 | 491 | 41 | 12.2 | 9.08 | 0 | 8.3515 | 93.205 | 81.0823 | 0 | 113 | 76.8424 | 44.0544 | 1.0587 | 34.4994 | 41.2278 | 0.0055262 | 25.0966 | 39.702 | 0.0041641 | 62.8587 | 62.8691 | 141190 | 13.2935 | 116816 | 123661 | 110073 | 0 | 0 | 109959 | 673.781 | 0 | 0 | 0 | 9.0072 | 109950 | 674.555 | 106388 | 104260.2031
2000 | 2008-03-25 07:00 | 344 | 799 | 63 | 11.82 | 9.08 | 0 | 20.5969 | 102.161 | 66.2863 | 0 | 344 | 321.238 | 72.4215 | 3.223 | 296.964 | 67.7748 | 0.016823 | 274.892 | 65.2665 | 0.012677 | 329.966 | 329.915 | 740916 | 17.5583 | 699872 | 722048 | 669514 | 0 | 0 | 666106 | 729.306 | 0 | 0 | 0 | 0 | 666106 | 729.306 | 655008 | 641907.5
2001 | 2008-03-25 08:00 | 553 | 893 | 75 | 13.85 | 9.08 | 0 | 32.3971 | 112.53 | 51.5145 | 0 | 553 | 555.2 | 86.1386 | 5.1812 | 555.2 | 80.6118 | 0.027044 | 538.352 | 77.6284 | 0.020378 | 597.521 | 597.516 | 1341870 | 24.2427 | 1312910 | 1317000 | 1281290 | 0 | 0 | 1269380 | 733.697 | 0 | 0 | 0 | 0 | 1269380 | 733.697 | 1247410 | 1222459
2002 | 2008-03-25 09:00 | 743 | 959 | 87 | 15.88 | 7.16 | 0 | 43.2112 | 125.74 | 36.8264 | 0 | 743 | 766.915 | 99.8498 | 6.9613 | 766.915 | 93.4432 | 0.036336 | 757.356 | 89.9849 | 0.02738 | 821.947 | 821.944 | 1845880 | 32.0086 | 1839160 | 1784870 | 1736420 | 0 | 0 | 1713730 | 716.838 | 0 | 0 | 0 | 0 | 1713730 | 716.838 | 1681260 | 1647633.125
2003 | 2008-03-25 10:00 | 871 | 987 | 94 | 17.91 | 7.16 | 0 | 52.0332 | 143.85 | 22.4154 | 0 | 871 | 911.114 | 107.636 | 8.1606 | 911.114 | 100.73 | 0.042596 | 907.391 | 97.0024 | 0.032097 | 974.292 | 974.289 | 2188010 | 37.028 | 2199110 | 2088780 | 2033810 | 0 | 0 | 2001680 | 703.376 | 0 | 0 | 0 | 0 | 2001680 | 703.376 | 1959620 | 1920422.75
2004 | 2008-03-25 11:00 | 934 | 998 | 98 | 19.29 | 7.16 | 0 | 57.1147 | 168.364 | 9.6572 | 0 | 934 | 981.416 | 111.955 | 8.7508 | 981.416 | 104.772 | 0.045677 | 980.71 | 100.894 | 0.034418 | 1049.19 | 1049.18 | 2356210 | 39.8776 | 2376510 | 2229500 | 2174250 | 0 | 0 | 2136720 | 694.852 | 89466.3 | 0 | 0 | 0 | 2043450 | 731.619 | 1999970 | 1959972
2005 | 2008-03-25 12:00 | 929 | 997 | 98 | 20.67 | 5.17 | 0 | 56.6547 | 195.983 | 11.3535 | 0 | 929 | 975.299 | 111.952 | 8.704 | 975.299 | 104.769 | 0.045432 | 974.325 | 100.891 | 0.034234 | 1042.99 | 1042.99 | 2342280 | 43.9266 | 2361810 | 2175240 | 2122430 | 0 | 0 | 2085120 | 680.186 | 39756.4 | 0 | 0 | 0 | 2043580 | 706.68 | 1999980 | 1959981
2006 | 2008-03-25 13:00 | 854 | 984 | 92 | 22.04 | 5.17 | 0 | 50.8523 | 219.538 | 24.6843 | 0 | 854 | 892.782 | 105.427 | 8.0013 | 892.782 | 98.6628 | 0.041764 | 888.293 | 95.0114 | 0.03147 | 953.835 | 953.832 | 2142060 | 43.3086 | 2150690 | 1985410 | 1936950 | 0 | 0 | 1905840 | 680.928 | 0 | 0 | 0 | 0 | 1905840 | 680.928 | 1867420 | 1830076.5
2007 | 2008-03-25 14:00 | 718 | 953 | 86 | 22.45 | 5.17 | 0 | 41.6283 | 236.74 | 39.1673 | 0 | 718 | 737.613 | 98.655 | 6.7271 | 737.613 | 92.3251 | 0.035113 | 726.925 | 88.9082 | 0.026458 | 791.384 | 791.378 | 1777230 | 40.0962 | 1767140 | 1653910 | 1611500 | 0 | 0 | 1590290 | 687.733 | 0 | 0 | 0 | 0 | 1590290 | 687.733 | 1562500 | 1531253.75
2008 | 2008-03-25 15:00 | 531 | 895 | 75 | 22.86 | 7.26 | 0 | 30.6167 | 249.395 | 53.8733 | 0 | 531 | 527.88 | 85.8971 | 4.9751 | 527.88 | 80.3857 | 0.025968 | 509.506 | 77.4107 | 0.019568 | 569.328 | 569.326 | 1278570 | 33.9609 | 1247340 | 1198900 | 1166770 | 0 | 0 | 1155930 | 699.78 | 0 | 0 | 0 | 0 | 1155930 | 699.78 | 1137880 | 1115122.375
2009 | 2008-03-25 16:00 | 297 | 749 | 56 | 23.26 | 7.26 | 0 | 18.7291 | 259.478 | 68.648 | 0 | 297 | 273.275 | 64.2911 | 2.7827 | 273.275 | 60.1661 | 0.014524 | 249.411 | 57.9394 | 0.010944 | 298.141 | 298.14 | 669547 | 29.0732 | 626744 | 615066 | 600268 | 0 | 0 | 597303 | 691.28 | 0 | 0 | 0 | 0 | 597303 | 691.28 | 588589 | 576817.5
2010 | 2008-03-25 17:00 | 71 | 499 | 13 | 22.29 | 7.26 | 0 | 6.462 | 268.328 | 83.4396 | 0 | 71 | 58.8796 | 14.8957 | 0.66522 | 58.8796 | 13.94 | 0.0034722 | 36.056 | 13.4241 | 0.0026164 | 47.9983 | 47.9977 | 107791 | 23.2259 | 85863.1 | 86670.6 | 84649.5 | 0 | 0 | 84578 | 630.512 | 0 | 0 | 0 | 2728.29 | 81849.8 | 660 | 79141.4 | 77558.6094
2011 | 2008-03-25 18:00 | 0 | 12 | 0 | 21.31 | 8.3 | 0
2012 | 2008-03-25 19:00 | 0 | 0 | 0 | 20.34 | 8.3 | 0
2013 | 2008-03-25 20:00 | 0 | 0 | 0 | 19.09 | 8.3 | 0
2014 | 2008-03-25 21:00 | 0 | 0 | 0 | 17.84 | 8.75 | 0
2015 | 2008-03-25 22:00 | 0 | 0 | 0 | 16.59 | 8.75 | 0
2016 | 2008-03-25 23:00 | 0 | 0 | 0 | 15.88 | 8.75 | 0
2017 | 2008-03-26 | 0 | 0 | 0 | 15.17 | 10.11 | 0
2018 | 2008-03-26 01:00 | 0 | 0 | 0 | 14.46 | 10.11 | 0
2019 | 2008-03-26 02:00 | 0 | 0 | 0 | 13.75 | 10.11 | 0
2020 | 2008-03-26 03:00 | 0 | 0 | 0 | 13.04 | 10.36 | 0
2021 | 2008-03-26 04:00 | 0 | 0 | 0 | 12.33 | 10.36 | 0
2022 | 2008-03-26 05:00 | 2 | 62 | 0 | 12.23 | 10.36 | 0 | -3.7152 | 84.4061 | 90 | 0 | 2 | 0 | 0 | 0.018738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.23 | 0 | 0 | 0 | 0 | 0 | 0 | 660 | 0 | 0 | 0 | 0 | 0 | 660 | 0 | 0
2023 | 2008-03-26 06:00 | 125 | 548 | 42 | 12.13 | 9.16 | 0 | 8.6365 | 92.922 | 80.9443 | 0 | 125 | 86.996 | 44.9136 | 1.1711 | 41.8519 | 42.0319 | 0.006113 | 30.6493 | 40.4763 | 0.0046063 | 68.9963 | 69.0044 | 154968 | 13.3243 | 129561 | 137035 | 120768 | 0 | 0 | 120632 | 679.908 | 0 | 0 | 0 | 1.9325 | 120630 | 680.079 | 116752 | 114417.3828
2024 | 2008-03-26 07:00 | 348 | 800 | 62 | 12.03 | 9.16 | 0 | 20.8899 | 101.87 | 66.1476 | 0 | 348 | 324.347 | 71.2128 | 3.2605 | 301.296 | 66.6437 | 0.017019 | 279.107 | 64.1772 | 0.012824 | 332.998 | 332.966 | 747770 | 17.7927 | 706728 | 728398 | 675074 | 0 | 0 | 671614 | 729.837 | 0 | 0 | 0 | 0 | 671614 | 729.837 | 660406 | 647197.75
2025 | 2008-03-26 08:00 | 560 | 897 | 75 | 13.65 | 9.16 | 0 | 32.7085 | 112.234 | 51.3697 | 0 | 560 | 560.328 | 85.9722 | 5.2468 | 560.328 | 80.4561 | 0.027386 | 543.467 | 77.4784 | 0.020636 | 602.338 | 602.334 | 1352690 | 24.0747 | 1324130 | 1329190 | 1293970 | 0 | 0 | 1281850 | 734.099 | 0 | 0 | 0 | 0 | 1281850 | 734.099 | 1259610 | 1234414.75
2026 | 2008-03-26 09:00 | 748 | 960 | 87 | 15.28 | 10.21 | 0 | 43.5529 | 125.456 | 36.6654 | 0 | 748 | 769.512 | 99.6623 | 7.0082 | 769.512 | 93.2678 | 0.03658 | 760.021 | 89.816 | 0.027564 | 824.369 | 824.366 | 1851320 | 28.6542 | 1844870 | 1816490 | 1767550 | 0 | 0 | 1744750 | 728.186 | 0 | 0 | 0 | 0 | 1744750 | 728.186 | 1711040 | 1676822.625
2027 | 2008-03-26 10:00 | 869 | 925 | 137 | 16.91 | 10.21 | 0 | 52.4124 | 143.645 | 22.2123 | 0 | 869 | 855.199 | 153.045 | 8.1418 | 855.199 | 143.225 | 0.042498 | 851.771 | 137.925 | 0.032023 | 960.036 | 960.024 | 2155980 | 32.4851 | 2165350 | 2097880 | 2043490 | 0 | 0 | 2012280 | 717.202 | 0 | 0 | 0 | 0 | 2012280 | 717.202 | 1969840 | 1930445.125
2028 | 2008-03-26 11:00 | 889 | 876 | 152 | 17.9 | 10.21 | 0 | 57.5139 | 168.382 | 9.3107 | 0 | 889 | 862.207 | 178.401 | 8.3292 | 862.207 | 166.954 | 0.043476 | 861.632 | 160.775 | 0.03276 | 991.767 | 991.757 | 2227230 | 33.9899 | 2240460 | 2156740 | 2101170 | 0 | 0 | 2067800 | 713.114 | 23363.7 | 0 | 0 | 0 | 2043460 | 732.329 | 1999980 | 1959981
2029 | 2008-03-26 12:00 | 870 | 847 | 161 | 18.89 | 8.31 | 0 | 57.019 | 196.282 | 11.1608 | 0 | 870 | 829.219 | 187.767 | 8.1512 | 829.219 | 175.72 | 0.042547 | 828.42 | 169.216 | 0.03206 | 967.738 | 967.728 | 2173280 | 36.5499 | 2183580 | 2078380 | 2026650 | 0 | 0 | 1994860 | 704.723 | 0 | 0 | 0 | 0 | 1994860 | 704.723 | 1953040 | 1913981.25
2030 | 2008-03-26 13:00 | 858 | 931 | 134 | 19.88 | 8.31 | 0 | 51.1455 | 219.969 | 24.6363 | 0 | 858 | 845.076 | 149.834 | 8.0388 | 845.076 | 140.22 | 0.04196 | 840.845 | 135.031 | 0.031618 | 946.63 | 946.622 | 2125870 | 37.1548 | 2133640 | 2025270 | 1974290 | 0 | 0 | 1943850 | 701.593 | 0 | 0 | 0 | 0 | 1943850 | 701.593 | 1903890 | 1865816.125
2031 | 2008-03-26 14:00 | 721 | 953 | 86 | 20.01 | 8.31 | 0 | 41.8593 | 237.176 | 39.1586 | 0 | 721 | 737.864 | 98.465 | 6.7552 | 737.864 | 92.1473 | 0.03526 | 727.178 | 88.737 | 0.026569 | 791.463 | 791.46 | 1777420 | 34.4532 | 1767340 | 1696740 | 1652880 | 0 | 0 | 1631690 | 706.141 | 0 | 0 | 0 | 0 | 1631690 | 706.141 | 1602040 | 1570003.625
2032 | 2008-03-26 15:00 | 525 | 888 | 70 | 20.15 | 8.4 | 0 | 30.8071 | 249.803 | 53.8794 | 0 | 525 | 523.708 | 80.3246 | 4.9188 | 523.708 | 75.1708 | 0.025675 | 505.473 | 72.3888 | 0.019346 | 560.545 | 560.542 | 1258830 | 30.3217 | 1226930 | 1198640 | 1167470 | 0 | 0 | 1156920 | 710.074 | 0 | 0 | 0 | 0 | 1156920 | 710.074 | 1138350 | 1115579.875
2033 | 2008-03-26 16:00 | 300 | 753 | 56 | 20.29 | 8.4 | 0 | 18.8971 | 259.861 | 68.6594 | 0 | 300 | 274.168 | 64.0963 | 2.8108 | 274.168 | 59.9838 | 0.014671 | 250.207 | 57.7638 | 0.011055 | 298.742 | 298.737 | 670887 | 25.711 | 628083 | 626010 | 609433 | 0 | 0 | 606478 | 702.833 | 0 | 0 | 0 | 0 | 606478 | 702.833 | 597295 | 585349.375
2034 | 2008-03-26 17:00 | 73 | 502 | 14 | 19.25 | 8.4 | 0 | 6.6216 | 268.696 | 83.4506 | 0 | 73 | 58.3591 | 15.8972 | 0.68395 | 58.3591 | 14.8772 | 0.00357 | 35.6944 | 14.3266 | 0.0026901 | 48.5231 | 48.5228 | 108970 | 20.1305 | 86915.4 | 89153 | 87044.4 | 0 | 0 | 86971.3 | 640.742 | 0 | 0 | 0 | 996.347 | 85974.9 | 660 | 83151.4 | 81488.3516
2035 | 2008-03-26 18:00 | 0 | 15 | 0 | 18.22 | 10.54 | 0
2036 | 2008-03-26 19:00 | 0 | 0 | 0 | 17.18 | 10.54 | 0
2037 | 2008-03-26 20:00 | 0 | 0 | 0 | 16.07 | 10.54 | 0
2038 | 2008-03-26 21:00 | 0 | 0 | 0 | 14.96 | 8.97 | 0
2039 | 2008-03-26 22:00 | 0 | 0 | 0 | 13.85 | 8.97 | 0
2040 | 2008-03-26 23:00 | 0 | 0 | 0 | 13.11 | 8.97 | 0
2041 | 2008-03-27 | 0 | 0 | 0 | 12.37 | 9.93 | 0
2042 | 2008-03-27 01:00 | 0 | 0 | 0 | 11.62 | 9.93 | 0
2043 | 2008-03-27 02:00 | 0 | 0 | 0 | 10.89 | 9.93 | 0
2044 | 2008-03-27 03:00 | 0 | 0 | 0 | 10.16 | 14.03 | 0
2045 | 2008-03-27 04:00 | 0 | 0 | 0 | 9.42 | 14.03 | 0
2046 | 2008-03-27 05:00 | 3 | 68 | 1 | 9.3 | 14.03 | 0 | -3.4294 | 84.1277 | 90 | 0 | 3 | 0 | 0.73228 | 0.028108 | 0 | 0.6853 | 0 | 0 | 0.65993 | 0 | 0.64014 | 0.64009 | 1437.47 | 9.3083 | 100.214 | 98.3485 | 97.591 | 0 | 0 | 97.5871 | 98.7439 | 0 | 0 | 0 | 97.5871 | 0 | 660 | 0 | 0
2047 | 2008-03-27 06:00 | 126 | 544 | 41 | 9.18 | 8.39 | 0 | 8.9207 | 92.6392 | 80.8069 | 0 | 126 | 87.5742 | 43.8073 | 1.1805 | 44.7309 | 40.9965 | 0.0061619 | 32.9683 | 39.4793 | 0.0046431 | 70.2786 | 70.3095 | 157899 | 10.4567 | 132277 | 141789 | 125104 | 0 | 0 | 124960 | 684.558 | 0 | 0 | 0 | 0 | 124960 | 684.558 | 120935 | 118516.4844
2048 | 2008-03-27 07:00 | 357 | 808 | 65 | 9.06 | 8.39 | 0 | 21.1817 | 101.58 | 66.0102 | 0 | 357 | 328.566 | 74.1982 | 3.3448 | 306.676 | 69.4375 | 0.017459 | 284.295 | 66.8676 | 0.013156 | 340.64 | 340.649 | 765034 | 15.2454 | 723979 | 754265 | 700004 | 0 | 0 | 696395 | 741.169 | 0 | 0 | 0 | 0 | 696395 | 741.169 | 684388 | 670699.75
2049 | 2008-03-27 08:00 | 573 | 909 | 78 | 10.64 | 8.39 | 0 | 33.0187 | 111.936 | 51.227 | 0 | 573 | 568.875 | 89.0374 | 5.3686 | 568.875 | 83.3246 | 0.028022 | 551.899 | 80.2408 | 0.021115 | 613.196 | 613.192 | 1377080 | 21.7741 | 1349440 | 1367740 | 1329530 | 0 | 0 | 1317020 | 741.83 | 0 | 0 | 0 | 0 | 1317020 | 741.83 | 1293680 | 1267810.875
2050 | 2008-03-27 09:00 | 752 | 960 | 87 | 12.22 | 5.68 | 0 | 43.8931 | 125.169 | 36.5079 | 0 | 752 | 770.948 | 99.4756 | 7.0457 | 770.948 | 93.093 | 0.036776 | 761.538 | 89.6477 | 0.027711 | 825.677 | 825.668 | 1854240 | 30.0329 | 1847930 | 1808730 | 1760080 | 0 | 0 | 1737160 | 723.401 | 0 | 0 | 0 | 0 | 1737160 | 723.401 | 1703800 | 1669724.25
2051 | 2008-03-27 10:00 | 879 | 988 | 94 | 13.8 | 5.68 | 0 | 52.7904 | 143.438 | 22.0147 | 0 | 879 | 913.784 | 107.229 | 8.2355 | 913.784 | 100.349 | 0.042987 | 910.191 | 96.6351 | 0.032391 | 976.653 | 976.65 | 2193300 | 34.8701 | 2204690 | 2113990 | 2056750 | 0 | 0 | 2024550 | 710.83 | 0 | 0 | 0 | 0 | 2024550 | 710.83 | 1981670 | 1942033.875
2052 | 2008-03-27 11:00 | 914 | 911 | 144 | 15.36 | 5.68 | 0 | 57.9121 | 168.4 | 8.9692 | 0 | 914 | 897.726 | 160.159 | 8.5635 | 897.726 | 149.883 | 0.044698 | 897.171 | 144.336 | 0.033681 | 1010.29 | 1010.29 | 2268840 | 37.1558 | 2284340 | 2168730 | 2112680 | 0 | 0 | 2078040 | 703.46 | 33151.2 | 0 | 0 | 0 | 2043490 | 726.099 | 1999980 | 1959980
2053 | 2008-03-27 12:00 | 936 | 997 | 98 | 16.92 | 2.02 | 0 | 57.3817 | 196.586 | 10.9796 | 0 | 936 | 976.706 | 111.523 | 8.7696 | 976.706 | 104.367 | 0.045774 | 975.796 | 100.505 | 0.034492 | 1044.04 | 1044.04 | 2344640 | 45.5694 | 2364300 | 2160940 | 2108580 | 0 | 0 | 2071360 | 676.807 | 26527.3 | 0 | 0 | 0 | 2043630 | 696.849 | 1999980 | 1959982.625
2054 | 2008-03-27 13:00 | 861 | 891 | 166 | 18.49 | 2.02 | 0 | 51.4364 | 220.404 | 24.5945 | 0 | 861 | 808.202 | 190.571 | 8.0669 | 808.202 | 178.344 | 0.042106 | 804.17 | 171.744 | 0.031728 | 946.667 | 946.653 | 2125940 | 44.4669 | 2133710 | 1959000 | 1911960 | 0 | 0 | 1881360 | 677.843 | 0 | 0 | 0 | 0 | 1881360 | 677.843 | 1843890 | 1807009
2055 | 2008-03-27 14:00 | 631 | 664 | 186 | 19.24 | 2.02 | 0 | 42.0881 | 237.615 | 39.1534 | 0 | 631 | 514.833 | 210.904 | 5.912 | 514.833 | 197.372 | 0.030859 | 507.38 | 190.068 | 0.023252 | 676.547 | 676.55 | 1519350 | 37.8051 | 1497470 | 1415180 | 1377950 | 0 | 0 | 1362530 | 691.658 | 0 | 0 | 0 | 0 | 1362530 | 691.658 | 1340480 | 1313667.25
2056 | 2008-03-27 15:00 | 451 | 592 | 146 | 19.98 | 4.89 | 0 | 30.9957 | 250.211 | 53.8876 | 0 | 451 | 349.063 | 162.667 | 4.2255 | 349.063 | 152.23 | 0.022056 | 336.903 | 146.596 | 0.016619 | 469.011 | 469 | 1053250 | 30.6299 | 1015340 | 990189 | 966710 | 0 | 0 | 959296 | 702.008 | 0 | 0 | 0 | 0 | 959296 | 702.008 | 944810 | 925913.6875
2057 | 2008-03-27 16:00 | 296 | 593 | 102 | 20.73 | 4.89 | 0 | 19.0638 | 260.243 | 68.6718 | 0 | 296 | 216.03 | 110.215 | 2.7733 | 216.03 | 103.144 | 0.014476 | 197.133 | 99.3265 | 0.010908 | 287.576 | 287.568 | 645807 | 27.26 | 603047 | 596775 | 581686 | 0 | 0 | 578938 | 695.979 | 0 | 0 | 0 | 0 | 578938 | 695.979 | 570255 | 558849.625
2058 | 2008-03-27 17:00 | 73 | 395 | 25 | 19.92 | 4.89 | 0 | 6.7806 | 269.064 | 83.462 | 0 | 73 | 46.2904 | 26.9867 | 0.68395 | 46.2904 | 25.2552 | 0.00357 | 28.2776 | 24.3205 | 0.0026901 | 51.0227 | 51.0213 | 114581 | 21.0786 | 91933.9 | 93834.8 | 91545.6 | 0 | 0 | 91464.7 | 640.507 | 0 | 0 | 0 | 1120.09 | 90344.6 | 660 | 87401.2 | 85653.1875
2059 | 2008-03-27 18:00 | 0 | 14 | 0 | 19.1 | 6.17 | 0
2060 | 2008-03-27 19:00 | 0 | 0 | 0 | 18.29 | 6.17 | 0
2061 | 2008-03-27 20:00 | 0 | 0 | 0 | 17.17 | 6.17 | 0
2062 | 2008-03-27 21:00 | 0 | 0 | 0 | 16.06 | 8.15 | 0
2063 | 2008-03-27 22:00 | 0 | 0 | 0 | 14.94 | 8.15 | 0
2064 | 2008-03-27 23:00 | 0 | 0 | 0 | 13.84 | 8.15 | 0
2065 | 2008-03-28 | 0 | 0 | 0 | 12.74 | 7.35 | 0
2066 | 2008-03-28 01:00 | 0 | 0 | 0 | 11.64 | 7.35 | 0
2067 | 2008-03-28 02:00 | 0 | 0 | 0 | 10.53 | 7.35 | 0
2068 | 2008-03-28 03:00 | 0 | 0 | 0 | 9.42 | 6.56 | 0
2069 | 2008-03-28 04:00 | 0 | 0 | 0 | 8.3 | 6.56 | 0
2070 | 2008-03-28 05:00 | 3 | 77 | 1 | 8.89 | 6.56 | 0 | -3.1443 | 83.8501 | 90 | 0 | 3 | 0 | 0.73032 | 0.028108 | 0 | 0.68346 | 0 | 0 | 0.65817 | 0 | 0.63842 | 0.63838 | 1433.64 | 8.903 | 99.6785 | 97.7753 | 97.0233 | 0 | 0 | 97.0195 | 98.4897 | 0 | 0 | 0 | 97.0195 | 0 | 660 | 0 | 0
2071 | 2008-03-28 06:00 | 135 | 567 | 43 | 9.48 | 6.02 | 0 | 9.204 | 92.3567 | 80.6702 | 0 | 135 | 93.2473 | 45.6489 | 1.2648 | 50.2087 | 42.72 | 0.0066021 | 37.2339 | 41.1389 | 0.0049748 | 76.0264 | 76.0374 | 170756 | 11.0849 | 144157 | 153961 | 136413 | 0 | 0 | 136243 | 684.867 | 0 | 0 | 0 | 0 | 136243 | 684.867 | 131959 | 129319.5938
2072 | 2008-03-28 07:00 | 356 | 803 | 62 | 10.08 | 6.02 | 0 | 21.4724 | 101.289 | 65.8741 | 0 | 356 | 328.286 | 70.8945 | 3.3354 | 307.938 | 66.3458 | 0.01741 | 285.666 | 63.8904 | 0.013119 | 339.082 | 339.131 | 761628 | 17.2378 | 720499 | 744262 | 690457 | 0 | 0 | 686895 | 735.754 | 0 | 0 | 0 | 0 | 686895 | 735.754 | 675219 | 661714.4375
2073 | 2008-03-28 08:00 | 566 | 893 | 76 | 12.16 | 6.02 | 0 | 33.3273 | 111.637 | 51.0866 | 0 | 566 | 560.21 | 86.7197 | 5.303 | 560.21 | 81.1557 | 0.02768 | 543.628 | 78.1521 | 0.020857 | 603.147 | 603.142 | 1354500 | 24.89 | 1326010 | 1326440 | 1289910 | 0 | 0 | 1277800 | 731.971 | 0 | 0 | 0 | 0 | 1277800 | 731.971 | 1255740 | 1230621.5
2074 | 2008-03-28 09:00 | 735 | 927 | 89 | 14.25 | 6.12 | 0 | 44.2318 | 124.879 | 36.3539 | 0 | 735 | 745.839 | 101.452 | 6.8864 | 745.839 | 94.9424 | 0.035945 | 736.827 | 91.4287 | 0.027085 | 803.434 | 803.428 | 1804290 | 31.0986 | 1795510 | 1749310 | 1703570 | 0 | 0 | 1681700 | 717.004 | 0 | 0 | 0 | 0 | 1681700 | 717.004 | 1650220 | 1617211
2075 | 2008-03-28 10:00 | 879 | 983 | 94 | 16.33 | 6.12 | 0 | 53.1671 | 143.228 | 21.8227 | 0 | 879 | 910.491 | 107.026 | 8.2355 | 910.491 | 100.159 | 0.042987 | 906.977 | 96.4522 | 0.032391 | 973.358 | 973.354 | 2185900 | 36.7421 | 2196890 | 2089270 | 2034350 | 0 | 0 | 2002260 | 704.21 | 0 | 0 | 0 | 0 | 2002260 | 704.21 | 1960180 | 1920973.75
2076 | 2008-03-28 11:00 | 947 | 999 | 99 | 17.71 | 6.12 | 0 | 58.3094 | 168.418 | 8.6334 | 0 | 947 | 985.303 | 112.39 | 8.8727 | 985.303 | 105.179 | 0.046312 | 984.738 | 101.286 | 0.034897 | 1053.48 | 1053.48 | 2365840 | 39.8024 | 2386680 | 2239780 | 2183290 | 0 | 0 | 2145530 | 695.274 | 97933.2 | 0 | 0 | 0 | 2043440 | 733.561 | 1999970 | 1959968.25
2077 | 2008-03-28 12:00 | 903 | 898 | 145 | 19.08 | 7.54 | 0 | 57.7428 | 196.895 | 10.8102 | 0 | 903 | 880.434 | 160.871 | 8.4604 | 880.434 | 150.549 | 0.04416 | 879.639 | 144.977 | 0.033276 | 993.91 | 993.902 | 2232050 | 38.1186 | 2245550 | 2122760 | 2068710 | 0 | 0 | 2035260 | 700.807 | 1024.58 | 0 | 0 | 0 | 2034180 | 702.91 | 1990920 | 1951103.375
2078 | 2008-03-28 13:00 | 865 | 931 | 135 | 20.45 | 7.54 | 0 | 51.725 | 220.843 | 24.5588 | 0 | 865 | 845.76 | 150.325 | 8.1044 | 845.76 | 140.68 | 0.042302 | 841.554 | 135.474 | 0.031876 | 947.747 | 947.738 | 2128390 | 38.6043 | 2136290 | 2014700 | 1962820 | 0 | 0 | 1932320 | 697.123 | 0 | 0 | 0 | 0 | 1932320 | 697.123 | 1892810 | 1854952.5
2079 | 2008-03-28 14:00 | 693 | 863 | 113 | 20.32 | 7.54 | 0 | 42.3147 | 238.055 | 39.1516 | 0 | 693 | 668.116 | 131.64 | 6.4929 | 668.116 | 123.193 | 0.033891 | 658.444 | 118.634 | 0.025537 | 753.791 | 753.782 | 1692800 | 34.759 | 1678690 | 1609190 | 1567750 | 0 | 0 | 1548560 | 704.847 | 0 | 0 | 0 | 0 | 1548560 | 704.847 | 1521460 | 1491033.875
2080 | 2008-03-28 15:00 | 519 | 869 | 69 | 20.2 | 7.88 | 0 | 31.1825 | 250.621 | 53.8977 | 0 | 519 | 512.109 | 78.9077 | 4.8626 | 512.109 | 73.8449 | 0.025381 | 494.258 | 71.1119 | 0.019125 | 548.428 | 548.425 | 1231620 | 30.4822 | 1198820 | 1170300 | 1141450 | 0 | 0 | 1131300 | 707.857 | 0 | 0 | 0 | 0 | 1131300 | 707.857 | 1113350 | 1091081.5
2081 | 2008-03-28 16:00 | 308 | 761 | 57 | 20.07 | 7.88 | 0 | 19.2293 | 260.625 | 68.6853 | 0 | 308 | 277.019 | 64.7563 | 2.8857 | 277.019 | 60.6014 | 0.015062 | 252.765 | 58.3586 | 0.01135 | 301.801 | 301.797 | 677759 | 25.7283 | 634953 | 632812 | 617089 | 0 | 0 | 614053 | 702.614 | 0 | 0 | 0 | 0 | 614053 | 702.614 | 604762 | 592667.0625
2082 | 2008-03-28 17:00 | 77 | 507 | 14 | 18.86 | 7.88 | 0 | 6.9389 | 269.431 | 83.4736 | 0 | 77 | 59.2713 | 15.7211 | 0.72143 | 59.2713 | 14.7124 | 0.0037656 | 36.1609 | 14.1679 | 0.0028375 | 48.8217 | 48.821 | 109640 | 19.7753 | 87513.6 | 89929.4 | 87790.5 | 0 | 0 | 87716.6 | 643.123 | 0 | 0 | 0 | 831.596 | 86885 | 660 | 84036.3 | 82355.5938
2083 | 2008-03-28 18:00 | 0 | 22 | 0 | 17.65 | 8.54 | 0
2084 | 2008-03-28 19:00 | 0 | 0 | 0 | 16.44 | 8.54 | 0
2085 | 2008-03-28 20:00 | 0 | 0 | 0 | 15.28 | 8.54 | 0
2086 | 2008-03-28 21:00 | 0 | 0 | 0 | 14.13 | 9.21 | 0
2087 | 2008-03-28 22:00 | 0 | 0 | 0 | 12.97 | 9.21 | 0
2088 | 2008-03-28 23:00 | 0 | 0 | 0 | 12.25 | 9.21 | 0
2089 | 2008-03-29 | 0 | 0 | 0 | 11.54 | 9.48 | 0
2090 | 2008-03-29 01:00 | 0 | 0 | 0 | 10.83 | 9.48 | 0
2091 | 2008-03-29 02:00 | 0 | 0 | 0 | 10.25 | 9.48 | 0
2092 | 2008-03-29 03:00 | 0 | 0 | 0 | 9.67 | 10.85 | 0
2093 | 2008-03-29 04:00 | 0 | 0 | 0 | 9.1 | 10.85 | 0
2094 | 2008-03-29 05:00 | 4 | 82 | 1 | 9.02 | 10.85 | 0 | -2.8598 | 83.5734 | 90 | 0 | 4 | 0 | 0.92331 | 0.037477 | 0 | 0.86407 | 0 | 0 | 0.83209 | 0 | 0.80713 | 0.80705 | 1812.42 | 9.0326 | 159.182 | 156.176 | 155.399 | 0 | 0 | 155.392 | 120.378 | 0 | 0 | 0 | 155.392 | 0 | 660 | 0 | 0
2095 | 2008-03-29 06:00 | 135 | 559 | 42 | 8.94 | 9 | 0 | 9.4862 | 92.0745 | 80.5342 | 0 | 135 | 92.8011 | 44.5362 | 1.2648 | 52.4083 | 41.6787 | 0.0066021 | 39.0951 | 40.1362 | 0.0049748 | 76.8592 | 76.8921 | 172672 | 10.2841 | 145924 | 156470 | 138141 | 0 | 0 | 137973 | 695.88 | 0 | 0 | 0 | 0 | 137973 | 695.88 | 133517 | 130846.5
2096 | 2008-03-29 07:00 | 356 | 793 | 62 | 8.86 | 9 | 0 | 21.7618 | 100.997 | 65.7396 | 0 | 356 | 325.827 | 70.7351 | 3.3354 | 306.915 | 66.1966 | 0.01741 | 284.912 | 63.7467 | 0.013119 | 338.212 | 338.162 | 759451 | 14.771 | 718191 | 749920 | 693614 | 0 | 0 | 690092 | 743.456 | 0 | 0 | 0 | 0 | 690092 | 743.456 | 678107 | 664545
2097 | 2008-03-29 08:00 | 578 | 906 | 76 | 10.76 | 9 | 0 | 33.6344 | 111.336 | 50.9485 | 0 | 578 | 570.995 | 86.5552 | 5.4154 | 570.995 | 81.0017 | 0.028267 | 554.229 | 78.0038 | 0.021299 | 613.286 | 613.283 | 1377270 | 21.4801 | 1349640 | 1369630 | 1331690 | 0 | 0 | 1319170 | 743.057 | 0 | 0 | 0 | 0 | 1319170 | 743.057 | 1295720 | 1269808.125
2098 | 2008-03-29 09:00 | 762 | 962 | 88 | 12.66 | 6.43 | 0 | 44.5688 | 124.587 | 36.2036 | 0 | 762 | 774.998 | 100.185 | 7.1394 | 774.998 | 93.7567 | 0.037265 | 765.726 | 90.2868 | 0.02808 | 830.359 | 830.352 | 1864760 | 29.7303 | 1858980 | 1821940 | 1773970 | 0 | 0 | 1750700 | 723.119 | 0 | 0 | 0 | 0 | 1750700 | 723.119 | 1716920 | 1682584.375
2099 | 2008-03-29 10:00 | 888 | 988 | 95 | 14.57 | 6.43 | 0 | 53.5424 | 143.014 | 21.6366 | 0 | 888 | 916.485 | 107.904 | 8.3199 | 916.485 | 100.981 | 0.043427 | 913.011 | 97.2437 | 0.032723 | 979.979 | 979.981 | 2200780 | 34.7164 | 2212580 | 2123010 | 2065060 | 0 | 0 | 2032630 | 711.377 | 0 | 0 | 0 | 0 | 2032630 | 711.377 | 1989450 | 1949663.5
2100 | 2008-03-29 11:00 | 951 | 999 | 99 | 15.84 | 6.43 | 0 | 58.7056 | 168.436 | 8.3039 | 0 | 951 | 986.61 | 112.173 | 8.9101 | 986.61 | 104.976 | 0.046508 | 986.087 | 101.091 | 0.035045 | 1054.6 | 1054.59 | 2368340 | 37.5202 | 2389310 | 2265140 | 2212330 | 0 | 0 | 2174060 | 700.384 | 125396 | 0 | 0 | 0 | 2044000 | 744.83 | 1999990 | 1959990.625
2101 | 2008-03-29 12:00 | 943 | 998 | 98 | 17.11 | 8.27 | 0 | 58.1021 | 197.209 | 10.6533 | 0 | 943 | 978.144 | 111.095 | 8.8352 | 978.144 | 103.967 | 0.046117 | 977.286 | 100.12 | 0.03475 | 1045.12 | 1045.11 | 2347060 | 36.2299 | 2366850 | 2256580 | 2199650 | 0 | 0 | 2162510 | 707.016 | 114431 | 0 | 0 | 0 | 2044290 | 747.425 | 1999980 | 1959978.5
2102 | 2008-03-29 13:00 | 868 | 984 | 94 | 18.37 | 8.27 | 0 | 52.0112 | 221.287 | 24.529 | 0 | 868 | 893.44 | 106.793 | 8.1325 | 893.44 | 99.9409 | 0.042449 | 889.008 | 96.2421 | 0.031986 | 955.724 | 955.718 | 2146290 | 35.8546 | 2155150 | 2057530 | 2002860 | 0 | 0 | 1971980 | 706.759 | 0 | 0 | 0 | 0 | 1971980 | 706.759 | 1930990 | 1892368.75
2103 | 2008-03-29 14:00 | 730 | 955 | 85 | 18.37 | 8.27 | 0 | 42.539 | 238.497 | 39.1531 | 0 | 730 | 739.8 | 96.8209 | 6.8395 | 739.8 | 90.6087 | 0.0357 | 729.089 | 87.2553 | 0.026901 | 791.88 | 791.875 | 1778350 | 32.8571 | 1768310 | 1709640 | 1665210 | 0 | 0 | 1644010 | 711.904 | 0 | 0 | 0 | 0 | 1644010 | 711.904 | 1613820 | 1581544.75
2104 | 2008-03-29 15:00 | 523 | 873 | 69 | 18.37 | 8.05 | 0 | 31.3676 | 251.03 | 53.9098 | 0 | 523 | 513.772 | 78.7431 | 4.9001 | 513.772 | 73.6908 | 0.025577 | 495.851 | 70.9635 | 0.019273 | 549.829 | 549.825 | 1234770 | 28.5688 | 1202070 | 1183440 | 1154020 | 0 | 0 | 1143830 | 714.153 | 0 | 0 | 0 | 0 | 1143830 | 714.153 | 1125320 | 1102818.375
2105 | 2008-03-29 16:00 | 312 | 765 | 58 | 18.37 | 8.05 | 0 | 19.3936 | 261.007 | 68.6997 | 0 | 312 | 277.865 | 65.6065 | 2.9232 | 277.865 | 61.3971 | 0.015258 | 253.512 | 59.1248 | 0.011497 | 303.269 | 303.267 | 681061 | 23.9953 | 638256 | 641116 | 624497 | 0 | 0 | 621440 | 708.339 | 0 | 0 | 0 | 0 | 621440 | 708.339 | 611859 | 599621.875
2106 | 2008-03-29 17:00 | 79 | 510 | 15 | 17.51 | 8.05 | 0 | 7.0965 | 269.797 | 83.4855 | 0 | 79 | 58.7747 | 16.7071 | 0.74017 | 58.7747 | 15.6352 | 0.0038634 | 35.8111 | 15.0565 | 0.0029112 | 49.3444 | 49.3435 | 110813 | 18.4253 | 88561.3 | 91631.5 | 89426.3 | 0 | 0 | 89350.8 | 648.317 | 0 | 0 | 0 | 385.773 | 88965 | 660 | 86059.2 | 84338.0547
2107 | 2008-03-29 18:00 | 0 | 25 | 0 | 16.65 | 10.01 | 0
2108 | 2008-03-29 19:00 | 0 | 0 | 0 | 15.8 | 10.01 | 0
2109 | 2008-03-29 20:00 | 0 | 0 | 0 | 14.7 | 10.01 | 0
2110 | 2008-03-29 21:00 | 0 | 0 | 0 | 13.61 | 9.31 | 0
2111 | 2008-03-29 22:00 | 0 | 0 | 0 | 12.51 | 9.31 | 0
2112 | 2008-03-29 23:00 | 0 | 0 | 0 | 11.72 | 9.31 | 0
2113 | 2008-03-30 | 0 | 0 | 0 | 10.93 | 12.57 | 0
2114 | 2008-03-30 01:00 | 0 | 0 | 0 | 10.14 | 12.57 | 0
2115 | 2008-03-30 02:00 | 0 | 0 | 0 | 9.56 | 12.57 | 0
2116 | 2008-03-30 03:00 | 0 | 0 | 0 | 8.97 | 9.94 | 0
2117 | 2008-03-30 04:00 | 0 | 0 | 0 | 8.39 | 9.94 | 0
2118 | 2008-03-30 05:00 | 4 | 63 | 2 | 8.17 | 9.94 | 0 | -2.5762 | 83.2976 | 90 | 0 | 4 | 0 | 1.4314 | 0.037477 | 0 | 1.3396 | 0 | 0 | 1.29 | 0 | 1.2513 | 1.2512 | 2809.91 | 8.1906 | 381.755 | 374.282 | 372.585 | 0 | 0 | 372.568 | 183.778 | 0 | 0 | 0 | 372.568 | 0 | 660 | 0 | 0
2119 | 2008-03-30 06:00 | 135 | 396 | 67 | 7.94 | 9.74 | 0 | 9.7674 | 91.7925 | 80.3992 | 0 | 135 | 66.851 | 67.1622 | 1.2648 | 39.3526 | 62.853 | 0.0066021 | 29.5226 | 60.5268 | 0.0049748 | 87.3528 | 87.3301 | 196115 | 9.3982 | 167008 | 179892 | 165173 | 0 | 0 | 164953 | 706.657 | 0 | 0 | 0 | 0 | 164953 | 706.657 | 159684 | 156490.8125
2120 | 2008-03-30 07:00 | 251 | 222 | 168 | 7.71 | 9.74 | 0 | 22.0497 | 100.705 | 65.6067 | 0 | 251 | 91.3103 | 165.952 | 2.3517 | 86.4229 | 155.304 | 0.012275 | 80.2811 | 149.556 | 0.0092494 | 222.951 | 222.937 | 500668 | 11.4326 | 459401 | 488004 | 465208 | 0 | 0 | 463654 | 741.647 | 0 | 0 | 0 | 0 | 463654 | 741.647 | 454797 | 445701.4375
2121 | 2008-03-30 08:00 | 273 | 129 | 201 | 8.96 | 9.74 | 0 | 33.9398 | 111.034 | 50.8129 | 0 | 273 | 81.4827 | 201.337 | 2.5578 | 81.4827 | 188.419 | 0.013351 | 79.1089 | 181.446 | 0.01006 | 252.748 | 252.736 | 567582 | 13.1802 | 525314 | 553584 | 537289 | 0 | 0 | 535209 | 739.35 | 0 | 0 | 0 | 0 | 535209 | 739.35 | 525613 | 515100.875
2122 | 2008-03-30 09:00 | 767 | 776 | 220 | 10.21 | 11.57 | 0 | 44.9039 | 124.292 | 36.057 | 0 | 767 | 626.433 | 245.412 | 7.1862 | 626.433 | 229.666 | 0.03751 | 619.011 | 221.166 | 0.028264 | 814.999 | 814.986 | 1830250 | 22.387 | 1822760 | 1842300 | 1790690 | 0 | 0 | 1768440 | 747.509 | 0 | 0 | 0 | 0 | 1768440 | 747.509 | 1733090 | 1698427.75
2123 | 2008-03-30 10:00 | 752 | 517 | 335 | 11.46 | 11.57 | 0 | 53.9162 | 142.797 | 21.4566 | 0 | 752 | 480.229 | 366.597 | 7.0457 | 480.229 | 343.075 | 0.036776 | 478.441 | 330.378 | 0.027711 | 784.581 | 784.57 | 1761950 | 23.1825 | 1751130 | 1764140 | 1713400 | 0 | 0 | 1692900 | 745.013 | 0 | 0 | 0 | 0 | 1692900 | 745.013 | 1660050 | 1626848.375
2124 | 2008-03-30 11:00 | 230 | 22 | 211 | 11.9 | 11.57 | 0 | 59.1006 | 168.455 | 7.9816 | 0 | 230 | 21.9282 | 210.893 | 2.1549 | 21.9282 | 197.361 | 0.011248 | 21.9175 | 190.057 | 0.0084756 | 205.624 | 205.618 | 461766 | 14.9722 | 421110 | 440755 | 427642 | 0 | 0 | 426267 | 724.162 | 0 | 0 | 0 | 0 | 426267 | 724.162 | 418394 | 410026.0312
2125 | 2008-03-30 12:00 | 425 | 68 | 367 | 12.33 | 13.18 | 0 | 58.4596 | 197.529 | 10.5091 | 0 | 425 | 66.9119 | 387.214 | 3.9819 | 66.9119 | 362.37 | 0.020784 | 66.8548 | 348.959 | 0.015661 | 403.354 | 403.332 | 905784 | 17.8085 | 864911 | 892093 | 866810 | 0 | 0 | 861439 | 740.564 | 0 | 0 | 0 | 0 | 861439 | 740.564 | 846774 | 829838.4375
2126 | 2008-03-30 13:00 | 634 | 319 | 382 | 12.77 | 13.18 | 0 | 52.2949 | 221.735 | 24.5052 | 0 | 634 | 289.825 | 404.651 | 5.9401 | 289.825 | 378.688 | 0.031005 | 288.391 | 364.673 | 0.023363 | 633.495 | 633.479 | 1422630 | 21.3746 | 1396780 | 1418040 | 1378050 | 0 | 0 | 1364750 | 745.864 | 0 | 0 | 0 | 0 | 1364750 | 745.864 | 1340190 | 1313390.5
2127 | 2008-03-30 14:00 | 381 | 105 | 310 | 12.75 | 13.18 | 0 | 42.7611 | 238.941 | 39.1578 | 0 | 381 | 81.088 | 325.454 | 3.5697 | 81.088 | 304.572 | 0.018632 | 79.9137 | 293.3 | 0.01404 | 362.031 | 362.021 | 813007 | 17.6674 | 770917 | 795871 | 773043 | 0 | 0 | 768722 | 737.165 | 0 | 0 | 0 | 0 | 768722 | 737.165 | 755763 | 740648.125
2128 | 2008-03-30 15:00 | 368 | 251 | 237 | 12.73 | 8.1 | 0 | 31.551 | 251.44 | 53.9237 | 0 | 368 | 147.425 | 243.781 | 3.4479 | 147.425 | 228.139 | 0.017997 | 142.278 | 219.696 | 0.013561 | 351.128 | 351.113 | 788509 | 19.2224 | 746184 | 765276 | 743252 | 0 | 0 | 739206 | 731.902 | 0 | 0 | 0 | 0 | 739206 | 731.902 | 726938 | 712399.5625
2129 | 2008-03-30 16:00 | 307 | 524 | 131 | 12.71 | 8.1 | 0 | 19.5568 | 261.389 | 68.715 | 0 | 307 | 190.862 | 135.635 | 2.8763 | 190.862 | 126.932 | 0.015014 | 174.116 | 122.235 | 0.011313 | 287.471 | 287.468 | 645582 | 18.0255 | 602826 | 621806 | 603764 | 0 | 0 | 601072 | 730.192 | 0 | 0 | 0 | 0 | 601072 | 730.192 | 591141 | 579317.875
2130 | 2008-03-30 17:00 | 51 | 0 | 51 | 12.05 | 8.1 | 0 | 7.2535 | 270.162 | 83.4975 | 0 | 51 | 0 | 46.8751 | 0.47783 | 0 | 43.8675 | 0.0024941 | 0 | 42.244 | 0.0018794 | 40.9785 | 40.978 | 92026.3 | 12.8077 | 71889.4 | 76531.6 | 74579.6 | 0 | 0 | 74528.7 | 658.672 | 0 | 0 | 0 | 7.6133 | 74521.1 | 660 | 72022.6 | 70582.125
2131 | 2008-03-30 18:00 | 0 | 0 | 0 | 11.39 | 10.33 | 0
2132 | 2008-03-30 19:00 | 0 | 0 | 0 | 10.73 | 10.33 | 0
2133 | 2008-03-30 20:00 | 0 | 0 | 0 | 9.91 | 10.33 | 0
2134 | 2008-03-30 21:00 | 0 | 0 | 0 | 9.08 | 8.71 | 0
2135 | 2008-03-30 22:00 | 0 | 0 | 0 | 8.25 | 8.71 | 0
2136 | 2008-03-30 23:00 | 0 | 0 | 0 | 7.68 | 8.71 | 0
2137 | 2008-03-31 | 0 | 0 | 0 | 7.11 | 8.86 | 0
2138 | 2008-03-31 01:00 | 0 | 0 | 0 | 6.54 | 8.86 | 0
2139 | 2008-03-31 02:00 | 0 | 0 | 0 | 6.01 | 8.86 | 0
2140 | 2008-03-31 03:00 | 0 | 0 | 0 | 5.47 | 7.32 | 0
2141 | 2008-03-31 04:00 | 0 | 0 | 0 | 4.94 | 7.32 | 0
2142 | 2008-03-31 05:00 | 5 | 100 | 1 | 5.07 | 7.32 | 0 | -2.2936 | 83.0226 | 90 | 0 | 5 | 0 | 0.9199 | 0.046846 | 0 | 0.86088 | 0 | 0 | 0.82902 | 0 | 0.80415 | 0.80411 | 1805.84 | 5.0856 | 158.044 | 154.32 | 153.519 | 0 | 0 | 153.513 | 119.995 | 0 | 0 | 0 | 153.513 | 0 | 660 | 0 | 0
2143 | 2008-03-31 06:00 | 149 | 590 | 45 | 5.2 | 4.57 | 0 | 10.0472 | 91.5109 | 80.2653 | 0 | 149 | 100.797 | 47.2333 | 1.396 | 61.6835 | 44.2027 | 0.0072867 | 46.5275 | 42.5668 | 0.0054907 | 86.4268 | 86.4002 | 194020 | 7.2033 | 165737 | 180013 | 159888 | 0 | 0 | 159672 | 709.057 | 0 | 0 | 0 | 0 | 159672 | 709.057 | 154558 | 151466.8594
2144 | 2008-03-31 07:00 | 371 | 811 | 62 | 5.32 | 4.57 | 0 | 22.336 | 100.413 | 65.4754 | 0 | 371 | 337.495 | 70.4165 | 3.476 | 320.727 | 65.8985 | 0.018143 | 298.129 | 63.4596 | 0.013671 | 350.754 | 350.743 | 787706 | 13.4524 | 746538 | 783531 | 721208 | 0 | 0 | 717477 | 751.299 | 0 | 0 | 0 | 0 | 717477 | 751.299 | 704812 | 690715.875
2145 | 2008-03-31 08:00 | 584 | 903 | 76 | 7.21 | 4.57 | 0 | 34.2433 | 110.731 | 50.6799 | 0 | 584 | 572.047 | 86.2296 | 5.4716 | 572.047 | 80.6969 | 0.02856 | 555.51 | 77.7104 | 0.021521 | 614.245 | 614.24 | 1379420 | 21.452 | 1351870 | 1372010 | 1332570 | 0 | 0 | 1320050 | 743.42 | 0 | 0 | 0 | 0 | 1320050 | 743.42 | 1296560 | 1270627.875
2146 | 2008-03-31 09:00 | 747 | 924 | 92 | 9.09 | 2.21 | 0 | 45.2371 | 123.995 | 35.9144 | 0 | 747 | 747.128 | 104.108 | 6.9988 | 747.128 | 97.428 | 0.036531 | 738.359 | 93.8222 | 0.027527 | 807.242 | 807.238 | 1812850 | 30.9621 | 1804500 | 1759010 | 1713710 | 0 | 0 | 1691680 | 718.404 | 0 | 0 | 0 | 0 | 1691680 | 718.404 | 1659850 | 1626653.25
2147 | 2008-03-31 10:00 | 857 | 880 | 144 | 10.97 | 2.21 | 0 | 54.2882 | 142.577 | 21.2829 | 0 | 857 | 818.231 | 167.014 | 8.0294 | 818.231 | 156.298 | 0.041911 | 815.236 | 150.514 | 0.031581 | 936.808 | 936.802 | 2103830 | 36.3527 | 2110420 | 2010100 | 1958240 | 0 | 0 | 1928450 | 704.134 | 0 | 0 | 0 | 0 | 1928450 | 704.134 | 1889030 | 1851248.125
2148 | 2008-03-31 11:00 | 958 | 999 | 99 | 12.46 | 2.21 | 0 | 59.4942 | 168.474 | 7.6671 | 0 | 958 | 988.095 | 111.742 | 8.9757 | 988.095 | 104.572 | 0.04685 | 987.649 | 100.702 | 0.035303 | 1055.73 | 1055.73 | 2370900 | 41.0649 | 2392010 | 2231960 | 2176910 | 0 | 0 | 2138830 | 690.263 | 91424.3 | 0 | 0 | 0 | 2043470 | 728.275 | 1999970 | 1959971.25
2149 | 2008-03-31 12:00 | 951 | 998 | 99 | 13.94 | 1.83 | 0 | 58.8152 | 197.854 | 10.378 | 0 | 951 | 979.615 | 111.745 | 8.9101 | 979.615 | 104.575 | 0.046508 | 978.8 | 100.705 | 0.035045 | 1047.15 | 1047.15 | 2351630 | 43.0419 | 2371670 | 2193090 | 2139460 | 0 | 0 | 2102040 | 684.616 | 56040.5 | 0 | 0 | 0 | 2043540 | 714.106 | 1999980 | 1959979.625
2150 | 2008-03-31 13:00 | 875 | 984 | 95 | 15.43 | 1.83 | 0 | 52.5761 | 222.187 | 24.4872 | 0 | 875 | 893.827 | 107.467 | 8.1981 | 893.827 | 100.572 | 0.042791 | 889.409 | 96.8501 | 0.032244 | 956.703 | 956.697 | 2148500 | 42.0181 | 2157480 | 2003410 | 1955370 | 0 | 0 | 1924070 | 685.148 | 0 | 0 | 0 | 0 | 1924070 | 685.148 | 1884950 | 1847246.75
2151 | 2008-03-31 14:00 | 737 | 955 | 87 | 15.89 | 1.83 | 0 | 42.9808 | 239.387 | 39.1656 | 0 | 737 | 739.213 | 98.6026 | 6.9051 | 739.213 | 92.2761 | 0.036042 | 728.502 | 88.861 | 0.027159 | 792.868 | 792.863 | 1780570 | 37.9249 | 1770640 | 1673590 | 1631620 | 0 | 0 | 1610350 | 695.393 | 0 | 0 | 0 | 0 | 1610350 | 695.393 | 1581700 | 1550066
2152 | 2008-03-31 15:00 | 549 | 900 | 76 | 16.36 | 0.51 | 0 | 31.7326 | 251.851 | 53.9393 | 0 | 549 | 529.376 | 85.9036 | 5.1437 | 529.376 | 80.3918 | 0.026848 | 510.879 | 77.4166 | 0.020231 | 570.666 | 570.663 | 1281560 | 33.6919 | 1250440 | 1203280 | 1172430 | 0 | 0 | 1161460 | 699.067 | 0 | 0 | 0 | 0 | 1161460 | 699.067 | 1143340 | 1120470.5
2153 | 2008-03-31 16:00 | 322 | 725 | 77 | 16.82 | 0.51 | 0 | 19.7187 | 261.769 | 68.7312 | 0 | 322 | 263.401 | 84.5281 | 3.0169 | 263.401 | 79.1046 | 0.015747 | 240.264 | 76.177 | 0.011866 | 306.96 | 306.956 | 689345 | 26.1428 | 646544 | 643118 | 626510 | 0 | 0 | 623378 | 702.429 | 0 | 0 | 0 | 0 | 623378 | 702.429 | 613952 | 601672.9375
2154 | 2008-03-31 17:00 | 48 | 0 | 48 | 16.72 | 0.51 | 0 | 7.4098 | 270.526 | 83.5096 | 0 | 48 | 0 | 44.0679 | 0.44972 | 0 | 41.2404 | 0.0023474 | 0 | 39.7141 | 0.0017688 | 38.5244 | 38.5208 | 86508 | 17.8899 | 67036.5 | 69582.1 | 67780.6 | 0 | 0 | 67735.9 | 637.551 | 0 | 0 | 0 | 1055.72 | 66680.1 | 660 | 64413.1 | 63124.8555
2155 | 2008-03-31 18:00 | 0 | 0 | 0 | 16.62 | 2.51 | 0
2156 | 2008-03-31 19:00 | 0 | 0 | 0 | 16.52 | 2.51 | 0
2157 | 2008-03-31 20:00 | 0 | 0 | 0 | 15.95 | 2.51 | 0
2158 | 2008-03-31 21:00 | 0 | 0 | 0 | 15.23 | 3.56 | 0
2159 | 2008-03-31 22:00 | 0 | 0 | 0 | 14.01 | 4.11 | 0
2160 | 2008-03-31 23:00 | 0 | 0 | 0 | 12.79 | 4.66 | 0
2161 | 2005-04-01 | 0 | 0 | 0 | 11.56 | 5.2 | 0
2162 | 2005-04-01 01:00 | 0 | 0 | 0 | 10.34 | 5.75 | 0
2163 | 2005-04-01 02:00 | 0 | 0 | 0 | 9.12 | 6.3 | 0
2164 | 2005-04-01 03:00 | 0 | 0 | 0 | 7.4 | 6.35 | 0
2165 | 2005-04-01 04:00 | 0 | 0 | 0 | 5.24 | 6.35 | 0
2166 | 2005-04-01 05:00 | 6 | 104 | 2 | 5.47 | 6.35 | 0 | -2.0883 | 82.8242 | 90 | 0 | 6 | 0 | 1.5055 | 0.056215 | 0 | 1.4089 | 0 | 0 | 1.3568 | 0 | 1.3161 | 1.316 | 2955.49 | 5.4972 | 422.237 | 412.669 | 410.75 | 0 | 0 | 410.732 | 192.957 | 0 | 0 | 0 | 410.732 | 0 | 660 | 0 | 0
2167 | 2005-04-01 06:00 | 148 | 584 | 43 | 5.69 | 5.25 | 0 | 10.2505 | 91.3073 | 80.1676 | 0 | 148 | 100.761 | 45.6653 | 1.3866 | 63.2926 | 42.7354 | 0.0072378 | 47.9253 | 41.1538 | 0.0054538 | 86.412 | 86.3805 | 193977 | 7.6062 | 165702 | 179676 | 160167 | 0 | 0 | 159948 | 704.847 | 0 | 0 | 0 | 0 | 159948 | 704.847 | 154885 | 151787.4531
2168 | 2005-04-01 07:00 | 371 | 809 | 61 | 5.91 | 5.25 | 0 | 22.5437 | 100.201 | 65.3802 | 0 | 371 | 336.85 | 69.2493 | 3.476 | 321.058 | 64.8061 | 0.018143 | 298.578 | 62.4077 | 0.013671 | 350.169 | 350.14 | 786347 | 13.677 | 745086 | 781388 | 718869 | 0 | 0 | 715155 | 750.371 | 0 | 0 | 0 | 0 | 715155 | 750.371 | 702553 | 688502.125
2169 | 2005-04-01 08:00 | 576 | 884 | 76 | 7.83 | 5.25 | 0 | 34.4632 | 110.511 | 50.584 | 0 | 576 | 561.029 | 86.1145 | 5.3967 | 561.029 | 80.5893 | 0.028169 | 544.901 | 77.6067 | 0.021226 | 603.853 | 603.848 | 1356090 | 21.2249 | 1327660 | 1348750 | 1310410 | 0 | 0 | 1298320 | 744.141 | 0 | 0 | 0 | 0 | 1298320 | 744.141 | 1275230 | 1249723
2170 | 2005-04-01 09:00 | 761 | 948 | 86 | 9.76 | 7.14 | 0 | 45.4785 | 123.778 | 35.8122 | 0 | 761 | 767.733 | 97.5302 | 7.13 | 767.733 | 91.2725 | 0.037216 | 758.784 | 87.8945 | 0.028043 | 821.305 | 821.3 | 1844430 | 25.8964 | 1837640 | 1830480 | 1780430 | 0 | 0 | 1757820 | 737.249 | 0 | 0 | 0 | 0 | 1757820 | 737.249 | 1723510 | 1689042.75
2171 | 2005-04-01 10:00 | 897 | 989 | 93 | 11.68 | 7.14 | 0 | 54.5578 | 142.416 | 21.1597 | 0 | 897 | 920.329 | 105.201 | 8.4042 | 920.329 | 98.4508 | 0.043867 | 917.002 | 94.8072 | 0.033055 | 981.487 | 981.484 | 2204170 | 30.9636 | 2216150 | 2161130 | 2101600 | 0 | 0 | 2069230 | 724.512 | 24919.2 | 0 | 0 | 0 | 2043690 | 743.084 | 1999890 | 1959887.625
2172 | 2005-04-01 11:00 | 958 | 944 | 144 | 13.26 | 7.14 | 0 | 59.7794 | 168.489 | 7.4434 | 0 | 958 | 934.089 | 158.773 | 8.9757 | 934.089 | 148.586 | 0.04685 | 933.693 | 143.087 | 0.035303 | 1044.51 | 1044.51 | 2345700 | 33.7818 | 2365420 | 2279300 | 2217790 | 0 | 0 | 2180950 | 715.732 | 132346 | 0 | 0 | 0 | 2045540 | 758.259 | 1999960 | 1959958.5
2173 | 2005-04-01 12:00 | 897 | 866 | 156 | 14.85 | 0.22 | 0 | 59.0718 | 198.095 | 10.2922 | 0 | 897 | 849.926 | 180.652 | 8.4042 | 849.926 | 169.061 | 0.043867 | 849.231 | 162.804 | 0.033055 | 981.706 | 981.695 | 2204650 | 45.2565 | 2216650 | 2028070 | 1979610 | 0 | 0 | 1946800 | 677.083 | 0 | 0 | 0 | 0 | 1946800 | 677.083 | 1906870 | 1868729.625
2174 | 2005-04-01 13:00 | 852 | 773 | 237 | 16.43 | 0.22 | 0 | 52.778 | 222.519 | 24.4787 | 0 | 852 | 702.904 | 267.248 | 7.9826 | 702.904 | 250.101 | 0.041666 | 699.433 | 240.845 | 0.031397 | 912.099 | 912.089 | 2048320 | 44.6805 | 2051970 | 1881550 | 1836130 | 0 | 0 | 1807670 | 675.175 | 0 | 0 | 0 | 0 | 1807670 | 675.175 | 1772920 | 1737466.25
2175 | 2005-04-01 14:00 | 419 | 156 | 312 | 17.84 | 0.22 | 0 | 43.1381 | 239.712 | 39.1743 | 0 | 419 | 121.314 | 316.573 | 3.9257 | 121.314 | 296.261 | 0.020491 | 119.555 | 285.297 | 0.01544 | 392.721 | 392.712 | 881930 | 30.0036 | 840683 | 821821 | 800128 | 0 | 0 | 794974 | 697.824 | 0 | 0 | 0 | 0 | 794974 | 697.824 | 783135 | 767472.6875
2176 | 2005-04-01 15:00 | 545 | 674 | 189 | 19.25 | 2.11 | 0 | 31.8625 | 252.149 | 53.9527 | 0 | 545 | 396.848 | 200.968 | 5.1062 | 396.848 | 188.074 | 0.026653 | 382.971 | 181.113 | 0.020083 | 547.182 | 547.169 | 1228800 | 34.1748 | 1195910 | 1148130 | 1117870 | 0 | 0 | 1107800 | 695.362 | 0 | 0 | 0 | 0 | 1107800 | 695.362 | 1090940 | 1069117.625
2177 | 2005-04-01 16:00 | 322 | 726 | 75 | 20.66 | 2.11 | 0 | 19.8348 | 262.046 | 68.7444 | 0 | 322 | 263.904 | 82.3159 | 3.0169 | 263.904 | 77.0344 | 0.015747 | 240.701 | 74.1834 | 0.011866 | 305.449 | 305.447 | 685960 | 28.9915 | 643158 | 631420 | 614540 | 0 | 0 | 611446 | 692.973 | 0 | 0 | 0 | 0 | 611446 | 692.973 | 602489 | 590439.5
2178 | 2005-04-01 17:00 | 84 | 484 | 19 | 20.31 | 2.11 | 0 | 7.5221 | 270.79 | 83.5194 | 0 | 84 | 56.0419 | 20.6571 | 0.78702 | 56.0419 | 19.3317 | 0.0041079 | 34.0174 | 18.6163 | 0.0030954 | 51.0576 | 51.0575 | 114662 | 21.7027 | 92006.3 | 93606.7 | 91490.6 | 0 | 0 | 91409.1 | 638.431 | 0 | 0 | 0 | 1495.06 | 89914.1 | 660 | 86982.4 | 85242.7891
2179 | 2005-04-01 18:00 | 1 | 32 | 0 | 19.96 | 0.74 | 0 | -4.7668 | 279.319 | 90 | 0 | 1 | 0 | 0 | 0.0093692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.96 | 0 | 0 | 0 | 0 | 0 | 0 | 660 | 0 | 0 | 0 | 0 | 0 | 660 | 0 | 0
2180 | 2005-04-01 19:00 | 0 | 0 | 0 | 19.61 | 0.74 | 0
2181 | 2005-04-01 20:00 | 0 | 0 | 0 | 19.18 | 0.74 | 0
2182 | 2005-04-01 21:00 | 0 | 0 | 0 | 18.74 | 2.61 | 0
2183 | 2005-04-01 22:00 | 0 | 0 | 0 | 18.31 | 2.61 | 0
2184 | 2005-04-01 23:00 | 0 | 0 | 0 | 17.46 | 2.61 | 0
2185 | 2005-04-02 | 0 | 0 | 0 | 16.61 | 2.48 | 0
2186 | 2005-04-02 01:00 | 0 | 0 | 0 | 15.76 | 2.48 | 0
2187 | 2005-04-02 02:00 | 0 | 0 | 0 | 15.08 | 2.48 | 0
2188 | 2005-04-02 03:00 | 0 | 0 | 0 | 14.4 | 1.77 | 0
2189 | 2005-04-02 04:00 | 0 | 0 | 0 | 13.72 | 1.77 | 0
2190 | 2005-04-02 05:00 | 6 | 85 | 3 | 13.22 | 1.77 | 0 | -1.8076 | 82.5508 | 90 | 0 | 6 | 0 | 2.2012 | 0.056215 | 0 | 2.06 | 0 | 0 | 1.9837 | 0 | 1.9242 | 1.9241 | 4321.12 | 13.2737 | 898.021 | 887.39 | 882.966 | 0 | 0 | 882.927 | 284.906 | 0 | 0 | 0 | 882.927 | 0 | 660 | 0 | 0
2191 | 2005-04-02 06:00 | 142 | 446 | 60 | 12.73 | 1.44 | 0 | 10.5278 | 91.0263 | 80.0356 | 0 | 142 | 77.6573 | 61.4903 | 1.3304 | 50.3566 | 57.545 | 0.0069444 | 38.3236 | 55.4153 | 0.0052327 | 90.9317 | 90.8989 | 204131 | 15.3231 | 174616 | 182819 | 168577 | 0 | 0 | 168330 | 685.025 | 0 | 0 | 0 | 0 | 168330 | 685.025 | 163330 | 160063.3594
2192 | 2005-04-02 07:00 | 376 | 726 | 94 | 12.23 | 1.44 | 0 | 22.827 | 99.9081 | 65.2521 | 0 | 376 | 304.298 | 102.989 | 3.5228 | 291.305 | 96.3813 | 0.018388 | 271.077 | 92.8143 | 0.013856 | 352.988 | 352.961 | 792674 | 22.2991 | 751142 | 759241 | 702319 | 0 | 0 | 698519 | 721.823 | 0 | 0 | 0 | 0 | 698519 | 721.823 | 687202 | 673457.875
2193 | 2005-04-02 08:00 | 586 | 820 | 119 | 13.56 | 1.44 | 0 | 34.7632 | 110.205 | 50.4556 | 0 | 586 | 521.457 | 133.569 | 5.4904 | 521.457 | 124.999 | 0.028658 | 506.578 | 120.373 | 0.021594 | 608.164 | 608.158 | 1365770 | 30.9092 | 1337700 | 1303580 | 1270540 | 0 | 0 | 1258060 | 709.992 | 0 | 0 | 0 | 0 | 1258060 | 709.992 | 1237430 | 1212679.375
2194 | 2005-04-02 09:00 | 728 | 807 | 150 | 14.9 | 2.69 | 0 | 45.808 | 123.476 | 35.6764 | 0 | 728 | 654.837 | 169.719 | 6.8208 | 654.837 | 158.829 | 0.035602 | 647.272 | 152.951 | 0.026827 | 776.242 | 776.237 | 1743240 | 35.2708 | 1731500 | 1656100 | 1613390 | 0 | 0 | 1593000 | 702.973 | 0 | 0 | 0 | 0 | 1593000 | 702.973 | 1564640 | 1533343.375
2195 | 2005-04-02 10:00 | 835 | 773 | 204 | 16.24 | 2.69 | 0 | 54.9266 | 142.19 | 20.9972 | 0 | 835 | 719.805 | 234.344 | 7.8233 | 719.805 | 219.308 | 0.040835 | 717.245 | 211.192 | 0.03077 | 900.614 | 900.596 | 2022510 | 39.8744 | 2024820 | 1898120 | 1851170 | 0 | 0 | 1823500 | 690.415 | 0 | 0 | 0 | 0 | 1823500 | 690.415 | 1787940 | 1752177.375
2196 | 2005-04-02 11:00 | 774 | 498 | 343 | 17.78 | 2.69 | 0 | 60.1705 | 168.508 | 7.1448 | 0 | 774 | 492.967 | 377.758 | 7.2518 | 492.967 | 353.521 | 0.037852 | 492.774 | 340.437 | 0.028522 | 808.242 | 808.221 | 1815060 | 38.9902 | 1806820 | 1699680 | 1657060 | 0 | 0 | 1634880 | 691.692 | 0 | 0 | 0 | 0 | 1634880 | 691.692 | 1605570 | 1573459.875
2197 | 2005-04-02 12:00 | 882 | 772 | 219 | 19.32 | 7.84 | 0 | 59.4239 | 198.429 | 10.1845 | 0 | 882 | 757.942 | 252.387 | 8.2637 | 757.942 | 236.193 | 0.043133 | 757.336 | 227.452 | 0.032502 | 955.276 | 955.262 | 2145280 | 37.2751 | 2154080 | 2043620 | 1992980 | 0 | 0 | 1961970 | 701.906 | 0 | 0 | 0 | 0 | 1961970 | 701.906 | 1921360 | 1882933.625
2198 | 2005-04-02 13:00 | 810 | 796 | 175 | 20.87 | 7.84 | 0 | 53.0547 | 222.977 | 24.4705 | 0 | 810 | 723.165 | 197.838 | 7.5891 | 723.165 | 185.144 | 0.039612 | 719.597 | 178.292 | 0.029849 | 870.981 | 870.97 | 1955980 | 37.2407 | 1954830 | 1854230 | 1807680 | 0 | 0 | 1781940 | 699.413 | 0 | 0 | 0 | 0 | 1781940 | 699.413 | 1747640 | 1712688.5
2199 | 2005-04-02 14:00 | 720 | 810 | 164 | 21.41 | 7.84 | 0 | 43.3538 | 240.16 | 39.1872 | 0 | 720 | 627.744 | 186.236 | 6.7458 | 627.744 | 174.287 | 0.035211 | 618.636 | 167.837 | 0.026532 | 762.905 | 762.898 | 1713280 | 35.7494 | 1700120 | 1622620 | 1580970 | 0 | 0 | 1561280 | 700.946 | 0 | 0 | 0 | 0 | 1561280 | 700.946 | 1533930 | 1503256.25
2200 | 2005-04-02 15:00 | 496 | 614 | 170 | 21.95 | 6.53 | 0 | 32.041 | 252.559 | 53.9711 | 0 | 496 | 361.435 | 181.568 | 4.6471 | 361.435 | 169.918 | 0.024257 | 348.783 | 163.63 | 0.018278 | 497.058 | 497.051 | 1116250 | 32.1031 | 1079970 | 1046370 | 1019520 | 0 | 0 | 1011180 | 698.25 | 0 | 0 | 0 | 0 | 1011180 | 698.25 | 996056 | 976134.8125
2201 | 2005-04-02 16:00 | 253 | 374 | 125 | 22.49 | 6.53 | 0 | 19.9947 | 262.425 | 68.7617 | 0 | 253 | 135.604 | 129.009 | 2.3704 | 135.604 | 120.732 | 0.012373 | 123.667 | 116.264 | 0.0093231 | 232.742 | 232.732 | 522656 | 27.2439 | 480917 | 475855 | 463333 | 0 | 0 | 461541 | 686.837 | 0 | 0 | 0 | 0 | 461541 | 686.837 | 454388 | 445300.5938
2202 | 2005-04-02 17:00 | 67 | 249 | 33 | 21.61 | 6.53 | 0 | 7.6773 | 271.152 | 83.5314 | 0 | 67 | 28.6718 | 33.4331 | 0.62774 | 28.6718 | 31.2879 | 0.0032766 | 17.3802 | 30.13 | 0.002469 | 46.0873 | 46.0868 | 103499 | 22.5514 | 82043.7 | 83110.7 | 81129 | 0 | 0 | 81063.2 | 630.115 | 0 | 0 | 0 | 2525.21 | 78538 | 660 | 75923.7 | 74405.2422
2203 | 2005-04-02 18:00 | 1 | 18 | 1 | 20.72 | 8.31 | 0 | -4.6045 | 279.675 | 90 | 0 | 1 | 0 | 1.0026 | 0.0093692 | 0 | 0.93829 | 0 | 0 | 0.90356 | 0 | 0.87645 | 0.87639 | 1968.14 | 20.736 | 187.66 | 186.718 | 185.839 | 0 | 0 | 185.831 | 130.402 | 0 | 0 | 0 | 185.831 | 0 | 660 | 0 | 0
2204 | 2005-04-02 19:00 | 0 | 0 | 0 | 19.84 | 8.31 | 0
2205 | 2005-04-02 20:00 | 0 | 0 | 0 | 18.77 | 8.31 | 0
2206 | 2005-04-02 21:00 | 0 | 0 | 0 | 17.7 | 8.14 | 0
2207 | 2005-04-02 22:00 | 0 | 0 | 0 | 16.62 | 8.14 | 0
2208 | 2005-04-02 23:00 | 0 | 0 | 0 | 15.78 | 8.14 | 0
2209 | 2005-04-03 | 0 | 0 | 0 | 14.93 | 11.74 | 0
2210 | 2005-04-03 01:00 | 0 | 0 | 0 | 14.09 | 11.74 | 0
2211 | 2005-04-03 02:00 | 0 | 0 | 0 | 13.52 | 11.74 | 0
2212 | 2005-04-03 03:00 | 0 | 0 | 0 | 12.95 | 8.89 | 0
2213 | 2005-04-03 04:00 | 0 | 0 | 0 | 12.37 | 8.89 | 0
2214 | 2005-04-03 05:00 | 7 | 103 | 3 | 12.03 | 8.89 | 0 | -1.5284 | 82.2785 | 90 | 0 | 7 | 0 | 2.1953 | 0.065585 | 0 | 2.0544 | 0 | 0 | 1.9784 | 0 | 1.919 | 1.9189 | 4309.47 | 12.0638 | 893.26 | 881.469 | 877.117 | 0 | 0 | 877.079 | 284.013 | 0 | 0 | 0 | 877.079 | 0 | 660 | 0 | 0
2215 | 2005-04-03 06:00 | 151 | 511 | 54 | 11.69 | 9.42 | 0 | 10.8036 | 90.7457 | 79.9048 | 0 | 151 | 90.7078 | 55.6551 | 1.4147 | 60.5858 | 52.0841 | 0.0073845 | 46.3329 | 50.1565 | 0.0055644 | 93.6001 | 93.5839 | 210158 | 13.2838 | 180451 | 190760 | 174823 | 0 | 0 | 174560 | 692.018 | 0 | 0 | 0 | 11.7064 | 174548 | 692.821 | 169339 | 165951.8594
2216 | 2005-04-03 07:00 | 379 | 763 | 79 | 11.35 | 9.42 | 0 | 23.1084 | 99.6149 | 65.126 | 0 | 379 | 321.519 | 87.5182 | 3.5509 | 308.956 | 81.9029 | 0.018535 | 287.678 | 78.8717 | 0.013966 | 355.567 | 355.543 | 798471 | 17.4052 | 757031 | 781923 | 720460 | 0 | 0 | 716616 | 736.805 | 0 | 0 | 0 | 0 | 716616 | 736.805 | 704479 | 690389.3125
2217 | 2005-04-03 08:00 | 587 | 857 | 95 | 13.07 | 9.42 | 0 | 35.061 | 109.898 | 50.3301 | 0 | 587 | 546.742 | 108.578 | 5.4997 | 546.742 | 101.611 | 0.028707 | 531.256 | 97.8508 | 0.021631 | 610.254 | 610.245 | 1370450 | 23.463 | 1342560 | 1351180 | 1313840 | 0 | 0 | 1301430 | 736.274 | 0 | 0 | 0 | 0 | 1301430 | 736.274 | 1278690 | 1253117.375
2218 | 2005-04-03 09:00 | 772 | 927 | 104 | 14.79 | 7.58 | 0 | 46.1351 | 123.171 | 35.5448 | 0 | 772 | 753.874 | 116.296 | 7.233 | 753.874 | 108.834 | 0.037754 | 745.242 | 104.807 | 0.028448 | 824.575 | 824.572 | 1851770 | 30.5451 | 1845350 | 1802260 | 1752360 | 0 | 0 | 1729580 | 721.925 | 0 | 0 | 0 | 0 | 1729580 | 721.925 | 1696480 | 1662554.75
2219 | 2005-04-03 10:00 | 897 | 955 | 113 | 16.51 | 7.58 | 0 | 55.2933 | 141.959 | 20.8415 | 0 | 897 | 891.28 | 126.054 | 8.4042 | 891.28 | 117.966 | 0.043867 | 888.16 | 113.6 | 0.033055 | 971.739 | 971.735 | 2182260 | 35.077 | 2193060 | 2100960 | 2046010 | 0 | 0 | 2013990 | 709.178 | 0 | 0 | 0 | 0 | 2013990 | 709.178 | 1971480 | 1932051
2220 | 2005-04-03 11:00 | 953 | 909 | 163 | 17.26 | 7.58 | 0 | 60.56 | 168.526 | 6.8569 | 0 | 953 | 900.649 | 187.558 | 8.9289 | 900.649 | 175.524 | 0.046606 | 900.325 | 169.028 | 0.035118 | 1037.31 | 1037.3 | 2329500 | 37.0797 | 2348330 | 2230510 | 2173390 | 0 | 0 | 2136910 | 704.845 | 89788.1 | 0 | 0 | 0 | 2043550 | 740.554 | 1999980 | 1959977.25
2221 | 2005-04-03 12:00 | 907 | 852 | 173 | 18.02 | 9.7 | 0 | 59.7737 | 198.767 | 10.0907 | 0 | 907 | 836.353 | 197.689 | 8.4979 | 836.353 | 185.005 | 0.044356 | 835.696 | 178.158 | 0.033423 | 983.471 | 983.456 | 2208590 | 34.4823 | 2220810 | 2133210 | 2078720 | 0 | 0 | 2045860 | 711.111 | 4123.52 | 0 | 0 | 0 | 2041550 | 717.92 | 1998080 | 1958116.875
2222 | 2005-04-03 13:00 | 843 | 898 | 124 | 18.77 | 9.7 | 0 | 53.3288 | 223.439 | 24.4678 | 0 | 843 | 815.92 | 137.461 | 7.8982 | 815.92 | 128.641 | 0.041226 | 811.895 | 123.88 | 0.031065 | 907.732 | 907.735 | 2038540 | 33.9648 | 2041680 | 1965120 | 1911510 | 0 | 0 | 1883710 | 712.047 | 0 | 0 | 0 | 0 | 1883710 | 712.047 | 1845770 | 1808857.375
2223 | 2005-04-03 14:00 | 698 | 772 | 166 | 18.57 | 9.7 | 0 | 43.5672 | 240.609 | 39.203 | 0 | 698 | 598.157 | 187.942 | 6.5397 | 598.157 | 175.883 | 0.034135 | 589.47 | 169.374 | 0.025722 | 736.104 | 736.092 | 1653070 | 30.8916 | 1637110 | 1596200 | 1557760 | 0 | 0 | 1539340 | 714.82 | 0 | 0 | 0 | 0 | 1539340 | 714.82 | 1512160 | 1481916
2224 | 2005-04-03 15:00 | 466 | 504 | 197 | 18.37 | 10.05 | 0 | 32.2179 | 252.969 | 53.9909 | 0 | 466 | 296.636 | 208.152 | 4.3661 | 296.636 | 194.797 | 0.022789 | 286.24 | 187.587 | 0.017172 | 459.629 | 459.614 | 1032180 | 25.9 | 993771 | 989771 | 963674 | 0 | 0 | 956646 | 719.213 | 0 | 0 | 0 | 0 | 956646 | 719.213 | 941378 | 922550.125
2225 | 2005-04-03 16:00 | 209 | 189 | 144 | 18.17 | 10.05 | 0 | 20.1536 | 262.804 | 68.7796 | 0 | 209 | 68.2861 | 140.414 | 1.9582 | 68.2861 | 131.404 | 0.010221 | 62.2675 | 126.541 | 0.0077017 | 183.152 | 183.145 | 411295 | 21.1705 | 371844 | 378571 | 368161 | 0 | 0 | 367063 | 697.969 | 0 | 0 | 0 | 0 | 367063 | 697.969 | 360125 | 352922.9688
2226 | 2005-04-03 17:00 | 56 | 126 | 39 | 17.23 | 10.05 | 0 | 7.8319 | 271.512 | 83.5433 | 0 | 56 | 14.0288 | 37.2293 | 0.52468 | 14.0288 | 34.8406 | 0.0027386 | 8.4926 | 33.5512 | 0.0020636 | 40.7844 | 40.7824 | 91586.9 | 17.8981 | 71499.6 | 74205.4 | 72371.8 | 0 | 0 | 72321.3 | 641.406 | 0 | 0 | 0 | 863.966 | 71457.3 | 660 | 69048.3 | 67667.3594
2227 | 2005-04-03 18:00 | 1 | 10 | 1 | 16.28 | 12.28 | 0 | -4.4425 | 280.03 | 90 | 0 | 1 | 0 | 1.0025 | 0.0093692 | 0 | 0.93815 | 0 | 0 | 0.90343 | 0 | 0.87632 | 0.87628 | 1967.9 | 16.2926 | 187.596 | 185.671 | 184.813 | 0 | 0 | 184.805 | 130.139 | 0 | 0 | 0 | 184.805 | 0 | 660 | 0 | 0
2228 | 2005-04-03 19:00 | 0 | 0 | 0 | 15.33 | 12.28 | 0
2229 | 2005-04-03 20:00 | 0 | 0 | 0 | 14.16 | 12.28 | 0
2230 | 2005-04-03 21:00 | 0 | 0 | 0 | 13 | 12.66 | 0
2231 | 2005-04-03 22:00 | 0 | 0 | 0 | 11.83 | 12.66 | 0
2232 | 2005-04-03 23:00 | 0 | 0 | 0 | 10.93 | 12.66 | 0
2233 | 2005-04-04 | 0 | 0 | 0 | 10.02 | 12.09 | 0
2234 | 2005-04-04 01:00 | 0 | 0 | 0 | 9.12 | 12.09 | 0
2235 | 2005-04-04 02:00 | 0 | 0 | 0 | 8.45 | 12.09 | 0
2236 | 2005-04-04 03:00 | 0 | 0 | 0 | 7.78 | 13.28 | 0
2237 | 2005-04-04 04:00 | 0 | 0 | 0 | 7.11 | 13.28 | 0
2238 | 2005-04-04 05:00 | 8 | 91 | 4 | 7.02 | 13.28 | 0 | -1.2506 | 82.007 | 90 | 0 | 8 | 0 | 3.0134 | 0.074954 | 0 | 2.8201 | 0 | 0 | 2.7157 | 0 | 2.6343 | 2.6341 | 5915.5 | 7.0556 | 1656.63 | 1642.01 | 1631.16 | 0 | 0 | 1631.09 | 388.166 | 0 | 0 | 0 | 1631.09 | 0 | 660 | 0 | 0
2239 | 2005-04-04 06:00 | 155 | 427 | 72 | 6.93 | 14.07 | 0 | 11.0776 | 90.4655 | 79.7755 | 0 | 155 | 76.6792 | 71.2181 | 1.4522 | 52.6 | 66.6486 | 0.0075801 | 40.4136 | 64.182 | 0.0057118 | 101.463 | 101.456 | 227841 | 8.2388 | 196700 | 212807 | 197971 | 0 | 0 | 197663 | 715.794 | 0 | 0 | 0 | 0 | 197663 | 715.794 | 191613 | 187780.4062
2240 | 2005-04-04 07:00 | 374 | 740 | 80 | 6.84 | 14.07 | 0 | 23.3877 | 99.3214 | 65.0019 | 0 | 374 | 312.988 | 88.3727 | 3.5041 | 301.916 | 82.7025 | 0.01829 | 281.289 | 79.6418 | 0.013782 | 350.116 | 350.142 | 786332 | 11.3567 | 744673 | 789082 | 725423 | 0 | 0 | 721738 | 757.648 | 0 | 0 | 0 | 0 | 721738 | 757.648 | 708820 | 694643.375
2241 | 2005-04-04 08:00 | 582 | 803 | 117 | 7.5 | 14.07 | 0 | 35.3564 | 109.59 | 50.2075 | 0 | 582 | 514.299 | 131.127 | 5.4529 | 514.299 | 122.713 | 0.028462 | 499.835 | 118.172 | 0.021447 | 599.487 | 599.48 | 1346280 | 15.2331 | 1317480 | 1371710 | 1331860 | 0 | 0 | 1319970 | 763.106 | 0 | 0 | 0 | 0 | 1319970 | 763.106 | 1295300 | 1269396.5
2242 | 2005-04-04 09:00 | 696 | 651 | 225 | 8.17 | 8.87 | 0 | 46.4598 | 122.863 | 35.4175 | 0 | 696 | 529.517 | 248.838 | 6.521 | 529.517 | 232.872 | 0.034037 | 523.505 | 224.254 | 0.025648 | 725.351 | 725.335 | 1628910 | 20.9516 | 1611850 | 1638920 | 1593290 | 0 | 0 | 1575730 | 749.691 | 0 | 0 | 0 | 0 | 1575730 | 749.691 | 1545940 | 1515019.125
2243 | 2005-04-04 10:00 | 872 | 835 | 184 | 8.84 | 8.87 | 0 | 55.6578 | 141.725 | 20.6928 | 0 | 872 | 779.495 | 207.045 | 8.17 | 779.495 | 193.761 | 0.042644 | 776.808 | 186.59 | 0.032134 | 934.527 | 934.521 | 2098690 | 25.3078 | 2105010 | 2101970 | 2042220 | 0 | 0 | 2013030 | 742.381 | 0 | 0 | 0 | 0 | 2013030 | 742.381 | 1970300 | 1930891
2244 | 2005-04-04 11:00 | 963 | 891 | 186 | 10.03 | 8.87 | 0 | 60.9478 | 168.543 | 6.581 | 0 | 963 | 882.978 | 210.895 | 9.0226 | 882.978 | 197.364 | 0.047095 | 882.685 | 190.06 | 0.035487 | 1040.6 | 1040.59 | 2336900 | 28.3669 | 2356130 | 2323140 | 2259730 | 0 | 0 | 2223360 | 734.173 | 175829 | 0 | 0 | 0 | 2045880 | 780.902 | 1997720 | 1957765.5
2245 | 2005-04-04 12:00 | 891 | 781 | 215 | 11.22 | 7.65 | 0 | 60.1214 | 199.11 | 10.011 | 0 | 891 | 767.756 | 247.369 | 8.348 | 767.756 | 231.497 | 0.043574 | 767.162 | 222.93 | 0.032834 | 960.421 | 960.406 | 2156840 | 29.4895 | 2166260 | 2125670 | 2067000 | 0 | 0 | 2036020 | 729.056 | 646.962 | 0 | 0 | 0 | 2035350 | 730.21 | 1992140 | 1952297.625
2246 | 2005-04-04 13:00 | 857 | 878 | 151 | 12.42 | 7.65 | 0 | 53.6001 | 223.904 | 24.4704 | 0 | 857 | 798.345 | 172.637 | 8.0294 | 798.345 | 161.56 | 0.041911 | 794.406 | 155.581 | 0.031581 | 921.517 | 921.508 | 2069470 | 29.9495 | 2074240 | 2031330 | 1977070 | 0 | 0 | 1948420 | 725.872 | 0 | 0 | 0 | 0 | 1948420 | 725.872 | 1908170 | 1870010.75
2247 | 2005-04-04 14:00 | 738 | 917 | 104 | 12.87 | 7.65 | 0 | 43.7782 | 241.059 | 39.2215 | 0 | 738 | 709.91 | 115.861 | 6.9145 | 709.91 | 108.427 | 0.036091 | 699.588 | 104.414 | 0.027196 | 779.908 | 779.905 | 1751470 | 27.7059 | 1740140 | 1720150 | 1672200 | 0 | 0 | 1651860 | 729.764 | 0 | 0 | 0 | 0 | 1651860 | 729.764 | 1620920 | 1588497.125
2248 | 2005-04-04 15:00 | 549 | 856 | 90 | 13.31 | 7.04 | 0 | 32.393 | 253.378 | 54.0122 | 0 | 549 | 503.458 | 102.079 | 5.1437 | 503.458 | 95.5297 | 0.026848 | 485.792 | 91.9942 | 0.020231 | 560.472 | 560.469 | 1258670 | 24.392 | 1226770 | 1229820 | 1195390 | 0 | 0 | 1184980 | 731.986 | 0 | 0 | 0 | 0 | 1184980 | 731.986 | 1164790 | 1141490.875
2249 | 2005-04-04 16:00 | 322 | 712 | 74 | 13.76 | 7.04 | 0 | 20.3113 | 263.181 | 68.798 | 0 | 322 | 258.385 | 80.5649 | 3.0169 | 258.385 | 75.3957 | 0.015747 | 235.582 | 72.6054 | 0.011866 | 298.953 | 298.948 | 671365 | 19.671 | 628560 | 643641 | 626670 | 0 | 0 | 623714 | 723.225 | 0 | 0 | 0 | 0 | 623714 | 723.225 | 613634 | 601361.4375
2250 | 2005-04-04 17:00 | 98 | 0 | 98 | 13.53 | 7.04 | 0 | 7.986 | 271.871 | 83.555 | 0 | 98 | 0 | 88.3416 | 0.91818 | 0 | 82.6735 | 0.0047926 | 0 | 79.6138 | 0.0036113 | 77.2289 | 77.2255 | 173429 | 15.057 | 145503 | 152858 | 148692 | 0 | 0 | 148504 | 682.069 | 0 | 0 | 0 | 0 | 148504 | 682.069 | 143887 | 141008.8125
2251 | 2005-04-04 18:00 | 1 | 0 | 1 | 13.31 | 6.38 | 0 | -4.2805 | 280.383 | 90 | 0 | 1 | 0 | 1.0023 | 0.0093692 | 0 | 0.93801 | 0 | 0 | 0.90329 | 0 | 0.87619 | 0.87616 | 1967.63 | 13.3281 | 187.564 | 184.98 | 184.109 | 0 | 0 | 184.101 | 129.935 | 0 | 0 | 0 | 184.101 | 0 | 660 | 0 | 0
2252 | 2005-04-04 19:00 | 0 | 0 | 0 | 13.09 | 6.38 | 0
2253 | 2005-04-04 20:00 | 0 | 0 | 0 | 12.21 | 6.38 | 0
2254 | 2005-04-04 21:00 | 0 | 0 | 0 | 11.33 | 9.36 | 0
2255 | 2005-04-04 22:00 | 0 | 0 | 0 | 10.46 | 9.36 | 0
2256 | 2005-04-04 23:00 | 0 | 0 | 0 | 9.91 | 9.36 | 0
2257 | 2005-04-05 | 0 | 0 | 0 | 9.37 | 3.69 | 0
2258 | 2005-04-05 01:00 | 0 | 0 | 0 | 8.83 | 3.69 | 0
2259 | 2005-04-05 02:00 | 0 | 0 | 0 | 8.36 | 3.69 | 0
2260 | 2005-04-05 03:00 | 0 | 0 | 0 | 7.9 | 5.74 | 0
2261 | 2005-04-05 04:00 | 0 | 0 | 0 | 7.43 | 5.74 | 0
2262 | 2005-04-05 05:00 | 9 | 122 | 3 | 7.2 | 5.74 | 0 | -0.97443 | 81.7365 | 90 | 0 | 9 | 0 | 2.3248 | 0.084323 | 0 | 2.1756 | 0 | 0 | 2.0951 | 0 | 2.0323 | 2.0321 | 4563.63 | 7.2437 | 1000.28 | 982.481 | 977.532 | 0 | 0 | 977.489 | 300.136 | 0 | 0 | 0 | 977.489 | 0 | 660 | 0 | 0
2263 | 2005-04-05 06:00 | 165 | 544 | 57 | 6.98 | 6.39 | 0 | 11.3497 | 90.1858 | 79.6476 | 0 | 165 | 98.6186 | 58.3069 | 1.5459 | 69.3061 | 54.5658 | 0.0080692 | 53.4877 | 52.5464 | 0.0060803 | 102.859 | 102.87 | 231014 | 9.1002 | 200030 | 215378 | 197029 | 0 | 0 | 196714 | 713.757 | 0 | 0 | 0 | 0 | 196714 | 713.757 | 190758 | 186942.9844
2264 | 2005-04-05 07:00 | 390 | 775 | 79 | 6.75 | 6.39 | 0 | 23.6648 | 99.0278 | 64.88 | 0 | 390 | 328.923 | 87.2064 | 3.654 | 318.566 | 81.6111 | 0.019073 | 296.973 | 78.5907 | 0.014372 | 364.311 | 364.326 | 818189 | 14.259 | 776795 | 812951 | 746819 | 0 | 0 | 742812 | 748.145 | 0 | 0 | 0 | 0 | 742812 | 748.145 | 729875 | 715277.5
2265 | 2005-04-05 08:00 | 604 | 876 | 94 | 8.92 | 6.39 | 0 | 35.6493 | 109.281 | 50.0879 | 0 | 604 | 561.444 | 107.113 | 5.659 | 561.444 | 100.24 | 0.029538 | 545.764 | 96.5303 | 0.022258 | 623.047 | 623.042 | 1399200 | 21.7613 | 1372410 | 1391050 | 1352040 | 0 | 0 | 1339140 | 742.709 | 0 | 0 | 0 | 0 | 1339140 | 742.709 | 1315300 | 1288994.375
2266 | 2005-04-05 09:00 | 777 | 873 | 141 | 11.09 | 5.7 | 0 | 46.7818 | 122.553 | 35.2946 | 0 | 777 | 712.313 | 159.741 | 7.2799 | 712.313 | 149.491 | 0.037998 | 704.292 | 143.959 | 0.028633 | 822.831 | 822.823 | 1847850 | 28.8186 | 1841230 | 1811530 | 1763760 | 0 | 0 | 1740950 | 726.259 | 0 | 0 | 0 | 0 | 1740950 | 726.259 | 1707410 | 1673258.375
2267 | 2005-04-05 10:00 | 859 | 805 | 193 | 13.26 | 5.7 | 0 | 56.02 | 141.486 | 20.5511 | 0 | 859 | 752.039 | 221.714 | 8.0482 | 752.039 | 207.489 | 0.042009 | 749.484 | 199.81 | 0.031654 | 920.845 | 920.841 | 2067980 | 33.1005 | 2072670 | 2002450 | 1949140 | 0 | 0 | 1920430 | 714.327 | 0 | 0 | 0 | 0 | 1920430 | 714.327 | 1881210 | 1843583.5
2268 | 2005-04-05 11:00 | 963 | 888 | 186 | 14.58 | 5.7 | 0 | 61.3338 | 168.56 | 6.3184 | 0 | 963 | 880.162 | 210.552 | 9.0226 | 880.162 | 197.043 | 0.047095 | 879.893 | 189.75 | 0.035487 | 1037.59 | 1037.58 | 2330130 | 36.9357 | 2348990 | 2232480 | 2173470 | 0 | 0 | 2137020 | 705.185 | 89895.6 | 0 | 0 | 0 | 2043590 | 741.28 | 1999980 | 1959975.875
2269 | 2005-04-05 12:00 | 916 | 857 | 172 | 15.91 | 6.14 | 0 | 60.4667 | 199.458 | 9.9453 | 0 | 916 | 842.255 | 195.978 | 8.5822 | 842.255 | 183.404 | 0.044796 | 841.612 | 176.616 | 0.033755 | 987.714 | 987.706 | 2218140 | 36.5965 | 2230870 | 2123050 | 2070190 | 0 | 0 | 2037040 | 704.684 | 1427.33 | 0 | 0 | 0 | 2035540 | 707.391 | 1992250 | 1952401.875
2270 | 2005-04-05 13:00 | 851 | 865 | 153 | 17.23 | 6.14 | 0 | 53.8687 | 224.373 | 24.4782 | 0 | 851 | 786.54 | 174.394 | 7.9732 | 786.54 | 163.204 | 0.041617 | 782.656 | 157.164 | 0.03136 | 911.656 | 911.651 | 2047340 | 36.3236 | 2050940 | 1953640 | 1903470 | 0 | 0 | 1875270 | 703.65 | 0 | 0 | 0 | 0 | 1875270 | 703.65 | 1837720 | 1800965.5
2271 | 2005-04-05 14:00 | 741 | 918 | 104 | 17.88 | 6.14 | 0 | 43.9869 | 241.509 | 39.2426 | 0 | 741 | 710.36 | 115.65 | 6.9426 | 710.36 | 108.23 | 0.036238 | 700.017 | 104.224 | 0.027306 | 780.14 | 780.131 | 1751980 | 34.2191 | 1740670 | 1672760 | 1630170 | 0 | 0 | 1609590 | 706.573 | 0 | 0 | 0 | 0 | 1609590 | 706.573 | 1580610 | 1548993.875
2272 | 2005-04-05 15:00 | 552 | 856 | 91 | 18.52 | 3.53 | 0 | 32.5665 | 253.786 | 54.0346 | 0 | 552 | 502.981 | 102.893 | 5.1718 | 502.981 | 96.2912 | 0.026995 | 485.308 | 92.7275 | 0.020341 | 560.714 | 560.709 | 1259210 | 32.439 | 1227320 | 1187690 | 1157530 | 0 | 0 | 1146950 | 702.681 | 0 | 0 | 0 | 0 | 1146950 | 702.681 | 1128940 | 1106361.375
2273 | 2005-04-05 16:00 | 312 | 666 | 79 | 19.17 | 3.53 | 0 | 20.468 | 263.557 | 68.8168 | 0 | 312 | 240.774 | 85.3843 | 2.9232 | 240.774 | 79.9059 | 0.015258 | 219.497 | 76.9486 | 0.011497 | 287.563 | 287.559 | 645786 | 26.3083 | 603023 | 599369 | 584403 | 0 | 0 | 581649 | 698.739 | 0 | 0 | 0 | 0 | 581649 | 698.739 | 572856 | 561398.875
2274 | 2005-04-05 17:00 | 74 | 0 | 74 | 18.93 | 3.53 | 0 | 8.1395 | 272.228 | 83.5664 | 0 | 74 | 0 | 67.078 | 0.69332 | 0 | 62.7741 | 0.0036189 | 0 | 60.4509 | 0.0027269 | 58.64 | 58.6364 | 131682 | 20.3856 | 107342 | 109925 | 107108 | 0 | 0 | 107000 | 649.133 | 0 | 0 | 0 | 357.77 | 106642 | 660 | 103272 | 101207.0391
2275 | 2005-04-05 18:00 | 1 | 0 | 1 | 18.69 | 3.25 | 0 | -4.1187 | 280.734 | 90 | 0 | 1 | 0 | 1.0022 | 0.0093692 | 0 | 0.93787 | 0 | 0 | 0.90316 | 0 | 0.87606 | 0.87603 | 1967.33 | 18.7122 | 187.507 | 186.119 | 185.243 | 0 | 0 | 185.235 | 130.217 | 0 | 0 | 0 | 185.235 | 0 | 660 | 0 | 0
2276 | 2005-04-05 19:00 | 0 | 0 | 0 | 18.45 | 3.25 | 0
2277 | 2005-04-05 20:00 | 0 | 0 | 0 | 17.83 | 3.25 | 0
2278 | 2005-04-05 21:00 | 0 | 0 | 0 | 17.21 | 5.85 | 0
2279 | 2005-04-05 22:00 | 0 | 0 | 0 | 16.59 | 5.85 | 0
2280 | 2005-04-05 23:00 | 0 | 0 | 0 | 16.08 | 5.85 | 0
2281 | 2005-04-06 | 0 | 0 | 0 | 15.56 | 6.26 | 0
2282 | 2005-04-06 01:00 | 0 | 0 | 0 | 15.05 | 6.26 | 0
2283 | 2005-04-06 02:00 | 0 | 0 | 0 | 14.75 | 6.26 | 0
2284 | 2005-04-06 03:00 | 0 | 0 | 0 | 14.45 | 6.42 | 0
2285 | 2005-04-06 04:00 | 0 | 0 | 0 | 14.16 | 6.42 | 0
2286 | 2005-04-06 05:00 | 10 | 95 | 5 | 13.84 | 6.42 | 0 | -0.69999 | 81.4671 | 90 | 0 | 10 | 0 | 3.8654 | 0.093692 | 0 | 3.6174 | 0 | 0 | 3.4835 | 0 | 3.379 | 3.3789 | 7588.05 | 13.9095 | 2621.87 | 2650.92 | 2620.79 | 0 | 0 | 2620.65 | 452.437 | 0 | 0 | 0 | 2620.65 | 0 | 660 | 0 | 0
2287 | 2005-04-06 06:00 | 170 | 406 | 88 | 13.52 | 7.19 | 0 | 11.6198 | 89.9065 | 79.5214 | 0 | 170 | 74.0422 | 85.8316 | 1.5928 | 53.2173 | 80.3245 | 0.0083137 | 41.2475 | 77.3517 | 0.0062645 | 115.047 | 115.048 | 258365 | 15.7732 | 225360 | 235420 | 220508 | 0 | 0 | 220111 | 698.773 | 0 | 0 | 0 | 0 | 220111 | 698.773 | 213985 | 209705.5156
2288 | 2005-04-06 07:00 | 326 | 419 | 156 | 13.2 | 7.19 | 0 | 23.9395 | 98.7339 | 64.7603 | 0 | 326 | 178.645 | 160.4 | 3.0544 | 173.637 | 150.109 | 0.015943 | 161.959 | 144.553 | 0.012013 | 297.328 | 297.313 | 667695 | 19.0229 | 625096 | 641761 | 601828 | 0 | 0 | 599111 | 726.851 | 0 | 0 | 0 | 0 | 599111 | 726.851 | 589178 | 577394.625
2289 | 2005-04-06 08:00 | 572 | 682 | 172 | 14.93 | 7.19 | 0 | 35.9396 | 108.97 | 49.9714 | 0 | 572 | 438.327 | 187.626 | 5.3592 | 438.327 | 175.588 | 0.027973 | 426.168 | 169.089 | 0.021078 | 577.42 | 577.409 | 1296720 | 26.2386 | 1266130 | 1259250 | 1224540 | 0 | 0 | 1213440 | 725.878 | 0 | 0 | 0 | 0 | 1213440 | 725.878 | 1192970 | 1169112.625
2290 | 2005-04-06 09:00 | 648 | 539 | 254 | 16.66 | 4.43 | 0 | 47.101 | 122.24 | 35.176 | 0 | 648 | 439.626 | 274.606 | 6.0713 | 439.626 | 256.987 | 0.03169 | 434.715 | 247.476 | 0.023879 | 661.748 | 661.733 | 1486090 | 32.1442 | 1462800 | 1418030 | 1381010 | 0 | 0 | 1366250 | 709.223 | 0 | 0 | 0 | 0 | 1366250 | 709.223 | 1343360 | 1316491.25
2291 | 2005-04-06 10:00 | 756 | 545 | 303 | 18.38 | 4.43 | 0 | 56.3796 | 141.244 | 20.4167 | 0 | 756 | 509.824 | 331.079 | 7.0831 | 509.824 | 309.836 | 0.036971 | 508.115 | 298.369 | 0.027859 | 782.317 | 782.307 | 1756870 | 36.6855 | 1745800 | 1659300 | 1615650 | 0 | 0 | 1594950 | 698.513 | 0 | 0 | 0 | 0 | 1594950 | 698.513 | 1566670 | 1535337.5
2292 | 2005-04-06 11:00 | 895 | 725 | 258 | 19.45 | 4.43 | 0 | 61.7179 | 168.576 | 6.0706 | 0 | 895 | 719.294 | 291.18 | 8.3855 | 719.294 | 272.497 | 0.043769 | 719.091 | 262.413 | 0.032981 | 952.09 | 952.082 | 2138140 | 41.7281 | 2146560 | 1995950 | 1944850 | 0 | 0 | 1914060 | 686.988 | 0 | 0 | 0 | 0 | 1914060 | 686.988 | 1875280 | 1837777.625
2293 | 2005-04-06 12:00 | 745 | 440 | 362 | 20.51 | 1.07 | 0 | 60.8096 | 199.811 | 9.8939 | 0 | 745 | 432.19 | 394.353 | 6.9801 | 432.19 | 369.051 | 0.036434 | 431.864 | 355.392 | 0.027453 | 763.666 | 763.642 | 1714950 | 42.8433 | 1701890 | 1572250 | 1534350 | 0 | 0 | 1514590 | 678.685 | 0 | 0 | 0 | 0 | 1514590 | 678.685 | 1489450 | 1459659.125
2294 | 2005-04-06 13:00 | 559 | 193 | 403 | 21.58 | 1.07 | 0 | 54.1345 | 224.844 | 24.4911 | 0 | 559 | 175.179 | 411.999 | 5.2374 | 175.179 | 385.564 | 0.027337 | 174.313 | 371.295 | 0.020599 | 529.26 | 529.244 | 1188540 | 37.0582 | 1154400 | 1093460 | 1065520 | 0 | 0 | 1056100 | 685.122 | 0 | 0 | 0 | 0 | 1056100 | 685.122 | 1040760 | 1019943.25
2295 | 2005-04-06 14:00 | 339 | 67 | 292 | 22.25 | 1.07 | 0 | 44.1932 | 241.96 | 39.2661 | 0 | 339 | 52.2007 | 302.772 | 3.1762 | 52.2007 | 283.346 | 0.016578 | 51.4395 | 272.86 | 0.012492 | 314.582 | 314.575 | 706455 | 31.45 | 663707 | 644146 | 627270 | 0 | 0 | 623972 | 684.344 | 0 | 0 | 0 | 0 | 623972 | 684.344 | 615101 | 602798.75
2296 | 2005-04-06 15:00 | 550 | 584 | 234 | 22.92 | 2.18 | 0 | 32.7382 | 254.194 | 54.0583 | 0 | 550 | 342.972 | 243.013 | 5.1531 | 342.972 | 227.421 | 0.026897 | 330.905 | 219.004 | 0.020268 | 533.431 | 533.418 | 1197920 | 37.4019 | 1164050 | 1100930 | 1073090 | 0 | 0 | 1063540 | 685.934 | 0 | 0 | 0 | 0 | 1063540 | 685.934 | 1048020 | 1027057.5
2297 | 2005-04-06 16:00 | 255 | 303 | 148 | 23.59 | 2.18 | 0 | 20.6236 | 263.932 | 68.8359 | 0 | 255 | 109.677 | 146.767 | 2.3891 | 109.677 | 137.35 | 0.012471 | 99.9722 | 132.267 | 0.0093968 | 225.281 | 225.272 | 505901 | 29.706 | 464417 | 454141 | 442818 | 0 | 0 | 441124 | 676.053 | 0 | 0 | 0 | 0 | 441124 | 676.053 | 434545 | 425853.9375
2298 | 2005-04-06 17:00 | 71 | 202 | 41 | 23.41 | 2.18 | 0 | 8.2925 | 272.584 | 83.5774 | 0 | 71 | 23.2677 | 39.3949 | 0.66522 | 23.2677 | 36.8673 | 0.0034722 | 14.0307 | 35.5028 | 0.0026164 | 48.0501 | 48.049 | 107906 | 24.7145 | 85969 | 86097.1 | 84018.4 | 0 | 0 | 83946.8 | 625.32 | 0 | 0 | 0 | 3831.73 | 80115.1 | 660 | 77455.9 | 75906.7422
2299 | 2005-04-06 18:00 | 1 | 20 | 0 | 23.22 | 4.9 | 0 | -3.9571 | 281.083 | 90 | 0 | 1 | 0 | 0 | 0.0093692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.22 | 0 | 0 | 0 | 0 | 0 | 0 | 660 | 0 | 0 | 0 | 0 | 0 | 660 | 0 | 0
2300 | 2005-04-06 19:00 | 0 | 0 | 0 | 23.04 | 4.9 | 0
2301 | 2005-04-06 20:00 | 0 | 0 | 0 | 22.32 | 4.9 | 0
2302 | 2005-04-06 21:00 | 0 | 0 | 0 | 21.6 | 6.6 | 0
2303 | 2005-04-06 22:00 | 0 | 0 | 0 | 20.87 | 6.6 | 0
2304 | 2005-04-06 23:00 | 0 | 0 | 0 | 19.82 | 6.6 | 0
2305 | 2005-04-07 | 0 | 0 | 0 | 18.77 | 13.14 | 0
2306 | 2005-04-07 01:00 | 0 | 0 | 0 | 17.71 | 13.14 | 0
2307 | 2005-04-07 02:00 | 0 | 0 | 0 | 16.97 | 13.14 | 0
2308 | 2005-04-07 03:00 | 0 | 0 | 0 | 16.23 | 7.41 | 0
2309 | 2005-04-07 04:00 | 0 | 0 | 0 | 15.49 | 7.41 | 0
2310 | 2005-04-07 05:00 | 10 | 109 | 4 | 15.21 | 7.41 | 0 | -0.42741 | 81.1986 | 90 | 0 | 10 | 0 | 2.9902 | 0.093692 | 0 | 2.7983 | 0 | 0 | 2.6947 | 0 | 2.6139 | 2.6138 | 5869.88 | 15.2605 | 1632.35 | 1627.33 | 1615.55 | 0 | 0 | 1615.48 | 381.607 | 0 | 0 | 0 | 1615.48 | 0 | 660 | 0 | 0
2311 | 2005-04-07 06:00 | 168 | 444 | 76 | 14.92 | 9.93 | 0 | 11.8877 | 89.6277 | 79.3967 | 0 | 168 | 82.1802 | 74.5613 | 1.574 | 60.3314 | 69.7773 | 0.0082159 | 46.9542 | 67.1949 | 0.0061909 | 110.731 | 110.735 | 248676 | 16.7476 | 216315 | 224963 | 209318 | 0 | 0 | 208951 | 692.651 | 0 | 0 | 0 | 0 | 208951 | 692.651 | 203119 | 199057.0625
2312 | 2005-04-07 07:00 | 383 | 707 | 93 | 14.63 | 9.93 | 0 | 24.2119 | 98.4398 | 64.6429 | 0 | 383 | 302.833 | 100.987 | 3.5884 | 295.368 | 94.5077 | 0.01873 | 275.652 | 91.01 | 0.014114 | 355.676 | 355.657 | 798730 | 20.4998 | 756920 | 771712 | 708952 | 0 | 0 | 705154 | 727.861 | 0 | 0 | 0 | 0 | 705154 | 727.861 | 693535 | 679664.75
2313 | 2005-04-07 08:00 | 609 | 826 | 121 | 16.03 | 9.93 | 0 | 36.2271 | 108.658 | 49.858 | 0 | 609 | 532.339 | 134.536 | 5.7059 | 532.339 | 125.904 | 0.029783 | 517.669 | 121.244 | 0.022442 | 619.768 | 619.76 | 1391830 | 26.2587 | 1364760 | 1357280 | 1319850 | 0 | 0 | 1307060 | 728.225 | 0 | 0 | 0 | 0 | 1307060 | 728.225 | 1284570 | 1258874.625
2314 | 2005-04-07 09:00 | 787 | 846 | 165 | 17.42 | 9.02 | 0 | 47.4173 | 121.923 | 35.062 | 0 | 787 | 691.464 | 183.44 | 7.3736 | 691.464 | 171.67 | 0.038488 | 683.799 | 165.317 | 0.029001 | 823.671 | 823.661 | 1849730 | 31.7996 | 1843210 | 1790470 | 1743550 | 0 | 0 | 1720610 | 716.383 | 0 | 0 | 0 | 0 | 1720610 | 716.383 | 1687930 | 1654172
2315 | 2005-04-07 10:00 | 800 | 586 | 311 | 18.81 | 9.02 | 0 | 56.7367 | 140.997 | 20.2896 | 0 | 800 | 548.53 | 338.804 | 7.4954 | 548.53 | 317.066 | 0.039123 | 546.716 | 305.331 | 0.02948 | 826.514 | 826.504 | 1856120 | 33.2392 | 1849920 | 1785740 | 1737550 | 0 | 0 | 1714610 | 713.111 | 0 | 0 | 0 | 0 | 1714610 | 713.111 | 1682200 | 1648554.875
2316 | 2005-04-07 11:00 | 919 | 804 | 210 | 19.25 | 9.02 | 0 | 62.0999 | 168.591 | 5.8392 | 0 | 919 | 798.087 | 241.349 | 8.6103 | 798.087 | 225.864 | 0.044943 | 797.879 | 217.505 | 0.033865 | 984.955 | 984.948 | 2211950 | 36.4453 | 2224350 | 2118310 | 2062270 | 0 | 0 | 2029450 | 705.554 | 0 | 0 | 0 | 0 | 2029450 | 705.554 | 1986370 | 1946641.375
2317 | 2005-04-07 12:00 | 963 | 788 | 274 | 19.69 | 12.33 | 0 | 61.15 | 200.168 | 9.8565 | 0 | 963 | 775.021 | 306.069 | 9.0226 | 775.021 | 286.431 | 0.047095 | 774.44 | 275.831 | 0.035487 | 1018.8 | 1018.78 | 2287930 | 34.2379 | 2304470 | 2216180 | 2159600 | 0 | 0 | 2124290 | 712.089 | 77756 | 0 | 0 | 0 | 2044210 | 746.806 | 1999970 | 1959971.5
2318 | 2005-04-07 13:00 | 574 | 222 | 394 | 20.12 | 12.33 | 0 | 54.3975 | 225.318 | 24.5088 | 0 | 574 | 201.435 | 402.13 | 5.3779 | 201.435 | 376.329 | 0.028071 | 200.437 | 362.401 | 0.021152 | 545.974 | 545.958 | 1226080 | 27.9161 | 1193120 | 1177990 | 1146300 | 0 | 0 | 1136330 | 717.076 | 0 | 0 | 0 | 0 | 1136330 | 717.076 | 1117830 | 1095469.75
2319 | 2005-04-07 14:00 | 235 | 19 | 222 | 19.44 | 12.33 | 0 | 44.3972 | 242.41 | 39.292 | 0 | 235 | 14.3806 | 208.594 | 2.2018 | 14.3806 | 195.21 | 0.011492 | 14.1705 | 187.985 | 0.0086598 | 196.1 | 196.093 | 440375 | 22.2402 | 400195 | 405375 | 394244 | 0 | 0 | 392986 | 698.031 | 0 | 0 | 0 | 0 | 392986 | 698.031 | 386193 | 378468.8438
2320 | 2005-04-07 15:00 | 499 | 537 | 207 | 18.75 | 11.28 | 0 | 32.9083 | 254.6 | 54.083 | 0 | 499 | 315.28 | 216.456 | 4.6752 | 315.28 | 202.568 | 0.024403 | 304.171 | 195.071 | 0.018388 | 484.283 | 484.27 | 1087540 | 26.1128 | 1050500 | 1045320 | 1016470 | 0 | 0 | 1008670 | 719.19 | 0 | 0 | 0 | 0 | 1008670 | 719.19 | 992548 | 972697
2321 | 2005-04-07 16:00 | 297 | 577 | 92 | 18.06 | 11.28 | 0 | 20.7781 | 264.305 | 68.8552 | 0 | 297 | 208.453 | 97.8202 | 2.7827 | 208.453 | 91.5439 | 0.014524 | 189.982 | 88.1559 | 0.010944 | 269.805 | 269.802 | 605910 | 22.162 | 563327 | 570603 | 554665 | 0 | 0 | 552274 | 712.146 | 0 | 0 | 0 | 0 | 552274 | 712.146 | 543351 | 532484.125
2322 | 2005-04-07 17:00 | 20 | 0 | 20 | 16.99 | 11.28 | 0 | 8.4448 | 272.937 | 83.5881 | 0 | 20 | 0 | 18.5035 | 0.18738 | 0 | 17.3162 | 0.00097808 | 0 | 16.6754 | 0.00073701 | 16.1758 | 16.1757 | 36326.5 | 17.2359 | 24342.9 | 25355.7 | 24793 | 0 | 0 | 24786 | 590.837 | 0 | 0 | 0 | 4619.08 | 20167 | 660 | 19425 | 19036.5195
2323 | 2005-04-07 18:00 | 0 | 0 | 0 | 15.92 | 11.83 | 0
2324 | 2005-04-07 19:00 | 0 | 0 | 0 | 14.85 | 11.83 | 0
2325 | 2005-04-07 20:00 | 0 | 0 | 0 | 13.55 | 11.83 | 0
2326 | 2005-04-07 21:00 | 0 | 0 | 0 | 12.24 | 12.31 | 0
2327 | 2005-04-07 22:00 | 0 | 0 | 0 | 10.94 | 12.31 | 0
2328 | 2005-04-07 23:00 | 0 | 0 | 0 | 10.19 | 12.31 | 0
2329 | 2005-04-08 | 0 | 0 | 0 | 9.44 | 10.45 | 0
2330 | 2005-04-08 01:00 | 0 | 0 | 0 | 8.7 | 10.45 | 0
2331 | 2005-04-08 02:00 | 0 | 0 | 0 | 7.77 | 10.45 | 0
2332 | 2005-04-08 03:00 | 0 | 0 | 0 | 6.85 | 11.05 | 0
2333 | 2005-04-08 04:00 | 0 | 0 | 0 | 5.92 | 11.05 | 0
2334 | 2005-04-08 05:00 | 1 | 41 | 0 | 6.03 | 11.05 | 0 | -0.15681 | 80.9312 | 90 | 0 | 1 | 0 | 0 | 0.0093692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.03 | 0 | 0 | 0 | 0 | 0 | 0 | 660 | 0 | 0 | 0 | 0 | 0 | 660 | 0 | 0
2335 | 2005-04-08 06:00 | 178 | 511 | 70 | 6.14 | 8.88 | 0 | 12.1534 | 89.3495 | 79.2739 | 0 | 178 | 95.4749 | 70.3383 | 1.6677 | 71.4597 | 65.8253 | 0.0087049 | 55.8349 | 63.3891 | 0.0065594 | 115.654 | 115.65 | 259710 | 8.1767 | 226890 | 245243 | 225135 | 0 | 0 | 224742 | 724 | 0 | 0 | 0 | 0 | 224742 | 724 | 218120 | 213757.875
2336 | 2005-04-08 07:00 | 403 | 778 | 80 | 6.25 | 8.88 | 0 | 24.4816 | 98.1457 | 64.5279 | 0 | 403 | 335.215 | 87.7441 | 3.7758 | 328.151 | 82.1142 | 0.019708 | 306.408 | 79.0752 | 0.014851 | 373.933 | 373.917 | 839740 | 12.8349 | 798364 | 840618 | 779185 | 0 | 0 | 774797 | 741.999 | 0 | 0 | 0 | 0 | 774797 | 741.999 | 761594 | 746361.875
2337 | 2005-04-08 08:00 | 609 | 863 | 96 | 8.04 | 8.88 | 0 | 36.5118 | 108.345 | 49.7479 | 0 | 609 | 557.114 | 108.605 | 5.7059 | 557.114 | 101.637 | 0.029783 | 541.859 | 97.8752 | 0.022442 | 620.564 | 620.558 | 1393610 | 18.9685 | 1366610 | 1401290 | 1360520 | 0 | 0 | 1347750 | 751.698 | 0 | 0 | 0 | 0 | 1347750 | 751.698 | 1323180 | 1296715.875
2338 | 2005-04-08 09:00 | 774 | 853 | 143 | 9.83 | 6.86 | 0 | 47.7306 | 121.604 | 34.9526 | 0 | 774 | 698.906 | 161.003 | 7.2518 | 698.906 | 150.673 | 0.037852 | 691.216 | 145.097 | 0.028522 | 811.251 | 811.245 | 1821850 | 26.0555 | 1813940 | 1805650 | 1757590 | 0 | 0 | 1735500 | 735.983 | 0 | 0 | 0 | 0 | 1735500 | 735.983 | 1701890 | 1667857
2339 | 2005-04-08 10:00 | 917 | 904 | 159 | 11.63 | 6.86 | 0 | 57.091 | 140.745 | 20.1701 | 0 | 917 | 847.51 | 180.389 | 8.5916 | 847.51 | 168.815 | 0.044845 | 844.742 | 162.567 | 0.033792 | 977.122 | 977.117 | 2194360 | 31.173 | 2205810 | 2149120 | 2091740 | 0 | 0 | 2059550 | 723.289 | 15471.1 | 0 | 0 | 0 | 2043560 | 737.918 | 1999990 | 1959991.875
2340 | 2005-04-08 11:00 | 950 | 886 | 166 | 12.8 | 6.86 | 0 | 62.4797 | 168.604 | 5.626 | 0 | 950 | 879.772 | 189.038 | 8.9008 | 879.772 | 176.909 | 0.046459 | 879.559 | 170.362 | 0.035008 | 1018.46 | 1018.44 | 2287170 | 33.1696 | 2303670 | 2225520 | 2167880 | 0 | 0 | 2132760 | 716.589 | 86013.9 | 0 | 0 | 0 | 2044750 | 751.811 | 1999930 | 1959927.5
2341 | 2005-04-08 12:00 | 966 | 912 | 166 | 13.98 | 11.38 | 0 | 61.4879 | 200.53 | 9.833 | 0 | 966 | 897.045 | 188.773 | 9.0507 | 897.045 | 176.661 | 0.047241 | 896.376 | 170.123 | 0.035597 | 1034.54 | 1034.53 | 2323280 | 29.6145 | 2341770 | 2296990 | 2235810 | 0 | 0 | 2199680 | 729.323 | 152307 | 0 | 0 | 0 | 2045650 | 773.76 | 1998310 | 1958344.25
2342 | 2005-04-08 13:00 | 872 | 928 | 116 | 15.16 | 11.38 | 0 | 54.6576 | 225.795 | 24.5313 | 0 | 872 | 843.142 | 127.972 | 8.17 | 843.142 | 119.761 | 0.042644 | 838.959 | 115.329 | 0.032134 | 925.69 | 925.683 | 2078850 | 29.1496 | 2084120 | 2048010 | 1994810 | 0 | 0 | 1965740 | 726.565 | 0 | 0 | 0 | 0 | 1965740 | 726.565 | 1924910 | 1886407.875
2343 | 2005-04-08 14:00 | 749 | 919 | 104 | 14.73 | 11.38 | 0 | 44.5989 | 242.861 | 39.3201 | 0 | 749 | 710.661 | 115.026 | 7.0175 | 710.661 | 107.645 | 0.036629 | 700.264 | 103.661 | 0.027601 | 779.834 | 779.828 | 1751300 | 26.5153 | 1739950 | 1728700 | 1682190 | 0 | 0 | 1661840 | 733.621 | 0 | 0 | 0 | 0 | 1661840 | 733.621 | 1630490 | 1597883.25
2344 | 2005-04-08 15:00 | 560 | 816 | 115 | 14.3 | 11.86 | 0 | 33.0768 | 255.006 | 54.1088 | 0 | 560 | 478.012 | 126.676 | 5.2468 | 478.012 | 118.548 | 0.027386 | 461.143 | 114.16 | 0.020636 | 558.065 | 558.06 | 1253260 | 22.4948 | 1221180 | 1234160 | 1200130 | 0 | 0 | 1189780 | 736.717 | 0 | 0 | 0 | 0 | 1189780 | 736.717 | 1169260 | 1145872
2345 | 2005-04-08 16:00 | 313 | 620 | 91 | 13.87 | 11.86 | 0 | 20.9316 | 264.676 | 68.8747 | 0 | 313 | 223.96 | 96.5874 | 2.9326 | 223.96 | 90.3902 | 0.015307 | 204.088 | 87.0449 | 0.011534 | 282.41 | 282.406 | 634212 | 18.017 | 591488 | 610173 | 593595 | 0 | 0 | 590977 | 728.368 | 0 | 0 | 0 | 0 | 590977 | 728.368 | 581202 | 569578.3125
2346 | 2005-04-08 17:00 | 119 | 453 | 50 | 13.11 | 11.86 | 0 | 8.5967 | 273.289 | 83.5982 | 0 | 119 | 51.4691 | 48.6827 | 1.1149 | 51.4691 | 45.5591 | 0.0058196 | 30.9621 | 43.873 | 0.0043852 | 72.5943 | 72.5904 | 163019 | 14.1759 | 135915 | 143427 | 139587 | 0 | 0 | 139421 | 681.668 | 0 | 0 | 0 | 0 | 139421 | 681.668 | 135014 | 132313.3906
2347 | 2005-04-08 18:00 | 2 | 51 | 1 | 12.35 | 12.23 | 0 | -3.6343 | 281.773 | 90 | 0 | 2 | 0 | 0.69999 | 0.018738 | 0 | 0.65508 | 0 | 0 | 0.63083 | 0 | 0.61191 | 0.6119 | 1374.17 | 12.3588 | 91.5975 | 90.2235 | 89.4878 | 0 | 0 | 89.4842 | 94.9067 | 0 | 0 | 0 | 89.4842 | 0 | 660 | 0 | 0
2348 | 2005-04-08 19:00 | 0 | 0 | 0 | 11.58 | 12.23 | 0
2349 | 2005-04-08 20:00 | 0 | 0 | 0 | 10.54 | 12.23 | 0
2350 | 2005-04-08 21:00 | 0 | 0 | 0 | 9.5 | 12.91 | 0
2351 | 2005-04-08 22:00 | 0 | 0 | 0 | 8.46 | 12.91 | 0
2352 | 2005-04-08 23:00 | 0 | 0 | 0 | 7.64 | 12.91 | 0
2353 | 2005-04-09 | 0 | 0 | 0 | 6.82 | 12.84 | 0
2354 | 2005-04-09 01:00 | 0 | 0 | 0 | 6.01 | 12.84 | 0
2355 | 2005-04-09 02:00 | 0 | 0 | 0 | 5.41 | 12.84 | 0
2356 | 2005-04-09 03:00 | 0 | 0 | 0 | 4.81 | 12.98 | 0
2357 | 2005-04-09 04:00 | 0 | 0 | 0 | 4.21 | 12.98 | 0
2358 | 2005-04-09 05:00 | 2 | 67 | 0 | 4.25 | 12.98 | 0 | 0.11168 | 80.6648 | 90 | 0 | 2 | 0 | 0 | 0.018738 | 0 | 0 | 9.7808e-05 | 0 | 0 | 7.3701e-05 | 7.149e-05 | 7.1369e-05 | 0.16042 | 4.25 | 0.00023958 | 0.0002337 | 0.00023157 | 0 | 0 | 0.00023157 | 1.9082 | 0 | 0 | 0 | 0.00023157 | 0 | 660 | 0 | 0
2359 | 2005-04-09 06:00 | 183 | 553 | 63 | 4.29 | 10.91 | 0 | 12.4168 | 89.0718 | 79.1529 | 0 | 183 | 105.025 | 63.5791 | 1.7146 | 79.9987 | 59.4997 | 0.0089495 | 62.7438 | 57.2977 | 0.0067436 | 116.447 | 116.481 | 261574 | 6.101 | 228788 | 249538 | 226837 | 0 | 0 | 226445 | 733.045 | 0 | 0 | 0 | 0 | 226445 | 733.045 | 219660 | 215267.2969
2360 | 2005-04-09 07:00 | 410 | 785 | 81 | 4.34 | 10.91 | 0 | 24.7487 | 97.8514 | 64.4153 | 0 | 410 | 339.378 | 88.595 | 3.8414 | 333.342 | 82.9106 | 0.020051 | 311.414 | 79.8421 | 0.015109 | 379.533 | 379.528 | 852339 | 10.2406 | 811053 | 863099 | 812197 | 0 | 0 | 807499 | 745.237 | 0 | 0 | 0 | 0 | 807499 | 745.237 | 793629 | 777756.625
2361 | 2005-04-09 08:00 | 622 | 880 | 95 | 5.94 | 10.91 | 0 | 36.7934 | 108.031 | 49.6411 | 0 | 622 | 569.8 | 107.351 | 5.8277 | 569.8 | 100.463 | 0.030418 | 554.295 | 96.7451 | 0.022921 | 631.531 | 631.526 | 1418250 | 15.7585 | 1392210 | 1446200 | 1404320 | 0 | 0 | 1391120 | 762.96 | 0 | 0 | 0 | 0 | 1391120 | 762.96 | 1364930 | 1337629.25
2362 | 2005-04-09 09:00 | 798 | 930 | 107 | 7.54 | 7.28 | 0 | 48.0407 | 121.283 | 34.8478 | 0 | 798 | 762.6 | 118.194 | 7.4766 | 762.6 | 110.61 | 0.039025 | 754.268 | 106.516 | 0.029406 | 834.989 | 834.979 | 1875150 | 23.8 | 1869890 | 1878880 | 1826180 | 0 | 0 | 1802910 | 744.577 | 0 | 0 | 0 | 0 | 1802910 | 744.577 | 1766760 | 1731421.125
2363 | 2005-04-09 10:00 | 920 | 957 | 115 | 9.15 | 7.28 | 0 | 57.4424 | 140.489 | 20.0581 | 0 | 920 | 897.161 | 126.761 | 8.6197 | 897.161 | 118.628 | 0.044992 | 894.264 | 114.237 | 0.033902 | 978.279 | 978.276 | 2196950 | 28.2005 | 2208540 | 2178980 | 2117250 | 0 | 0 | 2085120 | 733.048 | 41602.6 | 0 | 0 | 0 | 2044030 | 757.353 | 1998600 | 1958629.375
2364 | 2005-04-09 11:00 | 963 | 899 | 165 | 10.13 | 7.28 | 0 | 62.8573 | 168.616 | 5.4328 | 0 | 963 | 892.729 | 187.672 | 9.0226 | 892.729 | 175.631 | 0.047095 | 892.527 | 169.131 | 0.035487 | 1029.84 | 1029.84 | 2312740 | 30.1845 | 2330650 | 2280470 | 2218470 | 0 | 0 | 2182750 | 727.643 | 135667 | 0 | 0 | 0 | 2045490 | 769.725 | 1998610 | 1958635.125
2365 | 2005-04-09 12:00 | 922 | 847 | 177 | 11.11 | 7.04 | 0 | 61.8231 | 200.896 | 9.8233 | 0 | 922 | 832.765 | 199.724 | 8.6384 | 832.765 | 186.91 | 0.04509 | 832.145 | 179.992 | 0.033976 | 981.807 | 981.799 | 2204870 | 30.5229 | 2216880 | 2165900 | 2108020 | 0 | 0 | 2075420 | 724.352 | 30958.1 | 0 | 0 | 0 | 2043980 | 746.225 | 1999810 | 1959815
2366 | 2005-04-09 13:00 | 891 | 900 | 156 | 12.09 | 7.04 | 0 | 54.9149 | 226.274 | 24.5584 | 0 | 891 | 816.951 | 176.216 | 8.348 | 816.951 | 164.909 | 0.043574 | 812.889 | 158.806 | 0.032834 | 942.576 | 942.562 | 2116760 | 30.727 | 2124040 | 2073260 | 2018820 | 0 | 0 | 1988800 | 723.078 | 0 | 0 | 0 | 0 | 1988800 | 723.078 | 1947180 | 1908241
2367 | 2005-04-09 14:00 | 751 | 918 | 105 | 12.22 | 7.04 | 0 | 44.7982 | 243.312 | 39.3503 | 0 | 751 | 708.959 | 115.856 | 7.0363 | 708.959 | 108.422 | 0.036727 | 698.566 | 104.41 | 0.027675 | 778.913 | 778.915 | 1749240 | 27.6213 | 1737800 | 1718430 | 1669600 | 0 | 0 | 1649310 | 729.781 | 0 | 0 | 0 | 0 | 1649310 | 729.781 | 1618440 | 1586068.875
2368 | 2005-04-09 15:00 | 553 | 844 | 90 | 12.36 | 8.55 | 0 | 33.2436 | 255.41 | 54.1354 | 0 | 553 | 494.818 | 100.932 | 5.1812 | 494.818 | 94.4562 | 0.027044 | 477.33 | 90.9605 | 0.020378 | 551.261 | 551.255 | 1237980 | 22.2698 | 1205380 | 1219350 | 1188700 | 0 | 0 | 1178460 | 734.147 | 0 | 0 | 0 | 0 | 1178460 | 734.147 | 1158290 | 1135125.25
2369 | 2005-04-09 16:00 | 343 | 741 | 76 | 12.49 | 8.55 | 0 | 21.0841 | 265.045 | 68.8943 | 0 | 343 | 267.261 | 81.4001 | 3.2136 | 267.261 | 76.1773 | 0.016774 | 243.514 | 73.358 | 0.01264 | 307.378 | 307.372 | 690281 | 18.0156 | 647481 | 667771 | 649756 | 0 | 0 | 646650 | 731.224 | 0 | 0 | 0 | 0 | 646650 | 731.224 | 635940 | 623221.5
2370 | 2005-04-09 17:00 | 122 | 347 | 68 | 12.1 | 8.55 | 0 | 8.748 | 273.638 | 83.6078 | 0 | 122 | 39.5296 | 63.6122 | 1.143 | 39.5296 | 59.5307 | 0.0059663 | 23.7532 | 57.3275 | 0.0044957 | 78.6527 | 78.6494 | 176626 | 13.5139 | 148448 | 157093 | 152782 | 0 | 0 | 152587 | 689.375 | 0 | 0 | 0 | 0 | 152587 | 689.375 | 147781 | 144825.0938
2371 | 2005-04-09 18:00 | 3 | 41 | 2 | 11.71 | 8.01 | 0 | -3.4731 | 282.114 | 90 | 0 | 3 | 0 | 1.5806 | 0.028108 | 0 | 1.4792 | 0 | 0 | 1.4245 | 0 | 1.3817 | 1.3817 | 3102.84 | 11.7357 | 465.168 | 458.08 | 455.981 | 0 | 0 | 455.961 | 203.296 | 0 | 0 | 0 | 455.961 | 0 | 660 | 0 | 0
2372 | 2005-04-09 19:00 | 0 | 0 | 0 | 11.32 | 8.01 | 0
2373 | 2005-04-09 20:00 | 0 | 0 | 0 | 10.79 | 8.01 | 0
2374 | 2005-04-09 21:00 | 0 | 0 | 0 | 10.26 | 8.48 | 0
2375 | 2005-04-09 22:00 | 0 | 0 | 0 | 9.73 | 8.48 | 0
2376 | 2005-04-09 23:00 | 0 | 0 | 0 | 9.23 | 8.48 | 0
2377 | 2005-04-10 | 0 | 0 | 0 | 8.72 | 6.81 | 0
2378 | 2005-04-10 01:00 | 0 | 0 | 0 | 8.22 | 6.81 | 0
2379 | 2005-04-10 02:00 | 0 | 0 | 0 | 7.3 | 6.81 | 0
2380 | 2005-04-10 03:00 | 0 | 0 | 0 | 6.39 | 6.42 | 0
2381 | 2005-04-10 04:00 | 0 | 0 | 0 | 5.48 | 6.42 | 0
2382 | 2005-04-10 05:00 | 3 | 84 | 0 | 5.56 | 6.42 | 0 | 0.37795 | 80.3996 | 90 | 0 | 3 | 0 | 0 | 0.028108 | 0 | 0 | 0.00014671 | 0 | 0 | 0.00011055 | 0.00010723 | 0.00010588 | 0.23802 | 5.56 | 0.00052728 | 0.00051512 | 0.00051172 | 0 | 0 | 0.0005117 | 2.8282 | 0 | 0 | 0 | 0.0005117 | 0 | 660 | 0 | 0
2383 | 2005-04-10 06:00 | 188 | 578 | 60 | 5.63 | 5.57 | 0 | 12.6776 | 88.7947 | 79.0338 | 0 | 188 | 110.949 | 60.5768 | 1.7614 | 85.9236 | 56.6901 | 0.009194 | 67.6356 | 54.592 | 0.0069279 | 118.568 | 118.572 | 266268 | 8.2063 | 233294 | 251983 | 228593 | 0 | 0 | 228180 | 720.941 | 0 | 0 | 0 | 0 | 228180 | 720.941 | 221623 | 217190.5938
2384 | 2005-04-10 07:00 | 407 | 769 | 82 | 5.71 | 5.57 | 0 | 25.013 | 97.5571 | 64.3053 | 0 | 407 | 333.265 | 89.4439 | 3.8133 | 328.376 | 83.705 | 0.019904 | 306.927 | 80.6071 | 0.014998 | 375.922 | 375.918 | 844224 | 13.8779 | 802756 | 841629 | 796524 | 0 | 0 | 791838 | 731.216 | 0 | 0 | 0 | 0 | 791838 | 731.216 | 778754 | 763179.3125
2385 | 2005-04-10 08:00 | 627 | 881 | 96 | 7.49 | 5.57 | 0 | 37.072 | 107.716 | 49.5377 | 0 | 627 | 571.634 | 108.198 | 5.8745 | 571.634 | 101.256 | 0.030663 | 556.173 | 97.5082 | 0.023105 | 634.093 | 634.086 | 1423990 | 21.2673 | 1398180 | 1420050 | 1380910 | 0 | 0 | 1367490 | 744.331 | 0 | 0 | 0 | 0 | 1367490 | 744.331 | 1342970 | 1316110.625
2386 | 2005-04-10 09:00 | 801 | 931 | 106 | 9.28 | 4.24 | 0 | 48.3475 | 120.958 | 34.7478 | 0 | 801 | 764.277 | 116.952 | 7.5047 | 764.277 | 109.449 | 0.039172 | 755.983 | 105.398 | 0.029517 | 835.568 | 835.563 | 1876460 | 29.0763 | 1871270 | 1839070 | 1789390 | 0 | 0 | 1765970 | 726.897 | 0 | 0 | 0 | 0 | 1765970 | 726.897 | 1731640 | 1697004
2387 | 2005-04-10 10:00 | 907 | 930 | 121 | 11.06 | 4.24 | 0 | 57.7908 | 140.228 | 19.9538 | 0 | 907 | 873.192 | 132.735 | 8.4979 | 873.192 | 124.218 | 0.044356 | 870.404 | 119.621 | 0.033423 | 960.357 | 960.349 | 2156710 | 33.8127 | 2166130 | 2086440 | 2030700 | 0 | 0 | 1999520 | 713.374 | 0 | 0 | 0 | 0 | 1999520 | 713.374 | 1957530 | 1918381.375
2388 | 2005-04-10 11:00 | 968 | 946 | 125 | 12.25 | 4.24 | 0 | 63.2326 | 168.627 | 5.2612 | 0 | 968 | 940.198 | 136.793 | 9.0694 | 940.198 | 128.016 | 0.047339 | 940 | 123.279 | 0.035671 | 1031.41 | 1031.41 | 2316280 | 36.6863 | 2334380 | 2220950 | 2164050 | 0 | 0 | 2127840 | 705.082 | 81069.1 | 0 | 0 | 0 | 2043530 | 740.092 | 1999980 | 1959977.25
2389 | 2005-04-10 12:00 | 966 | 959 | 120 | 13.44 | 1.9 | 0 | 62.1556 | 201.266 | 9.8271 | 0 | 966 | 942.738 | 131.65 | 9.0507 | 942.738 | 123.203 | 0.047241 | 942.036 | 118.643 | 0.035597 | 1028.89 | 1028.89 | 2310630 | 41.9009 | 2328420 | 2164120 | 2108510 | 0 | 0 | 2072610 | 689.115 | 27817.2 | 0 | 0 | 0 | 2043570 | 709.454 | 1999980 | 1959983.75
2390 | 2005-04-10 13:00 | 871 | 915 | 121 | 14.63 | 1.9 | 0 | 55.1693 | 226.755 | 24.5898 | 0 | 871 | 830.832 | 132.67 | 8.1606 | 830.832 | 124.157 | 0.042596 | 826.689 | 119.562 | 0.032097 | 917.895 | 917.891 | 2061350 | 40.0205 | 2065700 | 1935300 | 1885190 | 0 | 0 | 1856550 | 690.948 | 0 | 0 | 0 | 0 | 1856550 | 690.948 | 1819810 | 1783414.625
2391 | 2005-04-10 14:00 | 742 | 901 | 105 | 15.03 | 1.9 | 0 | 44.9952 | 243.763 | 39.3825 | 0 | 742 | 696.352 | 115.651 | 6.952 | 696.352 | 108.23 | 0.036287 | 686.124 | 104.225 | 0.027343 | 766.664 | 766.657 | 1721720 | 36.2371 | 1708970 | 1627420 | 1586640 | 0 | 0 | 1566710 | 699.234 | 0 | 0 | 0 | 0 | 1566710 | 699.234 | 1539270 | 1508481.375
2392 | 2005-04-10 15:00 | 565 | 816 | 116 | 15.43 | 4.27 | 0 | 33.4087 | 255.813 | 54.1627 | 0 | 565 | 477.441 | 127.181 | 5.2936 | 477.441 | 119.02 | 0.027631 | 460.54 | 114.616 | 0.02082 | 557.921 | 557.916 | 1252930 | 28.6223 | 1220840 | 1201620 | 1170210 | 0 | 0 | 1159770 | 715.228 | 0 | 0 | 0 | 0 | 1159770 | 715.228 | 1140890 | 1118067.625
2393 | 2005-04-10 16:00 | 324 | 672 | 80 | 15.83 | 4.27 | 0 | 21.2355 | 265.413 | 68.9139 | 0 | 324 | 242.361 | 85.1821 | 3.0356 | 242.361 | 79.7167 | 0.015845 | 220.797 | 76.7664 | 0.01194 | 288.648 | 288.645 | 648223 | 22.6552 | 605455 | 611853 | 595818 | 0 | 0 | 593064 | 712.564 | 0 | 0 | 0 | 0 | 593064 | 712.564 | 583748 | 572073.0625
2394 | 2005-04-10 17:00 | 93 | 448 | 23 | 15.81 | 4.27 | 0 | 8.8987 | 273.985 | 83.6168 | 0 | 93 | 50.31 | 23.0708 | 0.87134 | 50.31 | 21.5905 | 0.0045481 | 30.1994 | 20.7915 | 0.0034271 | 49.4645 | 49.4631 | 111081 | 16.9796 | 88802 | 92550.8 | 90240.7 | 0 | 0 | 90165.1 | 653.338 | 0 | 0 | 0 | 117.743 | 90047.4 | 660 | 87112.1 | 85369.8594
2395 | 2005-04-10 18:00 | 2 | 56 | 0 | 15.78 | 3.42 | 0 | -3.3121 | 282.453 | 90 | 0 | 2 | 0 | 0 | 0.018738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.78 | 0 | 0 | 0 | 0 | 0 | 0 | 660 | 0 | 0 | 0 | 0 | 0 | 660 | 0 | 0
2396 | 2005-04-10 19:00 | 0 | 0 | 0 | 15.76 | 3.42 | 0
2397 | 2005-04-10 20:00 | 0 | 0 | 0 | 15.44 | 3.42 | 0
2398 | 2005-04-10 21:00 | 0 | 0 | 0 | 15.11 | 4.48 | 0
2399 | 2005-04-10 22:00 | 0 | 0 | 0 | 14.79 | 4.48 | 0
2400 | 2005-04-10 23:00 | 0 | 0 | 0 | 14.07 | 4.48 | 0
2401 | 2005-04-11 | 0 | 0 | 0 | 13.34 | 2.36 | 0
2402 | 2005-04-11 01:00 | 0 | 0 | 0 | 12.61 | 2.36 | 0
2403 | 2005-04-11 02:00 | 0 | 0 | 0 | 11.92 | 2.36 | 0
2404 | 2005-04-11 03:00 | 0 | 0 | 0 | 11.22 | 0.45 | 0
2405 | 2005-04-11 04:00 | 0 | 0 | 0 | 10.52 | 0.45 | 0
2406 | 2005-04-11 05:00 | 5 | 90 | 0 | 10.38 | 0.45 | 0 | 0.64188 | 80.1354 | 90 | 0 | 5 | 0 | 0 | 0.046846 | 0 | 0 | 0.00024452 | 0 | 0 | 0.00018425 | 0.00017872 | 0.00018018 | 0.40497 | 10.38 | 0.0015251 | 0.0014983 | 0.0014859 | 0 | 0 | 0.0014858 | 4.835 | 0 | 0 | 0 | 0.0014858 | 0 | 660 | 0 | 0
2407 | 2005-04-11 06:00 | 186 | 550 | 62 | 10.25 | 1.43 | 0 | 12.9359 | 88.5182 | 78.9167 | 0 | 186 | 106.482 | 62.3718 | 1.7427 | 83.7434 | 58.3699 | 0.0090962 | 66.149 | 56.2097 | 0.0068542 | 118.695 | 118.688 | 266532 | 13.6382 | 233450 | 246034 | 223655 | 0 | 0 | 223245 | 706.703 | 0 | 0 | 0 | 0 | 223245 | 706.703 | 217017 | 212677.0625
2408 | 2005-04-11 07:00 | 416 | 782 | 82 | 10.11 | 1.43 | 0 | 25.2743 | 97.2628 | 64.1979 | 0 | 416 | 340.502 | 89.2847 | 3.8976 | 336.503 | 83.5561 | 0.020344 | 314.673 | 80.4637 | 0.01533 | 383.297 | 383.274 | 860740 | 21.0512 | 819422 | 833329 | 793092 | 0 | 0 | 788244 | 714.843 | 0 | 0 | 0 | 0 | 788244 | 714.843 | 775835 | 760318.25
2409 | 2005-04-11 08:00 | 625 | 828 | 123 | 12.11 | 1.43 | 0 | 37.3473 | 107.4 | 49.4377 | 0 | 625 | 538.104 | 135.693 | 5.8558 | 538.104 | 126.986 | 0.030565 | 523.634 | 122.287 | 0.023031 | 626.565 | 626.563 | 1407100 | 29.9963 | 1380620 | 1350910 | 1314790 | 0 | 0 | 1301580 | 714.254 | 0 | 0 | 0 | 0 | 1301580 | 714.254 | 1279840 | 1254245
2410 | 2005-04-11 09:00 | 760 | 773 | 180 | 14.11 | 1.93 | 0 | 48.6509 | 120.63 | 34.6525 | 0 | 760 | 635.564 | 201.364 | 7.1206 | 635.564 | 188.444 | 0.037167 | 628.712 | 181.47 | 0.028006 | 785.903 | 785.892 | 1764910 | 35.8056 | 1754220 | 1673870 | 1629590 | 0 | 0 | 1608760 | 702.38 | 0 | 0 | 0 | 0 | 1608760 | 702.38 | 1579940 | 1548339
2411 | 2005-04-11 10:00 | 928 | 905 | 161 | 16.11 | 1.93 | 0 | 58.1361 | 139.962 | 19.8572 | 0 | 928 | 849.396 | 181.531 | 8.6946 | 849.396 | 169.884 | 0.045383 | 846.711 | 163.596 | 0.034197 | 980.032 | 980.025 | 2200890 | 43.1649 | 2212690 | 2044180 | 1995340 | 0 | 0 | 1962450 | 681.871 | 0 | 0 | 0 | 0 | 1962450 | 681.871 | 1921900 | 1883458.75
2412 | 2005-04-11 11:00 | 964 | 934 | 129 | 17.25 | 1.93 | 0 | 63.6053 | 168.636 | 5.1132 | 0 | 964 | 928.467 | 140.64 | 9.0319 | 928.467 | 131.616 | 0.047144 | 928.282 | 126.745 | 0.035524 | 1023.41 | 1023.41 | 2298320 | 45.5025 | 2315430 | 2116670 | 2065410 | 0 | 0 | 2029680 | 676.342 | 0 | 0 | 0 | 0 | 2029680 | 676.342 | 1986500 | 1946772
2413 | 2005-04-11 12:00 | 961 | 947 | 123 | 18.39 | 1.82 | 0 | 62.4853 | 201.64 | 9.844 | 0 | 961 | 930.961 | 134.499 | 9.0038 | 930.961 | 125.869 | 0.046997 | 930.265 | 121.211 | 0.035413 | 1019.97 | 1019.96 | 2290570 | 46.7552 | 2307250 | 2096840 | 2047030 | 0 | 0 | 2011510 | 671.904 | 0 | 0 | 0 | 0 | 2011510 | 671.904 | 1969050 | 1929665.875
2414 | 2005-04-11 13:00 | 884 | 934 | 116 | 19.53 | 1.82 | 0 | 55.4207 | 227.238 | 24.6254 | 0 | 884 | 847.949 | 127.29 | 8.2824 | 847.949 | 119.122 | 0.043231 | 843.708 | 114.714 | 0.032576 | 929.7 | 929.693 | 2087850 | 45.385 | 2093590 | 1913720 | 1867900 | 0 | 0 | 1838450 | 674.968 | 0 | 0 | 0 | 0 | 1838450 | 674.968 | 1802590 | 1766536
2415 | 2005-04-11 14:00 | 756 | 871 | 138 | 20.06 | 1.82 | 0 | 45.1899 | 244.212 | 39.4166 | 0 | 756 | 672.969 | 153.84 | 7.0831 | 672.969 | 143.969 | 0.036971 | 663.063 | 138.641 | 0.027859 | 777.68 | 777.671 | 1746460 | 41.6872 | 1734880 | 1611620 | 1572900 | 0 | 0 | 1552380 | 682.895 | 0 | 0 | 0 | 0 | 1552380 | 682.895 | 1525940 | 1495419.125
2416 | 2005-04-11 15:00 | 539 | 772 | 112 | 20.59 | 2.94 | 0 | 33.5723 | 256.214 | 54.1908 | 0 | 539 | 451.786 | 123.584 | 5.05 | 451.786 | 115.655 | 0.026359 | 435.766 | 111.374 | 0.019862 | 530.746 | 530.739 | 1191910 | 34.2891 | 1157840 | 1110910 | 1083020 | 0 | 0 | 1073560 | 695.306 | 0 | 0 | 0 | 0 | 1073560 | 695.306 | 1057380 | 1036229.125
2417 | 2005-04-11 16:00 | 312 | 621 | 85 | 21.13 | 2.94 | 0 | 21.386 | 265.778 | 68.9335 | 0 | 312 | 223.765 | 89.9249 | 2.9232 | 223.765 | 84.1551 | 0.015258 | 203.827 | 81.0406 | 0.011497 | 276.333 | 276.33 | 620567 | 28.2624 | 577902 | 569203 | 554634 | 0 | 0 | 552091 | 690.135 | 0 | 0 | 0 | 0 | 552091 | 690.135 | 543850 | 532973
2418 | 2005-04-11 17:00 | 91 | 414 | 25 | 20.89 | 2.94 | 0 | 9.049 | 274.33 | 83.6252 | 0 | 91 | 46.5933 | 24.9301 | 0.8526 | 46.5933 | 23.3305 | 0.0044503 | 27.9411 | 22.4671 | 0.0033534 | 48.8993 | 48.8983 | 109813 | 22.1521 | 87668.8 | 88989.1 | 86907.1 | 0 | 0 | 86832.8 | 635.059 | 0 | 0 | 0 | 1931.44 | 84901.4 | 660 | 82107.6 | 80465.4766
2419 | 2005-04-11 18:00 | 2 | 54 | 0 | 20.64 | 4.56 | 0 | -3.1512 | 282.789 | 90 | 0 | 2 | 0 | 0 | 0.018738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.64 | 0 | 0 | 0 | 0 | 0 | 0 | 660 | 0 | 0 | 0 | 0 | 0 | 660 | 0 | 0
2420 | 2005-04-11 19:00 | 0 | 0 | 0 | 20.4 | 4.56 | 0
2421 | 2005-04-11 20:00 | 0 | 0 | 0 | 19.37 | 4.56 | 0
2422 | 2005-04-11 21:00 | 0 | 0 | 0 | 18.33 | 5.53 | 0
2423 | 2005-04-11 22:00 | 0 | 0 | 0 | 17.3 | 5.53 | 0
2424 | 2005-04-11 23:00 | 0 | 0 | 0 | 16.31 | 5.53 | 0
2425 | 2005-04-12 | 0 | 0 | 0 | 15.32 | 4.36 | 0
2426 | 2005-04-12 01:00 | 0 | 0 | 0 | 14.33 | 4.36 | 0
2427 | 2005-04-12 02:00 | 0 | 0 | 0 | 13.54 | 4.36 | 0
2428 | 2005-04-12 03:00 | 0 | 0 | 0 | 12.75 | 5.29 | 0
2429 | 2005-04-12 04:00 | 0 | 0 | 0 | 11.96 | 5.29 | 0
2430 | 2005-04-12 05:00 | 7 | 96 | 1 | 11.64 | 5.29 | 0 | 0.90334 | 79.8724 | 90 | 0 | 7 | 0 | 0.90287 | 0.065585 | 0 | 0.84494 | 0.00034233 | 0 | 0.81367 | 0.00025795 | 0.78951 | 0.7895 | 1773.01 | 11.6575 | 152.371 | 149.966 | 149.189 | 0 | 0 | 149.182 | 118.131 | 0 | 0 | 0 | 149.182 | 0 | 660 | 0 | 0
2431 | 2005-04-12 06:00 | 194 | 581 | 61 | 11.33 | 5.86 | 0 | 13.1914 | 88.2425 | 78.8018 | 0 | 194 | 113.184 | 61.2829 | 1.8176 | 90.2885 | 57.3509 | 0.0094874 | 71.5571 | 55.2283 | 0.007149 | 122.989 | 122.96 | 276123 | 13.9521 | 242601 | 255345 | 231759 | 0 | 0 | 231318 | 706.767 | 0 | 0 | 0 | 0 | 231318 | 706.767 | 224994 | 220494.3906
2432 | 2005-04-12 07:00 | 417 | 779 | 81 | 11.01 | 5.86 | 0 | 25.5326 | 96.9685 | 64.0932 | 0 | 417 | 340.586 | 88.1173 | 3.907 | 337.359 | 82.4635 | 0.020393 | 315.62 | 79.4116 | 0.015367 | 383.195 | 383.182 | 860531 | 19.1813 | 819169 | 839937 | 805091 | 0 | 0 | 800207 | 722.223 | 0 | 0 | 0 | 0 | 800207 | 722.223 | 787315 | 771568.4375
2433 | 2005-04-12 08:00 | 625 | 865 | 97 | 13.02 | 5.86 | 0 | 37.6193 | 107.083 | 49.3412 | 0 | 625 | 563.588 | 108.839 | 5.8558 | 563.588 | 101.856 | 0.030565 | 548.518 | 98.0865 | 0.023031 | 627.228 | 627.223 | 1408590 | 26.3954 | 1382160 | 1373760 | 1336510 | 0 | 0 | 1323400 | 728.116 | 0 | 0 | 0 | 0 | 1323400 | 728.116 | 1300570 | 1274561.625
2434 | 2005-04-12 09:00 | 793 | 904 | 112 | 15.03 | 3.58 | 0 | 48.9507 | 120.3 | 34.562 | 0 | 793 | 743.64 | 122.738 | 7.4298 | 743.64 | 114.863 | 0.038781 | 735.671 | 110.612 | 0.029222 | 820.923 | 820.916 | 1843570 | 35.3413 | 1836740 | 1756540 | 1710390 | 0 | 0 | 1687630 | 704.856 | 0 | 0 | 0 | 0 | 1687630 | 704.856 | 1656280 | 1623152.25
2435 | 2005-04-12 10:00 | 901 | 905 | 131 | 17.05 | 3.58 | 0 | 58.478 | 139.691 | 19.7684 | 0 | 901 | 850.057 | 142.48 | 8.4417 | 850.057 | 133.338 | 0.044063 | 847.395 | 128.403 | 0.033202 | 946.556 | 946.548 | 2125710 | 40.4697 | 2133460 | 1995100 | 1945460 | 0 | 0 | 1914830 | 689.896 | 0 | 0 | 0 | 0 | 1914830 | 689.896 | 1876000 | 1838484.125
2436 | 2005-04-12 11:00 | 968 | 937 | 128 | 18.73 | 3.58 | 0 | 63.9755 | 168.643 | 4.9902 | 0 | 968 | 931.237 | 139.358 | 9.0694 | 931.237 | 130.417 | 0.047339 | 931.06 | 125.59 | 0.035671 | 1024.99 | 1024.98 | 2301850 | 44.0903 | 2319160 | 2134060 | 2080280 | 0 | 0 | 2044530 | 681.362 | 3334.67 | 0 | 0 | 0 | 2041040 | 685.138 | 1997450 | 1957501.625
2437 | 2005-04-12 12:00 | 977 | 967 | 119 | 20.41 | 4.02 | 0 | 62.8122 | 202.018 | 9.8737 | 0 | 977 | 950.285 | 130.136 | 9.1537 | 950.285 | 121.786 | 0.047779 | 949.571 | 117.279 | 0.036003 | 1034.88 | 1034.88 | 2324070 | 45.2847 | 2342600 | 2143900 | 2090270 | 0 | 0 | 2053800 | 677.477 | 9666.19 | 0 | 0 | 0 | 2043670 | 689.048 | 1999990 | 1959994.25
2438 | 2005-04-12 13:00 | 897 | 949 | 114 | 22.09 | 4.02 | 0 | 55.6691 | 227.723 | 24.665 | 0 | 897 | 861.669 | 125.002 | 8.4042 | 861.669 | 116.982 | 0.043867 | 857.344 | 112.653 | 0.033055 | 940.928 | 940.92 | 2113080 | 44.7064 | 2120160 | 1944400 | 1897960 | 0 | 0 | 1867830 | 677.893 | 0 | 0 | 0 | 0 | 1867830 | 677.893 | 1830850 | 1794235.125
2439 | 2005-04-12 14:00 | 759 | 920 | 105 | 22.39 | 4.02 | 0 | 45.3823 | 244.661 | 39.4523 | 0 | 759 | 709.444 | 115.245 | 7.1112 | 709.444 | 107.851 | 0.037118 | 698.977 | 103.859 | 0.027969 | 778.778 | 778.774 | 1748920 | 41.1089 | 1737470 | 1618430 | 1578670 | 0 | 0 | 1558090 | 684.343 | 0 | 0 | 0 | 0 | 1558090 | 684.343 | 1531420 | 1500793.5
2440 | 2005-04-12 15:00 | 570 | 817 | 116 | 22.7 | 6.27 | 0 | 33.7343 | 256.613 | 54.2195 | 0 | 570 | 477.985 | 126.692 | 5.3405 | 477.985 | 118.564 | 0.027875 | 461.009 | 114.176 | 0.021005 | 557.949 | 557.946 | 1253000 | 34.2885 | 1220910 | 1171660 | 1142120 | 0 | 0 | 1131650 | 696.8 | 0 | 0 | 0 | 0 | 1131650 | 696.8 | 1114230 | 1091948.5
2441 | 2005-04-12 16:00 | 326 | 631 | 94 | 23 | 6.27 | 0 | 21.5354 | 266.142 | 68.9528 | 0 | 326 | 226.982 | 98.5438 | 3.0544 | 226.982 | 92.2211 | 0.015943 | 206.73 | 88.808 | 0.012013 | 286.683 | 286.677 | 643803 | 28.9543 | 601048 | 590131 | 574711 | 0 | 0 | 571980 | 689.422 | 0 | 0 | 0 | 0 | 571980 | 689.422 | 563564 | 552293.125
2442 | 2005-04-12 17:00 | 121 | 420 | 53 | 22.38 | 6.27 | 0 | 9.1988 | 274.672 | 83.6328 | 0 | 121 | 47.1742 | 50.8259 | 1.1337 | 47.1742 | 47.5648 | 0.0059174 | 28.2643 | 45.8045 | 0.0044589 | 71.851 | 71.8497 | 161357 | 23.8723 | 134389 | 135167 | 131680 | 0 | 0 | 131517 | 648.366 | 0 | 0 | 0 | 634.25 | 130883 | 660 | 126937 | 124398.2188
2443 | 2005-04-12 18:00 | 3 | 58 | 1 | 21.77 | 6.21 | 0 | -2.9905 | 283.122 | 90 | 0 | 3 | 0 | 0.7295 | 0.028108 | 0 | 0.6827 | 0 | 0 | 0.65743 | 0 | 0.63771 | 0.6377 | 1432.12 | 21.7833 | 99.4758 | 99.0966 | 98.4128 | 0 | 0 | 98.4088 | 98.3413 | 0 | 0 | 0 | 98.4088 | 0 | 660 | 0 | 0
2444 | 2005-04-12 19:00 | 0 | 0 | 0 | 21.15 | 6.21 | 0
2445 | 2005-04-12 20:00 | 0 | 0 | 0 | 19.83 | 6.21 | 0
2446 | 2005-04-12 21:00 | 0 | 0 | 0 | 18.52 | 6.91 | 0
2447 | 2005-04-12 22:00 | 0 | 0 | 0 | 17.2 | 6.91 | 0
2448 | 2005-04-12 23:00 | 0 | 0 | 0 | 16.28 | 6.91 | 0
2449 | 2005-04-13 | 0 | 0 | 0 | 15.35 | 8.9 | 0
2450 | 2005-04-13 01:00 | 0 | 0 | 0 | 14.43 | 8.9 | 0
2451 | 2005-04-13 02:00 | 0 | 0 | 0 | 13.74 | 8.9 | 0
2452 | 2005-04-13 03:00 | 0 | 0 | 0 | 13.05 | 11.37 | 0
2453 | 2005-04-13 04:00 | 0 | 0 | 0 | 12.36 | 11.37 | 0
2454 | 2005-04-13 05:00 | 7 | 40 | 4 | 12.15 | 11.37 | 0 | 1.1622 | 79.6105 | 90 | 0 | 7 | 0 | 3.0619 | 0.065585 | 0 | 2.8654 | 0.00034233 | 0 | 2.7594 | 0.00025795 | 2.6769 | 2.6767 | 6011.28 | 12.1905 | 1708.13 | 1701.45 | 1688.84 | 0 | 0 | 1688.77 | 391.196 | 0 | 0 | 0 | 1688.77 | 0 | 660 | 0 | 0
2455 | 2005-04-13 06:00 | 199 | 493 | 84 | 11.94 | 9.11 | 0 | 13.4441 | 87.9674 | 78.689 | 0 | 199 | 97.0143 | 81.2111 | 1.8645 | 78.4212 | 76.0004 | 0.0097319 | 62.3506 | 73.1877 | 0.0073332 | 131.479 | 131.467 | 295227 | 14.2224 | 260496 | 273911 | 252542 | 0 | 0 | 252029 | 706.733 | 0 | 0 | 0 | 0 | 252029 | 706.733 | 245407 | 240498.625
2456 | 2005-04-13 07:00 | 422 | 783 | 81 | 11.72 | 9.11 | 0 | 25.7878 | 96.6744 | 63.9913 | 0 | 422 | 343.718 | 87.9578 | 3.9538 | 341.185 | 82.3143 | 0.020638 | 319.341 | 79.2679 | 0.015551 | 386.666 | 386.648 | 868318 | 18.4325 | 827010 | 850747 | 815099 | 0 | 0 | 810144 | 725.948 | 0 | 0 | 0 | 0 | 810144 | 725.948 | 796940 | 781001.6875
2457 | 2005-04-13 08:00 | 636 | 878 | 97 | 13.44 | 9.11 | 0 | 37.8877 | 106.765 | 49.2482 | 0 | 636 | 572.938 | 108.638 | 5.9588 | 572.938 | 101.667 | 0.031103 | 557.701 | 97.9047 | 0.023437 | 635.96 | 635.954 | 1428190 | 24.4807 | 1402540 | 1405460 | 1365830 | 0 | 0 | 1352370 | 734.519 | 0 | 0 | 0 | 0 | 1352370 | 734.519 | 1328670 | 1302092.875
2458 | 2005-04-13 09:00 | 813 | 933 | 107 | 15.15 | 6.92 | 0 | 49.2469 | 119.967 | 34.4764 | 0 | 813 | 768.285 | 117.386 | 7.6172 | 768.285 | 109.854 | 0.039759 | 760.1 | 105.789 | 0.029959 | 839.941 | 839.936 | 1886280 | 31.8852 | 1881590 | 1827100 | 1780500 | 0 | 0 | 1756590 | 715.865 | 0 | 0 | 0 | 0 | 1756590 | 715.865 | 1722780 | 1688325.25
2459 | 2005-04-13 10:00 | 928 | 950 | 117 | 16.86 | 6.92 | 0 | 58.8165 | 139.416 | 19.6875 | 0 | 928 | 892.554 | 127.917 | 8.6946 | 892.554 | 119.71 | 0.045383 | 889.784 | 115.279 | 0.034197 | 974.944 | 974.94 | 2189470 | 36.2851 | 2200660 | 2097120 | 2043190 | 0 | 0 | 2010910 | 705.262 | 0 | 0 | 0 | 0 | 2010910 | 705.262 | 1968510 | 1929143
2460 | 2005-04-13 11:00 | 981 | 954 | 123 | 17.93 | 6.92 | 0 | 64.3431 | 168.648 | 4.8938 | 0 | 981 | 948.38 | 133.985 | 9.1912 | 948.38 | 125.388 | 0.047975 | 948.206 | 120.748 | 0.03615 | 1036.92 | 1036.91 | 2328640 | 38.5898 | 2347420 | 2214780 | 2159500 | 0 | 0 | 2122860 | 698.298 | 76192.8 | 0 | 0 | 0 | 2043450 | 732.903 | 1999970 | 1959975.375
2461 | 2005-04-13 12:00 | 979 | 965 | 120 | 18.99 | 7.41 | 0 | 63.1361 | 202.399 | 9.9156 | 0 | 979 | 948.532 | 130.927 | 9.1725 | 948.532 | 122.526 | 0.047877 | 947.813 | 117.992 | 0.036076 | 1033.87 | 1033.86 | 2321780 | 38.9576 | 2340180 | 2204310 | 2149300 | 0 | 0 | 2112830 | 697.092 | 66544.6 | 0 | 0 | 0 | 2043470 | 729.572 | 1999980 | 1959975.875
2462 | 2005-04-13 13:00 | 900 | 950 | 114 | 20.05 | 7.41 | 0 | 55.9146 | 228.209 | 24.7085 | 0 | 900 | 862.154 | 124.783 | 8.4323 | 862.154 | 116.777 | 0.044014 | 857.81 | 112.455 | 0.033165 | 941.189 | 941.182 | 2113660 | 38.2277 | 2120770 | 2003390 | 1954300 | 0 | 0 | 1924160 | 698.331 | 0 | 0 | 0 | 0 | 1924160 | 698.331 | 1884930 | 1847232.625
2463 | 2005-04-13 14:00 | 761 | 920 | 104 | 20.03 | 7.41 | 0 | 45.5723 | 245.11 | 39.4897 | 0 | 761 | 709.996 | 114.016 | 7.13 | 709.996 | 106.7 | 0.037216 | 699.496 | 102.751 | 0.028043 | 778.207 | 778.201 | 1747640 | 35.0599 | 1736120 | 1662190 | 1620000 | 0 | 0 | 1599500 | 703.511 | 0 | 0 | 0 | 0 | 1599500 | 703.511 | 1570930 | 1539507.25
2464 | 2005-04-13 15:00 | 573 | 817 | 117 | 20.01 | 6.66 | 0 | 33.8947 | 257.011 | 54.2487 | 0 | 573 | 477.751 | 127.444 | 5.3686 | 477.751 | 119.267 | 0.028022 | 460.754 | 114.853 | 0.021115 | 558.359 | 558.354 | 1253920 | 31.3209 | 1221860 | 1188370 | 1157470 | 0 | 0 | 1146990 | 706.037 | 0 | 0 | 0 | 0 | 1146990 | 706.037 | 1128810 | 1106237.5
2465 | 2005-04-13 16:00 | 329 | 635 | 94 | 19.99 | 6.66 | 0 | 21.684 | 266.503 | 68.972 | 0 | 329 | 228.219 | 98.3009 | 3.0825 | 228.219 | 91.9937 | 0.016089 | 207.829 | 88.5891 | 0.012124 | 287.537 | 287.533 | 645726 | 25.8147 | 602965 | 600677 | 585188 | 0 | 0 | 582444 | 701.215 | 0 | 0 | 0 | 0 | 582444 | 701.215 | 573569 | 562097.3125
2466 | 2005-04-13 17:00 | 132 | 478 | 53 | 18.77 | 6.66 | 0 | 9.348 | 275.012 | 83.6396 | 0 | 132 | 53.8805 | 50.6481 | 1.2367 | 53.8805 | 47.3984 | 0.0064554 | 32.2564 | 45.6442 | 0.0048642 | 75.5683 | 75.5642 | 169698 | 20.3008 | 142057 | 145473 | 141712 | 0 | 0 | 141531 | 662.495 | 0 | 0 | 0 | -3.5072 | 141534 | 662.764 | 137322 | 134575.7812
2467 | 2005-04-13 18:00 | 4 | 69 | 2 | 17.55 | 6.25 | 0 | -2.83 | 283.452 | 90 | 0 | 4 | 0 | 1.4359 | 0.037477 | 0 | 1.3437 | 0 | 0 | 1.294 | 0 | 1.2552 | 1.2552 | 2818.78 | 17.5761 | 384.21 | 380.922 | 379.147 | 0 | 0 | 379.13 | 185.375 | 0 | 0 | 0 | 379.13 | 0 | 660 | 0 | 0
2468 | 2005-04-13 19:00 | 0 | 0 | 0 | 16.33 | 6.25 | 0
2469 | 2005-04-13 20:00 | 0 | 0 | 0 | 14.83 | 6.25 | 0
2470 | 2005-04-13 21:00 | 0 | 0 | 0 | 13.33 | 7.35 | 0
2471 | 2005-04-13 22:00 | 0 | 0 | 0 | 11.83 | 7.35 | 0
2472 | 2005-04-13 23:00 | 0 | 0 | 0 | 10.94 | 7.35 | 0
2473 | 2005-04-14 | 0 | 0 | 0 | 10.06 | 9.53 | 0
2474 | 2005-04-14 01:00 | 0 | 0 | 0 | 9.18 | 9.53 | 0
2475 | 2005-04-14 02:00 | 0 | 0 | 0 | 8.38 | 9.53 | 0
2476 | 2005-04-14 03:00 | 0 | 0 | 0 | 7.57 | 6.29 | 0
2477 | 2005-04-14 04:00 | 0 | 0 | 0 | 6.77 | 6.29 | 0
2478 | 2005-04-14 05:00 | 9 | 41 | 6 | 6.62 | 6.29 | 0 | 1.4184 | 79.3498 | 90 | 0 | 9 | 0 | 4.6141 | 0.084323 | 0 | 4.3181 | 0.00044014 | 0 | 4.1583 | 0.00033165 | 4.0338 | 4.0335 | 9058.29 | 6.7037 | 3554.72 | 3670.89 | 3618.84 | 0 | 0 | 3618.64 | 504.652 | 0 | 0 | 0 | 3533.21 | 85.4296 | 660 | 82.1837 | 80.5401
2479 | 2005-04-14 06:00 | 199 | 483 | 84 | 6.46 | 5.99 | 0 | 13.6939 | 87.6931 | 78.5784 | 0 | 199 | 96.1967 | 81.079 | 1.8645 | 78.6947 | 75.8768 | 0.0097319 | 62.7597 | 73.0686 | 0.0073332 | 131.761 | 131.776 | 295925 | 9.2467 | 261141 | 280763 | 259050 | 0 | 0 | 258536 | 724.259 | 0 | 0 | 0 | 0 | 258536 | 724.259 | 251472 | 246442.0781
2480 | 2005-04-14 07:00 | 432 | 755 | 100 | 6.31 | 5.99 | 0 | 26.0398 | 96.3804 | 63.8921 | 0 | 432 | 332.807 | 106.615 | 4.0475 | 331.022 | 99.7745 | 0.021127 | 309.962 | 96.0819 | 0.015919 | 393.878 | 393.862 | 884514 | 14.639 | 843377 | 881470 | 847805 | 0 | 0 | 842747 | 746.829 | 0 | 0 | 0 | 0 | 842747 | 746.829 | 828165 | 811601.375
2481 | 2005-04-14 08:00 | 635 | 871 | 97 | 8.76 | 5.99 | 0 | 38.1527 | 106.446 | 49.1588 | 0 | 635 | 569.532 | 108.437 | 5.9495 | 569.532 | 101.479 | 0.031054 | 554.464 | 97.7238 | 0.0234 | 632.645 | 632.639 | 1420750 | 22.1384 | 1394810 | 1411500 | 1372030 | 0 | 0 | 1358710 | 741.593 | 0 | 0 | 0 | 0 | 1358710 | 741.593 | 1334530 | 1307843.875
2482 | 2005-04-14 09:00 | 817 | 933 | 108 | 11.21 | 6.16 | 0 | 49.5392 | 119.631 | 34.3956 | 0 | 817 | 768.925 | 118.218 | 7.6547 | 768.925 | 110.632 | 0.039955 | 760.778 | 106.538 | 0.030107 | 841.326 | 841.316 | 1889380 | 28.8079 | 1884840 | 1854570 | 1804230 | 0 | 0 | 1780400 | 727.259 | 0 | 0 | 0 | 0 | 1780400 | 727.259 | 1745610 | 1710697.125
2483 | 2005-04-14 10:00 | 932 | 951 | 117 | 13.66 | 6.16 | 0 | 59.1515 | 139.135 | 19.6144 | 0 | 932 | 894.216 | 127.691 | 8.7321 | 894.216 | 119.498 | 0.045579 | 891.462 | 115.075 | 0.034345 | 976.375 | 976.371 | 2192670 | 34.0829 | 2204030 | 2120620 | 2062870 | 0 | 0 | 2030760 | 714.059 | 0 | 0 | 0 | 0 | 2030760 | 714.059 | 1987660 | 1947905.75
2484 | 2005-04-14 11:00 | 993 | 967 | 121 | 15.31 | 6.16 | 0 | 64.7078 | 168.651 | 4.8249 | 0 | 993 | 961.034 | 131.688 | 9.3036 | 961.034 | 123.238 | 0.048562 | 960.863 | 118.677 | 0.036592 | 1047.19 | 1047.18 | 2351700 | 37.2141 | 2371750 | 2251450 | 2193240 | 0 | 0 | 2156000 | 703.996 | 108114 | 0 | 0 | 0 | 2043850 | 743.542 | 1999990 | 1959989.625
2485 | 2005-04-14 12:00 | 982 | 967 | 119 | 16.96 | 4.97 | 0 | 63.4571 | 202.784 | 9.9693 | 0 | 982 | 950.111 | 129.661 | 9.2006 | 950.111 | 121.342 | 0.048024 | 949.383 | 116.851 | 0.036187 | 1034.28 | 1034.28 | 2322720 | 40.324 | 2341170 | 2191740 | 2137010 | 0 | 0 | 2100400 | 692.08 | 54537.9 | 0 | 0 | 0 | 2043500 | 722.44 | 1999980 | 1959977.375
2486 | 2005-04-14 13:00 | 904 | 951 | 115 | 18.61 | 4.97 | 0 | 56.1571 | 228.696 | 24.7555 | 0 | 904 | 862.655 | 125.594 | 8.4698 | 862.655 | 117.536 | 0.044209 | 858.29 | 113.186 | 0.033313 | 942.364 | 942.36 | 2116310 | 39.8977 | 2123560 | 1990980 | 1939540 | 0 | 0 | 1909400 | 692.834 | 0 | 0 | 0 | 0 | 1909400 | 692.834 | 1870750 | 1833330.375
2487 | 2005-04-14 14:00 | 764 | 920 | 105 | 19.34 | 4.97 | 0 | 45.7601 | 245.556 | 39.5285 | 0 | 764 | 709.484 | 114.846 | 7.1581 | 709.484 | 107.477 | 0.037363 | 698.966 | 103.5 | 0.028154 | 778.419 | 778.415 | 1748130 | 36.9242 | 1736630 | 1648830 | 1605740 | 0 | 0 | 1585270 | 698.052 | 0 | 0 | 0 | 0 | 1585270 | 698.052 | 1557300 | 1526154.125
2488 | 2005-04-14 15:00 | 575 | 862 | 92 | 20.07 | 3 | 0 | 34.0536 | 257.406 | 54.2782 | 0 | 575 | 503.599 | 101.891 | 5.3873 | 503.599 | 95.3539 | 0.02812 | 485.652 | 91.8249 | 0.021189 | 560.173 | 560.166 | 1258000 | 34.4712 | 1226070 | 1175620 | 1146420 | 0 | 0 | 1135840 | 696.027 | 0 | 0 | 0 | 0 | 1135840 | 696.027 | 1118380 | 1096016.875
2489 | 2005-04-14 16:00 | 356 | 748 | 77 | 20.8 | 3 | 0 | 21.8315 | 266.861 | 68.9908 | 0 | 356 | 268.976 | 81.8263 | 3.3354 | 268.976 | 76.5762 | 0.01741 | 244.913 | 73.7421 | 0.013119 | 309.108 | 309.105 | 694169 | 28.7467 | 651373 | 640230 | 624081 | 0 | 0 | 620900 | 693.76 | 0 | 0 | 0 | 0 | 620900 | 693.76 | 611780 | 599544.4375
2490 | 2005-04-14 17:00 | 101 | 151 | 76 | 20.49 | 3 | 0 | 9.4967 | 275.349 | 83.6455 | 0 | 101 | 16.7704 | 69.0984 | 0.94629 | 16.7704 | 64.6649 | 0.0049393 | 10.0328 | 62.2717 | 0.0037219 | 70.139 | 70.1365 | 157508 | 22.2931 | 130863 | 132687 | 129310 | 0 | 0 | 129153 | 650.436 | 0 | 0 | 0 | 282.567 | 128871 | 660 | 124970 | 122470.8359
2491 | 2005-04-14 18:00 | 3 | 23 | 2 | 20.17 | 3.83 | 0 | -2.6697 | 283.779 | 90 | 0 | 3 | 0 | 1.571 | 0.028108 | 0 | 1.4702 | 0 | 0 | 1.4158 | 0 | 1.3733 | 1.3732 | 3083.86 | 20.2034 | 459.514 | 457.018 | 454.91 | 0 | 0 | 454.89 | 202.965 | 0 | 0 | 0 | 454.89 | 0 | 660 | 0 | 0
2492 | 2005-04-14 19:00 | 0 | 0 | 0 | 19.86 | 3.83 | 0
2493 | 2005-04-14 20:00 | 0 | 0 | 0 | 19.17 | 3.83 | 0
2494 | 2005-04-14 21:00 | 0 | 0 | 0 | 18.49 | 5.4 | 0
2495 | 2005-04-14 22:00 | 0 | 0 | 0 | 17.81 | 5.4 | 0
2496 | 2005-04-14 23:00 | 0 | 0 | 0 | 16.87 | 5.4 | 0
2497 | 2005-04-15 | 0 | 0 | 0 | 15.92 | 5.54 | 0
2498 | 2005-04-15 01:00 | 0 | 0 | 0 | 14.98 | 5.54 | 0
2499 | 2005-04-15 02:00 | 0 | 0 | 0 | 14.53 | 5.54 | 0
2500 | 2005-04-15 03:00 | 0 | 0 | 0 | 14.08 | 7.52 | 0
2501 | 2005-04-15 04:00 | 0 | 0 | 0 | 13.62 | 7.52 | 0
2502 | 2005-04-15 05:00 | 10 | 42 | 7 | 13.34 | 7.52 | 0 | 1.6718 | 79.0904 | 90 | 0 | 10 | 0 | 5.3829 | 0.093692 | 0 | 5.0375 | 0.00048904 | 0 | 4.8511 | 0.0003685 | 4.7059 | 4.7058 | 10567.9 | 13.4303 | 4563.22 | 4714.79 | 4638.97 | 0 | 0 | 4638.64 | 506.873 | 0 | 0 | 0 | 4638.64 | 0 | 660 | 0 | 0
2503 | 2005-04-15 06:00 | 181 | 357 | 95 | 13.06 | 5.67 | 0 | 13.9406 | 87.4196 | 78.4702 | 0 | 181 | 71.3506 | 91.0862 | 1.6958 | 59.0157 | 85.2419 | 0.0088517 | 47.2036 | 82.0872 | 0.0066699 | 125.418 | 125.412 | 281635 | 15.7674 | 247300 | 258317 | 241629 | 0 | 0 | 241159 | 701.815 | 0 | 0 | 0 | 0 | 241159 | 701.815 | 234696 | 230002.2031
2504 | 2005-04-15 07:00 | 394 | 636 | 112 | 12.77 | 5.67 | 0 | 26.2884 | 96.0867 | 63.7959 | 0 | 394 | 281.16 | 118.29 | 3.6915 | 280.101 | 110.701 | 0.019268 | 262.389 | 106.604 | 0.014519 | 357.937 | 357.927 | 803812 | 20.4969 | 761666 | 776784 | 748940 | 0 | 0 | 744773 | 726.996 | 0 | 0 | 0 | 0 | 744773 | 726.996 | 732596 | 717944.5
2505 | 2005-04-15 08:00 | 613 | 736 | 156 | 14.78 | 5.67 | 0 | 38.4139 | 106.126 | 49.073 | 0 | 613 | 481.83 | 169.392 | 5.7433 | 481.83 | 158.524 | 0.029978 | 469.146 | 152.657 | 0.022589 | 603.171 | 603.17 | 1354570 | 27.8011 | 1326080 | 1310010 | 1276850 | 0 | 0 | 1264580 | 719.447 | 0 | 0 | 0 | 0 | 1264580 | 719.447 | 1243360 | 1218497.5
2506 | 2005-04-15 09:00 | 813 | 846 | 167 | 16.78 | 4.18 | 0 | 49.8276 | 119.293 | 34.3197 | 0 | 813 | 698.246 | 183.245 | 7.6172 | 698.246 | 171.487 | 0.039759 | 690.886 | 165.141 | 0.029959 | 830.375 | 830.368 | 1864800 | 36.5307 | 1859020 | 1768540 | 1723090 | 0 | 0 | 1699770 | 701.096 | 0 | 0 | 0 | 0 | 1699770 | 701.096 | 1668130 | 1634768.375
2507 | 2005-04-15 10:00 | 854 | 674 | 274 | 18.78 | 4.18 | 0 | 59.4827 | 138.849 | 19.5492 | 0 | 854 | 634.452 | 299.661 | 8.0013 | 634.452 | 280.434 | 0.041764 | 632.512 | 270.056 | 0.03147 | 875.521 | 875.507 | 1966170 | 39.6044 | 1965540 | 1844590 | 1799220 | 0 | 0 | 1773100 | 691.265 | 0 | 0 | 0 | 0 | 1773100 | 691.265 | 1739260 | 1704475.875
2508 | 2005-04-15 11:00 | 699 | 310 | 419 | 20.12 | 4.18 | 0 | 65.0697 | 168.651 | 4.7841 | 0 | 699 | 307.695 | 439.171 | 6.5491 | 307.695 | 410.993 | 0.034184 | 307.641 | 395.782 | 0.025758 | 682.346 | 682.337 | 1532360 | 36.3497 | 1511050 | 1437560 | 1399730 | 0 | 0 | 1384050 | 696.643 | 0 | 0 | 0 | 0 | 1384050 | 696.643 | 1361310 | 1334080.875
2509 | 2005-04-15 12:00 | 699 | 300 | 430 | 21.46 | 1.27 | 0 | 63.7749 | 203.173 | 10.0341 | 0 | 699 | 295.28 | 449.762 | 6.5491 | 295.28 | 420.904 | 0.034184 | 295.051 | 405.327 | 0.025758 | 679.391 | 679.366 | 1525680 | 41.0631 | 1504080 | 1400130 | 1363800 | 0 | 0 | 1348270 | 681.447 | 0 | 0 | 0 | 0 | 1348270 | 681.447 | 1326980 | 1300437.875
2510 | 2005-04-15 13:00 | 820 | 672 | 261 | 22.8 | 1.27 | 0 | 56.3965 | 229.184 | 24.806 | 0 | 820 | 609.233 | 284.801 | 7.6828 | 609.233 | 266.527 | 0.040101 | 606.137 | 256.663 | 0.030217 | 836.946 | 836.935 | 1879540 | 46.9498 | 1874510 | 1699540 | 1660220 | 0 | 0 | 1636220 | 665.718 | 0 | 0 | 0 | 0 | 1636220 | 665.718 | 1607640 | 1575488.625
2511 | 2005-04-15 14:00 | 636 | 495 | 280 | 23.37 | 1.27 | 0 | 45.9456 | 246.002 | 39.5687 | 0 | 636 | 381.848 | 294.172 | 5.9588 | 381.848 | 275.298 | 0.031103 | 376.173 | 265.109 | 0.023437 | 622.066 | 622.056 | 1396980 | 41.3195 | 1370120 | 1273280 | 1241870 | 0 | 0 | 1228760 | 675.917 | 0 | 0 | 0 | 0 | 1228760 | 675.917 | 1210340 | 1186135.5
2512 | 2005-04-15 15:00 | 260 | 47 | 234 | 23.95 | 2.83 | 0 | 34.211 | 257.799 | 54.3081 | 0 | 260 | 26.9797 | 239.813 | 2.436 | 26.9797 | 224.426 | 0.012715 | 26.0165 | 216.121 | 0.0095811 | 234.882 | 234.865 | 527448 | 30.0565 | 485657 | 474142 | 461794 | 0 | 0 | 459969 | 677.958 | 0 | 0 | 0 | 0 | 459969 | 677.958 | 453109 | 444047.2188
2513 | 2005-04-15 16:00 | 260 | 267 | 160 | 24.52 | 2.83 | 0 | 21.9782 | 267.217 | 69.0093 | 0 | 260 | 95.7151 | 155.71 | 2.436 | 95.7151 | 145.719 | 0.012715 | 87.1409 | 140.326 | 0.0095811 | 220.652 | 220.644 | 495510 | 30.2568 | 454200 | 442948 | 431826 | 0 | 0 | 430212 | 674.706 | 0 | 0 | 0 | 0 | 430212 | 674.706 | 423803 | 415326.9062
2514 | 2005-04-15 17:00 | 129 | 248 | 87 | 24.24 | 2.83 | 0 | 9.645 | 275.682 | 83.6506 | 0 | 129 | 27.7232 | 78.4424 | 1.2086 | 27.7232 | 73.4094 | 0.0063086 | 16.5753 | 70.6926 | 0.0047537 | 84.6544 | 84.6501 | 190103 | 26.4409 | 160926 | 159733 | 155833 | 0 | 0 | 155601 | 644.648 | 0 | 0 | 0 | 1060.02 | 154541 | 660 | 150102 | 147099.625
2515 | 2005-04-15 18:00 | 4 | 39 | 3 | 23.97 | 2.03 | 0 | -2.5096 | 284.103 | 90 | 0 | 4 | 0 | 2.6445 | 0.037477 | 0 | 2.4748 | 0 | 0 | 2.3832 | 0 | 2.3117 | 2.3116 | 5191.17 | 24.0334 | 1287.69 | 1287.01 | 1278.59 | 0 | 0 | 1278.53 | 338.437 | 0 | 0 | 0 | 1278.53 | 0 | 660 | 0 | 0
2516 | 2005-04-15 19:00 | 0 | 0 | 0 | 23.69 | 2.03 | 0
2517 | 2005-04-15 20:00 | 0 | 0 | 0 | 22.84 | 2.03 | 0
2518 | 2005-04-15 21:00 | 0 | 0 | 0 | 22 | 1.47 | 0
2519 | 2005-04-15 22:00 | 0 | 0 | 0 | 21.15 | 1.47 | 0
2520 | 2005-04-15 23:00 | 0 | 0 | 0 | 20.09 | 1.47 | 0
2521 | 2005-04-16 | 0 | 0 | 0 | 19.02 | 2.5 | 0
2522 | 2005-04-16 01:00 | 0 | 0 | 0 | 17.96 | 2.5 | 0
2523 | 2005-04-16 02:00 | 0 | 0 | 0 | 17.38 | 2.5 | 0
2524 | 2005-04-16 03:00 | 0 | 0 | 0 | 16.8 | 1.33 | 0
2525 | 2005-04-16 04:00 | 0 | 0 | 0 | 16.22 | 1.33 | 0
2526 | 2005-04-16 05:00 | 17 | 128 | 8 | 15.88 | 1.33 | 0 | 1.9223 | 78.8322 | 90 | 0 | 17 | 0 | 5.8749 | 0.15928 | 0 | 5.498 | 0.00083137 | 0 | 5.2945 | 0.00062646 | 5.1363 | 5.1361 | 11534.3 | 16.0276 | 5228.32 | 5385.45 | 5291.71 | 0 | 0 | 5291.28 | 509.856 | 0 | 0 | 0 | 5291.28 | 0 | 660 | 0 | 0
2527 | 2005-04-16 06:00 | 209 | 594 | 63 | 15.54 | 0.14 | 0 | 14.1842 | 87.147 | 78.3643 | 0 | 209 | 120.17 | 62.6845 | 1.9582 | 100.447 | 58.6626 | 0.010221 | 80.5673 | 56.4915 | 0.0077017 | 132.955 | 132.921 | 298498 | 19.6794 | 263845 | 270271 | 247011 | 0 | 0 | 246482 | 685.778 | 0 | 0 | 0 | 0 | 246482 | 685.778 | 240392 | 235584.3281
2528 | 2005-04-16 07:00 | 440 | 800 | 82 | 15.21 | 0.14 | 0 | 26.5335 | 95.7932 | 63.7025 | 0 | 440 | 355.044 | 88.488 | 4.1225 | 354.074 | 82.8104 | 0.021518 | 331.818 | 79.7457 | 0.016214 | 399.232 | 399.209 | 896512 | 27.6421 | 855518 | 845305 | 819077 | 0 | 0 | 813787 | 704.823 | 0 | 0 | 0 | 0 | 813787 | 704.823 | 801384 | 785355.9375
2529 | 2005-04-16 08:00 | 651 | 887 | 97 | 17.44 | 0.14 | 0 | 38.6713 | 105.805 | 48.9909 | 0 | 651 | 581.775 | 105.54 | 6.0994 | 581.775 | 98.7687 | 0.031837 | 566.533 | 95.1134 | 0.02399 | 641.821 | 641.819 | 1441360 | 37.4274 | 1416240 | 1340400 | 1306570 | 0 | 0 | 1292630 | 689.512 | 0 | 0 | 0 | 0 | 1292630 | 689.512 | 1272200 | 1246761
2530 | 2005-04-16 09:00 | 824 | 934 | 108 | 19.67 | 2.18 | 0 | 50.1119 | 118.952 | 34.2487 | 0 | 824 | 771.338 | 117.823 | 7.7202 | 771.338 | 110.263 | 0.040297 | 763.248 | 106.182 | 0.030365 | 843.377 | 843.369 | 1893990 | 42.5669 | 1889690 | 1749110 | 1706050 | 0 | 0 | 1681870 | 681.782 | 0 | 0 | 0 | 0 | 1681870 | 681.782 | 1651320 | 1618291
2531 | 2005-04-16 10:00 | 933 | 942 | 120 | 21.89 | 2.18 | 0 | 59.8102 | 138.557 | 19.4918 | 0 | 933 | 886.671 | 130.313 | 8.7415 | 886.671 | 121.951 | 0.045628 | 883.975 | 117.438 | 0.034381 | 971.404 | 971.4 | 2181520 | 48.2628 | 2192270 | 1977550 | 1933100 | 0 | 0 | 1900730 | 665.924 | 0 | 0 | 0 | 0 | 1900730 | 665.924 | 1862650 | 1825395.375
2532 | 2005-04-16 11:00 | 992 | 957 | 124 | 23.15 | 2.18 | 0 | 65.4286 | 168.648 | 4.7717 | 0 | 992 | 951.121 | 134.269 | 9.2943 | 951.121 | 125.654 | 0.048513 | 950.956 | 121.003 | 0.036555 | 1039.84 | 1039.83 | 2335190 | 51.3806 | 2354330 | 2093400 | 2046830 | 0 | 0 | 2009450 | 655.113 | 0 | 0 | 0 | 964.151 | 2008490 | 660 | 1966140 | 1926815.875
2533 | 2005-04-16 12:00 | 988 | 967 | 120 | 24.4 | 4.04 | 0 | 64.0897 | 203.565 | 10.1096 | 0 | 988 | 950.02 | 130.217 | 9.2568 | 950.02 | 121.862 | 0.048317 | 949.271 | 117.352 | 0.036408 | 1034.66 | 1034.65 | 2323580 | 49.2367 | 2342080 | 2103980 | 2053980 | 0 | 0 | 2017370 | 664.274 | 0 | 0 | 0 | 0 | 2017370 | 664.274 | 1974660 | 1935168.75
2534 | 2005-04-16 13:00 | 908 | 952 | 114 | 25.66 | 4.04 | 0 | 56.633 | 229.673 | 24.8597 | 0 | 908 | 862.618 | 124.135 | 8.5073 | 862.618 | 116.17 | 0.044405 | 858.213 | 111.871 | 0.03346 | 941.014 | 941.003 | 2113250 | 48.2487 | 2120340 | 1912380 | 1866700 | 0 | 0 | 1836580 | 666.902 | 0 | 0 | 0 | 0 | 1836580 | 666.902 | 1800910 | 1764888.75
2535 | 2005-04-16 14:00 | 768 | 920 | 105 | 26.19 | 4.04 | 0 | 46.1288 | 246.446 | 39.6101 | 0 | 768 | 708.525 | 114.455 | 7.1956 | 708.525 | 107.111 | 0.037558 | 697.967 | 103.147 | 0.028301 | 777.108 | 777.105 | 1745170 | 44.8443 | 1733540 | 1586780 | 1547080 | 0 | 0 | 1526520 | 670.903 | 0 | 0 | 0 | 0 | 1526520 | 670.903 | 1501300 | 1471271.5
2536 | 2005-04-16 15:00 | 580 | 863 | 93 | 26.72 | 4.05 | 0 | 34.3668 | 258.19 | 54.3382 | 0 | 580 | 502.97 | 102.485 | 5.4341 | 502.97 | 95.9097 | 0.028364 | 484.982 | 92.3601 | 0.021373 | 560.043 | 560.039 | 1257700 | 40.1549 | 1225760 | 1144760 | 1116520 | 0 | 0 | 1105920 | 676.856 | 0 | 0 | 0 | 0 | 1105920 | 676.856 | 1090010 | 1068210.625
2537 | 2005-04-16 16:00 | 361 | 752 | 77 | 27.24 | 4.05 | 0 | 22.1239 | 267.57 | 69.0273 | 0 | 361 | 269.908 | 81.4547 | 3.3823 | 269.908 | 76.2284 | 0.017654 | 245.699 | 73.4073 | 0.013303 | 309.546 | 309.543 | 695152 | 34.6657 | 652357 | 623514 | 608295 | 0 | 0 | 605104 | 675.269 | 0 | 0 | 0 | 0 | 605104 | 675.269 | 596776 | 584840.625
2538 | 2005-04-16 17:00 | 101 | 129 | 79 | 26.52 | 4.05 | 0 | 9.7927 | 276.013 | 83.6547 | 0 | 101 | 14.2954 | 70.8468 | 0.94629 | 14.2954 | 66.3012 | 0.0049393 | 8.5428 | 63.8474 | 0.0037219 | 70.2221 | 70.2168 | 157689 | 28.2044 | 131029 | 128843 | 125731 | 0 | 0 | 125573 | 629.623 | 0 | 0 | 0 | 3883.41 | 121690 | 660 | 117954 | 115595.0391
2539 | 2005-04-16 18:00 | 4 | 21 | 3 | 25.8 | 4.97 | 0 | -2.3497 | 284.424 | 90 | 0 | 4 | 0 | 2.6421 | 0.037477 | 0 | 2.4726 | 0 | 0 | 2.3811 | 0 | 2.3096 | 2.3097 | 5186.97 | 25.8522 | 1285.91 | 1286.36 | 1277.45 | 0 | 0 | 1277.39 | 337.016 | 0 | 0 | 0 | 1277.39 | 0 | 660 | 0 | 0
2540 | 2005-04-16 19:00 | 0 | 0 | 0 | 25.08 | 4.97 | 0
2541 | 2005-04-16 20:00 | 0 | 0 | 0 | 24.08 | 4.97 | 0
2542 | 2005-04-16 21:00 | 0 | 0 | 0 | 23.07 | 6.41 | 0
2543 | 2005-04-16 22:00 | 0 | 0 | 0 | 22.07 | 6.41 | 0
2544 | 2005-04-16 23:00 | 0 | 0 | 0 | 20.99 | 6.41 | 0
2545 | 2005-04-17 | 0 | 0 | 0 | 19.91 | 7.93 | 0
2546 | 2005-04-17 01:00 | 0 | 0 | 0 | 18.84 | 7.93 | 0
2547 | 2005-04-17 02:00 | 0 | 0 | 0 | 18.23 | 7.93 | 0
2548 | 2005-04-17 03:00 | 0 | 0 | 0 | 17.63 | 3.87 | 0
2549 | 2005-04-17 04:00 | 0 | 0 | 0 | 17.02 | 3.87 | 0
2550 | 2005-04-17 05:00 | 16 | 83 | 10 | 16.82 | 3.87 | 0 | 2.1698 | 78.5753 | 90 | 0 | 16 | 0 | 7.7081 | 0.14991 | 0 | 7.2136 | 0.00078247 | 0 | 6.9466 | 0.0005896 | 6.7388 | 6.7383 | 15132.4 | 16.9836 | 7798.06 | 8065.6 | 7913.09 | 0 | 0 | 7912.22 | 534.773 | 0 | 0 | 0 | 7482.58 | 429.643 | 660 | 413.329 | 405.0621
2551 | 2005-04-17 06:00 | 211 | 492 | 88 | 16.62 | 3.45 | 0 | 14.4245 | 86.8753 | 78.2609 | 0 | 211 | 100.46 | 84.3831 | 1.9769 | 84.8089 | 78.969 | 0.010319 | 68.2072 | 76.0464 | 0.0077754 | 139.933 | 139.905 | 314188 | 20.1114 | 278557 | 284924 | 264270 | 0 | 0 | 263680 | 689.324 | 0 | 0 | 0 | 0 | 263680 | 689.324 | 257302 | 252156.3906
2552 | 2005-04-17 07:00 | 445 | 802 | 83 | 16.42 | 3.45 | 0 | 26.7751 | 95.5001 | 63.6121 | 0 | 445 | 357.144 | 89.3348 | 4.1693 | 356.514 | 83.6029 | 0.021762 | 334.232 | 80.5088 | 0.016398 | 402.314 | 402.295 | 903444 | 26.4594 | 862526 | 856828 | 829735 | 0 | 0 | 824372 | 709.154 | 0 | 0 | 0 | 0 | 824372 | 709.154 | 811630 | 795397
2553 | 2005-04-17 08:00 | 655 | 889 | 97 | 18.35 | 3.45 | 0 | 38.9248 | 105.484 | 48.9125 | 0 | 655 | 583.676 | 105.372 | 6.1368 | 583.676 | 98.6107 | 0.032032 | 568.454 | 94.9612 | 0.024137 | 643.537 | 643.531 | 1445210 | 34.4095 | 1420240 | 1362820 | 1328030 | 0 | 0 | 1314070 | 701.279 | 0 | 0 | 0 | 0 | 1314070 | 701.279 | 1292650 | 1266798.75
2554 | 2005-04-17 09:00 | 815 | 914 | 111 | 20.28 | 2.35 | 0 | 50.3921 | 118.608 | 34.1827 | 0 | 815 | 755.925 | 120.697 | 7.6359 | 755.925 | 112.953 | 0.039857 | 748.032 | 108.773 | 0.030033 | 831.13 | 831.124 | 1866500 | 42.5901 | 1860800 | 1722060 | 1682210 | 0 | 0 | 1658580 | 679.888 | 0 | 0 | 0 | 0 | 1658580 | 679.888 | 1628850 | 1596276
2555 | 2005-04-17 10:00 | 944 | 954 | 118 | 22.21 | 2.35 | 0 | 60.1337 | 138.261 | 19.4422 | 0 | 944 | 898.188 | 128.043 | 8.8445 | 898.188 | 119.828 | 0.046165 | 895.473 | 115.393 | 0.034787 | 980.574 | 980.57 | 2202110 | 48.5318 | 2213980 | 1994710 | 1948070 | 0 | 0 | 1915200 | 665.482 | 0 | 0 | 0 | 0 | 1915200 | 665.482 | 1876560 | 1839030.25
2556 | 2005-04-17 11:00 | 1003 | 969 | 121 | 23.02 | 2.35 | 0 | 65.7845 | 168.643 | 4.787 | 0 | 1003 | 963.722 | 130.966 | 9.3973 | 963.722 | 122.563 | 0.049051 | 963.554 | 118.027 | 0.036961 | 1049.17 | 1049.16 | 2356150 | 51.183 | 2376440 | 2115230 | 2065280 | 0 | 0 | 2027620 | 658.209 | 0 | 0 | 0 | 348.938 | 2027270 | 660.39 | 1984140 | 1944459.375
2557 | 2005-04-17 12:00 | 991 | 967 | 121 | 23.83 | 4.98 | 0 | 64.4013 | 203.96 | 10.195 | 0 | 991 | 949.46 | 131.005 | 9.2849 | 949.46 | 122.599 | 0.048464 | 948.699 | 118.062 | 0.036519 | 1034.79 | 1034.79 | 2323860 | 47.1903 | 2342370 | 2124760 | 2074560 | 0 | 0 | 2037800 | 670.119 | 1836.78 | 0 | 0 | 0 | 2035870 | 673.106 | 1992440 | 1952587.875
2558 | 2005-04-17 13:00 | 910 | 952 | 114 | 24.64 | 4.98 | 0 | 56.8664 | 230.162 | 24.9164 | 0 | 910 | 862.088 | 123.922 | 8.526 | 862.088 | 115.971 | 0.044503 | 857.664 | 111.679 | 0.033534 | 940.296 | 940.292 | 2111660 | 45.8671 | 2118660 | 1932530 | 1884920 | 0 | 0 | 1854760 | 673.05 | 0 | 0 | 0 | 0 | 1854760 | 673.05 | 1818330 | 1781963
2559 | 2005-04-17 14:00 | 748 | 845 | 137 | 25 | 4.98 | 0 | 46.3097 | 246.888 | 39.6526 | 0 | 748 | 650.582 | 151.151 | 7.0082 | 650.582 | 141.452 | 0.03658 | 640.861 | 136.217 | 0.027564 | 753.793 | 753.792 | 1692830 | 42.0169 | 1678710 | 1556850 | 1518580 | 0 | 0 | 1499300 | 680.215 | 0 | 0 | 0 | 0 | 1499300 | 680.215 | 1474550 | 1445059.625
2560 | 2005-04-17 15:00 | 582 | 863 | 93 | 25.37 | 7.82 | 0 | 34.5212 | 258.578 | 54.3684 | 0 | 582 | 502.686 | 102.269 | 5.4529 | 502.686 | 95.7076 | 0.028462 | 484.677 | 92.1655 | 0.021447 | 559.558 | 559.554 | 1256610 | 35.9006 | 1224640 | 1166650 | 1137720 | 0 | 0 | 1127140 | 690.923 | 0 | 0 | 0 | 0 | 1127140 | 690.923 | 1110100 | 1087900
2561 | 2005-04-17 16:00 | 357 | 737 | 77 | 25.73 | 7.82 | 0 | 22.2687 | 267.92 | 69.0448 | 0 | 357 | 264.252 | 81.2714 | 3.3448 | 264.252 | 76.0568 | 0.017459 | 240.521 | 73.242 | 0.013156 | 304.363 | 304.36 | 683516 | 31.458 | 640712 | 621805 | 606735 | 0 | 0 | 603651 | 685.163 | 0 | 0 | 0 | 0 | 603651 | 685.163 | 595044 | 583143.5625
2562 | 2005-04-17 17:00 | 121 | 262 | 75 | 24.56 | 7.82 | 0 | 9.94 | 276.341 | 83.6579 | 0 | 121 | 29.4375 | 67.8003 | 1.1337 | 29.4375 | 63.4501 | 0.0059174 | 17.585 | 61.1019 | 0.0044589 | 76.3306 | 76.3295 | 171417 | 25.9965 | 143644 | 142902 | 139314 | 0 | 0 | 139127 | 640.819 | 0 | 0 | 0 | 1397.37 | 137730 | 660 | 133634 | 130961.4297
2563 | 2005-04-17 18:00 | 4 | 45 | 2 | 23.39 | 8.37 | 0 | -2.19 | 284.741 | 90 | 0 | 4 | 0 | 1.4268 | 0.037477 | 0 | 1.3352 | 0 | 0 | 1.2858 | 0 | 1.2472 | 1.2472 | 2800.82 | 23.4127 | 379.324 | 378.636 | 376.885 | 0 | 0 | 376.868 | 184.774 | 0 | 0 | 0 | 376.868 | 0 | 660 | 0 | 0
2564 | 2005-04-17 19:00 | 0 | 0 | 0 | 22.22 | 8.37 | 0
2565 | 2005-04-17 20:00 | 0 | 0 | 0 | 20.85 | 8.37 | 0
2566 | 2005-04-17 21:00 | 0 | 0 | 0 | 19.49 | 9.19 | 0
2567 | 2005-04-17 22:00 | 0 | 0 | 0 | 18.12 | 9.19 | 0
2568 | 2005-04-17 23:00 | 0 | 0 | 0 | 17.14 | 9.19 | 0
2569 | 2005-04-18 | 0 | 0 | 0 | 16.15 | 8.75 | 0
2570 | 2005-04-18 01:00 | 0 | 0 | 0 | 15.17 | 8.75 | 0
2571 | 2005-04-18 02:00 | 0 | 0 | 0 | 14.34 | 8.75 | 0
2572 | 2005-04-18 03:00 | 0 | 0 | 0 | 13.51 | 10.25 | 0
2573 | 2005-04-18 04:00 | 0 | 0 | 0 | 12.69 | 10.25 | 0
2574 | 2005-04-18 05:00 | 21 | 128 | 11 | 12.79 | 10.25 | 0 | 2.4142 | 78.3197 | 90 | 0 | 21 | 0 | 8.2621 | 0.19675 | 0 | 7.732 | 0.001027 | 0 | 7.4459 | 0.00077386 | 7.2232 | 7.2232 | 16221.4 | 12.9069 | 8598.37 | 9051.78 | 8868.54 | 0 | 0 | 8867.52 | 553.079 | 0 | 0 | 0 | 4924.14 | 3943.38 | 660 | 3794.47 | 3718.5767
2575 | 2005-04-18 06:00 | 213 | 575 | 67 | 12.9 | 8.59 | 0 | 14.6615 | 86.6046 | 78.16 | 0 | 213 | 118.353 | 66.2535 | 1.9956 | 100.79 | 62.0025 | 0.010417 | 81.2677 | 59.7079 | 0.0078491 | 136.754 | 136.71 | 307009 | 15.3515 | 271889 | 284340 | 260594 | 0 | 0 | 260033 | 700.527 | 0 | 0 | 0 | 6.9945 | 260026 | 701.234 | 253475 | 248405.75
2576 | 2005-04-18 07:00 | 435 | 771 | 85 | 13 | 8.59 | 0 | 27.013 | 95.2074 | 63.5247 | 0 | 435 | 343.541 | 91.1816 | 4.0756 | 343.251 | 85.3312 | 0.021273 | 321.916 | 82.1731 | 0.01603 | 391.982 | 391.974 | 880272 | 20.0289 | 838990 | 857281 | 832169 | 0 | 0 | 827086 | 730.887 | 0 | 0 | 0 | 0 | 827086 | 730.887 | 813402 | 797134.1875
2577 | 2005-04-18 08:00 | 653 | 879 | 98 | 14.12 | 8.59 | 0 | 39.1744 | 105.163 | 48.8378 | 0 | 653 | 578.293 | 108.684 | 6.1181 | 578.293 | 101.71 | 0.031934 | 563.277 | 97.946 | 0.024063 | 641.41 | 641.405 | 1440430 | 25.6217 | 1415280 | 1411360 | 1372950 | 0 | 0 | 1359220 | 730.879 | 0 | 0 | 0 | 0 | 1359220 | 730.879 | 1335540 | 1308825.5
2578 | 2005-04-18 09:00 | 819 | 916 | 111 | 15.24 | 6.11 | 0 | 50.6681 | 118.262 | 34.1216 | 0 | 819 | 757.76 | 120.499 | 7.6734 | 757.76 | 112.768 | 0.040052 | 749.881 | 108.594 | 0.03018 | 832.75 | 832.743 | 1870140 | 32.7146 | 1864630 | 1804060 | 1755780 | 0 | 0 | 1732400 | 713.995 | 0 | 0 | 0 | 0 | 1732400 | 713.995 | 1699410 | 1665419.375
2579 | 2005-04-18 10:00 | 925 | 877 | 163 | 16.36 | 6.11 | 0 | 60.4531 | 137.958 | 19.4003 | 0 | 925 | 826.176 | 181.439 | 8.6665 | 826.176 | 169.798 | 0.045236 | 823.69 | 163.514 | 0.034086 | 957.62 | 957.61 | 2150550 | 36.4549 | 2159640 | 2056340 | 2003770 | 0 | 0 | 1972580 | 704.244 | 0 | 0 | 0 | 0 | 1972580 | 704.244 | 1931570 | 1892942.875
2580 | 2005-04-18 11:00 | 1006 | 969 | 122 | 17.29 | 6.11 | 0 | 66.1371 | 168.634 | 4.8293 | 0 | 1006 | 963.2 | 131.747 | 9.4254 | 963.2 | 123.294 | 0.049198 | 963.028 | 118.731 | 0.037071 | 1049.34 | 1049.34 | 2356550 | 39.3097 | 2376870 | 2235460 | 2177270 | 0 | 0 | 2139870 | 697.031 | 92520.8 | 0 | 0 | 0 | 2043440 | 734.333 | 1999970 | 1959970.375
2581 | 2005-04-18 12:00 | 993 | 967 | 121 | 18.22 | 6.76 | 0 | 64.7096 | 204.358 | 10.2898 | 0 | 993 | 948.926 | 130.771 | 9.3036 | 948.926 | 122.381 | 0.048562 | 948.15 | 117.852 | 0.036592 | 1034.06 | 1034.05 | 2322230 | 39.0341 | 2340650 | 2203990 | 2146660 | 0 | 0 | 2110410 | 698.271 | 64234.5 | 0 | 0 | 0 | 2043470 | 729.142 | 1999980 | 1959975.625
2582 | 2005-04-18 13:00 | 913 | 952 | 115 | 19.15 | 6.76 | 0 | 57.0967 | 230.652 | 24.976 | 0 | 913 | 861.583 | 124.734 | 8.5541 | 861.583 | 116.731 | 0.04465 | 857.138 | 112.411 | 0.033644 | 940.495 | 940.488 | 2112100 | 38.0808 | 2119130 | 2003150 | 1953200 | 0 | 0 | 1923090 | 698.112 | 0 | 0 | 0 | 0 | 1923090 | 698.112 | 1883900 | 1846224.125
2583 | 2005-04-18 14:00 | 768 | 915 | 105 | 19.04 | 6.76 | 0 | 46.4885 | 247.328 | 39.6961 | 0 | 768 | 703.414 | 114.071 | 7.1956 | 703.414 | 106.752 | 0.037558 | 692.875 | 102.801 | 0.028301 | 771.833 | 771.829 | 1733330 | 34.5759 | 1721120 | 1651320 | 1609150 | 0 | 0 | 1588960 | 704.942 | 0 | 0 | 0 | 0 | 1588960 | 704.942 | 1560660 | 1529446.875
2584 | 2005-04-18 15:00 | 577 | 852 | 92 | 18.93 | 10.25 | 0 | 34.674 | 258.963 | 54.3986 | 0 | 577 | 496.284 | 101.028 | 5.406 | 496.284 | 94.5461 | 0.028218 | 478.472 | 91.047 | 0.021263 | 552.454 | 552.451 | 1240660 | 27.8709 | 1208160 | 1193100 | 1161780 | 0 | 0 | 1151570 | 718.327 | 0 | 0 | 0 | 0 | 1151570 | 718.327 | 1132700 | 1110047.875
2585 | 2005-04-18 16:00 | 345 | 690 | 81 | 18.83 | 10.25 | 0 | 22.4126 | 268.268 | 69.0618 | 0 | 345 | 247.443 | 84.3514 | 3.2324 | 247.443 | 78.9392 | 0.016872 | 225.194 | 76.0178 | 0.012713 | 292.188 | 292.183 | 656167 | 23.5587 | 613382 | 617360 | 600664 | 0 | 0 | 597842 | 708.914 | 0 | 0 | 0 | 0 | 597842 | 708.914 | 588592 | 576820
2586 | 2005-04-18 17:00 | 142 | 499 | 54 | 17.77 | 10.25 | 0 | 10.0867 | 276.666 | 83.66 | 0 | 142 | 55.486 | 50.7263 | 1.3304 | 55.486 | 47.4716 | 0.0069444 | 33.1374 | 45.7147 | 0.0052327 | 76.4916 | 76.4903 | 171778 | 19.0079 | 143975 | 148382 | 144404 | 0 | 0 | 144220 | 668.84 | 0 | 0 | 0 | 0 | 144220 | 668.84 | 139871 | 137073.875
2587 | 2005-04-18 18:00 | 5 | 88 | 2 | 16.71 | 11.91 | 0 | -2.0306 | 285.055 | 90 | 0 | 5 | 0 | 1.4245 | 0.046846 | 0 | 1.3331 | 0 | 0 | 1.2838 | 0 | 1.2453 | 1.2452 | 2796.5 | 16.7282 | 378.185 | 374.571 | 372.821 | 0 | 0 | 372.805 | 183.849 | 0 | 0 | 0 | 372.805 | 0 | 660 | 0 | 0
2588 | 2005-04-18 19:00 | 0 | 0 | 0 | 15.66 | 11.91 | 0
2589 | 2005-04-18 20:00 | 0 | 0 | 0 | 14.78 | 11.91 | 0
2590 | 2005-04-18 21:00 | 0 | 0 | 0 | 13.9 | 11.07 | 0
2591 | 2005-04-18 22:00 | 0 | 0 | 0 | 13.02 | 11.07 | 0
2592 | 2005-04-18 23:00 | 0 | 0 | 0 | 12.23 | 11.07 | 0
2593 | 2005-04-19 | 0 | 0 | 0 | 11.43 | 11.28 | 0
2594 | 2005-04-19 01:00 | 0 | 0 | 0 | 10.64 | 11.28 | 0
2595 | 2005-04-19 02:00 | 0 | 0 | 0 | 9.45 | 11.28 | 0
2596 | 2005-04-19 03:00 | 0 | 0 | 0 | 8.26 | 10.21 | 0
2597 | 2005-04-19 04:00 | 0 | 0 | 0 | 7.07 | 10.21 | 0
2598 | 2005-04-19 05:00 | 21 | 103 | 13 | 7.19 | 10.21 | 0 | 2.6553 | 78.0655 | 90 | 0 | 21 | 0 | 10.0304 | 0.19675 | 0 | 9.3868 | 0.001027 | 0 | 9.0394 | 0.00077386 | 8.769 | 8.7686 | 19692.1 | 7.3323 | 11199.3 | 12118.9 | 11850.5 | 0 | 0 | 11848.9 | 588.593 | 0 | 0 | 0 | 2205.08 | 9643.77 | 660 | 9282.89 | 9097.2305
2599 | 2005-04-19 06:00 | 199 | 453 | 82 | 7.31 | 7.74 | 0 | 14.895 | 86.3349 | 78.0617 | 0 | 199 | 94.1546 | 78.5772 | 1.8645 | 80.8671 | 73.5356 | 0.0097319 | 65.3639 | 70.8141 | 0.0073332 | 132.1 | 132.074 | 296598 | 9.8082 | 261682 | 280698 | 260742 | 0 | 0 | 260217 | 719.986 | 0 | 0 | 0 | 0 | 260217 | 719.986 | 253192 | 248128.375
2600 | 2005-04-19 07:00 | 436 | 735 | 99 | 7.43 | 7.74 | 0 | 27.2472 | 94.9153 | 63.4404 | 0 | 436 | 329.122 | 104.627 | 4.085 | 329.019 | 97.9143 | 0.021322 | 308.677 | 94.2906 | 0.016067 | 390.895 | 390.895 | 877852 | 14.8237 | 836531 | 873769 | 848282 | 0 | 0 | 843247 | 749.488 | 0 | 0 | 0 | 0 | 843247 | 749.488 | 828548 | 811977.125
2601 | 2005-04-19 08:00 | 636 | 833 | 107 | 8.66 | 7.74 | 0 | 39.4198 | 104.841 | 48.7668 | 0 | 636 | 549.1 | 117.766 | 5.9588 | 549.1 | 110.21 | 0.031103 | 534.901 | 106.132 | 0.023437 | 621.825 | 621.818 | 1396440 | 20.4216 | 1369550 | 1395910 | 1355580 | 0 | 0 | 1342760 | 747.341 | 0 | 0 | 0 | 0 | 1342760 | 747.341 | 1318570 | 1292197
2602 | 2005-04-19 09:00 | 804 | 876 | 124 | 9.88 | 4.69 | 0 | 50.9396 | 117.913 | 34.0653 | 0 | 804 | 725.466 | 133.445 | 7.5328 | 725.466 | 124.883 | 0.039319 | 717.952 | 120.261 | 0.029628 | 813.095 | 813.09 | 1825990 | 28.5855 | 1818290 | 1790690 | 1743810 | 0 | 0 | 1721580 | 727.779 | 0 | 0 | 0 | 0 | 1721580 | 727.779 | 1688600 | 1654825.125
2603 | 2005-04-19 10:00 | 937 | 934 | 123 | 11.11 | 4.69 | 0 | 60.7683 | 137.651 | 19.3662 | 0 | 937 | 880.01 | 132.684 | 8.779 | 880.01 | 124.171 | 0.045823 | 877.371 | 119.575 | 0.034529 | 967.071 | 967.067 | 2171790 | 33.3578 | 2182020 | 2105980 | 2050630 | 0 | 0 | 2019020 | 715.496 | 0 | 0 | 0 | 0 | 2019020 | 715.496 | 1976350 | 1936819.75
2604 | 2005-04-19 11:00 | 976 | 915 | 139 | 12.06 | 4.69 | 0 | 66.4865 | 168.622 | 4.8971 | 0 | 976 | 909.461 | 148.644 | 9.1444 | 909.461 | 139.107 | 0.047731 | 909.294 | 133.958 | 0.035966 | 1011.99 | 1011.98 | 2272650 | 35.341 | 2288360 | 2189910 | 2133950 | 0 | 0 | 2099210 | 709.198 | 53576.4 | 0 | 0 | 0 | 2043500 | 737.839 | 1999980 | 1959976.5
2605 | 2005-04-19 12:00 | 960 | 870 | 173 | 13.01 | 5.01 | 0 | 65.0147 | 204.758 | 10.3934 | 0 | 960 | 854.009 | 192.247 | 8.9945 | 854.009 | 179.912 | 0.046948 | 853.297 | 173.254 | 0.035376 | 995.788 | 995.777 | 2236260 | 35.4459 | 2249980 | 2152090 | 2096980 | 0 | 0 | 2063340 | 708.674 | 19027.2 | 0 | 0 | 0 | 2043500 | 725.75 | 1999990 | 1959989
2606 | 2005-04-19 13:00 | 915 | 899 | 159 | 13.96 | 5.01 | 0 | 57.324 | 231.141 | 25.0381 | 0 | 915 | 813.741 | 176.141 | 8.5728 | 813.741 | 164.839 | 0.044747 | 809.521 | 158.739 | 0.033718 | 939.245 | 939.235 | 2109290 | 35.1219 | 2116170 | 2026620 | 1975870 | 0 | 0 | 1945860 | 707.867 | 0 | 0 | 0 | 0 | 1945860 | 707.867 | 1905790 | 1867678.5
2607 | 2005-04-19 14:00 | 773 | 917 | 106 | 14.17 | 5.01 | 0 | 46.665 | 247.766 | 39.7404 | 0 | 773 | 705.144 | 114.9 | 7.2424 | 705.144 | 107.528 | 0.037803 | 694.55 | 103.548 | 0.028485 | 774.183 | 774.177 | 1738600 | 31.613 | 1726650 | 1678320 | 1634690 | 0 | 0 | 1614480 | 715.232 | 0 | 0 | 0 | 0 | 1614480 | 715.232 | 1585080 | 1553378.75
2608 | 2005-04-19 15:00 | 587 | 820 | 119 | 14.37 | 7.47 | 0 | 34.8255 | 259.345 | 54.4288 | 0 | 587 | 476.716 | 127.997 | 5.4997 | 476.716 | 119.785 | 0.028707 | 459.577 | 115.352 | 0.021631 | 557.702 | 557.697 | 1252450 | 25.1003 | 1220330 | 1219660 | 1186530 | 0 | 0 | 1176160 | 727.73 | 0 | 0 | 0 | 0 | 1176160 | 727.73 | 1156350 | 1133218.375
2609 | 2005-04-19 16:00 | 347 | 687 | 83 | 14.57 | 7.47 | 0 | 22.5556 | 268.612 | 69.078 | 0 | 347 | 245.773 | 86.1099 | 3.2511 | 245.773 | 80.5849 | 0.01697 | 223.648 | 77.6025 | 0.012787 | 292.226 | 292.223 | 656256 | 20.1925 | 613471 | 626776 | 609966 | 0 | 0 | 607156 | 722.205 | 0 | 0 | 0 | 0 | 607156 | 722.205 | 597375 | 585427.25
2610 | 2005-04-19 17:00 | 135 | 447 | 55 | 14.04 | 7.47 | 0 | 10.233 | 276.988 | 83.6609 | 0 | 135 | 49.7206 | 51.5063 | 1.2648 | 49.7206 | 48.2016 | 0.0066021 | 29.6906 | 46.4177 | 0.0049748 | 73.8299 | 73.8257 | 165794 | 15.4604 | 138465 | 145208 | 141339 | 0 | 0 | 141168 | 678.96 | 0 | 0 | 0 | 0 | 141168 | 678.96 | 136755 | 134019.9375
2611 | 2005-04-19 18:00 | 5 | 82 | 2 | 13.5 | 8.25 | 0 | -1.8715 | 285.365 | 90 | 0 | 5 | 0 | 1.4223 | 0.046846 | 0 | 1.331 | 0 | 0 | 1.2817 | 0 | 1.2433 | 1.2433 | 2792.05 | 13.5228 | 376.983 | 371.965 | 370.234 | 0 | 0 | 370.218 | 183.205 | 0 | 0 | 0 | 370.218 | 0 | 660 | 0 | 0
2612 | 2005-04-19 19:00 | 0 | 0 | 0 | 12.97 | 8.25 | 0
2613 | 2005-04-19 20:00 | 0 | 0 | 0 | 11.94 | 8.25 | 0
2614 | 2005-04-19 21:00 | 0 | 0 | 0 | 10.9 | 6.85 | 0
2615 | 2005-04-19 22:00 | 0 | 0 | 0 | 9.87 | 6.85 | 0
2616 | 2005-04-19 23:00 | 0 | 0 | 0 | 9.47 | 6.85 | 0
2617 | 2005-04-20 | 0 | 0 | 0 | 9.07 | 7.66 | 0
2618 | 2005-04-20 01:00 | 0 | 0 | 0 | 8.67 | 7.66 | 0
2619 | 2005-04-20 02:00 | 0 | 0 | 0 | 8.01 | 7.66 | 0
2620 | 2005-04-20 03:00 | 0 | 0 | 0 | 7.35 | 6.51 | 0
2621 | 2005-04-20 04:00 | 0 | 0 | 0 | 6.69 | 6.51 | 0
2622 | 2005-04-20 05:00 | 27 | 143 | 16 | 6.69 | 6.51 | 0 | 2.8932 | 77.8127 | 90 | 0 | 27 | 0 | 12.3963 | 0.25297 | 0 | 11.6009 | 0.0013204 | 0 | 11.1715 | 0.00099496 | 10.8374 | 10.8365 | 24336.1 | 6.9116 | 14774.4 | 16096.5 | 15728.5 | 0 | 0 | 15725.8 | 602.197 | 0 | 0 | 0 | 1589.18 | 14136.6 | 660 | 13611.4 | 13339.165
2623 | 2005-04-20 06:00 | 227 | 602 | 69 | 6.69 | 3.56 | 0 | 15.125 | 86.0663 | 77.9661 | 0 | 227 | 126.249 | 67.8987 | 2.1268 | 109.326 | 63.5422 | 0.011101 | 88.5738 | 61.1905 | 0.008365 | 145.28 | 145.284 | 326263 | 10.2894 | 290336 | 310433 | 286051 | 0 | 0 | 285411 | 719.235 | 0 | 0 | 0 | 0 | 285411 | 719.235 | 278251 | 272686.0312
2624 | 2005-04-20 07:00 | 456 | 806 | 84 | 6.69 | 3.56 | 0 | 27.4776 | 94.6237 | 63.3592 | 0 | 456 | 361.515 | 89.8636 | 4.2724 | 361.445 | 84.0978 | 0.0223 | 339.213 | 80.9854 | 0.016804 | 407.609 | 407.605 | 915379 | 16.7883 | 874632 | 905949 | 881263 | 0 | 0 | 875738 | 742.797 | 0 | 0 | 0 | 0 | 875738 | 742.797 | 860739 | 843524.0625
2625 | 2005-04-20 08:00 | 666 | 890 | 98 | 8.57 | 3.56 | 0 | 39.661 | 104.518 | 48.6996 | 0 | 666 | 587.367 | 105.887 | 6.2399 | 587.367 | 99.0929 | 0.03257 | 572.238 | 95.4255 | 0.024542 | 647.658 | 647.652 | 1454470 | 24.6155 | 1429880 | 1431960 | 1392410 | 0 | 0 | 1378400 | 733.722 | 0 | 0 | 0 | 0 | 1378400 | 733.722 | 1354190 | 1327107.25
2626 | 2005-04-20 09:00 | 821 | 864 | 148 | 10.46 | 0.21 | 0 | 51.2066 | 117.562 | 34.014 | 0 | 821 | 715.733 | 162.924 | 7.6921 | 715.733 | 152.471 | 0.04015 | 708.346 | 146.828 | 0.030254 | 829.548 | 829.534 | 1862920 | 36.1709 | 1857050 | 1769380 | 1723640 | 0 | 0 | 1700350 | 702.124 | 0 | 0 | 0 | 0 | 1700350 | 702.124 | 1668660 | 1635289.875
2627 | 2005-04-20 10:00 | 955 | 960 | 116 | 12.34 | 0.21 | 0 | 61.0792 | 137.337 | 19.3396 | 0 | 955 | 904.452 | 125.346 | 8.9476 | 904.452 | 117.304 | 0.046704 | 901.748 | 112.963 | 0.035192 | 984.303 | 984.3 | 2210480 | 42.8478 | 2222800 | 2056480 | 2003530 | 0 | 0 | 1970630 | 684.464 | 0 | 0 | 0 | 0 | 1970630 | 684.464 | 1929750 | 1891157.125
2628 | 2005-04-20 11:00 | 1010 | 969 | 121 | 13.65 | 0.21 | 0 | 66.8324 | 168.606 | 4.9889 | 0 | 1010 | 963.316 | 130.258 | 9.4629 | 963.316 | 121.9 | 0.049393 | 963.133 | 117.389 | 0.037219 | 1048.14 | 1048.14 | 2353840 | 46.1364 | 2374010 | 2164040 | 2110960 | 0 | 0 | 2073540 | 675.239 | 28595.2 | 0 | 0 | 0 | 2043630 | 695.897 | 1999980 | 1959984.625
2629 | 2005-04-20 12:00 | 997 | 967 | 120 | 14.96 | 2.48 | 0 | 65.3163 | 205.161 | 10.505 | 0 | 997 | 949.015 | 129.294 | 9.3411 | 949.015 | 120.998 | 0.048757 | 948.206 | 116.52 | 0.03674 | 1032.82 | 1032.82 | 2319430 | 42.4453 | 2337710 | 2167450 | 2113820 | 0 | 0 | 2077450 | 686.223 | 32447.4 | 0 | 0 | 0 | 2043570 | 709.044 | 1999980 | 1959980.25
2630 | 2005-04-20 13:00 | 913 | 946 | 116 | 16.27 | 2.48 | 0 | 57.5482 | 231.63 | 25.1027 | 0 | 913 | 855.28 | 125.334 | 8.5541 | 855.28 | 117.292 | 0.04465 | 850.82 | 112.951 | 0.033644 | 934.89 | 934.88 | 2099500 | 41.149 | 2105860 | 1963060 | 1914800 | 0 | 0 | 1885000 | 688.151 | 0 | 0 | 0 | 0 | 1885000 | 688.151 | 1847270 | 1810326
2631 | 2005-04-20 14:00 | 777 | 921 | 105 | 16.68 | 2.48 | 0 | 46.8393 | 248.202 | 39.7854 | 0 | 777 | 707.937 | 113.695 | 7.2799 | 707.937 | 106.4 | 0.037998 | 697.271 | 102.462 | 0.028633 | 775.769 | 775.771 | 1742180 | 37.3248 | 1730400 | 1639850 | 1596260 | 0 | 0 | 1575960 | 697.218 | 0 | 0 | 0 | 0 | 1575960 | 697.218 | 1548300 | 1517335.375
2632 | 2005-04-20 15:00 | 589 | 821 | 118 | 17.09 | 1.65 | 0 | 34.9755 | 259.725 | 54.4588 | 0 | 589 | 477.625 | 126.779 | 5.5185 | 477.625 | 118.645 | 0.028805 | 460.423 | 114.254 | 0.021705 | 557.458 | 557.45 | 1251890 | 32.7703 | 1219750 | 1178580 | 1150830 | 0 | 0 | 1140310 | 700.559 | 0 | 0 | 0 | 0 | 1140310 | 700.559 | 1122540 | 1100089.375
2633 | 2005-04-20 16:00 | 347 | 646 | 97 | 17.5 | 1.65 | 0 | 22.6977 | 268.953 | 69.0936 | 0 | 347 | 231.193 | 99.5728 | 3.2511 | 231.193 | 93.184 | 0.01697 | 210.359 | 89.7354 | 0.012787 | 291.104 | 291.096 | 653731 | 25.6881 | 610951 | 608975 | 593403 | 0 | 0 | 590588 | 701.765 | 0 | 0 | 0 | 0 | 590588 | 701.765 | 581620 | 569988
2634 | 2005-04-20 17:00 | 146 | 459 | 62 | 17.41 | 1.65 | 0 | 10.3787 | 277.306 | 83.6608 | 0 | 146 | 51.4825 | 57.9979 | 1.3679 | 51.4825 | 54.2766 | 0.00714 | 30.7432 | 52.2679 | 0.0053801 | 80.526 | 80.523 | 180834 | 19.675 | 152336 | 156462 | 152373 | 0 | 0 | 152166 | 666.149 | 0 | 0 | 0 | 0 | 152166 | 666.149 | 147688 | 144734.4062
2635 | 2005-04-20 18:00 | 6 | 87 | 2 | 17.31 | 1.53 | 0 | -1.7126 | 285.671 | 90 | 0 | 6 | 0 | 1.5016 | 0.056215 | 0 | 1.4053 | 0 | 0 | 1.3533 | 0 | 1.3127 | 1.3126 | 2947.75 | 17.3472 | 420.004 | 416.318 | 414.408 | 0 | 0 | 414.39 | 193.801 | 0 | 0 | 0 | 414.39 | 0 | 660 | 0 | 0
2636 | 2005-04-20 19:00 | 0 | 0 | 0 | 17.22 | 1.53 | 0
2637 | 2005-04-20 20:00 | 0 | 0 | 0 | 16.68 | 1.53 | 0
2638 | 2005-04-20 21:00 | 0 | 0 | 0 | 16.15 | 1.2 | 0
2639 | 2005-04-20 22:00 | 0 | 0 | 0 | 15.61 | 1.2 | 0
2640 | 2005-04-20 23:00 | 0 | 0 | 0 | 14.88 | 1.2 | 0
2641 | 2005-04-21 | 0 | 0 | 0 | 14.15 | 1.85 | 0
2642 | 2005-04-21 01:00 | 0 | 0 | 0 | 13.41 | 1.85 | 0
2643 | 2005-04-21 02:00 | 0 | 0 | 0 | 12.61 | 1.85 | 0
2644 | 2005-04-21 03:00 | 0 | 0 | 0 | 11.81 | 3.42 | 0
2645 | 2005-04-21 04:00 | 0 | 0 | 0 | 11 | 3.42 | 0
2646 | 2005-04-21 05:00 | 28 | 134 | 17 | 10.84 | 3.42 | 0 | 3.1276 | 77.5614 | 90 | 0 | 28 | 0 | 13.1512 | 0.26234 | 0 | 12.3074 | 0.0013693 | 0 | 11.8519 | 0.0010318 | 11.4973 | 11.4969 | 25819.1 | 11.1275 | 15934.3 | 17055.1 | 16678.8 | 0 | 0 | 16675.7 | 589.15 | 0 | 0 | 0 | 2773.36 | 13902.3 | 660 | 13385.6 | 13117.9092
2647 | 2005-04-21 06:00 | 221 | 573 | 69 | 10.68 | 4.52 | 0 | 15.3514 | 85.7988 | 77.8731 | 0 | 221 | 120.617 | 67.7661 | 2.0706 | 105.256 | 63.4181 | 0.010808 | 85.4674 | 61.0711 | 0.0081439 | 142.15 | 142.113 | 319146 | 13.9859 | 283436 | 298167 | 276756 | 0 | 0 | 276132 | 703.171 | 0 | 0 | 0 | 19.3297 | 276112 | 704.092 | 269342 | 263955.25
2648 | 2005-04-21 07:00 | 441 | 731 | 101 | 10.52 | 4.52 | 0 | 27.704 | 94.3328 | 63.2811 | 0 | 441 | 328.818 | 106.227 | 4.1318 | 328.786 | 99.4112 | 0.021567 | 308.662 | 95.732 | 0.016251 | 392.278 | 392.273 | 880945 | 19.6451 | 839662 | 859364 | 835544 | 0 | 0 | 830458 | 733.849 | 0 | 0 | 0 | 0 | 830458 | 733.849 | 816596 | 800263.5625
2649 | 2005-04-21 08:00 | 666 | 840 | 127 | 12.66 | 4.52 | 0 | 39.898 | 104.196 | 48.6362 | 0 | 666 | 555.315 | 137.547 | 6.2399 | 555.315 | 128.722 | 0.03257 | 541.064 | 123.958 | 0.024542 | 645.095 | 645.089 | 1448710 | 27.6662 | 1423890 | 1407520 | 1369600 | 0 | 0 | 1355700 | 724.201 | 0 | 0 | 0 | 0 | 1355700 | 724.201 | 1332380 | 1305728.75
2650 | 2005-04-21 09:00 | 811 | 844 | 151 | 14.79 | 2.31 | 0 | 51.4691 | 117.209 | 33.9676 | 0 | 811 | 699.723 | 165.684 | 7.5984 | 699.723 | 155.054 | 0.039661 | 692.524 | 149.315 | 0.029886 | 816.613 | 816.603 | 1833890 | 36.7689 | 1826580 | 1735670 | 1690450 | 0 | 0 | 1667890 | 699.712 | 0 | 0 | 0 | 0 | 1667890 | 699.712 | 1637310 | 1604560.375
2651 | 2005-04-21 10:00 | 958 | 960 | 117 | 16.93 | 2.31 | 0 | 61.3857 | 137.018 | 19.3205 | 0 | 958 | 904.055 | 126.151 | 8.9757 | 904.055 | 118.057 | 0.04685 | 901.358 | 113.687 | 0.035303 | 984.628 | 984.621 | 2211210 | 43.4311 | 2223570 | 2051810 | 2001400 | 0 | 0 | 1968270 | 681.904 | 0 | 0 | 0 | 0 | 1968270 | 681.904 | 1927500 | 1888946
2652 | 2005-04-21 11:00 | 1013 | 969 | 122 | 18 | 2.31 | 0 | 67.1749 | 168.586 | 5.1024 | 0 | 1013 | 962.868 | 131.038 | 9.491 | 962.868 | 122.631 | 0.04954 | 962.677 | 118.092 | 0.037329 | 1048.38 | 1048.38 | 2354400 | 46.2171 | 2374600 | 2163890 | 2109950 | 0 | 0 | 2072590 | 675.263 | 27692.8 | 0 | 0 | 0 | 2043630 | 695.572 | 1999980 | 1959982.5
2653 | 2005-04-21 12:00 | 999 | 967 | 120 | 19.07 | 2.09 | 0 | 65.6146 | 205.566 | 10.624 | 0 | 999 | 948.554 | 129.068 | 9.3598 | 948.554 | 120.786 | 0.048855 | 947.727 | 116.316 | 0.036813 | 1032.16 | 1032.15 | 2317960 | 47.2611 | 2336150 | 2118240 | 2065890 | 0 | 0 | 2029640 | 671.175 | 0 | 0 | 0 | 0 | 2029640 | 671.175 | 1986440 | 1946716.125
2654 | 2005-04-21 13:00 | 919 | 952 | 115 | 20.14 | 2.09 | 0 | 57.7694 | 232.118 | 25.1695 | 0 | 919 | 860.215 | 124.109 | 8.6103 | 860.215 | 116.146 | 0.044943 | 855.703 | 111.848 | 0.033865 | 938.557 | 938.549 | 2107750 | 45.7745 | 2114550 | 1929500 | 1883670 | 0 | 0 | 1853710 | 674.638 | 0 | 0 | 0 | 0 | 1853710 | 674.638 | 1817300 | 1780953.5
2655 | 2005-04-21 14:00 | 779 | 920 | 106 | 20.97 | 2.09 | 0 | 47.0115 | 248.635 | 39.831 | 0 | 779 | 706.533 | 114.525 | 7.2986 | 706.533 | 107.177 | 0.038096 | 695.857 | 103.211 | 0.028706 | 775.124 | 775.119 | 1740720 | 42.1407 | 1728870 | 1602640 | 1563570 | 0 | 0 | 1543180 | 680.815 | 0 | 0 | 0 | 0 | 1543180 | 680.815 | 1517090 | 1486747.875
2656 | 2005-04-21 15:00 | 592 | 865 | 94 | 21.81 | 3.08 | 0 | 35.1241 | 260.101 | 54.4885 | 0 | 592 | 502.775 | 102.45 | 5.5466 | 502.775 | 95.8768 | 0.028951 | 484.636 | 92.3284 | 0.021815 | 559.677 | 559.674 | 1256880 | 36.1225 | 1224920 | 1165660 | 1136530 | 0 | 0 | 1125940 | 689.918 | 0 | 0 | 0 | 0 | 1125940 | 689.918 | 1108980 | 1086803.625
2657 | 2005-04-21 16:00 | 361 | 726 | 79 | 22.65 | 3.08 | 0 | 22.839 | 269.29 | 69.1084 | 0 | 361 | 259.083 | 81.7333 | 3.3823 | 259.083 | 76.4891 | 0.017654 | 235.711 | 73.6583 | 0.013303 | 300.101 | 300.096 | 673937 | 30.3244 | 631133 | 615750 | 599812 | 0 | 0 | 596814 | 686.616 | 0 | 0 | 0 | 0 | 596814 | 686.616 | 588245 | 576480.0625
2658 | 2005-04-21 17:00 | 148 | 514 | 53 | 22.31 | 3.08 | 0 | 10.524 | 277.62 | 83.6595 | 0 | 148 | 57.4414 | 49.2756 | 1.3866 | 57.4414 | 46.114 | 0.0072378 | 34.307 | 44.4074 | 0.0054538 | 76.3582 | 76.357 | 171479 | 24.2627 | 143699 | 144238 | 140525 | 0 | 0 | 140339 | 648.905 | 0 | 0 | 0 | 513.201 | 139826 | 660 | 135686 | 132972.0469
2659 | 2005-04-21 18:00 | 7 | 101 | 3 | 21.98 | 3.3 | 0 | -1.554 | 285.974 | 90 | 0 | 7 | 0 | 2.1981 | 0.065585 | 0 | 2.057 | 0 | 0 | 1.9809 | 0 | 1.9215 | 1.9215 | 4315.13 | 22.0284 | 895.66 | 893.18 | 888.424 | 0 | 0 | 888.385 | 285.125 | 0 | 0 | 0 | 888.385 | 0 | 660 | 0 | 0
2660 | 2005-04-21 19:00 | 0 | 0 | 0 | 21.64 | 3.3 | 0
2661 | 2005-04-21 20:00 | 0 | 0 | 0 | 21.09 | 3.3 | 0
2662 | 2005-04-21 21:00 | 0 | 0 | 0 | 20.55 | 3.91 | 0
2663 | 2005-04-21 22:00 | 0 | 0 | 0 | 20 | 3.91 | 0
2664 | 2005-04-21 23:00 | 0 | 0 | 0 | 19.49 | 3.91 | 0
2665 | 2005-04-22 | 0 | 0 | 0 | 18.98 | 6.09 | 0
2666 | 2005-04-22 01:00 | 0 | 0 | 0 | 18.47 | 6.09 | 0
2667 | 2005-04-22 02:00 | 0 | 0 | 0 | 18.33 | 6.09 | 0
2668 | 2005-04-22 03:00 | 0 | 0 | 0 | 18.19 | 5.92 | 0
2669 | 2005-04-22 04:00 | 0 | 0 | 0 | 18.06 | 5.92 | 0
2670 | 2005-04-22 05:00 | 6 | 0 | 6 | 17.67 | 5.92 | 0 | 3.3585 | 77.3115 | 90 | 0 | 6 | 0 | 5.8655 | 0.056215 | 0 | 5.4891 | 0.00029342 | 0 | 5.286 | 0.0002211 | 5.1276 | 5.1274 | 11514.8 | 17.7789 | 5214.8 | 5342.78 | 5249.56 | 0 | 0 | 5249.13 | 504.311 | 0 | 0 | 0 | 5249.13 | 0 | 660 | 0 | 0
2671 | 2005-04-22 06:00 | 92 | 10 | 89 | 17.28 | 2.98 | 0 | 15.574 | 85.5325 | 77.7828 | 0 | 92 | 2.3646 | 81.3656 | 0.86197 | 2.0779 | 76.145 | 0.0044992 | 1.6909 | 73.3269 | 0.0033902 | 72.7706 | 72.7662 | 163414 | 19.1532 | 136285 | 140368 | 136603 | 0 | 0 | 136435 | 662.968 | 0 | 0 | 0 | 0 | 136435 | 662.968 | 132331 | 129684.2578
2672 | 2005-04-22 07:00 | 268 | 119 | 212 | 16.89 | 2.98 | 0 | 27.9264 | 94.0426 | 63.2061 | 0 | 268 | 53.9009 | 203.062 | 2.5109 | 53.9009 | 190.034 | 0.013106 | 50.6173 | 183.001 | 0.0098759 | 226.619 | 226.615 | 508920 | 22.7237 | 467398 | 472298 | 459200 | 0 | 0 | 457515 | 702.445 | 0 | 0 | 0 | 0 | 457515 | 702.445 | 449925 | 440926.5
2673 | 2005-04-22 08:00 | 259 | 31 | 239 | 18.26 | 2.98 | 0 | 40.1305 | 103.873 | 48.5766 | 0 | 259 | 20.5302 | 242.791 | 2.4266 | 20.5302 | 227.213 | 0.012666 | 20.0052 | 218.804 | 0.0095442 | 231.654 | 231.64 | 520204 | 24.2231 | 478518 | 480188 | 466556 | 0 | 0 | 464797 | 698.22 | 0 | 0 | 0 | 0 | 464797 | 698.22 | 457252 | 448106.875
2674 | 2005-04-22 09:00 | 472 | 125 | 374 | 19.63 | 7.86 | 0 | 51.7268 | 116.854 | 33.926 | 0 | 472 | 103.579 | 372.599 | 4.4223 | 103.579 | 348.692 | 0.023083 | 102.516 | 335.788 | 0.017393 | 425.172 | 425.157 | 954795 | 27.6112 | 914774 | 904131 | 880140 | 0 | 0 | 874124 | 710.099 | 0 | 0 | 0 | 0 | 874124 | 710.099 | 860571 | 843359.8125
2675 | 2005-04-22 10:00 | 526 | 126 | 415 | 20.99 | 7.86 | 0 | 61.6875 | 136.694 | 19.3089 | 0 | 526 | 118.991 | 418.299 | 4.9282 | 118.991 | 391.46 | 0.025724 | 118.636 | 376.972 | 0.019383 | 480.759 | 480.745 | 1079630 | 30.0147 | 1042410 | 1019440 | 991762 | 0 | 0 | 984050 | 705.936 | 0 | 0 | 0 | 0 | 984050 | 705.936 | 968998 | 949617.75
2676 | 2005-04-22 11:00 | 908 | 622 | 335 | 20.89 | 7.86 | 0 | 67.5138 | 168.562 | 5.2358 | 0 | 908 | 617.561 | 359.949 | 8.5073 | 617.561 | 336.854 | 0.044405 | 617.432 | 324.387 | 0.03346 | 913.597 | 913.571 | 2051650 | 38.0398 | 2055480 | 1943100 | 1894380 | 0 | 0 | 1866000 | 697.396 | 0 | 0 | 0 | 0 | 1866000 | 697.396 | 1828850 | 1792269.5
2677 | 2005-04-22 12:00 | 999 | 888 | 190 | 20.78 | 9.53 | 0 | 65.9094 | 205.973 | 10.7497 | 0 | 999 | 870.634 | 208.289 | 9.3598 | 870.634 | 194.924 | 0.048855 | 869.857 | 187.71 | 0.036813 | 1025.88 | 1025.86 | 2303830 | 38.133 | 2321240 | 2194490 | 2139460 | 0 | 0 | 2103580 | 699.729 | 57685.2 | 0 | 0 | 0 | 2043460 | 730.019 | 1999970 | 1959975.25
2678 | 2005-04-22 13:00 | 921 | 768 | 271 | 20.68 | 9.53 | 0 | 57.9875 | 232.605 | 25.2383 | 0 | 921 | 693.395 | 291.37 | 8.629 | 693.395 | 272.676 | 0.045041 | 689.737 | 262.584 | 0.033939 | 923.784 | 923.768 | 2074550 | 36.306 | 2079590 | 1981230 | 1931980 | 0 | 0 | 1902930 | 703.58 | 0 | 0 | 0 | 0 | 1902930 | 703.58 | 1864410 | 1827126.25
2679 | 2005-04-22 14:00 | 421 | 114 | 337 | 20.02 | 9.53 | 0 | 47.1815 | 249.065 | 39.877 | 0 | 421 | 87.8836 | 333.541 | 3.9444 | 87.8836 | 312.14 | 0.020589 | 86.5518 | 300.588 | 0.015514 | 375.541 | 375.523 | 843329 | 26.3722 | 801572 | 796592 | 775038 | 0 | 0 | 770367 | 709.651 | 0 | 0 | 0 | 0 | 770367 | 709.651 | 758440 | 743270.75
2680 | 2005-04-22 15:00 | 584 | 649 | 209 | 19.36 | 11.89 | 0 | 35.2713 | 260.474 | 54.518 | 0 | 584 | 376.948 | 212.952 | 5.4716 | 376.948 | 199.289 | 0.02856 | 363.325 | 191.913 | 0.021521 | 538.601 | 538.594 | 1209550 | 27.2548 | 1176040 | 1164490 | 1133170 | 0 | 0 | 1123500 | 719.877 | 0 | 0 | 0 | 0 | 1123500 | 719.877 | 1105110 | 1083007.875
2681 | 2005-04-22 16:00 | 358 | 714 | 79 | 18.69 | 11.89 | 0 | 22.9794 | 269.624 | 69.1224 | 0 | 358 | 254.682 | 81.5276 | 3.3542 | 254.682 | 76.2966 | 0.017508 | 231.684 | 73.4729 | 0.013192 | 296.015 | 296.012 | 664766 | 23.029 | 621968 | 627488 | 611008 | 0 | 0 | 608103 | 711.363 | 0 | 0 | 0 | 0 | 608103 | 711.363 | 598636 | 586663.25
2682 | 2005-04-22 17:00 | 153 | 518 | 56 | 17.95 | 11.89 | 0 | 10.6687 | 277.931 | 83.657 | 0 | 153 | 57.887 | 51.9549 | 1.4335 | 57.887 | 48.6214 | 0.0074823 | 34.5835 | 46.8219 | 0.0056381 | 78.9688 | 78.9645 | 177334 | 19.1075 | 149100 | 153577 | 149572 | 0 | 0 | 149375 | 669.109 | 0 | 0 | 0 | 0 | 149375 | 669.109 | 144914 | 142015.5938
2683 | 2005-04-22 18:00 | 7 | 105 | 2 | 17.2 | 9.61 | 0 | -1.3958 | 286.273 | 90 | 0 | 7 | 0 | 1.8133 | 0.065585 | 0 | 1.697 | 0 | 0 | 1.6342 | 0 | 1.5852 | 1.5851 | 3559.78 | 17.2267 | 611.47 | 606.239 | 603.374 | 0 | 0 | 603.347 | 233.89 | 0 | 0 | 0 | 603.347 | 0 | 660 | 0 | 0
2684 | 2005-04-22 19:00 | 0 | 0 | 0 | 16.45 | 9.61 | 0
2685 | 2005-04-22 20:00 | 0 | 0 | 0 | 15.57 | 9.61 | 0
2686 | 2005-04-22 21:00 | 0 | 0 | 0 | 14.68 | 9.89 | 0
2687 | 2005-04-22 22:00 | 0 | 0 | 0 | 13.8 | 9.89 | 0
2688 | 2005-04-22 23:00 | 0 | 0 | 0 | 13.11 | 9.89 | 0
2689 | 2005-04-23 | 0 | 0 | 0 | 12.41 | 8.28 | 0
2690 | 2005-04-23 01:00 | 0 | 0 | 0 | 11.72 | 8.28 | 0
2691 | 2005-04-23 02:00 | 0 | 0 | 0 | 11.41 | 8.28 | 0
2692 | 2005-04-23 03:00 | 0 | 0 | 0 | 11.1 | 7.69 | 0
2693 | 2005-04-23 04:00 | 0 | 0 | 0 | 10.79 | 7.69 | 0
2694 | 2005-04-23 05:00 | 33 | 116 | 23 | 10.73 | 7.69 | 0 | 3.5858 | 77.0632 | 90 | 0 | 33 | 0 | 17.9026 | 0.30918 | 0 | 16.754 | 0.0016138 | 0 | 16.1339 | 0.0012161 | 15.6511 | 15.6499 | 35145.7 | 11.027 | 23383.7 | 25109.2 | 24512.7 | 0 | 0 | 24506.3 | 610.528 | 0 | 0 | 0 | 1805.43 | 22700.8 | 660 | 21869.1 | 21431.7617
2695 | 2005-04-23 06:00 | 242 | 536 | 96 | 10.68 | 4.22 | 0 | 15.7929 | 85.2675 | 77.6953 | 0 | 242 | 114.322 | 90.9439 | 2.2673 | 101.147 | 85.1087 | 0.011835 | 82.4736 | 81.9589 | 0.0089178 | 159.508 | 159.514 | 358223 | 14.4642 | 320856 | 336731 | 315757 | 0 | 0 | 314971 | 712.061 | 0 | 0 | 0 | 0 | 314971 | 712.061 | 307766 | 301610.2812
2696 | 2005-04-23 07:00 | 382 | 425 | 181 | 10.62 | 4.22 | 0 | 28.1447 | 93.7532 | 63.1344 | 0 | 382 | 192.562 | 180.222 | 3.579 | 192.562 | 168.658 | 0.018681 | 180.885 | 162.416 | 0.014077 | 333.016 | 333.005 | 747845 | 18.5199 | 705234 | 725564 | 706211 | 0 | 0 | 702539 | 730.938 | 0 | 0 | 0 | 0 | 702539 | 730.938 | 690915 | 677096.25
2697 | 2005-04-23 08:00 | 435 | 195 | 309 | 12.15 | 4.22 | 0 | 40.3587 | 103.55 | 48.5208 | 0 | 435 | 128.875 | 302.497 | 4.0756 | 128.875 | 283.088 | 0.021273 | 125.59 | 272.611 | 0.01603 | 386.271 | 386.256 | 867437 | 21.3132 | 825985 | 839316 | 815573 | 0 | 0 | 810660 | 728.558 | 0 | 0 | 0 | 0 | 810660 | 728.558 | 797342 | 781395.5
2698 | 2005-04-23 09:00 | 550 | 227 | 371 | 13.69 | 3.53 | 0 | 51.9797 | 116.496 | 33.8892 | 0 | 550 | 188.617 | 369.213 | 5.1531 | 188.617 | 345.523 | 0.026897 | 186.687 | 332.736 | 0.020268 | 503.86 | 503.827 | 1131460 | 26.197 | 1095630 | 1089750 | 1059370 | 0 | 0 | 1050960 | 722.11 | 0 | 0 | 0 | 0 | 1050960 | 722.11 | 1033880 | 1013200.5625
2699 | 2005-04-23 10:00 | 768 | 509 | 319 | 15.22 | 3.53 | 0 | 61.9847 | 136.364 | 19.3044 | 0 | 768 | 480.001 | 339.799 | 7.1956 | 480.001 | 317.997 | 0.037558 | 478.571 | 306.228 | 0.028301 | 761.282 | 761.273 | 1709620 | 34.1178 | 1696300 | 1630640 | 1586530 | 0 | 0 | 1567040 | 707.128 | 0 | 0 | 0 | 0 | 1567040 | 707.128 | 1539320 | 1508532
2700 | 2005-04-23 11:00 | 980 | 793 | 247 | 16.36 | 3.53 | 0 | 67.849 | 168.534 | 5.3867 | 0 | 980 | 787.916 | 272.717 | 9.1818 | 787.916 | 255.219 | 0.047926 | 787.741 | 245.774 | 0.036113 | 1002.54 | 1002.54 | 2251430 | 41.2468 | 2265980 | 2112120 | 2058890 | 0 | 0 | 2024600 | 688.719 | 0 | 0 | 0 | 0 | 2024600 | 688.719 | 1981660 | 1942021.875
2701 | 2005-04-23 12:00 | 738 | 326 | 440 | 17.5 | 6.94 | 0 | 66.2007 | 206.382 | 10.8817 | 0 | 738 | 319.839 | 455.583 | 6.9145 | 319.839 | 426.352 | 0.036091 | 319.547 | 410.573 | 0.027196 | 708.242 | 708.225 | 1590490 | 31.593 | 1571720 | 1527550 | 1486780 | 0 | 0 | 1469900 | 713.044 | 0 | 0 | 0 | 0 | 1469900 | 713.044 | 1444580 | 1415688.875
2702 | 2005-04-23 13:00 | 866 | 742 | 236 | 18.64 | 6.94 | 0 | 58.2026 | 233.092 | 25.3089 | 0 | 866 | 670.102 | 256.843 | 8.1137 | 670.102 | 240.363 | 0.042351 | 666.544 | 231.468 | 0.031912 | 871.102 | 871.083 | 1956230 | 35.9737 | 1955100 | 1864950 | 1817900 | 0 | 0 | 1792120 | 703.364 | 0 | 0 | 0 | 0 | 1792120 | 703.364 | 1757410 | 1722259.75
2703 | 2005-04-23 14:00 | 713 | 733 | 174 | 18.34 | 6.94 | 0 | 47.3493 | 249.492 | 39.9234 | 0 | 713 | 562.015 | 188.997 | 6.6803 | 562.015 | 176.87 | 0.034869 | 553.473 | 170.324 | 0.026274 | 702.109 | 702.112 | 1576760 | 32.3113 | 1557370 | 1508840 | 1467610 | 0 | 0 | 1451060 | 711.154 | 0 | 0 | 0 | 0 | 1451060 | 711.154 | 1426230 | 1397707.375
2704 | 2005-04-23 15:00 | 571 | 743 | 140 | 18.05 | 5.09 | 0 | 35.4171 | 260.843 | 54.547 | 0 | 571 | 431.38 | 148.419 | 5.3498 | 431.38 | 138.897 | 0.027924 | 415.763 | 133.756 | 0.021042 | 533.054 | 533.044 | 1197080 | 29.9978 | 1163170 | 1137860 | 1110650 | 0 | 0 | 1101040 | 707.641 | 0 | 0 | 0 | 0 | 1101040 | 707.641 | 1083700 | 1062025.625
2705 | 2005-04-23 16:00 | 374 | 735 | 85 | 17.75 | 5.09 | 0 | 23.119 | 269.955 | 69.1354 | 0 | 374 | 262.148 | 87.2236 | 3.5041 | 262.148 | 81.6271 | 0.01829 | 238.453 | 78.6062 | 0.013782 | 307.561 | 307.555 | 690692 | 24.6436 | 647892 | 648882 | 632175 | 0 | 0 | 629035 | 707.614 | 0 | 0 | 0 | 0 | 629035 | 707.614 | 619360 | 606972.625
2706 | 2005-04-23 17:00 | 147 | 462 | 60 | 17.14 | 5.09 | 0 | 10.8129 | 278.238 | 83.6532 | 0 | 147 | 51.2652 | 55.5863 | 1.3773 | 51.2652 | 52.0197 | 0.0071889 | 30.6412 | 50.0945 | 0.005417 | 78.319 | 78.3161 | 175878 | 18.8954 | 147756 | 152353 | 148363 | 0 | 0 | 148168 | 667.698 | 0 | 0 | 0 | 0 | 148168 | 667.698 | 143752 | 140876.5
2707 | 2005-04-23 18:00 | 7 | 97 | 3 | 16.53 | 10.72 | 0 | -1.238 | 286.567 | 90 | 0 | 7 | 0 | 2.1914 | 0.065585 | 0 | 2.0508 | 0 | 0 | 1.9749 | 0 | 1.9157 | 1.9156 | 4301.83 | 16.5601 | 890.138 | 882.717 | 878.246 | 0 | 0 | 878.208 | 284.032 | 0 | 0 | 0 | 878.208 | 0 | 660 | 0 | 0
2708 | 2005-04-23 19:00 | 0 | 0 | 0 | 15.92 | 10.72 | 0
2709 | 2005-04-23 20:00 | 0 | 0 | 0 | 14.73 | 10.72 | 0
2710 | 2005-04-23 21:00 | 0 | 0 | 0 | 13.54 | 9.27 | 0
2711 | 2005-04-23 22:00 | 0 | 0 | 0 | 12.35 | 9.27 | 0
2712 | 2005-04-23 23:00 | 0 | 0 | 0 | 11.84 | 9.27 | 0
2713 | 2005-04-24 | 0 | 0 | 0 | 11.32 | 8.75 | 0
2714 | 2005-04-24 01:00 | 0 | 0 | 0 | 10.81 | 8.75 | 0
2715 | 2005-04-24 02:00 | 0 | 0 | 0 | 10.27 | 8.75 | 0
2716 | 2005-04-24 03:00 | 0 | 0 | 0 | 9.74 | 8.3 | 0
2717 | 2005-04-24 04:00 | 0 | 0 | 0 | 9.2 | 8.3 | 0
2718 | 2005-04-24 05:00 | 38 | 175 | 23 | 9.33 | 8.3 | 0 | 3.8094 | 76.8165 | 90 | 0 | 38 | 0 | 17.8304 | 0.35603 | 0 | 16.6864 | 0.0018584 | 0 | 16.0688 | 0.0014003 | 15.5881 | 15.5877 | 35005.9 | 9.6146 | 23270.5 | 25155 | 24560.3 | 0 | 0 | 24554 | 614.595 | 0 | 0 | 0 | 1395.29 | 23158.7 | 660 | 22310.8 | 21864.623
2719 | 2005-04-24 06:00 | 245 | 582 | 84 | 9.45 | 9.38 | 0 | 16.0078 | 85.0038 | 77.6107 | 0 | 245 | 125.261 | 81.5765 | 2.2955 | 111.546 | 76.3424 | 0.011982 | 91.1282 | 73.517 | 0.0090283 | 159.715 | 159.705 | 358654 | 12.1766 | 321339 | 340719 | 317762 | 0 | 0 | 316980 | 719.868 | 0 | 0 | 0 | 0 | 316980 | 719.868 | 309588 | 303396.5312
2720 | 2005-04-24 07:00 | 463 | 758 | 103 | 9.58 | 9.38 | 0 | 28.3589 | 93.4648 | 63.0659 | 0 | 463 | 343.305 | 107.628 | 4.338 | 343.305 | 100.722 | 0.022643 | 322.575 | 96.9945 | 0.017062 | 406.999 | 406.993 | 913998 | 16.5286 | 873226 | 905516 | 880540 | 0 | 0 | 875070 | 745.973 | 0 | 0 | 0 | 0 | 875070 | 745.973 | 859956 | 842757.0625
2721 | 2005-04-24 08:00 | 627 | 628 | 218 | 10.79 | 9.38 | 0 | 40.5822 | 103.227 | 48.4687 | 0 | 627 | 416.852 | 224.82 | 5.8745 | 416.852 | 210.395 | 0.030663 | 406.26 | 202.609 | 0.023105 | 590.625 | 590.618 | 1326380 | 20.8736 | 1296850 | 1319460 | 1281720 | 0 | 0 | 1270170 | 744.773 | 0 | 0 | 0 | 0 | 1270170 | 744.773 | 1247610 | 1222658.5
2722 | 2005-04-24 09:00 | 370 | 105 | 287 | 11.99 | 8.2 | 0 | 52.2278 | 116.137 | 33.8572 | 0 | 370 | 87.1976 | 284.873 | 3.4666 | 87.1976 | 266.595 | 0.018094 | 86.3073 | 256.728 | 0.013635 | 332.758 | 332.755 | 747285 | 18.1044 | 704687 | 726303 | 705690 | 0 | 0 | 702055 | 733.341 | 0 | 0 | 0 | 0 | 702055 | 733.341 | 690354 | 676546.875
2723 | 2005-04-24 10:00 | 164 | 4 | 160 | 13.2 | 8.2 | 0 | 62.2771 | 136.028 | 19.307 | 0 | 164 | 4.2646 | 149.114 | 1.5366 | 4.2646 | 139.547 | 0.0080203 | 4.2519 | 134.382 | 0.0060434 | 134.481 | 134.475 | 301996 | 15.671 | 266432 | 278477 | 270681 | 0 | 0 | 270096 | 704.237 | 0 | 0 | 0 | 0 | 270096 | 704.237 | 263217 | 257953.0156
2724 | 2005-04-24 11:00 | 291 | 3 | 288 | 14.07 | 8.2 | 0 | 68.1805 | 168.501 | 5.5531 | 0 | 291 | 3.2163 | 271.741 | 2.7264 | 3.2163 | 254.306 | 0.014231 | 3.2156 | 244.894 | 0.010723 | 240.677 | 240.668 | 540480 | 18.4923 | 498527 | 513416 | 498881 | 0 | 0 | 496987 | 719.779 | 0 | 0 | 0 | 0 | 496987 | 719.779 | 488403 | 478634.875
2725 | 2005-04-24 12:00 | 324 | 11 | 314 | 14.93 | 9.21 | 0 | 66.4884 | 206.792 | 11.0191 | 0 | 324 | 10.7043 | 296.809 | 3.0356 | 10.7043 | 277.765 | 0.015845 | 10.6943 | 267.485 | 0.01194 | 269.846 | 269.841 | 605993 | 19.5857 | 563438 | 577290 | 560458 | 0 | 0 | 558068 | 719.065 | 0 | 0 | 0 | 0 | 558068 | 719.065 | 548875 | 537897.6875
2726 | 2005-04-24 13:00 | 189 | 0 | 189 | 15.8 | 9.21 | 0 | 58.4146 | 233.576 | 25.3811 | 0 | 189 | 0 | 176.433 | 1.7708 | 0 | 165.113 | 0.0092429 | 0 | 159.002 | 0.0069647 | 154.239 | 154.231 | 346362 | 18.461 | 308996 | 318681 | 309594 | 0 | 0 | 308823 | 700.779 | 0 | 0 | 0 | 0 | 308823 | 700.779 | 301794 | 295758.375
2727 | 2005-04-24 14:00 | 163 | 0 | 163 | 15.77 | 9.21 | 0 | 47.5151 | 249.916 | 39.97 | 0 | 163 | 0 | 151.509 | 1.5272 | 0 | 141.788 | 0.0079714 | 0 | 136.541 | 0.0060066 | 132.45 | 132.443 | 297434 | 18.0551 | 262077 | 270924 | 263245 | 0 | 0 | 262677 | 694.368 | 0 | 0 | 0 | 0 | 262677 | 694.368 | 256082 | 250959.9062
2728 | 2005-04-24 15:00 | 159 | 0 | 159 | 15.74 | 10.78 | 0 | 35.5616 | 261.209 | 54.5755 | 0 | 159 | 0 | 147.451 | 1.4897 | 0 | 137.99 | 0.0077758 | 0 | 132.883 | 0.0058592 | 128.902 | 128.894 | 289463 | 17.7598 | 254475 | 263453 | 255900 | 0 | 0 | 255366 | 695.734 | 0 | 0 | 0 | 0 | 255366 | 695.734 | 248808 | 243832
2729 | 2005-04-24 16:00 | 343 | 435 | 171 | 15.71 | 10.78 | 0 | 23.2577 | 270.282 | 69.1475 | 0 | 343 | 155.053 | 165.874 | 3.2136 | 155.053 | 155.231 | 0.016774 | 141.027 | 149.486 | 0.01264 | 281.809 | 281.8 | 632852 | 20.1259 | 590139 | 603171 | 586798 | 0 | 0 | 584184 | 720.609 | 0 | 0 | 0 | 0 | 584184 | 720.609 | 574703 | 563209.0625
2730 | 2005-04-24 17:00 | 89 | 60 | 77 | 15.34 | 10.78 | 0 | 10.9566 | 278.541 | 83.6481 | 0 | 89 | 6.985 | 77.6269 | 0.83386 | 6.985 | 72.6462 | 0.0043525 | 4.1774 | 69.9576 | 0.0032797 | 71.9142 | 71.9118 | 161496 | 16.4669 | 134522 | 140401 | 136536 | 0 | 0 | 136374 | 674.588 | 0 | 0 | 0 | 0 | 136374 | 674.588 | 132126 | 129483.1172
2731 | 2005-04-24 18:00 | 5 | 13 | 4 | 14.96 | 10.12 | 0 | -1.0805 | 286.858 | 90 | 0 | 5 | 0 | 3.4702 | 0.046846 | 0 | 3.2476 | 0 | 0 | 3.1274 | 0 | 3.0336 | 3.0335 | 6812.4 | 15.0095 | 2158.12 | 2166.83 | 2145.81 | 0 | 0 | 2145.7 | 424.92 | 0 | 0 | 0 | 2145.7 | 0 | 660 | 0 | 0
2732 | 2005-04-24 19:00 | 0 | 0 | 0 | 14.59 | 10.12 | 0
2733 | 2005-04-24 20:00 | 0 | 0 | 0 | 13.79 | 10.12 | 0
2734 | 2005-04-24 21:00 | 0 | 0 | 0 | 12.99 | 9.61 | 0
2735 | 2005-04-24 22:00 | 0 | 0 | 0 | 12.19 | 9.61 | 0
2736 | 2005-04-24 23:00 | 0 | 0 | 0 | 11.52 | 9.61 | 0
2737 | 2005-04-25 | 0 | 0 | 0 | 10.85 | 9.21 | 0
2738 | 2005-04-25 01:00 | 0 | 0 | 0 | 10.18 | 9.21 | 0
2739 | 2005-04-25 02:00 | 0 | 0 | 0 | 9.7 | 9.21 | 0
2740 | 2005-04-25 03:00 | 0 | 0 | 0 | 9.22 | 7.28 | 0
2741 | 2005-04-25 04:00 | 0 | 0 | 0 | 8.74 | 7.28 | 0
2742 | 2005-04-25 05:00 | 41 | 185 | 25 | 9.17 | 7.28 | 0 | 4.0292 | 76.5715 | 90 | 0 | 41 | 0 | 19.3883 | 0.38414 | 0 | 18.1443 | 0.0020051 | 0 | 17.4728 | 0.0015109 | 16.9501 | 16.9489 | 38063.2 | 9.5001 | 25758.9 | 27873.2 | 27223.7 | 0 | 0 | 27216.1 | 621.005 | 0 | 0 | 0 | 1148.28 | 26067.8 | 660 | 25118 | 24615.6562
2743 | 2005-04-25 06:00 | 249 | 625 | 74 | 9.6 | 5.56 | 0 | 16.2188 | 84.7416 | 77.5289 | 0 | 249 | 135.302 | 71.9885 | 2.3329 | 121.21 | 67.3696 | 0.012177 | 99.2058 | 64.8763 | 0.0091757 | 159.169 | 159.148 | 357405 | 13.0602 | 320214 | 338125 | 314864 | 0 | 0 | 314091 | 719.471 | 0 | 0 | 0 | 0 | 314091 | 719.471 | 306728 | 300593.4062
2744 | 2005-04-25 07:00 | 467 | 796 | 86 | 10.03 | 5.56 | 0 | 28.5688 | 93.1774 | 63.0006 | 0 | 467 | 361.694 | 91.0823 | 4.3754 | 361.694 | 85.2383 | 0.022838 | 339.943 | 82.0837 | 0.017209 | 409.382 | 409.38 | 919361 | 18.9306 | 878678 | 901957 | 877252 | 0 | 0 | 871695 | 736.914 | 0 | 0 | 0 | 0 | 871695 | 736.914 | 857010 | 839870.0625
2745 | 2005-04-25 08:00 | 677 | 886 | 98 | 11.76 | 5.56 | 0 | 40.8012 | 102.904 | 48.4205 | 0 | 677 | 588.058 | 105.086 | 6.343 | 588.058 | 98.3431 | 0.033108 | 573.157 | 94.7035 | 0.024948 | 647.849 | 647.842 | 1454890 | 25.8452 | 1430310 | 1424960 | 1385170 | 0 | 0 | 1371150 | 729.632 | 0 | 0 | 0 | 0 | 1371150 | 729.632 | 1347270 | 1320326.25
2746 | 2005-04-25 09:00 | 839 | 918 | 111 | 13.49 | 0.88 | 0 | 52.4708 | 115.776 | 33.83 | 0 | 839 | 762.562 | 119.167 | 7.8608 | 762.562 | 111.521 | 0.041031 | 754.791 | 107.394 | 0.030917 | 836.349 | 836.346 | 1878230 | 38.2646 | 1873130 | 1768100 | 1720960 | 0 | 0 | 1697400 | 696.87 | 0 | 0 | 0 | 0 | 1697400 | 696.87 | 1665950 | 1632627
2747 | 2005-04-25 10:00 | 965 | 955 | 119 | 15.23 | 0.88 | 0 | 62.5645 | 135.687 | 19.3166 | 0 | 965 | 899.546 | 127.331 | 9.0413 | 899.546 | 119.161 | 0.047192 | 896.863 | 114.751 | 0.035561 | 981.301 | 981.3 | 2203750 | 44.2985 | 2215710 | 2036260 | 1988960 | 0 | 0 | 1956110 | 679.76 | 0 | 0 | 0 | 0 | 1956110 | 679.76 | 1915800 | 1877487.75
2748 | 2005-04-25 11:00 | 1022 | 968 | 123 | 16.55 | 0.88 | 0 | 68.508 | 168.463 | 5.733 | 0 | 1022 | 961.347 | 131.126 | 9.5753 | 961.347 | 122.712 | 0.04998 | 961.106 | 118.171 | 0.037661 | 1046.93 | 1046.93 | 2351140 | 47.5626 | 2371160 | 2147070 | 2095440 | 0 | 0 | 2058060 | 670.335 | 13717.7 | 0 | 0 | 0 | 2043690 | 684.127 | 1999990 | 1959987.25
2749 | 2005-04-25 12:00 | 1007 | 967 | 120 | 17.88 | 2.54 | 0 | 66.7726 | 207.204 | 11.1615 | 0 | 1007 | 946.979 | 128.183 | 9.4348 | 946.979 | 119.959 | 0.049246 | 946.066 | 115.519 | 0.037108 | 1029.77 | 1029.77 | 2312590 | 45.175 | 2330490 | 2133780 | 2083160 | 0 | 0 | 2046890 | 677.26 | 4064.91 | 0 | 0 | 0 | 2042630 | 684.035 | 1998970 | 1958987.75
2750 | 2005-04-25 13:00 | 927 | 952 | 115 | 19.2 | 2.54 | 0 | 58.6235 | 234.059 | 25.4547 | 0 | 927 | 858.756 | 123.307 | 8.6853 | 858.756 | 115.395 | 0.045334 | 854.14 | 111.124 | 0.03416 | 936.339 | 936.337 | 2102780 | 44.0185 | 2109310 | 1940530 | 1892600 | 0 | 0 | 1862620 | 678.154 | 0 | 0 | 0 | 0 | 1862620 | 678.154 | 1825830 | 1789314.625
2751 | 2005-04-25 14:00 | 774 | 901 | 108 | 19.42 | 2.54 | 0 | 47.6787 | 250.336 | 40.0168 | 0 | 774 | 689.848 | 115.817 | 7.2518 | 689.848 | 108.386 | 0.037852 | 679.303 | 104.375 | 0.028522 | 760.195 | 760.189 | 1707190 | 39.5695 | 1693740 | 1588680 | 1547820 | 0 | 0 | 1528230 | 688.176 | 0 | 0 | 0 | 0 | 1528230 | 688.176 | 1502330 | 1472286.375
2752 | 2005-04-25 15:00 | 600 | 867 | 94 | 19.64 | 4.89 | 0 | 35.7047 | 261.571 | 54.6035 | 0 | 600 | 502.206 | 101.643 | 5.6215 | 502.206 | 95.1216 | 0.029343 | 483.965 | 91.6012 | 0.02211 | 558.321 | 558.317 | 1253840 | 32.318 | 1221770 | 1182970 | 1153440 | 0 | 0 | 1142960 | 703.257 | 0 | 0 | 0 | 0 | 1142960 | 703.257 | 1125000 | 1102500.625
2753 | 2005-04-25 16:00 | 381 | 761 | 78 | 19.86 | 4.89 | 0 | 23.3956 | 270.605 | 69.1587 | 0 | 381 | 271.488 | 80.858 | 3.5697 | 271.488 | 75.67 | 0.018632 | 246.908 | 72.8695 | 0.01404 | 310.198 | 310.196 | 696622 | 26.9038 | 653829 | 648136 | 631411 | 0 | 0 | 628211 | 699.904 | 0 | 0 | 0 | 0 | 628211 | 699.904 | 618791 | 606414.75
2754 | 2005-04-25 17:00 | 154 | 486 | 60 | 19.5 | 4.89 | 0 | 11.0998 | 278.841 | 83.6418 | 0 | 154 | 54.0727 | 55.2606 | 1.4429 | 54.0727 | 51.715 | 0.0075312 | 32.3631 | 49.8011 | 0.0056749 | 79.7047 | 79.7006 | 178988 | 21.3098 | 150628 | 153462 | 149655 | 0 | 0 | 149452 | 661.213 | 0 | 0 | 0 | -3.8164 | 149456 | 661.542 | 145096 | 142193.7969
2755 | 2005-04-25 18:00 | 9 | 108 | 4 | 19.13 | 6.9 | 0 | -0.92347 | 287.145 | 90 | 0 | 9 | 0 | 3.0086 | 0.084323 | 0 | 2.8155 | 0 | 0 | 2.7113 | 0 | 2.63 | 2.6298 | 5905.9 | 19.1825 | 1651.5 | 1649.82 | 1637.11 | 0 | 0 | 1637.03 | 379.893 | 0 | 0 | 0 | 1637.03 | 0 | 660 | 0 | 0
2756 | 2005-04-25 19:00 | 0 | 0 | 0 | 18.76 | 6.9 | 0
2757 | 2005-04-25 20:00 | 0 | 0 | 0 | 17.9 | 6.9 | 0
2758 | 2005-04-25 21:00 | 0 | 0 | 0 | 17.04 | 6.79 | 0
2759 | 2005-04-25 22:00 | 0 | 0 | 0 | 16.18 | 6.79 | 0
2760 | 2005-04-25 23:00 | 0 | 0 | 0 | 15.33 | 6.79 | 0
2761 | 2005-04-26 | 0 | 0 | 0 | 14.47 | 6.18 | 0
2762 | 2005-04-26 01:00 | 0 | 0 | 0 | 13.62 | 6.18 | 0
2763 | 2005-04-26 02:00 | 0 | 0 | 0 | 13.03 | 6.18 | 0
2764 | 2005-04-26 03:00 | 0 | 0 | 0 | 12.44 | 1.78 | 0
2765 | 2005-04-26 04:00 | 0 | 0 | 0 | 11.85 | 1.78 | 0
2766 | 2005-04-26 05:00 | 42 | 143 | 29 | 11.89 | 1.78 | 0 | 4.2452 | 76.3281 | 90 | 0 | 42 | 0 | 22.5871 | 0.39351 | 0 | 21.1378 | 0.002054 | 0 | 20.3555 | 0.0015477 | 19.7464 | 19.7451 | 44342.7 | 12.4406 | 30929.7 | 33012.2 | 32232.6 | 0 | 0 | 32221.8 | 618.551 | 0 | 0 | 0 | 1566.69 | 30655.1 | 660 | 29546.6 | 28955.6543
2767 | 2005-04-26 06:00 | 254 | 589 | 87 | 11.94 | 2.67 | 0 | 16.4258 | 84.4808 | 77.45 | 0 | 254 | 128.328 | 84.1287 | 2.3798 | 115.589 | 78.7309 | 0.012422 | 94.7704 | 75.8171 | 0.00936 | 165.479 | 165.466 | 371595 | 16.2881 | 333809 | 347355 | 325394 | 0 | 0 | 324547 | 707.283 | 0 | 0 | 0 | 0 | 324547 | 707.283 | 317438 | 311088.875
2768 | 2005-04-26 07:00 | 467 | 756 | 103 | 11.98 | 2.67 | 0 | 28.7743 | 92.8911 | 62.9386 | 0 | 467 | 344.025 | 107.245 | 4.3754 | 344.025 | 100.364 | 0.022838 | 323.416 | 96.6493 | 0.017209 | 407.481 | 407.477 | 915090 | 22.6876 | 874337 | 883125 | 859156 | 0 | 0 | 853653 | 725.113 | 0 | 0 | 0 | 0 | 853653 | 725.113 | 839776 | 822980.8125
2769 | 2005-04-26 08:00 | 686 | 894 | 99 | 14 | 2.67 | 0 | 41.0155 | 102.582 | 48.376 | 0 | 686 | 594.135 | 105.934 | 6.4273 | 594.135 | 99.1373 | 0.033548 | 579.119 | 95.4683 | 0.025279 | 654.374 | 654.37 | 1469550 | 31.1955 | 1445570 | 1407150 | 1370260 | 0 | 0 | 1355870 | 712.58 | 0 | 0 | 0 | 0 | 1355870 | 712.58 | 1333050 | 1306392.375
2770 | 2005-04-26 09:00 | 855 | 937 | 110 | 16.02 | 3.19 | 0 | 52.7088 | 115.414 | 33.8074 | 0 | 855 | 778.099 | 117.976 | 8.0107 | 778.099 | 110.406 | 0.041813 | 770.182 | 106.32 | 0.031507 | 850.238 | 850.228 | 1909400 | 37.6052 | 1905870 | 1804550 | 1757840 | 0 | 0 | 1733370 | 698.034 | 0 | 0 | 0 | 0 | 1733370 | 698.034 | 1700720 | 1666701.5
2771 | 2005-04-26 10:00 | 970 | 959 | 118 | 18.04 | 3.19 | 0 | 62.8469 | 135.34 | 19.3329 | 0 | 970 | 903.535 | 126.116 | 9.0881 | 903.535 | 118.024 | 0.047437 | 900.835 | 113.656 | 0.035745 | 984.091 | 984.089 | 2210020 | 43.0236 | 2222310 | 2054500 | 2003400 | 0 | 0 | 1970590 | 685.01 | 0 | 0 | 0 | 0 | 1970590 | 685.01 | 1929710 | 1891117.5
2772 | 2005-04-26 11:00 | 1007 | 944 | 129 | 19.24 | 3.19 | 0 | 68.8315 | 168.421 | 5.9245 | 0 | 1007 | 936.503 | 136.904 | 9.4348 | 936.503 | 128.12 | 0.049246 | 936.252 | 123.378 | 0.037108 | 1027.88 | 1027.87 | 2308330 | 45.3351 | 2325990 | 2128080 | 2076500 | 0 | 0 | 2040370 | 676.598 | 984.567 | 0 | 0 | 0 | 2039330 | 679.203 | 1995780 | 1955866.5
2773 | 2005-04-26 12:00 | 1009 | 914 | 169 | 20.45 | 5.11 | 0 | 67.053 | 207.616 | 11.3082 | 0 | 1009 | 894.476 | 185.928 | 9.4535 | 894.476 | 173.998 | 0.049344 | 893.591 | 167.559 | 0.037182 | 1029.35 | 1029.34 | 2311650 | 43.492 | 2329490 | 2149600 | 2099440 | 0 | 0 | 2063310 | 683.988 | 18846.2 | 0 | 0 | 0 | 2043620 | 699.287 | 1999980 | 1959983.25
2774 | 2005-04-26 13:00 | 884 | 719 | 269 | 21.65 | 5.11 | 0 | 58.8294 | 234.54 | 25.5295 | 0 | 884 | 648.59 | 287.727 | 8.2824 | 648.59 | 269.266 | 0.043231 | 645.082 | 259.301 | 0.032576 | 877.283 | 877.265 | 1970120 | 41.2877 | 1969700 | 1834420 | 1790580 | 0 | 0 | 1764320 | 686.175 | 0 | 0 | 0 | 0 | 1764320 | 686.175 | 1730880 | 1696264.125
2775 | 2005-04-26 14:00 | 321 | 69 | 270 | 21.79 | 5.11 | 0 | 47.8403 | 250.753 | 40.0635 | 0 | 321 | 52.655 | 274.903 | 3.0075 | 52.655 | 257.265 | 0.015698 | 51.8478 | 247.743 | 0.011829 | 290.615 | 290.602 | 652620 | 28.2951 | 609864 | 600620 | 584395 | 0 | 0 | 581602 | 693.253 | 0 | 0 | 0 | 0 | 581602 | 693.253 | 572977 | 561517.1875
2776 | 2005-04-26 15:00 | 573 | 626 | 206 | 21.92 | 5.8 | 0 | 35.8465 | 261.929 | 54.6308 | 0 | 573 | 362.756 | 208.761 | 5.3686 | 362.756 | 195.366 | 0.028022 | 349.559 | 188.136 | 0.021115 | 521.584 | 521.566 | 1171300 | 33.0854 | 1136610 | 1096500 | 1068130 | 0 | 0 | 1058980 | 697.737 | 0 | 0 | 0 | 0 | 1058980 | 697.737 | 1042950 | 1022093.875
2777 | 2005-04-26 16:00 | 361 | 654 | 99 | 22.06 | 5.8 | 0 | 23.5327 | 270.924 | 69.1687 | 0 | 361 | 233.354 | 100.187 | 3.3823 | 233.354 | 93.7591 | 0.017654 | 212.212 | 90.2892 | 0.013303 | 293.439 | 293.437 | 658982 | 28.3417 | 616192 | 606751 | 590779 | 0 | 0 | 587919 | 692.744 | 0 | 0 | 0 | 0 | 587919 | 692.744 | 579249 | 567664.0625
2778 | 2005-04-26 17:00 | 135 | 252 | 85 | 21.61 | 5.8 | 0 | 11.2424 | 279.136 | 83.6341 | 0 | 135 | 28.4362 | 75.2842 | 1.2648 | 28.4362 | 70.4539 | 0.0066021 | 17.0348 | 67.8464 | 0.0049748 | 82.3397 | 82.337 | 184907 | 23.3726 | 156109 | 157400 | 153335 | 0 | 0 | 153119 | 655.876 | 0 | 0 | 0 | 88.2877 | 153031 | 660 | 148621 | 145648.4219
2779 | 2005-04-26 18:00 | 8 | 58 | 5 | 21.17 | 7.66 | 0 | -0.76686 | 287.427 | 90 | 0 | 8 | 0 | 3.9474 | 0.074954 | 0 | 3.6941 | 0 | 0 | 3.5574 | 0 | 3.4507 | 3.4505 | 7748.95 | 21.2356 | 2720.88 | 2735.64 | 2702.98 | 0 | 0 | 2702.82 | 438.721 | 0 | 0 | 0 | 2702.82 | 0 | 660 | 0 | 0
2780 | 2005-04-26 19:00 | 0 | 0 | 0 | 20.72 | 7.66 | 0
2781 | 2005-04-26 20:00 | 0 | 0 | 0 | 19.81 | 7.66 | 0
2782 | 2005-04-26 21:00 | 0 | 0 | 0 | 18.9 | 5.27 | 0
2783 | 2005-04-26 22:00 | 0 | 0 | 0 | 17.99 | 5.27 | 0
2784 | 2005-04-26 23:00 | 0 | 0 | 0 | 17.1 | 5.27 | 0
2785 | 2005-04-27 | 0 | 0 | 0 | 16.22 | 8.95 | 0
2786 | 2005-04-27 01:00 | 0 | 0 | 0 | 15.33 | 8.95 | 0
2787 | 2005-04-27 02:00 | 0 | 0 | 0 | 14.47 | 8.95 | 0
2788 | 2005-04-27 03:00 | 0 | 0 | 0 | 13.61 | 7.88 | 0
2789 | 2005-04-27 04:00 | 0 | 0 | 0 | 12.75 | 7.88 | 0
2790 | 2005-04-27 05:00 | 44 | 191 | 27 | 12.75 | 7.88 | 0 | 4.4572 | 76.0865 | 90 | 0 | 44 | 0 | 20.8679 | 0.41225 | 0 | 19.5289 | 0.0021518 | 0 | 18.8062 | 0.0016214 | 18.2436 | 18.242 | 40966.9 | 13.092 | 28140.7 | 29934.5 | 29231.9 | 0 | 0 | 29222.9 | 612.098 | 0 | 0 | 0 | 2058.98 | 27163.9 | 660 | 26175.9 | 25652.4082
2791 | 2005-04-27 06:00 | 237 | 570 | 73 | 12.75 | 7.22 | 0 | 16.6286 | 84.2216 | 77.3741 | 0 | 237 | 125.269 | 70.7739 | 2.2205 | 113.475 | 66.2329 | 0.01159 | 93.1923 | 63.7817 | 0.0087335 | 152.273 | 152.316 | 342063 | 15.7274 | 305336 | 318697 | 298162 | 0 | 0 | 297436 | 701.402 | 0 | 0 | 0 | 0 | 297436 | 701.402 | 290557 | 284745.9688
2792 | 2005-04-27 07:00 | 462 | 740 | 103 | 12.75 | 7.22 | 0 | 28.9755 | 92.606 | 62.8798 | 0 | 462 | 337.822 | 107.055 | 4.3286 | 337.822 | 100.186 | 0.022594 | 317.66 | 96.4787 | 0.017025 | 401.731 | 401.724 | 902169 | 20.6028 | 861204 | 877778 | 855830 | 0 | 0 | 850423 | 728.916 | 0 | 0 | 0 | 0 | 850423 | 728.916 | 836437 | 819708.1875
2793 | 2005-04-27 08:00 | 689 | 846 | 132 | 13.76 | 7.22 | 0 | 41.225 | 102.26 | 48.3352 | 0 | 689 | 561.863 | 141.234 | 6.4554 | 561.863 | 132.172 | 0.033695 | 547.696 | 127.281 | 0.02539 | 654.752 | 654.742 | 1470390 | 26.5588 | 1446450 | 1436690 | 1398450 | 0 | 0 | 1384080 | 727.78 | 0 | 0 | 0 | 0 | 1384080 | 727.78 | 1360010 | 1332811.625
2794 | 2005-04-27 09:00 | 847 | 920 | 113 | 14.76 | 7.95 | 0 | 52.9417 | 115.05 | 33.7894 | 0 | 847 | 764.413 | 120.817 | 7.9357 | 764.413 | 113.065 | 0.041422 | 756.645 | 108.881 | 0.031212 | 839.59 | 839.584 | 1885490 | 30.4318 | 1880750 | 1837790 | 1787300 | 0 | 0 | 1763600 | 721.644 | 0 | 0 | 0 | 0 | 1763600 | 721.644 | 1729450 | 1694858.875
2795 | 2005-04-27 10:00 | 948 | 879 | 165 | 15.76 | 7.95 | 0 | 63.1241 | 134.988 | 19.3558 | 0 | 948 | 828.199 | 180.786 | 8.882 | 828.199 | 169.187 | 0.046361 | 825.719 | 162.925 | 0.034934 | 959.018 | 959.01 | 2153700 | 33.6611 | 2162950 | 2084870 | 2033280 | 0 | 0 | 2001940 | 712.361 | 0 | 0 | 0 | 0 | 2001940 | 712.361 | 1959870 | 1920670.25
2796 | 2005-04-27 11:00 | 1026 | 969 | 123 | 16.31 | 7.95 | 0 | 69.151 | 168.373 | 6.1258 | 0 | 1026 | 960.752 | 130.675 | 9.6128 | 960.752 | 122.291 | 0.050176 | 960.477 | 117.765 | 0.037808 | 1045.93 | 1045.93 | 2348890 | 35.8335 | 2368780 | 2262340 | 2204670 | 0 | 0 | 2167510 | 708.281 | 119276 | 0 | 0 | 0 | 2044520 | 749.514 | 1999960 | 1959965.625
2797 | 2005-04-27 12:00 | 1011 | 848 | 230 | 16.85 | 9.67 | 0 | 67.3298 | 208.029 | 11.4587 | 0 | 1011 | 829.523 | 253.148 | 9.4723 | 829.523 | 236.905 | 0.049442 | 828.68 | 228.137 | 0.037256 | 1025.15 | 1025.14 | 2302190 | 34.0417 | 2319510 | 2232510 | 2173520 | 0 | 0 | 2137930 | 714.154 | 90924.2 | 0 | 0 | 0 | 2044610 | 750.273 | 1999960 | 1959960.5
2798 | 2005-04-27 13:00 | 661 | 289 | 413 | 17.4 | 9.67 | 0 | 59.0323 | 235.019 | 25.6053 | 0 | 661 | 260.823 | 421.231 | 6.1931 | 260.823 | 394.204 | 0.032326 | 259.403 | 379.615 | 0.024358 | 619.871 | 619.845 | 1392010 | 27.7949 | 1364960 | 1348500 | 1312280 | 0 | 0 | 1299410 | 722.123 | 0 | 0 | 0 | 0 | 1299410 | 722.123 | 1277360 | 1251808.125
2799 | 2005-04-27 14:00 | 488 | 175 | 358 | 17.05 | 9.67 | 0 | 47.9998 | 251.166 | 40.11 | 0 | 488 | 133.79 | 352.511 | 4.5722 | 133.79 | 329.893 | 0.023865 | 131.733 | 317.684 | 0.017983 | 435.952 | 435.942 | 979014 | 24.3608 | 939467 | 941992 | 915361 | 0 | 0 | 909049 | 720.985 | 0 | 0 | 0 | 0 | 909049 | 720.985 | 894459 | 876570.0625
2800 | 2005-04-27 15:00 | 317 | 80 | 270 | 16.71 | 12.27 | 0 | 35.987 | 262.283 | 54.6574 | 0 | 317 | 46.2692 | 278.54 | 2.97 | 46.2692 | 260.668 | 0.015503 | 44.5833 | 251.021 | 0.011681 | 286.748 | 286.745 | 643958 | 20.8192 | 601226 | 612588 | 595413 | 0 | 0 | 592722 | 719.476 | 0 | 0 | 0 | 0 | 592722 | 719.476 | 583201 | 571537.25
2801 | 2005-04-27 16:00 | 267 | 262 | 162 | 16.36 | 12.27 | 0 | 23.6689 | 271.238 | 69.1777 | 0 | 267 | 92.9741 | 154.572 | 2.5016 | 92.9741 | 144.654 | 0.013057 | 84.5453 | 139.301 | 0.009839 | 217.14 | 217.134 | 487626 | 19.4717 | 446455 | 457923 | 445608 | 0 | 0 | 444060 | 711.762 | 0 | 0 | 0 | 0 | 444060 | 711.762 | 436343 | 427616.5312
2802 | 2005-04-27 17:00 | 109 | 142 | 81 | 15.51 | 12.27 | 0 | 11.3844 | 279.427 | 83.625 | 0 | 109 | 15.7505 | 71.7913 | 1.0212 | 15.7505 | 67.1851 | 0.0053305 | 9.4455 | 64.6986 | 0.0040167 | 71.9237 | 71.9213 | 161517 | 16.5407 | 134540 | 140369 | 136709 | 0 | 0 | 136546 | 672.824 | 0 | 0 | 0 | 0 | 136546 | 672.824 | 132316 | 129669.2109
2803 | 2005-04-27 18:00 | 6 | 34 | 4 | 14.66 | 10.8 | 0 | -0.61073 | 287.705 | 90 | 0 | 6 | 0 | 3.1337 | 0.056215 | 0 | 2.9326 | 0 | 0 | 2.8241 | 0 | 2.7393 | 2.7393 | 6151.76 | 14.7029 | 1784.57 | 1782.15 | 1767.77 | 0 | 0 | 1767.69 | 396.502 | 0 | 0 | 0 | 1767.69 | 0 | 660 | 0 | 0
2804 | 2005-04-27 19:00 | 0 | 0 | 0 | 13.81 | 10.8 | 0
2805 | 2005-04-27 20:00 | 0 | 0 | 0 | 13.03 | 10.8 | 0
2806 | 2005-04-27 21:00 | 0 | 0 | 0 | 12.24 | 11.86 | 0
2807 | 2005-04-27 22:00 | 0 | 0 | 0 | 11.46 | 11.86 | 0
2808 | 2005-04-27 23:00 | 0 | 0 | 0 | 10.87 | 11.86 | 0
2809 | 2005-04-28 | 0 | 0 | 0 | 10.28 | 13.54 | 0
2810 | 2005-04-28 01:00 | 0 | 0 | 0 | 9.69 | 13.54 | 0
2811 | 2005-04-28 02:00 | 0 | 0 | 0 | 9.27 | 13.54 | 0
2812 | 2005-04-28 03:00 | 0 | 0 | 0 | 8.85 | 11.62 | 0
2813 | 2005-04-28 04:00 | 0 | 0 | 0 | 8.43 | 11.62 | 0
2814 | 2005-04-28 05:00 | 29 | 22 | 27 | 8.12 | 11.62 | 0 | 4.6652 | 75.8466 | 90 | 0 | 29 | 0 | 28.2769 | 0.27171 | 0 | 26.4626 | 0.0014182 | 0 | 25.4833 | 0.0010687 | 24.7198 | 24.7185 | 55511.4 | 8.4882 | 40288.7 | 43844.3 | 42719.2 | 0 | 0 | 42701.8 | 646.076 | 0 | 0 | 0 | 175.337 | 42526.5 | 660 | 41019 | 40198.6172
2815 | 2005-04-28 06:00 | 132 | 58 | 115 | 7.82 | 9.43 | 0 | 16.8272 | 83.964 | 77.3012 | 0 | 132 | 12.9093 | 115.809 | 1.2367 | 11.7485 | 108.378 | 0.0064554 | 9.6637 | 104.367 | 0.0048642 | 110.615 | 110.613 | 248409 | 9.7027 | 215539 | 231712 | 224294 | 0 | 0 | 223907 | 717.149 | 0 | 0 | 0 | 0 | 223907 | 717.149 | 217308 | 212962.0156
2816 | 2005-04-28 07:00 | 485 | 639 | 173 | 7.52 | 9.43 | 0 | 29.1722 | 92.3223 | 62.8244 | 0 | 485 | 292.339 | 171.554 | 4.5441 | 292.339 | 160.547 | 0.023718 | 274.952 | 154.605 | 0.017872 | 416.687 | 416.679 | 935757 | 14.612 | 895363 | 935805 | 908966 | 0 | 0 | 903256 | 752.979 | 0 | 0 | 0 | 0 | 903256 | 752.979 | 887368 | 869620.5625
2817 | 2005-04-28 08:00 | 691 | 720 | 215 | 8.59 | 9.43 | 0 | 41.4296 | 101.939 | 48.2982 | 0 | 691 | 478.556 | 222.854 | 6.4741 | 478.556 | 208.555 | 0.033793 | 466.516 | 200.837 | 0.025464 | 647.357 | 647.344 | 1453770 | 19.608 | 1429160 | 1461460 | 1419250 | 0 | 0 | 1405350 | 750.806 | 0 | 0 | 0 | 0 | 1405350 | 750.806 | 1379630 | 1352033.25
2818 | 2005-04-28 09:00 | 463 | 185 | 315 | 9.66 | 10.66 | 0 | 53.1693 | 114.685 | 33.7759 | 0 | 463 | 153.697 | 311.726 | 4.338 | 153.697 | 291.725 | 0.022643 | 152.136 | 280.929 | 0.017062 | 420.09 | 420.072 | 943376 | 16.2907 | 903134 | 937349 | 910294 | 0 | 0 | 904472 | 747.174 | 0 | 0 | 0 | 0 | 904472 | 747.174 | 888801 | 871025
2819 | 2005-04-28 10:00 | 898 | 691 | 281 | 10.74 | 10.66 | 0 | 63.3961 | 134.63 | 19.385 | 0 | 898 | 650.941 | 301.015 | 8.4136 | 650.941 | 281.702 | 0.043916 | 648.985 | 271.276 | 0.033092 | 892.685 | 892.676 | 2004730 | 24.8307 | 2006110 | 2007200 | 1949950 | 0 | 0 | 1923290 | 742.353 | 0 | 0 | 0 | 0 | 1923290 | 742.353 | 1883520 | 1845851.625
2820 | 2005-04-28 11:00 | 984 | 857 | 183 | 11.66 | 10.66 | 0 | 69.4663 | 168.319 | 6.3353 | 0 | 984 | 850.12 | 199.685 | 9.2193 | 850.12 | 186.873 | 0.048122 | 849.859 | 179.957 | 0.036261 | 998.957 | 998.951 | 2243390 | 27.4282 | 2257500 | 2234600 | 2171570 | 0 | 0 | 2138220 | 737.516 | 93824.8 | 0 | 0 | 0 | 2044720 | 771.379 | 1997680 | 1957728.375
2821 | 2005-04-28 12:00 | 975 | 866 | 176 | 12.58 | 12.16 | 0 | 67.6029 | 208.443 | 11.6125 | 0 | 975 | 846.501 | 192.342 | 9.135 | 846.501 | 180.001 | 0.047682 | 845.617 | 173.34 | 0.035929 | 988.423 | 988.411 | 2219730 | 26.8373 | 2232550 | 2215360 | 2155830 | 0 | 0 | 2122910 | 737.169 | 79108 | 0 | 0 | 0 | 2044470 | 769.931 | 1997610 | 1957655.5
2822 | 2005-04-28 13:00 | 932 | 899 | 160 | 13.5 | 12.16 | 0 | 59.2321 | 235.495 | 25.682 | 0 | 932 | 809.705 | 174.483 | 8.7321 | 809.705 | 163.288 | 0.045579 | 805.267 | 157.245 | 0.034345 | 933.67 | 933.664 | 2096770 | 26.9676 | 2102980 | 2085600 | 2029060 | 0 | 0 | 1999710 | 735.488 | 0 | 0 | 0 | 0 | 1999710 | 735.488 | 1957730 | 1918570.625
2823 | 2005-04-28 14:00 | 763 | 834 | 142 | 13.45 | 12.16 | 0 | 48.1573 | 251.575 | 40.1563 | 0 | 763 | 637.095 | 153.284 | 7.1487 | 637.095 | 143.449 | 0.037314 | 627.271 | 138.14 | 0.028117 | 742.476 | 742.472 | 1667400 | 24.1597 | 1652100 | 1657720 | 1612350 | 0 | 0 | 1593860 | 738.828 | 0 | 0 | 0 | 0 | 1593860 | 738.828 | 1564280 | 1532999.375
2824 | 2005-04-28 15:00 | 601 | 719 | 177 | 13.39 | 11.06 | 0 | 36.1262 | 262.633 | 54.6831 | 0 | 601 | 415.753 | 182.784 | 5.6309 | 415.753 | 171.056 | 0.029391 | 400.582 | 164.725 | 0.022147 | 548.369 | 548.358 | 1231470 | 21.8385 | 1198670 | 1214780 | 1180190 | 0 | 0 | 1170250 | 739.245 | 0 | 0 | 0 | 0 | 1170250 | 739.245 | 1149990 | 1126991.375
2825 | 2005-04-28 16:00 | 291 | 344 | 152 | 13.33 | 11.06 | 0 | 23.8043 | 271.549 | 69.1854 | 0 | 291 | 122.377 | 145.041 | 2.7264 | 122.377 | 135.735 | 0.014231 | 111.276 | 130.711 | 0.010723 | 234.738 | 234.735 | 527156 | 16.9465 | 485358 | 503343 | 488653 | 0 | 0 | 486865 | 725.747 | 0 | 0 | 0 | 0 | 486865 | 725.747 | 478208 | 468643.5938
2826 | 2005-04-28 17:00 | 107 | 87 | 89 | 12.85 | 11.06 | 0 | 11.5259 | 279.714 | 83.6145 | 0 | 107 | 10.0191 | 78.2706 | 1.0025 | 10.0191 | 73.2486 | 0.0052327 | 6.0158 | 70.5377 | 0.003943 | 74.2607 | 74.26 | 166769 | 13.9941 | 139367 | 147183 | 143293 | 0 | 0 | 143118 | 682.735 | 0 | 0 | 0 | 0 | 143118 | 682.735 | 138613 | 135840.5625
2827 | 2005-04-28 18:00 | 6 | 21 | 5 | 12.36 | 10.26 | 0 | -0.4551 | 287.978 | 90 | 0 | 6 | 0 | 4.532 | 0.056215 | 0 | 4.2412 | 0 | 0 | 4.0843 | 0 | 3.9618 | 3.9616 | 8896.72 | 12.4241 | 3449.51 | 3532.3 | 3482.79 | 0 | 0 | 3482.59 | 485.504 | 0 | 0 | 0 | 3482.59 | 0 | 660 | 0 | 0
2828 | 2005-04-28 19:00 | 0 | 0 | 0 | 11.88 | 10.26 | 0
2829 | 2005-04-28 20:00 | 0 | 0 | 0 | 11.28 | 10.26 | 0
2830 | 2005-04-28 21:00 | 0 | 0 | 0 | 10.67 | 7.65 | 0
2831 | 2005-04-28 22:00 | 0 | 0 | 0 | 10.06 | 7.65 | 0
2832 | 2005-04-28 23:00 | 0 | 0 | 0 | 9.44 | 7.65 | 0
2833 | 2005-04-29 | 0 | 0 | 0 | 8.82 | 10.11 | 0
2834 | 2005-04-29 01:00 | 0 | 0 | 0 | 8.2 | 10.11 | 0
2835 | 2005-04-29 02:00 | 0 | 0 | 0 | 8.05 | 10.11 | 0
2836 | 2005-04-29 03:00 | 0 | 0 | 0 | 7.9 | 5.69 | 0
2837 | 2005-04-29 04:00 | 0 | 0 | 0 | 7.75 | 5.69 | 0
2838 | 2005-04-29 05:00 | 54 | 253 | 30 | 8.19 | 5.69 | 0 | 4.8691 | 75.6087 | 90 | 0 | 54 | 0 | 24.3029 | 0.50594 | 0 | 22.7436 | 0.0026408 | 0 | 21.9019 | 0.0019899 | 21.2467 | 21.2456 | 47712.2 | 8.648 | 33733.1 | 36677.2 | 35770 | 0 | 0 | 35757.5 | 638.258 | 0 | 0 | 0 | 448 | 35309.5 | 660 | 34042.6 | 33361.7148
2839 | 2005-04-29 06:00 | 266 | 669 | 69 | 8.64 | 6.05 | 0 | 17.0215 | 83.7081 | 77.2312 | 0 | 266 | 148.739 | 66.7178 | 2.4922 | 136.069 | 62.437 | 0.013008 | 112.09 | 60.1263 | 0.0098022 | 167.059 | 167.031 | 375111 | 12.1586 | 337313 | 357529 | 334213 | 0 | 0 | 333345 | 719.515 | 0 | 0 | 0 | 0 | 333345 | 719.515 | 325921 | 319402.7188
2840 | 2005-04-29 07:00 | 489 | 821 | 86 | 9.09 | 6.05 | 0 | 29.3644 | 92.04 | 62.7722 | 0 | 489 | 376.017 | 90.4738 | 4.5816 | 376.017 | 84.6688 | 0.023914 | 353.726 | 81.5353 | 0.01802 | 422.221 | 422.216 | 948187 | 17.9842 | 908015 | 935736 | 908882 | 0 | 0 | 903013 | 742.826 | 0 | 0 | 0 | 0 | 903013 | 742.826 | 887546 | 869795.0625
2841 | 2005-04-29 08:00 | 686 | 880 | 101 | 10.82 | 6.05 | 0 | 41.6294 | 101.618 | 48.2649 | 0 | 686 | 586.213 | 107.473 | 6.4273 | 586.213 | 100.578 | 0.033548 | 571.493 | 96.8553 | 0.025279 | 648.322 | 648.318 | 1455960 | 24.4772 | 1431430 | 1434380 | 1396280 | 0 | 0 | 1382190 | 734.139 | 0 | 0 | 0 | 0 | 1382190 | 734.139 | 1357890 | 1330729.625
2842 | 2005-04-29 09:00 | 862 | 937 | 110 | 12.56 | 1.44 | 0 | 53.3916 | 114.318 | 33.7669 | 0 | 862 | 778.77 | 117.446 | 8.0763 | 778.77 | 109.91 | 0.042155 | 770.869 | 105.843 | 0.031765 | 850.441 | 850.437 | 1909870 | 36.8208 | 1906370 | 1811340 | 1764980 | 0 | 0 | 1740460 | 700.444 | 0 | 0 | 0 | 0 | 1740460 | 700.444 | 1707520 | 1673366.875
2843 | 2005-04-29 10:00 | 975 | 955 | 120 | 14.29 | 1.44 | 0 | 63.6627 | 134.267 | 19.4204 | 0 | 975 | 899.75 | 127.517 | 9.135 | 899.75 | 119.336 | 0.047682 | 897.036 | 114.919 | 0.035929 | 981.632 | 981.622 | 2204480 | 42.2932 | 2216470 | 2055880 | 2005630 | 0 | 0 | 1972810 | 685.994 | 0 | 0 | 0 | 0 | 1972810 | 685.994 | 1931850 | 1893212.375
2844 | 2005-04-29 11:00 | 1029 | 968 | 123 | 15.72 | 1.44 | 0 | 69.7773 | 168.259 | 6.5516 | 0 | 1029 | 959.213 | 130.234 | 9.6409 | 959.213 | 121.878 | 0.050322 | 958.898 | 117.368 | 0.037919 | 1044.01 | 1044.01 | 2344570 | 45.5029 | 2364230 | 2161510 | 2109460 | 0 | 0 | 2072310 | 677.261 | 27433.4 | 0 | 0 | 0 | 2043630 | 697.357 | 1999990 | 1959985.625
2845 | 2005-04-29 12:00 | 1014 | 965 | 122 | 17.16 | 2.56 | 0 | 67.8721 | 208.856 | 11.7689 | 0 | 1014 | 942.681 | 129.336 | 9.5004 | 942.681 | 121.037 | 0.049589 | 941.669 | 116.558 | 0.037366 | 1026.52 | 1026.51 | 2305280 | 44.3325 | 2322780 | 2134980 | 2084480 | 0 | 0 | 2048470 | 680.312 | 6115.73 | 0 | 0 | 0 | 2042070 | 688.028 | 1998450 | 1958479
2846 | 2005-04-29 13:00 | 934 | 951 | 116 | 18.59 | 2.56 | 0 | 59.429 | 235.967 | 25.7593 | 0 | 934 | 855.649 | 123.546 | 8.7508 | 855.649 | 115.619 | 0.045677 | 850.929 | 111.34 | 0.034418 | 933.434 | 933.427 | 2096240 | 43.2985 | 2102430 | 1940610 | 1893510 | 0 | 0 | 1863800 | 680.987 | 0 | 0 | 0 | 0 | 1863800 | 680.987 | 1826930 | 1790391.125
2847 | 2005-04-29 14:00 | 794 | 922 | 106 | 18.84 | 2.56 | 0 | 48.3128 | 251.979 | 40.2023 | 0 | 794 | 703.646 | 113.116 | 7.4392 | 703.646 | 105.858 | 0.03883 | 692.765 | 101.94 | 0.029259 | 770.892 | 770.888 | 1731220 | 39.246 | 1718920 | 1614790 | 1574300 | 0 | 0 | 1554110 | 689.23 | 0 | 0 | 0 | 0 | 1554110 | 689.23 | 1527390 | 1496839.5
2848 | 2005-04-29 15:00 | 608 | 824 | 120 | 19.08 | 3.97 | 0 | 36.2641 | 262.978 | 54.708 | 0 | 608 | 476.644 | 126.775 | 5.6965 | 476.644 | 118.64 | 0.029734 | 459.226 | 114.25 | 0.022405 | 556.293 | 556.288 | 1249280 | 32.4951 | 1217060 | 1177440 | 1147240 | 0 | 0 | 1136830 | 702.22 | 0 | 0 | 0 | 0 | 1136830 | 702.22 | 1119040 | 1096661.125
2849 | 2005-04-29 16:00 | 370 | 700 | 86 | 19.32 | 3.97 | 0 | 23.9388 | 271.856 | 69.192 | 0 | 370 | 248.637 | 87.0077 | 3.4666 | 248.637 | 81.4251 | 0.018094 | 226.073 | 78.4116 | 0.013635 | 295.363 | 295.356 | 663295 | 26.4426 | 620499 | 616368 | 600097 | 0 | 0 | 597205 | 699.62 | 0 | 0 | 0 | 0 | 597205 | 699.62 | 588240 | 576475.625
2850 | 2005-04-29 17:00 | 169 | 540 | 59 | 19.08 | 3.97 | 0 | 11.6667 | 279.997 | 83.6026 | 0 | 169 | 60.6108 | 53.7012 | 1.5834 | 60.6108 | 50.2556 | 0.0082648 | 36.443 | 48.3957 | 0.0062277 | 82.2996 | 82.2988 | 184822 | 21.0647 | 156027 | 159148 | 155104 | 0 | 0 | 154888 | 663.426 | 0 | 0 | 0 | 0 | 154888 | 663.426 | 150394 | 147385.9531
2851 | 2005-04-29 18:00 | 11 | 135 | 4 | 18.84 | 5.66 | 0 | -0.30003 | 288.247 | 90 | 0 | 11 | 0 | 3.2067 | 0.10306 | 0 | 3.0009 | 0 | 0 | 2.8899 | 0 | 2.8032 | 2.803 | 6294.75 | 18.9005 | 1863.36 | 1864.75 | 1848.44 | 0 | 0 | 1848.36 | 397.954 | 0 | 0 | 0 | 1848.36 | 0 | 660 | 0 | 0
2852 | 2005-04-29 19:00 | 0 | 0 | 0 | 18.6 | 5.66 | 0
2853 | 2005-04-29 20:00 | 0 | 0 | 0 | 17.74 | 5.66 | 0
2854 | 2005-04-29 21:00 | 0 | 0 | 0 | 16.89 | 5.11 | 0
2855 | 2005-04-29 22:00 | 0 | 0 | 0 | 16.04 | 5.11 | 0
2856 | 2005-04-29 23:00 | 0 | 0 | 0 | 15.26 | 5.11 | 0
2857 | 2005-04-30 | 0 | 0 | 0 | 14.47 | 5.3 | 0
2858 | 2005-04-30 01:00 | 0 | 0 | 0 | 13.68 | 5.3 | 0
2859 | 2005-04-30 02:00 | 0 | 0 | 0 | 13.07 | 5.3 | 0
2860 | 2005-04-30 03:00 | 0 | 0 | 0 | 12.45 | 6.24 | 0
2861 | 2005-04-30 04:00 | 0 | 0 | 0 | 11.83 | 6.24 | 0
2862 | 2005-04-30 05:00 | 55 | 248 | 31 | 11.87 | 6.24 | 0 | 5.0688 | 75.3727 | 90 | 0 | 55 | 0 | 25.0682 | 0.51531 | 0 | 23.4598 | 0.0026897 | 0 | 22.5915 | 0.0020268 | 21.9157 | 21.9149 | 49215.3 | 12.326 | 34989.7 | 37372.5 | 36492.2 | 0 | 0 | 36478.8 | 627.134 | 0 | 0 | 0 | 1208.1 | 35270.7 | 660 | 34005.1 | 33324.9609
2863 | 2005-04-30 06:00 | 261 | 629 | 74 | 11.92 | 3.09 | 0 | 17.2116 | 83.4541 | 77.1643 | 0 | 261 | 140.396 | 71.3257 | 2.4454 | 129.007 | 66.7493 | 0.012764 | 106.422 | 64.279 | 0.0096179 | 165.589 | 165.589 | 371873 | 16.1518 | 334107 | 347881 | 326870 | 0 | 0 | 326015 | 708.3 | 0 | 0 | 0 | 0 | 326015 | 708.3 | 318865 | 312487.4062
2864 | 2005-04-30 07:00 | 492 | 822 | 86 | 11.96 | 3.09 | 0 | 29.552 | 91.7592 | 62.7233 | 0 | 492 | 377.251 | 90.3247 | 4.6097 | 377.251 | 84.5293 | 0.024061 | 354.955 | 81.4009 | 0.01813 | 423.283 | 423.279 | 950580 | 22.7773 | 910453 | 919212 | 894215 | 0 | 0 | 888295 | 727.526 | 0 | 0 | 0 | 0 | 888295 | 727.526 | 873748 | 856273.25
2865 | 2005-04-30 08:00 | 697 | 897 | 99 | 13.66 | 3.09 | 0 | 41.8242 | 101.299 | 48.2353 | 0 | 697 | 597.305 | 105.329 | 6.5304 | 597.305 | 98.5707 | 0.034086 | 582.332 | 94.9227 | 0.025685 | 656.962 | 656.953 | 1475350 | 30.4492 | 1451610 | 1417690 | 1380050 | 0 | 0 | 1365570 | 715.556 | 0 | 0 | 0 | 0 | 1365570 | 715.556 | 1342420 | 1315569.25
2866 | 2005-04-30 09:00 | 864 | 937 | 110 | 15.36 | 2.18 | 0 | 53.6085 | 113.951 | 33.7622 | 0 | 864 | 778.699 | 117.274 | 8.095 | 778.699 | 109.749 | 0.042253 | 770.801 | 105.688 | 0.031839 | 850.225 | 850.222 | 1909380 | 38.4429 | 1905850 | 1797720 | 1750420 | 0 | 0 | 1725990 | 695.756 | 0 | 0 | 0 | 0 | 1725990 | 695.756 | 1693630 | 1659753.875
2867 | 2005-04-30 10:00 | 945 | 864 | 170 | 17.06 | 2.18 | 0 | 63.9238 | 133.899 | 19.4617 | 0 | 945 | 813.529 | 184.936 | 8.8539 | 813.529 | 173.07 | 0.046214 | 811.064 | 166.665 | 0.034824 | 948.431 | 948.424 | 2129910 | 42.809 | 2137890 | 1977950 | 1928760 | 0 | 0 | 1898140 | 683.377 | 0 | 0 | 0 | 0 | 1898140 | 683.377 | 1859990 | 1822790
2868 | 2005-04-30 11:00 | 1031 | 919 | 169 | 17.92 | 2.18 | 0 | 70.0839 | 168.193 | 6.7734 | 0 | 1031 | 910.434 | 185.013 | 9.6597 | 910.434 | 173.142 | 0.05042 | 910.114 | 166.734 | 0.037993 | 1044.58 | 1044.57 | 2345840 | 46.2794 | 2365570 | 2154970 | 2103080 | 0 | 0 | 2065760 | 673.889 | 21131.2 | 0 | 0 | 0 | 2043650 | 692.23 | 1999980 | 1959983.875
2869 | 2005-04-30 12:00 | 979 | 840 | 201 | 18.79 | 7.6 | 0 | 68.1376 | 209.269 | 11.9277 | 0 | 979 | 820.19 | 216.385 | 9.1725 | 820.19 | 202.501 | 0.047877 | 819.285 | 195.007 | 0.036076 | 983.898 | 983.881 | 2209550 | 37.5653 | 2221820 | 2105410 | 2052640 | 0 | 0 | 2019610 | 700.171 | 0 | 0 | 0 | 0 | 2019610 | 700.171 | 1976880 | 1937339.75
2870 | 2005-04-30 13:00 | 842 | 679 | 257 | 19.65 | 7.6 | 0 | 59.6228 | 236.437 | 25.837 | 0 | 842 | 610.308 | 274.518 | 7.8889 | 610.308 | 256.905 | 0.041177 | 606.919 | 247.397 | 0.031028 | 828.716 | 828.721 | 1861090 | 35.4644 | 1855140 | 1773290 | 1725500 | 0 | 0 | 1702330 | 704.772 | 0 | 0 | 0 | 0 | 1702330 | 704.772 | 1670510 | 1637099.25
2871 | 2005-04-30 14:00 | 794 | 736 | 243 | 19.76 | 7.6 | 0 | 48.4664 | 252.38 | 40.2478 | 0 | 794 | 561.814 | 253.652 | 7.4392 | 561.814 | 237.377 | 0.03883 | 553.101 | 228.592 | 0.029259 | 758.27 | 758.254 | 1702840 | 34.2297 | 1689200 | 1623100 | 1584530 | 0 | 0 | 1564990 | 705.144 | 0 | 0 | 0 | 0 | 1564990 | 705.144 | 1537390 | 1506645.125
2872 | 2005-04-30 15:00 | 437 | 291 | 264 | 19.87 | 4.66 | 0 | 36.4008 | 263.319 | 54.7319 | 0 | 437 | 168.328 | 258.593 | 4.0944 | 168.328 | 242.002 | 0.021371 | 162.168 | 233.045 | 0.016104 | 383.372 | 383.353 | 860917 | 28.7065 | 819371 | 805752 | 784784 | 0 | 0 | 779879 | 701.78 | 0 | 0 | 0 | 0 | 779879 | 701.78 | 768112 | 752749.5625
2873 | 2005-04-30 16:00 | 264 | 212 | 177 | 19.98 | 4.66 | 0 | 24.0725 | 272.158 | 69.1974 | 0 | 264 | 75.7503 | 165.665 | 2.4735 | 75.7503 | 155.035 | 0.012911 | 68.8733 | 149.297 | 0.0097285 | 211.635 | 211.626 | 475258 | 24.8581 | 434320 | 434572 | 422806 | 0 | 0 | 421336 | 692.01 | 0 | 0 | 0 | 0 | 421336 | 692.01 | 414507 | 406216.625
2874 | 2005-04-30 17:00 | 161 | 278 | 104 | 19.62 | 4.66 | 0 | 11.8069 | 280.275 | 83.5893 | 0 | 161 | 31.1039 | 90.6782 | 1.5084 | 31.1039 | 84.8601 | 0.0078736 | 18.7305 | 81.7195 | 0.0059329 | 97.4422 | 97.4372 | 218819 | 21.866 | 187700 | 190646 | 185664 | 0 | 0 | 185358 | 668.602 | 0 | 0 | 0 | 0 | 185358 | 668.602 | 180235 | 176630.5469
2875 | 2005-04-30 18:00 | 11 | 71 | 7 | 19.26 | 7.08 | 0 | -0.14554 | 288.512 | 90 | 0 | 11 | 0 | 5.5724 | 0.10306 | 0 | 5.2148 | 0 | 0 | 5.0218 | 0 | 4.8712 | 4.8709 | 10938.9 | 19.3561 | 4816.86 | 4904.67 | 4824.9 | 0 | 0 | 4824.53 | 493.685 | 0 | 0 | 0 | 4824.53 | 0 | 660 | 0 | 0
2876 | 2005-04-30 19:00 | 0 | 0 | 0 | 18.91 | 7.08 | 0
2877 | 2005-04-30 20:00 | 0 | 0 | 0 | 18.17 | 7.08 | 0
2878 | 2005-04-30 21:00 | 0 | 0 | 0 | 18.01 | 7.43 | 0
2879 | 2005-04-30 22:00 | 0 | 0 | 0 | 17.36 | 7.29 | 0
2880 | 2005-04-30 23:00 | 0 | 0 | 0 | 16.7 | 7.14 | 0
2881 | 2005-05-01 | 0 | 0 | 0 | 16.04 | 6.99 | 0
2882 | 2005-05-01 01:00 | 0 | 0 | 0 | 15.38 | 6.84 | 0
2883 | 2005-05-01 02:00 | 0 | 0 | 0 | 14.73 | 6.7 | 0
2884 | 2005-05-01 03:00 | 0 | 0 | 0 | 13.57 | 6.05 | 0
2885 | 2005-05-01 04:00 | 0 | 0 | 0 | 13.08 | 6.05 | 0
2886 | 2005-05-01 05:00 | 53 | 204 | 33 | 13.16 | 6.05 | 0 | 5.2643 | 75.1386 | 90 | 0 | 53 | 0 | 25.4358 | 0.49657 | 0 | 23.8038 | 0.0025919 | 0 | 22.9228 | 0.0019531 | 22.237 | 22.2364 | 49937.4 | 13.6284 | 35594.6 | 37774.3 | 36860 | 0 | 0 | 36846.1 | 622.637 | 0 | 0 | 0 | 1574.55 | 35271.6 | 660 | 34005.9 | 33325.8008
2887 | 2005-05-01 06:00 | 252 | 557 | 85 | 13.24 | 6.89 | 0 | 17.3972 | 83.2019 | 77.1004 | 0 | 252 | 124.69 | 81.5658 | 2.361 | 115.072 | 76.3324 | 0.012324 | 95.053 | 73.5074 | 0.0092863 | 163.513 | 163.519 | 367223 | 16.5042 | 329481 | 342641 | 322941 | 0 | 0 | 322107 | 707.014 | 0 | 0 | 0 | 0 | 322107 | 707.014 | 314970 | 308670.5625
2888 | 2005-05-01 07:00 | 481 | 759 | 104 | 13.32 | 6.89 | 0 | 29.7349 | 91.4801 | 62.6776 | 0 | 481 | 348.883 | 107.297 | 4.5066 | 348.883 | 100.412 | 0.023523 | 328.322 | 96.6963 | 0.017725 | 412.285 | 412.278 | 925868 | 21.5501 | 885296 | 898624 | 874584 | 0 | 0 | 868943 | 729.8 | 0 | 0 | 0 | 0 | 868943 | 729.8 | 854615 | 837522.25
2889 | 2005-05-01 08:00 | 680 | 858 | 106 | 14.92 | 6.89 | 0 | 42.0141 | 100.98 | 48.2094 | 0 | 680 | 571.511 | 114.417 | 6.3711 | 571.511 | 107.076 | 0.033255 | 557.207 | 103.113 | 0.025058 | 640.535 | 640.531 | 1438470 | 27.7066 | 1413240 | 1396770 | 1358450 | 0 | 0 | 1344780 | 724.684 | 0 | 0 | 0 | 0 | 1344780 | 724.684 | 1321670 | 1295232.5
2890 | 2005-05-01 09:00 | 843 | 896 | 120 | 16.53 | 5.77 | 0 | 53.8199 | 113.583 | 33.7619 | 0 | 843 | 744.666 | 127.08 | 7.8982 | 744.666 | 118.926 | 0.041226 | 737.113 | 114.525 | 0.031065 | 826.119 | 826.118 | 1855250 | 34.2493 | 1849000 | 1776910 | 1730730 | 0 | 0 | 1707680 | 708.332 | 0 | 0 | 0 | 0 | 1707680 | 708.332 | 1675600 | 1642088
2891 | 2005-05-01 10:00 | 944 | 894 | 140 | 18.13 | 5.77 | 0 | 64.1794 | 133.525 | 19.5087 | 0 | 944 | 841.896 | 146.893 | 8.8445 | 841.896 | 137.468 | 0.046165 | 839.333 | 132.38 | 0.034787 | 942.595 | 942.589 | 2116810 | 38.3475 | 2124090 | 2005430 | 1955160 | 0 | 0 | 1924820 | 696.822 | 0 | 0 | 0 | 0 | 1924820 | 696.822 | 1885580 | 1847864
2892 | 2005-05-01 11:00 | 972 | 819 | 202 | 19.1 | 5.77 | 0 | 70.3861 | 168.121 | 6.9997 | 0 | 972 | 811.338 | 217.428 | 9.1069 | 811.338 | 203.477 | 0.047535 | 811.034 | 195.947 | 0.035819 | 976.806 | 976.799 | 2193640 | 40.0513 | 2205050 | 2066300 | 2016060 | 0 | 0 | 1983450 | 692.18 | 0 | 0 | 0 | 0 | 1983450 | 692.18 | 1942080 | 1903234.875
2893 | 2005-05-01 12:00 | 936 | 764 | 227 | 20.07 | 8.04 | 0 | 68.3992 | 209.682 | 12.0881 | 0 | 936 | 745.645 | 248.526 | 8.7696 | 745.645 | 232.58 | 0.045774 | 744.799 | 223.972 | 0.034492 | 939.742 | 939.731 | 2110400 | 37.5122 | 2117340 | 2006530 | 1955200 | 0 | 0 | 1925330 | 701.598 | 0 | 0 | 0 | 0 | 1925330 | 701.598 | 1886040 | 1848318.75
2894 | 2005-05-01 13:00 | 910 | 867 | 161 | 21.04 | 8.04 | 0 | 59.8137 | 236.903 | 25.915 | 0 | 910 | 779.37 | 174.647 | 8.526 | 779.37 | 163.441 | 0.044503 | 775.013 | 157.392 | 0.033534 | 904.466 | 904.455 | 2031180 | 37.8274 | 2033940 | 1924500 | 1874750 | 0 | 0 | 1847000 | 698.647 | 0 | 0 | 0 | 0 | 1847000 | 698.647 | 1810500 | 1774285.875
2895 | 2005-05-01 14:00 | 774 | 844 | 141 | 21.22 | 8.04 | 0 | 48.6179 | 252.775 | 40.2927 | 0 | 774 | 643.489 | 151.559 | 7.2518 | 643.489 | 141.835 | 0.037852 | 633.481 | 136.586 | 0.028522 | 746.993 | 746.984 | 1677540 | 35.0846 | 1662710 | 1591530 | 1550970 | 0 | 0 | 1532050 | 702.361 | 0 | 0 | 0 | 0 | 1532050 | 702.361 | 1505520 | 1475411.375
2896 | 2005-05-01 15:00 | 572 | 750 | 125 | 21.41 | 7.46 | 0 | 36.5362 | 263.656 | 54.7549 | 0 | 572 | 433.294 | 131.472 | 5.3592 | 433.294 | 123.037 | 0.027973 | 417.417 | 118.483 | 0.021078 | 519.843 | 519.839 | 1167430 | 31.4183 | 1132620 | 1100920 | 1071720 | 0 | 0 | 1062690 | 704.82 | 0 | 0 | 0 | 0 | 1062690 | 704.82 | 1046250 | 1025322.9375
2897 | 2005-05-01 16:00 | 374 | 588 | 133 | 21.59 | 7.46 | 0 | 24.2054 | 272.455 | 69.2015 | 0 | 374 | 208.715 | 129.099 | 3.5041 | 208.715 | 120.816 | 0.01829 | 189.761 | 116.344 | 0.013782 | 296.936 | 296.932 | 666835 | 27.3067 | 624038 | 617442 | 601014 | 0 | 0 | 598092 | 697.234 | 0 | 0 | 0 | 0 | 598092 | 697.234 | 589190 | 577406.1875
2898 | 2005-05-01 17:00 | 136 | 297 | 74 | 21.01 | 7.46 | 0 | 11.9465 | 280.549 | 83.5745 | 0 | 136 | 33.5194 | 65.4033 | 1.2742 | 33.5194 | 61.2069 | 0.006651 | 20.2194 | 58.9417 | 0.0050116 | 76.7911 | 76.7872 | 172445 | 22.4884 | 144591 | 146449 | 142863 | 0 | 0 | 142674 | 653.937 | 0 | 0 | 0 | 104.371 | 142569 | 660 | 138371 | 135604.0469
2899 | 2005-05-01 18:00 | 9 | 78 | 5 | 20.43 | 9.69 | 0 | 0.0083336 | 288.771 | 90 | 0 | 9 | 0 | 3.8456 | 0.084323 | 0 | 3.5988 | 0.00044014 | 0 | 3.4656 | 0.00033165 | 3.362 | 3.3619 | 7549.84 | 20.4863 | 2598.49 | 2613.15 | 2582.76 | 0 | 0 | 2582.62 | 435.93 | 0 | 0 | 0 | 2582.62 | 0 | 660 | 0 | 0
2900 | 2005-05-01 19:00 | 0 | 0 | 0 | 19.84 | 9.69 | 0
2901 | 2005-05-01 20:00 | 0 | 0 | 0 | 18.92 | 9.69 | 0
2902 | 2005-05-01 21:00 | 0 | 0 | 0 | 18 | 8.63 | 0
2903 | 2005-05-01 22:00 | 0 | 0 | 0 | 17.08 | 8.63 | 0
2904 | 2005-05-01 23:00 | 0 | 0 | 0 | 16.39 | 8.63 | 0
2905 | 2005-05-02 | 0 | 0 | 0 | 15.7 | 8.64 | 0
2906 | 2005-05-02 01:00 | 0 | 0 | 0 | 15.01 | 8.64 | 0
2907 | 2005-05-02 02:00 | 0 | 0 | 0 | 14.59 | 8.64 | 0
2908 | 2005-05-02 03:00 | 0 | 0 | 0 | 14.17 | 7.77 | 0
2909 | 2005-05-02 04:00 | 0 | 0 | 0 | 13.75 | 7.77 | 0
2910 | 2005-05-02 05:00 | 56 | 171 | 39 | 13.97 | 7.77 | 0 | 5.4554 | 74.9066 | 90 | 0 | 56 | 0 | 30.2644 | 0.52468 | 0 | 28.3226 | 0.0027386 | 0 | 27.2744 | 0.0020636 | 26.4581 | 26.4572 | 59416.1 | 14.4695 | 43601.8 | 46075.8 | 44946.3 | 0 | 0 | 44926 | 628.635 | 0 | 0 | 0 | 1268.42 | 43657.6 | 660 | 42113 | 41270.7617
2911 | 2005-05-02 06:00 | 268 | 597 | 87 | 14.18 | 5.36 | 0 | 17.5784 | 82.9517 | 77.0396 | 0 | 268 | 134.414 | 83.309 | 2.5109 | 124.614 | 77.9638 | 0.013106 | 103.064 | 75.0784 | 0.0098759 | 172.807 | 172.802 | 388074 | 17.986 | 349684 | 361113 | 340165 | 0 | 0 | 339237 | 705.41 | 0 | 0 | 0 | 0 | 339237 | 705.41 | 332129 | 325486.6562
2912 | 2005-05-02 07:00 | 488 | 805 | 86 | 14.39 | 5.36 | 0 | 29.9132 | 91.2027 | 62.6353 | 0 | 488 | 370.534 | 90.0305 | 4.5722 | 370.534 | 84.254 | 0.023865 | 348.755 | 81.1358 | 0.017983 | 417.011 | 417.009 | 936500 | 23.5746 | 896117 | 901633 | 876118 | 0 | 0 | 870395 | 725.256 | 0 | 0 | 0 | 0 | 870395 | 725.256 | 856240 | 839115.25
2913 | 2005-05-02 08:00 | 694 | 885 | 100 | 16.01 | 5.36 | 0 | 42.1988 | 100.663 | 48.187 | 0 | 694 | 589.575 | 106.033 | 6.5022 | 589.575 | 99.2299 | 0.033939 | 574.838 | 95.5575 | 0.025574 | 650.308 | 650.308 | 1460430 | 30.333 | 1436080 | 1403250 | 1368320 | 0 | 0 | 1354030 | 713.915 | 0 | 0 | 0 | 0 | 1354030 | 713.915 | 1331200 | 1304574
2914 | 2005-05-02 09:00 | 853 | 915 | 113 | 17.63 | 4.74 | 0 | 54.0259 | 113.215 | 33.7658 | 0 | 853 | 760.148 | 119.938 | 7.992 | 760.148 | 112.242 | 0.041715 | 752.436 | 108.088 | 0.031433 | 834.739 | 834.734 | 1874600 | 36.7709 | 1869320 | 1776480 | 1730910 | 0 | 0 | 1707340 | 700.447 | 0 | 0 | 0 | 0 | 1707340 | 700.447 | 1675470 | 1641962.75
2915 | 2005-05-02 10:00 | 974 | 951 | 117 | 19.25 | 4.74 | 0 | 64.4293 | 133.147 | 19.5611 | 0 | 974 | 895.222 | 123.931 | 9.1256 | 895.222 | 115.979 | 0.047633 | 892.481 | 111.687 | 0.035892 | 974.078 | 974.072 | 2187520 | 41.586 | 2198590 | 2045930 | 1996260 | 0 | 0 | 1963790 | 686.824 | 0 | 0 | 0 | 0 | 1963790 | 686.824 | 1923170 | 1884702.875
2916 | 2005-05-02 11:00 | 1001 | 919 | 136 | 20.31 | 4.74 | 0 | 70.6836 | 168.043 | 7.2293 | 0 | 1001 | 909.312 | 142.432 | 9.3786 | 909.312 | 133.294 | 0.048953 | 908.948 | 128.361 | 0.036887 | 1006.22 | 1006.22 | 2259720 | 43.3833 | 2274720 | 2099820 | 2047640 | 0 | 0 | 2012970 | 681.447 | 0 | 0 | 0 | 0 | 2012970 | 681.447 | 1970460 | 1931054.625
2917 | 2005-05-02 12:00 | 987 | 920 | 132 | 21.37 | 5.2 | 0 | 68.6569 | 210.093 | 12.25 | 0 | 987 | 897.055 | 138.62 | 9.2474 | 897.055 | 129.726 | 0.048268 | 896.01 | 124.925 | 0.036371 | 990.342 | 990.334 | 2224030 | 43.4096 | 2237090 | 2064650 | 2012600 | 0 | 0 | 1979210 | 682.531 | 0 | 0 | 0 | 0 | 1979210 | 682.531 | 1938010 | 1899253.5
2918 | 2005-05-02 13:00 | 922 | 931 | 116 | 22.43 | 5.2 | 0 | 60.0016 | 237.365 | 25.9931 | 0 | 922 | 836.533 | 122.994 | 8.6384 | 836.533 | 115.103 | 0.04509 | 831.826 | 110.843 | 0.033976 | 914.422 | 914.417 | 2053550 | 42.7801 | 2057480 | 1903530 | 1858200 | 0 | 0 | 1829580 | 681.48 | 0 | 0 | 0 | 0 | 1829580 | 681.48 | 1793940 | 1758060.625
2919 | 2005-05-02 14:00 | 791 | 913 | 105 | 22.47 | 5.2 | 0 | 48.7675 | 253.166 | 40.3369 | 0 | 791 | 695.313 | 111.627 | 7.4111 | 695.313 | 104.465 | 0.038683 | 684.47 | 100.599 | 0.029149 | 761.545 | 761.541 | 1710230 | 39.4179 | 1696930 | 1592860 | 1553080 | 0 | 0 | 1533430 | 689.173 | 0 | 0 | 0 | 0 | 1533430 | 689.173 | 1507340 | 1477194
2920 | 2005-05-02 15:00 | 608 | 818 | 119 | 22.52 | 6.63 | 0 | 36.6703 | 263.987 | 54.7767 | 0 | 608 | 472.26 | 125.19 | 5.6965 | 472.26 | 117.157 | 0.029734 | 454.932 | 112.821 | 0.022405 | 550.742 | 550.733 | 1236810 | 33.698 | 1204170 | 1158660 | 1129580 | 0 | 0 | 1119340 | 696.927 | 0 | 0 | 0 | 0 | 1119340 | 696.927 | 1102170 | 1080126
2921 | 2005-05-02 16:00 | 371 | 690 | 86 | 22.56 | 6.63 | 0 | 24.3374 | 272.748 | 69.2042 | 0 | 371 | 245.531 | 86.4577 | 3.476 | 245.531 | 80.9104 | 0.018143 | 223.23 | 77.9159 | 0.013671 | 292.125 | 292.12 | 656026 | 28.489 | 613241 | 603430 | 588283 | 0 | 0 | 585436 | 691.565 | 0 | 0 | 0 | 0 | 585436 | 691.565 | 576825 | 565288.5625
2922 | 2005-05-02 17:00 | 157 | 442 | 64 | 22.04 | 6.63 | 0 | 12.0855 | 280.818 | 83.5583 | 0 | 157 | 49.8345 | 57.9791 | 1.471 | 49.8345 | 54.2591 | 0.007678 | 30.1167 | 52.251 | 0.0057855 | 79.9023 | 79.8991 | 179434 | 23.6617 | 151041 | 152070 | 148393 | 0 | 0 | 148187 | 651.814 | 0 | 0 | 0 | 258.38 | 147929 | 660 | 143621 | 140748.3438
2923 | 2005-05-02 18:00 | 11 | 119 | 4 | 21.53 | 8.88 | 0 | 0.16154 | 289.026 | 90 | 0 | 11 | 0 | 3.162 | 0.10306 | 0 | 2.9591 | 0.00053795 | 0 | 2.8496 | 0.00040535 | 2.7645 | 2.7644 | 6208.05 | 21.5787 | 1815.38 | 1816.29 | 1800.55 | 0 | 0 | 1800.46 | 390.577 | 0 | 0 | 0 | 1800.46 | 0 | 660 | 0 | 0
2924 | 2005-05-02 19:00 | 0 | 0 | 0 | 21.01 | 8.88 | 0
2925 | 2005-05-02 20:00 | 0 | 0 | 0 | 19.86 | 8.88 | 0
2926 | 2005-05-02 21:00 | 0 | 0 | 0 | 18.7 | 8.51 | 0
2927 | 2005-05-02 22:00 | 0 | 0 | 0 | 17.54 | 8.51 | 0
2928 | 2005-05-02 23:00 | 0 | 0 | 0 | 16.94 | 8.51 | 0
2929 | 2005-05-03 | 0 | 0 | 0 | 16.35 | 9.35 | 0
2930 | 2005-05-03 01:00 | 0 | 0 | 0 | 15.75 | 9.35 | 0
2931 | 2005-05-03 02:00 | 0 | 0 | 0 | 14.98 | 9.35 | 0
2932 | 2005-05-03 03:00 | 0 | 0 | 0 | 14.21 | 5.25 | 0
2933 | 2005-05-03 04:00 | 0 | 1 | 0 | 13.45 | 5.25 | 0
2934 | 2005-05-03 05:00 | 61 | 263 | 34 | 13.99 | 5.25 | 0 | 5.6422 | 74.6767 | 90 | 0 | 61 | 0 | 27.3756 | 0.57152 | 0 | 25.6191 | 0.0029831 | 0 | 24.6709 | 0.0022479 | 23.933 | 23.9314 | 53743.9 | 14.5209 | 38795.6 | 40988 | 39968.8 | 0 | 0 | 39952.5 | 623.512 | 0 | 0 | 0 | 1625.76 | 38326.7 | 660 | 36958.4 | 36219.2695
2935 | 2005-05-03 06:00 | 266 | 624 | 75 | 14.53 | 2.63 | 0 | 17.7551 | 82.7035 | 76.9818 | 0 | 266 | 141.088 | 71.8802 | 2.4922 | 131.276 | 67.2682 | 0.013008 | 108.701 | 64.7787 | 0.0098022 | 168.285 | 168.241 | 377836 | 18.9628 | 339806 | 349322 | 328436 | 0 | 0 | 327559 | 702.821 | 0 | 0 | 0 | 0 | 327559 | 702.821 | 320529 | 314118.625
2936 | 2005-05-03 07:00 | 492 | 771 | 105 | 15.07 | 2.63 | 0 | 30.0867 | 90.9272 | 62.5962 | 0 | 492 | 355.309 | 107.915 | 4.6097 | 355.309 | 100.991 | 0.024061 | 334.476 | 97.2538 | 0.01813 | 418.795 | 418.792 | 940504 | 26.1043 | 900192 | 895699 | 871382 | 0 | 0 | 865558 | 714.625 | 0 | 0 | 0 | 0 | 865558 | 714.625 | 851941 | 834902.625
2937 | 2005-05-03 08:00 | 681 | 853 | 106 | 17.06 | 2.63 | 0 | 42.3785 | 100.347 | 48.1682 | 0 | 681 | 568.961 | 114.055 | 6.3804 | 568.961 | 106.737 | 0.033304 | 554.755 | 102.787 | 0.025095 | 637.84 | 637.836 | 1432420 | 33.8656 | 1406950 | 1353310 | 1317510 | 0 | 0 | 1303840 | 702.554 | 0 | 0 | 0 | 0 | 1303840 | 702.554 | 1282580 | 1256931.375
2938 | 2005-05-03 09:00 | 834 | 871 | 128 | 19.05 | 3.01 | 0 | 54.2263 | 112.846 | 33.7737 | 0 | 834 | 723.323 | 134.603 | 7.8139 | 723.323 | 125.967 | 0.040786 | 715.98 | 121.305 | 0.030733 | 812.196 | 812.188 | 1823970 | 39.9166 | 1816170 | 1701380 | 1659680 | 0 | 0 | 1637240 | 688.664 | 0 | 0 | 0 | 0 | 1637240 | 688.664 | 1607950 | 1575788.875
2939 | 2005-05-03 10:00 | 954 | 913 | 130 | 21.05 | 3.01 | 0 | 64.6734 | 132.764 | 19.6187 | 0 | 954 | 858.7 | 136.644 | 8.9382 | 858.7 | 127.876 | 0.046655 | 856.054 | 123.144 | 0.035155 | 949.856 | 949.85 | 2133120 | 45.4534 | 2141270 | 1957000 | 1910040 | 0 | 0 | 1879230 | 674.668 | 0 | 0 | 0 | 0 | 1879230 | 674.668 | 1841870 | 1805032.875
2940 | 2005-05-03 11:00 | 1017 | 947 | 124 | 22.24 | 3.01 | 0 | 70.9766 | 167.957 | 7.4613 | 0 | 1017 | 936.59 | 130.374 | 9.5285 | 936.59 | 122.009 | 0.049736 | 936.19 | 117.493 | 0.037477 | 1022.11 | 1022.11 | 2295390 | 48.4998 | 2312340 | 2084320 | 2035260 | 0 | 0 | 1999380 | 665.095 | 0 | 0 | 0 | 0 | 1999380 | 665.095 | 1957410 | 1918260.5
2941 | 2005-05-03 12:00 | 1011 | 957 | 120 | 23.43 | 3.84 | 0 | 68.9108 | 210.504 | 12.4127 | 0 | 1011 | 932.64 | 126.525 | 9.4723 | 932.64 | 118.407 | 0.049442 | 931.524 | 114.025 | 0.037256 | 1014.22 | 1014.21 | 2277650 | 48.098 | 2293630 | 2071310 | 2020430 | 0 | 0 | 1985340 | 667.55 | 0 | 0 | 0 | 0 | 1985340 | 667.55 | 1943930 | 1905048.875
2942 | 2005-05-03 13:00 | 931 | 943 | 114 | 24.63 | 3.84 | 0 | 60.1865 | 237.824 | 26.0711 | 0 | 931 | 845.815 | 120.817 | 8.7227 | 845.815 | 113.065 | 0.04553 | 841.024 | 108.881 | 0.034308 | 921.441 | 921.438 | 2069320 | 47.0415 | 2074090 | 1881110 | 1833890 | 0 | 0 | 1805130 | 670.445 | 0 | 0 | 0 | 0 | 1805130 | 670.445 | 1770550 | 1735141.875
2943 | 2005-05-03 14:00 | 793 | 912 | 106 | 24.73 | 3.84 | 0 | 48.9152 | 253.551 | 40.3804 | 0 | 793 | 694.312 | 112.47 | 7.4298 | 694.312 | 105.253 | 0.038781 | 683.454 | 101.358 | 0.029222 | 761.296 | 761.296 | 1709680 | 43.2465 | 1696350 | 1564270 | 1528230 | 0 | 0 | 1508500 | 676.546 | 0 | 0 | 0 | 0 | 1508500 | 676.546 | 1483620 | 1453949.5
2944 | 2005-05-03 15:00 | 609 | 860 | 94 | 24.83 | 6.09 | 0 | 36.8032 | 264.314 | 54.7974 | 0 | 609 | 495.572 | 100.164 | 5.7059 | 495.572 | 93.7377 | 0.029783 | 477.368 | 90.2686 | 0.022442 | 550.629 | 550.625 | 1236560 | 36.3994 | 1203920 | 1144180 | 1115430 | 0 | 0 | 1105220 | 688.957 | 0 | 0 | 0 | 0 | 1105220 | 688.957 | 1088720 | 1066949.125
2945 | 2005-05-03 16:00 | 395 | 763 | 78 | 24.93 | 6.09 | 0 | 24.4686 | 273.036 | 69.2056 | 0 | 395 | 271.708 | 79.6148 | 3.7008 | 271.708 | 74.5066 | 0.019317 | 247.026 | 71.7491 | 0.014556 | 309.226 | 309.222 | 694434 | 31.4272 | 651638 | 632521 | 617044 | 0 | 0 | 613846 | 684.152 | 0 | 0 | 0 | 0 | 613846 | 684.152 | 605124 | 593021.9375
2946 | 2005-05-03 17:00 | 168 | 503 | 61 | 24.44 | 6.09 | 0 | 12.2237 | 281.082 | 83.5406 | 0 | 168 | 56.8527 | 55.0169 | 1.574 | 56.8527 | 51.4869 | 0.0082159 | 34.4272 | 49.5814 | 0.0061909 | 81.4944 | 81.4933 | 183014 | 26.1523 | 154353 | 153437 | 149663 | 0 | 0 | 149450 | 644.981 | 0 | 0 | 0 | 1083.99 | 148366 | 660 | 144049 | 141167.5469
2947 | 2005-05-03 18:00 | 12 | 139 | 4 | 23.95 | 6.66 | 0 | 0.31404 | 289.276 | 90 | 0 | 12 | 0 | 3.1317 | 0.11243 | 0 | 2.9308 | 0.00058685 | 0 | 2.8223 | 0.0004422 | 2.7381 | 2.7379 | 6148.62 | 24.0055 | 1782.75 | 1783.02 | 1767.34 | 0 | 0 | 1767.26 | 384.351 | 0 | 0 | 0 | 1767.26 | 0 | 660 | 0 | 0
2948 | 2005-05-03 19:00 | 0 | 0 | 0 | 23.47 | 6.66 | 0
2949 | 2005-05-03 20:00 | 0 | 0 | 0 | 22.38 | 6.66 | 0
2950 | 2005-05-03 21:00 | 0 | 0 | 0 | 21.3 | 3.91 | 0
2951 | 2005-05-03 22:00 | 0 | 0 | 0 | 20.22 | 3.91 | 0
2952 | 2005-05-03 23:00 | 0 | 0 | 0 | 19.42 | 3.91 | 0
2953 | 2005-05-04 | 0 | 0 | 0 | 18.61 | 7.12 | 0
2954 | 2005-05-04 01:00 | 0 | 0 | 0 | 17.81 | 7.12 | 0
2955 | 2005-05-04 02:00 | 0 | 0 | 0 | 17 | 7.12 | 0
2956 | 2005-05-04 03:00 | 0 | 0 | 0 | 16.19 | 7.69 | 0
2957 | 2005-05-04 04:00 | 0 | 3 | 0 | 15.37 | 7.69 | 0
2958 | 2005-05-04 05:00 | 63 | 251 | 37 | 15.44 | 7.69 | 0 | 5.8246 | 74.449 | 90 | 0 | 63 | 0 | 28.4425 | 0.59026 | 0 | 26.6176 | 0.003081 | 0 | 25.6325 | 0.0023216 | 24.8658 | 24.8646 | 55839.7 | 15.9118 | 40566.4 | 42557.9 | 41543.8 | 0 | 0 | 41526.1 | 620.345 | 0 | 0 | 0 | 2066.5 | 39459.6 | 660 | 38053.5 | 37292.4688
2959 | 2005-05-04 06:00 | 275 | 642 | 77 | 15.5 | 2.86 | 0 | 17.9272 | 82.4575 | 76.9272 | 0 | 275 | 145.498 | 73.6364 | 2.5765 | 135.941 | 68.9118 | 0.013449 | 112.688 | 66.3614 | 0.010134 | 173.688 | 173.679 | 390050 | 20.0067 | 351626 | 359721 | 338283 | 0 | 0 | 337351 | 701.384 | 0 | 0 | 0 | 0 | 337351 | 701.384 | 330352 | 323744.9375
2960 | 2005-05-04 07:00 | 497 | 815 | 86 | 15.56 | 2.86 | 0 | 30.2555 | 90.6538 | 62.5603 | 0 | 497 | 375.89 | 89.7422 | 4.6565 | 375.89 | 83.9842 | 0.024305 | 353.899 | 80.876 | 0.018315 | 421.75 | 421.743 | 947130 | 26.5036 | 906936 | 900819 | 877437 | 0 | 0 | 871514 | 713.246 | 0 | 0 | 0 | 0 | 871514 | 713.246 | 857864 | 840706.375
2961 | 2005-05-04 08:00 | 700 | 844 | 129 | 17.54 | 2.86 | 0 | 42.553 | 100.032 | 48.1529 | 0 | 700 | 563.294 | 136.859 | 6.5584 | 563.294 | 128.078 | 0.034233 | 549.242 | 123.338 | 0.025795 | 652.427 | 652.42 | 1465170 | 34.4694 | 1441020 | 1382430 | 1347450 | 0 | 0 | 1333080 | 700.726 | 0 | 0 | 0 | 0 | 1333080 | 700.726 | 1311270 | 1285045.125
2962 | 2005-05-04 09:00 | 824 | 784 | 187 | 19.51 | 3.02 | 0 | 54.4211 | 112.478 | 33.7857 | 0 | 824 | 650.948 | 201.171 | 7.7202 | 650.948 | 188.263 | 0.040297 | 644.335 | 181.296 | 0.030365 | 800.891 | 800.88 | 1798580 | 40.0724 | 1789530 | 1675090 | 1634710 | 0 | 0 | 1612830 | 687.017 | 0 | 0 | 0 | 0 | 1612830 | 687.017 | 1584360 | 1552671.5
2963 | 2005-05-04 10:00 | 885 | 689 | 262 | 21.49 | 3.02 | 0 | 64.9117 | 132.376 | 19.6813 | 0 | 885 | 647.713 | 280.252 | 8.2918 | 647.713 | 262.271 | 0.04328 | 645.704 | 252.564 | 0.032613 | 871.352 | 871.336 | 1956800 | 43.8614 | 1955700 | 1799720 | 1756190 | 0 | 0 | 1730300 | 677.113 | 0 | 0 | 0 | 0 | 1730300 | 677.113 | 1698230 | 1664265
2964 | 2005-05-04 11:00 | 951 | 735 | 256 | 22.64 | 3.02 | 0 | 71.2647 | 167.864 | 7.695 | 0 | 951 | 727.278 | 277.112 | 8.9101 | 727.278 | 259.332 | 0.046508 | 726.948 | 249.735 | 0.035045 | 947.416 | 947.406 | 2127630 | 46.9645 | 2135500 | 1937860 | 1891220 | 0 | 0 | 1860570 | 669.3 | 0 | 0 | 0 | 0 | 1860570 | 669.3 | 1823970 | 1787490.25
2965 | 2005-05-04 12:00 | 870 | 615 | 296 | 23.79 | 6.55 | 0 | 69.1606 | 210.912 | 12.5759 | 0 | 870 | 599.444 | 315.086 | 8.1512 | 599.444 | 294.87 | 0.042547 | 598.707 | 283.957 | 0.03206 | 856.215 | 856.203 | 1922810 | 41.2571 | 1919970 | 1788140 | 1743550 | 0 | 0 | 1718670 | 686.466 | 0 | 0 | 0 | 0 | 1718670 | 686.466 | 1686780 | 1653039.875
2966 | 2005-05-04 13:00 | 809 | 602 | 286 | 24.94 | 6.55 | 0 | 60.3685 | 238.277 | 26.1488 | 0 | 809 | 540.105 | 300.585 | 7.5797 | 540.105 | 281.298 | 0.039564 | 537.026 | 270.888 | 0.029812 | 783.706 | 783.681 | 1759950 | 40.9276 | 1749030 | 1630640 | 1589200 | 0 | 0 | 1568340 | 683.833 | 0 | 0 | 0 | 0 | 1568340 | 683.833 | 1541360 | 1510537.25
2967 | 2005-05-04 14:00 | 714 | 681 | 200 | 24.81 | 6.55 | 0 | 49.0611 | 253.932 | 40.423 | 0 | 714 | 517.994 | 211.152 | 6.6896 | 517.994 | 197.604 | 0.034918 | 509.873 | 190.291 | 0.026311 | 679.184 | 679.181 | 1525270 | 38.6657 | 1503640 | 1415520 | 1379980 | 0 | 0 | 1364370 | 687.734 | 0 | 0 | 0 | 0 | 1364370 | 687.734 | 1342450 | 1315602
2968 | 2005-05-04 15:00 | 575 | 606 | 211 | 24.68 | 7.36 | 0 | 36.9349 | 264.635 | 54.8169 | 0 | 575 | 349.029 | 211.132 | 5.3873 | 349.029 | 197.586 | 0.02812 | 336.192 | 190.273 | 0.021189 | 510.692 | 510.678 | 1146850 | 34.5744 | 1111440 | 1064890 | 1037940 | 0 | 0 | 1029160 | 692.486 | 0 | 0 | 0 | 0 | 1029160 | 692.486 | 1013980 | 993698.8125
2969 | 2005-05-04 16:00 | 127 | 0 | 127 | 24.54 | 7.36 | 0 | 24.5989 | 273.319 | 69.2056 | 0 | 127 | 0 | 116.666 | 1.1899 | 0 | 109.181 | 0.0062108 | 0 | 105.14 | 0.00468 | 101.991 | 101.987 | 229036 | 26.516 | 197287 | 195775 | 190903 | 0 | 0 | 190564 | 652.768 | 0 | 0 | 0 | 213.195 | 190351 | 660 | 185292 | 181586.25
2970 | 2005-05-04 17:00 | 154 | 225 | 105 | 23.79 | 7.36 | 0 | 12.3612 | 281.342 | 83.5215 | 0 | 154 | 25.8262 | 91.1443 | 1.4429 | 25.8262 | 85.2963 | 0.0075312 | 15.6729 | 82.1396 | 0.0056749 | 94.8836 | 94.8781 | 213072 | 25.6283 | 182323 | 181737 | 177252 | 0 | 0 | 176958 | 650.991 | 0 | 0 | 0 | 233.393 | 176725 | 660 | 171883 | 168445.5469
2971 | 2005-05-04 18:00 | 12 | 63 | 8 | 23.04 | 8.32 | 0 | 0.46579 | 289.521 | 90 | 0 | 12 | 0 | 6.3245 | 0.11243 | 0 | 5.9188 | 0.00058685 | 0 | 5.6997 | 0.0004422 | 5.5291 | 5.5288 | 12416.4 | 23.1408 | 5845.99 | 5887.68 | 5779.96 | 0 | 0 | 5779.42 | 496.919 | 0 | 0 | 0 | 5779.42 | 0 | 660 | 0 | 0
2972 | 2005-05-04 19:00 | 0 | 0 | 0 | 22.29 | 8.32 | 0
2973 | 2005-05-04 20:00 | 0 | 0 | 0 | 21.31 | 8.32 | 0
2974 | 2005-05-04 21:00 | 0 | 0 | 0 | 20.32 | 6.74 | 0
2975 | 2005-05-04 22:00 | 0 | 0 | 0 | 19.34 | 6.74 | 0
2976 | 2005-05-04 23:00 | 0 | 0 | 0 | 18.5 | 6.74 | 0
2977 | 2005-05-05 | 0 | 0 | 0 | 17.65 | 10.99 | 0
2978 | 2005-05-05 01:00 | 0 | 0 | 0 | 16.81 | 10.99 | 0
2979 | 2005-05-05 02:00 | 0 | 0 | 0 | 16.04 | 10.99 | 0
2980 | 2005-05-05 03:00 | 0 | 0 | 0 | 15.27 | 5.14 | 0
2981 | 2005-05-05 04:00 | 0 | 6 | 0 | 14.5 | 5.14 | 0
2982 | 2005-05-05 05:00 | 68 | 296 | 36 | 14.66 | 5.14 | 0 | 6.0024 | 74.2236 | 90 | 0 | 68 | 0 | 28.9263 | 0.63711 | 0 | 27.0703 | 0.0033255 | 0 | 26.0685 | 0.0025058 | 25.2888 | 25.2863 | 56786.5 | 15.2249 | 41368.3 | 43550.6 | 42469.2 | 0 | 0 | 42450.8 | 623.621 | 0 | 0 | 0 | 1697.28 | 40753.6 | 660 | 39304.6 | 38518.5078
2983 | 2005-05-05 06:00 | 273 | 545 | 103 | 14.82 | 5.77 | 0 | 18.0948 | 82.2137 | 76.8756 | 0 | 273 | 124.283 | 95.7654 | 2.5578 | 116.565 | 89.6209 | 0.013351 | 96.7255 | 86.3041 | 0.01006 | 177.548 | 177.545 | 398729 | 18.6282 | 359910 | 370617 | 350289 | 0 | 0 | 349310 | 706.332 | 0 | 0 | 0 | 0 | 349310 | 706.332 | 342160 | 335316.5
2984 | 2005-05-05 07:00 | 329 | 202 | 227 | 14.98 | 5.77 | 0 | 30.4194 | 90.3824 | 62.5277 | 0 | 329 | 92.9334 | 214.503 | 3.0825 | 92.9334 | 200.74 | 0.016089 | 87.5075 | 193.311 | 0.012124 | 272.406 | 272.398 | 611734 | 20.8226 | 569129 | 579917 | 563774 | 0 | 0 | 561329 | 715.442 | 0 | 0 | 0 | 0 | 561329 | 715.442 | 552217 | 541173.0625
2985 | 2005-05-05 08:00 | 476 | 230 | 320 | 15.83 | 5.77 | 0 | 42.7223 | 99.7198 | 48.1411 | 0 | 476 | 153.437 | 309.61 | 4.4597 | 153.437 | 289.745 | 0.023278 | 149.612 | 279.021 | 0.017541 | 415.791 | 415.78 | 933733 | 24.748 | 893319 | 894191 | 869732 | 0 | 0 | 863963 | 716.808 | 0 | 0 | 0 | 0 | 863963 | 716.808 | 850277 | 833271.625
2986 | 2005-05-05 09:00 | 835 | 727 | 243 | 16.69 | 10.23 | 0 | 54.6102 | 112.11 | 33.8015 | 0 | 835 | 603.429 | 255.695 | 7.8233 | 603.429 | 239.29 | 0.040835 | 597.292 | 230.434 | 0.03077 | 802.924 | 802.904 | 1803120 | 29.7001 | 1794290 | 1758740 | 1712560 | 0 | 0 | 1690830 | 722.581 | 0 | 0 | 0 | 0 | 1690830 | 722.581 | 1658910 | 1625736
2987 | 2005-05-05 10:00 | 626 | 258 | 392 | 17.55 | 10.23 | 0 | 65.144 | 131.984 | 19.7486 | 0 | 626 | 242.721 | 399.082 | 5.8651 | 242.721 | 373.476 | 0.030614 | 241.963 | 359.654 | 0.023068 | 583.591 | 583.597 | 1310610 | 27.0065 | 1280530 | 1269350 | 1233180 | 0 | 0 | 1221870 | 723.878 | 0 | 0 | 0 | 0 | 1221870 | 723.878 | 1201320 | 1177294.875
2988 | 2005-05-05 11:00 | 712 | 254 | 472 | 17.83 | 10.23 | 0 | 71.548 | 167.764 | 7.9297 | 0 | 712 | 250.588 | 482.783 | 6.6709 | 250.588 | 451.807 | 0.03482 | 250.467 | 435.086 | 0.026237 | 665.012 | 664.981 | 1493380 | 28.6052 | 1470410 | 1447700 | 1411140 | 0 | 0 | 1396220 | 720.392 | 0 | 0 | 0 | 0 | 1396220 | 720.392 | 1372210 | 1344762.625
2989 | 2005-05-05 12:00 | 278 | 13 | 266 | 18.11 | 12.94 | 0 | 69.4065 | 211.319 | 12.7392 | 0 | 278 | 12.5036 | 249.84 | 2.6046 | 12.5036 | 233.81 | 0.013595 | 12.4878 | 225.157 | 0.010244 | 230.525 | 230.507 | 517661 | 21.2853 | 476013 | 484178 | 470734 | 0 | 0 | 468990 | 707.266 | 0 | 0 | 0 | 0 | 468990 | 707.266 | 461115 | 451892.4688
2990 | 2005-05-05 13:00 | 259 | 10 | 250 | 18.39 | 12.94 | 0 | 60.5476 | 238.726 | 26.2261 | 0 | 259 | 9.2718 | 234.032 | 2.4266 | 9.2718 | 219.016 | 0.012666 | 9.2186 | 210.91 | 0.0095442 | 213.534 | 213.522 | 479515 | 21.3313 | 438508 | 445991 | 433222 | 0 | 0 | 431736 | 705.213 | 0 | 0 | 0 | 0 | 431736 | 705.213 | 424374 | 415886.3438
2991 | 2005-05-05 14:00 | 763 | 693 | 238 | 17.92 | 12.94 | 0 | 49.205 | 254.307 | 40.4646 | 0 | 763 | 527.605 | 247.244 | 7.1487 | 527.605 | 231.38 | 0.037314 | 519.311 | 222.817 | 0.028117 | 719.891 | 719.878 | 1616660 | 27.8365 | 1599050 | 1579750 | 1537310 | 0 | 0 | 1519910 | 726.442 | 0 | 0 | 0 | 0 | 1519910 | 726.442 | 1492870 | 1463011
2992 | 2005-05-05 15:00 | 594 | 791 | 117 | 17.44 | 9.88 | 0 | 37.0653 | 264.951 | 54.8351 | 0 | 594 | 455.795 | 122.658 | 5.5653 | 455.795 | 114.788 | 0.029049 | 439.015 | 110.54 | 0.021889 | 533.089 | 533.083 | 1197170 | 26.2652 | 1163270 | 1156800 | 1127680 | 0 | 0 | 1118120 | 720.782 | 0 | 0 | 0 | 0 | 1118120 | 720.782 | 1099800 | 1077801.125
2993 | 2005-05-05 16:00 | 399 | 742 | 88 | 16.96 | 9.88 | 0 | 24.7284 | 273.597 | 69.2042 | 0 | 399 | 263.955 | 87.8719 | 3.7383 | 263.955 | 82.2339 | 0.019513 | 239.98 | 79.1905 | 0.014703 | 309.61 | 309.608 | 695300 | 22.0856 | 652506 | 661043 | 643622 | 0 | 0 | 640456 | 717.188 | 0 | 0 | 0 | 0 | 640456 | 717.188 | 630299 | 617692.5625
2994 | 2005-05-05 17:00 | 172 | 502 | 63 | 15.25 | 9.88 | 0 | 12.498 | 281.597 | 83.5008 | 0 | 172 | 57.0115 | 56.6267 | 1.6115 | 57.0115 | 52.9934 | 0.0084115 | 34.6779 | 51.0321 | 0.0063383 | 83.1449 | 83.1419 | 186715 | 16.6264 | 157781 | 164469 | 160180 | 0 | 0 | 159960 | 680.262 | 0 | 0 | 0 | 0 | 159960 | 680.262 | 155125 | 152022.9219
2995 | 2005-05-05 18:00 | 14 | 145 | 5 | 13.53 | 10.25 | 0 | 0.61674 | 289.762 | 90 | 0 | 14 | 0 | 3.9671 | 0.13117 | 0 | 3.7126 | 0.00068466 | 0 | 3.5752 | 0.0005159 | 3.4684 | 3.4682 | 7788.64 | 13.5861 | 2745.38 | 2781.34 | 2748.79 | 0 | 0 | 2748.65 | 458.749 | 0 | 0 | 0 | 2748.65 | 0 | 660 | 0 | 0
2996 | 2005-05-05 19:00 | 0 | 0 | 0 | 11.82 | 10.25 | 0
2997 | 2005-05-05 20:00 | 0 | 0 | 0 | 11.43 | 10.25 | 0
2998 | 2005-05-05 21:00 | 0 | 0 | 0 | 11.04 | 9.19 | 0
2999 | 2005-05-05 22:00 | 0 | 0 | 0 | 10.65 | 9.19 | 0
3000 | 2005-05-05 23:00 | 0 | 0 | 0 | 10.22 | 9.19 | 0
3001 | 2005-05-06 | 0 | 0 | 0 | 9.79 | 9.97 | 0
3002 | 2005-05-06 01:00 | 0 | 0 | 0 | 9.36 | 9.97 | 0
3003 | 2005-05-06 02:00 | 0 | 0 | 0 | 9.27 | 9.97 | 0
3004 | 2005-05-06 03:00 | 0 | 0 | 0 | 9.18 | 7.21 | 0
3005 | 2005-05-06 04:00 | 0 | 9 | 0 | 9.09 | 7.21 | 0
3006 | 2005-05-06 05:00 | 75 | 305 | 41 | 9.23 | 7.21 | 0 | 6.1757 | 74.0004 | 90 | 0 | 75 | 0 | 33.7946 | 0.70269 | 0 | 31.6263 | 0.0036678 | 0 | 30.4558 | 0.0027638 | 29.5448 | 29.5438 | 66347.9 | 9.8079 | 49528.2 | 53548.6 | 52143 | 0 | 0 | 52117.6 | 652.541 | 0 | 0 | 0 | 80.5043 | 52037.1 | 660 | 50222.2 | 49217.7852
3007 | 2005-05-06 06:00 | 266 | 568 | 87 | 9.36 | 9.52 | 0 | 18.2577 | 81.9722 | 76.8272 | 0 | 266 | 130.205 | 82.769 | 2.4922 | 122.506 | 77.4583 | 0.013008 | 101.753 | 74.5917 | 0.0098022 | 171.064 | 171.06 | 384168 | 12.2554 | 345817 | 366506 | 344642 | 0 | 0 | 343742 | 725.971 | 0 | 0 | 0 | 0 | 343742 | 725.971 | 336068 | 329346.4062
3008 | 2005-05-06 07:00 | 503 | 778 | 107 | 9.49 | 9.52 | 0 | 30.5784 | 90.1134 | 62.4983 | 0 | 503 | 359.458 | 109.338 | 4.7127 | 359.458 | 102.323 | 0.024599 | 338.51 | 98.5358 | 0.018536 | 423.952 | 423.948 | 952076 | 16.6657 | 911976 | 945034 | 918808 | 0 | 0 | 912869 | 747.238 | 0 | 0 | 0 | 0 | 912869 | 747.238 | 897050 | 879108.875
3009 | 2005-05-06 08:00 | 704 | 720 | 214 | 10.61 | 9.52 | 0 | 42.8864 | 99.4089 | 48.1327 | 0 | 704 | 480.539 | 219.744 | 6.5959 | 480.539 | 205.645 | 0.034429 | 468.566 | 198.034 | 0.025943 | 646.627 | 646.62 | 1452150 | 21.5547 | 1427470 | 1448060 | 1408710 | 0 | 0 | 1394780 | 744.715 | 0 | 0 | 0 | 0 | 1394780 | 744.715 | 1369660 | 1342270.375
3010 | 2005-05-06 09:00 | 281 | 39 | 249 | 11.72 | 8.79 | 0 | 54.7936 | 111.742 | 33.8211 | 0 | 281 | 32.5365 | 250.408 | 2.6328 | 32.5365 | 234.341 | 0.013742 | 32.2051 | 225.668 | 0.010355 | 250.147 | 250.143 | 561758 | 16.15 | 519559 | 540557 | 524734 | 0 | 0 | 522685 | 727.442 | 0 | 0 | 0 | 0 | 522685 | 727.442 | 513586 | 503313.8125
3011 | 2005-05-06 10:00 | 196 | 2 | 194 | 12.84 | 8.79 | 0 | 65.3704 | 131.588 | 19.8203 | 0 | 196 | 2.0698 | 181.088 | 1.8364 | 2.0698 | 169.469 | 0.0095852 | 2.0633 | 163.197 | 0.0072227 | 160.31 | 160.301 | 359996 | 15.6789 | 322141 | 336450 | 327230 | 0 | 0 | 326395 | 711.816 | 0 | 0 | 0 | 0 | 326395 | 711.816 | 319039 | 312658.125
3012 | 2005-05-06 11:00 | 210 | 2 | 208 | 13.43 | 8.79 | 0 | 71.8263 | 167.657 | 8.1646 | 0 | 210 | 2.0837 | 194.658 | 1.9675 | 2.0837 | 182.169 | 0.01027 | 2.0826 | 175.427 | 0.0077386 | 172.192 | 172.187 | 386688 | 16.4794 | 347963 | 362006 | 351682 | 0 | 0 | 350723 | 713.327 | 0 | 0 | 0 | 0 | 350723 | 713.327 | 343317 | 336450.2812
3013 | 2005-05-06 12:00 | 310 | 19 | 292 | 14.01 | 10.8 | 0 | 69.6485 | 211.723 | 12.9023 | 0 | 310 | 18.7137 | 274.7 | 2.9045 | 18.7137 | 257.074 | 0.01516 | 18.6895 | 247.56 | 0.011424 | 258.273 | 258.259 | 579983 | 18.0521 | 537614 | 554646 | 538594 | 0 | 0 | 536413 | 724.151 | 0 | 0 | 0 | 0 | 536413 | 724.151 | 527275 | 516729.9062
3014 | 2005-05-06 13:00 | 381 | 25 | 359 | 14.6 | 10.8 | 0 | 60.7238 | 239.17 | 26.3028 | 0 | 381 | 22.6102 | 338.483 | 3.5697 | 22.6102 | 316.766 | 0.018632 | 22.4796 | 305.042 | 0.01404 | 317.71 | 317.689 | 713446 | 19.5722 | 670720 | 686999 | 667506 | 0 | 0 | 664186 | 726.486 | 0 | 0 | 0 | 0 | 664186 | 726.486 | 653344 | 640277.1875
3015 | 2005-05-06 14:00 | 139 | 0 | 139 | 14.74 | 10.8 | 0 | 49.347 | 254.676 | 40.5051 | 0 | 139 | 0 | 128.816 | 1.3023 | 0 | 120.551 | 0.0067977 | 0 | 116.089 | 0.0051222 | 112.611 | 112.608 | 252888 | 16.5025 | 219761 | 228966 | 222411 | 0 | 0 | 222004 | 693.176 | 0 | 0 | 0 | 0 | 222004 | 693.176 | 215891 | 211573.2031
3016 | 2005-05-06 15:00 | 483 | 271 | 319 | 14.87 | 8.9 | 0 | 37.1946 | 265.262 | 54.852 | 0 | 483 | 156.178 | 304.77 | 4.5253 | 156.178 | 285.215 | 0.023621 | 150.422 | 274.659 | 0.017799 | 412.346 | 412.344 | 926021 | 22.1226 | 885473 | 896570 | 871665 | 0 | 0 | 866070 | 729.122 | 0 | 0 | 0 | 0 | 866070 | 729.122 | 851818 | 834781.5
3017 | 2005-05-06 16:00 | 118 | 0 | 118 | 15.01 | 8.9 | 0 | 24.8569 | 273.871 | 69.2014 | 0 | 118 | 0 | 108.418 | 1.1056 | 0 | 101.462 | 0.0057707 | 0 | 97.707 | 0.0043483 | 94.78 | 94.7759 | 212842 | 16.677 | 182112 | 189699 | 184503 | 0 | 0 | 184217 | 686.3 | 0 | 0 | 0 | 0 | 184217 | 686.3 | 178825 | 175248.0312
3018 | 2005-05-06 17:00 | 134 | 125 | 106 | 14.61 | 8.9 | 0 | 12.634 | 281.846 | 83.4787 | 0 | 134 | 14.5391 | 91.5287 | 1.2555 | 14.5391 | 85.6561 | 0.0065532 | 8.8653 | 82.486 | 0.0049379 | 88.6155 | 88.6112 | 198998 | 16.1686 | 169196 | 176714 | 171858 | 0 | 0 | 171609 | 684.288 | 0 | 0 | 0 | 0 | 171609 | 684.288 | 166483 | 163152.9375
3019 | 2005-05-06 18:00 | 11 | 37 | 9 | 14.22 | 10.5 | 0 | 0.76685 | 289.997 | 90 | 0 | 11 | 0 | 7.5564 | 0.10306 | 0 | 7.0715 | 0.00053795 | 0 | 6.8098 | 0.00040535 | 6.6059 | 6.6055 | 14834.3 | 14.3253 | 7580.69 | 7917.54 | 7761.42 | 0 | 0 | 7760.6 | 540.926 | 0 | 0 | 0 | 5953.71 | 1806.89 | 659.999 | 1738.42 | 1703.6559
3020 | 2005-05-06 19:00 | 0 | 0 | 0 | 13.83 | 10.5 | 0
3021 | 2005-05-06 20:00 | 0 | 0 | 0 | 13.1 | 10.5 | 0
3022 | 2005-05-06 21:00 | 0 | 0 | 0 | 12.37 | 8.34 | 0
3023 | 2005-05-06 22:00 | 0 | 0 | 0 | 11.64 | 8.34 | 0
3024 | 2005-05-06 23:00 | 0 | 0 | 0 | 11.05 | 8.34 | 0
3025 | 2005-05-07 | 0 | 0 | 0 | 10.45 | 9.23 | 0
3026 | 2005-05-07 01:00 | 0 | 0 | 0 | 9.85 | 9.23 | 0
3027 | 2005-05-07 02:00 | 0 | 0 | 0 | 9.43 | 9.23 | 0
3028 | 2005-05-07 03:00 | 0 | 0 | 0 | 9.01 | 8.33 | 0
3029 | 2005-05-07 04:00 | 0 | 10 | 0 | 8.59 | 8.33 | 0
3030 | 2005-05-07 05:00 | 70 | 280 | 38 | 9.13 | 8.33 | 0 | 6.3444 | 73.7797 | 90 | 0 | 70 | 0 | 29.0157 | 0.65585 | 0 | 27.154 | 0.0034233 | 0 | 26.149 | 0.0025795 | 25.367 | 25.3654 | 56964.4 | 9.5923 | 41519.2 | 44944 | 43809 | 0 | 0 | 43790.7 | 644.101 | 0 | 0 | 0 | 268.632 | 43522 | 660 | 41981.9 | 41142.2422
3031 | 2005-05-07 06:00 | 266 | 591 | 79 | 9.68 | 6.27 | 0 | 18.4158 | 81.7332 | 76.7818 | 0 | 266 | 135.352 | 75.1319 | 2.4922 | 127.794 | 70.3113 | 0.013008 | 106.239 | 67.7091 | 0.0098022 | 168.739 | 168.73 | 378937 | 13.1845 | 340761 | 359662 | 336778 | 0 | 0 | 335905 | 721.263 | 0 | 0 | 0 | 0 | 335905 | 721.263 | 328368 | 321800.6562
3032 | 2005-05-07 07:00 | 505 | 779 | 107 | 10.22 | 6.27 | 0 | 30.7326 | 89.8467 | 62.4721 | 0 | 505 | 359.954 | 109.163 | 4.7315 | 359.954 | 102.159 | 0.024697 | 339.01 | 98.3783 | 0.018609 | 424.285 | 424.282 | 952831 | 19.0323 | 912747 | 936451 | 909772 | 0 | 0 | 903839 | 739.533 | 0 | 0 | 0 | 0 | 903839 | 739.533 | 888496 | 870726.375
3033 | 2005-05-07 08:00 | 705 | 887 | 100 | 11.66 | 6.27 | 0 | 43.0453 | 99.1002 | 48.1276 | 0 | 705 | 591.613 | 105.337 | 6.6053 | 591.613 | 98.5788 | 0.034477 | 576.877 | 94.9304 | 0.025979 | 651.678 | 651.672 | 1463490 | 25.1951 | 1439270 | 1437880 | 1399430 | 0 | 0 | 1385200 | 731.84 | 0 | 0 | 0 | 0 | 1385200 | 731.84 | 1360930 | 1333715.25
3034 | 2005-05-07 09:00 | 855 | 902 | 117 | 13.11 | 3.3 | 0 | 54.9712 | 111.374 | 33.8444 | 0 | 855 | 748.535 | 123.081 | 8.0107 | 748.535 | 115.184 | 0.041813 | 740.899 | 110.921 | 0.031507 | 826.296 | 826.292 | 1855640 | 33.9355 | 1849400 | 1779700 | 1733750 | 0 | 0 | 1710650 | 709.234 | 0 | 0 | 0 | 0 | 1710650 | 709.234 | 1678460 | 1644888.625
3035 | 2005-05-07 10:00 | 962 | 917 | 128 | 14.55 | 3.3 | 0 | 65.5906 | 131.188 | 19.8962 | 0 | 962 | 861.196 | 133.89 | 9.0132 | 861.196 | 125.299 | 0.047046 | 858.463 | 120.662 | 0.03545 | 949.786 | 949.782 | 2132960 | 38.4879 | 2141110 | 2020200 | 1969110 | 0 | 0 | 1938490 | 697.872 | 0 | 0 | 0 | 0 | 1938490 | 697.872 | 1898750 | 1860770.875
3036 | 2005-05-07 11:00 | 1032 | 959 | 121 | 15.83 | 3.3 | 0 | 72.0996 | 167.541 | 8.3994 | 0 | 1032 | 947.074 | 126.598 | 9.669 | 947.074 | 118.475 | 0.050469 | 946.561 | 114.09 | 0.03803 | 1028.87 | 1028.86 | 2310550 | 41.761 | 2328340 | 2165480 | 2109700 | 0 | 0 | 2073800 | 689.452 | 28965.4 | 0 | 0 | 0 | 2043560 | 710.272 | 1999980 | 1959983.25
3037 | 2005-05-07 12:00 | 1011 | 949 | 121 | 17.11 | 4.18 | 0 | 69.8863 | 212.124 | 13.0649 | 0 | 1011 | 923.27 | 126.749 | 9.4723 | 923.27 | 118.617 | 0.049442 | 922.044 | 114.227 | 0.037256 | 1005.22 | 1005.22 | 2257470 | 41.0195 | 2272340 | 2120300 | 2064580 | 0 | 0 | 2030430 | 692.245 | 0 | 0 | 0 | 0 | 2030430 | 692.245 | 1987270 | 1947528.5
3038 | 2005-05-07 13:00 | 927 | 928 | 117 | 18.39 | 4.18 | 0 | 60.8971 | 239.608 | 26.3788 | 0 | 927 | 830.514 | 123.122 | 8.6853 | 830.514 | 115.222 | 0.045334 | 825.688 | 110.958 | 0.03416 | 908.579 | 908.579 | 2040440 | 40.001 | 2043680 | 1914830 | 1869330 | 0 | 0 | 1841110 | 690.507 | 0 | 0 | 0 | 0 | 1841110 | 690.507 | 1804930 | 1768829
3039 | 2005-05-07 14:00 | 800 | 913 | 106 | 18.66 | 4.18 | 0 | 49.4873 | 255.04 | 40.5445 | 0 | 800 | 693.672 | 111.866 | 7.4954 | 693.672 | 104.689 | 0.039123 | 682.713 | 100.814 | 0.02948 | 760.05 | 760.045 | 1706870 | 36.7381 | 1693410 | 1608970 | 1567840 | 0 | 0 | 1548320 | 698.081 | 0 | 0 | 0 | 0 | 1548320 | 698.081 | 1521470 | 1491040.25
3040 | 2005-05-07 15:00 | 606 | 807 | 117 | 18.94 | 5.07 | 0 | 37.3226 | 265.568 | 54.8676 | 0 | 606 | 464.132 | 122.295 | 5.6777 | 464.132 | 114.448 | 0.029636 | 447.012 | 110.213 | 0.022331 | 540.53 | 540.524 | 1213880 | 31.0712 | 1180500 | 1149330 | 1120210 | 0 | 0 | 1110380 | 705.749 | 0 | 0 | 0 | 0 | 1110380 | 705.749 | 1092950 | 1071090.125
3041 | 2005-05-07 16:00 | 382 | 697 | 87 | 19.21 | 5.07 | 0 | 24.9846 | 274.139 | 69.1971 | 0 | 382 | 248.051 | 86.5804 | 3.579 | 248.051 | 81.0252 | 0.018681 | 225.532 | 78.0265 | 0.014077 | 294.466 | 294.464 | 661293 | 25.8188 | 618500 | 616149 | 600004 | 0 | 0 | 597123 | 701.686 | 0 | 0 | 0 | 0 | 597123 | 701.686 | 588098 | 576335.875
3042 | 2005-05-07 17:00 | 165 | 447 | 66 | 18.78 | 5.07 | 0 | 12.7693 | 282.091 | 83.4551 | 0 | 165 | 51.054 | 59.183 | 1.5459 | 51.054 | 55.3857 | 0.0080692 | 31.2111 | 53.3359 | 0.0060803 | 82.0165 | 82.0132 | 184180 | 20.6207 | 155433 | 158893 | 154725 | 0 | 0 | 154511 | 665.355 | 0 | 0 | 0 | 0 | 154511 | 665.355 | 149997 | 146997.2031
3043 | 2005-05-07 18:00 | 14 | 135 | 6 | 18.34 | 6.55 | 0 | 0.91607 | 290.227 | 90 | 0 | 14 | 0 | 4.4712 | 0.13117 | 0 | 4.1843 | 0.00068466 | 0 | 4.0295 | 0.0005159 | 3.9091 | 3.9089 | 8778.41 | 18.4197 | 3372.74 | 3418.72 | 3372.64 | 0 | 0 | 3372.43 | 466.666 | 0 | 0 | 0 | 3372.43 | 0 | 660 | 0 | 0
3044 | 2005-05-07 19:00 | 0 | 0 | 0 | 17.9 | 6.55 | 0
3045 | 2005-05-07 20:00 | 0 | 0 | 0 | 17.15 | 6.55 | 0
3046 | 2005-05-07 21:00 | 0 | 0 | 0 | 16.39 | 6.52 | 0
3047 | 2005-05-07 22:00 | 0 | 0 | 0 | 15.64 | 6.52 | 0
3048 | 2005-05-07 23:00 | 0 | 0 | 0 | 15.06 | 6.52 | 0
3049 | 2005-05-08 | 0 | 0 | 0 | 14.49 | 5.94 | 0
3050 | 2005-05-08 01:00 | 0 | 0 | 0 | 13.91 | 5.94 | 0
3051 | 2005-05-08 02:00 | 0 | 0 | 0 | 13.56 | 5.94 | 0
3052 | 2005-05-08 03:00 | 0 | 0 | 0 | 13.21 | 2.06 | 0
3053 | 2005-05-08 04:00 | 0 | 12 | 0 | 12.86 | 2.06 | 0
3054 | 2005-05-08 05:00 | 73 | 281 | 40 | 13.29 | 2.06 | 0 | 6.5085 | 73.5614 | 90 | 0 | 73 | 0 | 30.554 | 0.68395 | 0 | 28.5936 | 0.00357 | 0 | 27.5354 | 0.0026901 | 26.7119 | 26.7105 | 59984.8 | 14.021 | 44085.9 | 46691.8 | 45522.5 | 0 | 0 | 45501.9 | 630.924 | 0 | 0 | 0 | 1082.18 | 44419.7 | 660 | 42850.2 | 41993.1758
3055 | 2005-05-08 06:00 | 289 | 613 | 93 | 13.72 | 2.14 | 0 | 18.5693 | 81.4967 | 76.7396 | 0 | 289 | 141.177 | 88.1163 | 2.7077 | 133.76 | 82.4626 | 0.014133 | 111.291 | 79.4108 | 0.01065 | 184.991 | 184.987 | 415445 | 18.7557 | 376178 | 387055 | 363456 | 0 | 0 | 362409 | 709.612 | 0 | 0 | 0 | 0 | 362409 | 709.612 | 355205 | 348100.4688
3056 | 2005-05-08 07:00 | 496 | 760 | 106 | 14.16 | 2.14 | 0 | 30.8818 | 89.5826 | 62.4491 | 0 | 496 | 351.452 | 108.015 | 4.6471 | 351.452 | 101.085 | 0.024257 | 331.033 | 97.3439 | 0.018278 | 415.543 | 415.538 | 933196 | 25.4717 | 892753 | 890778 | 866474 | 0 | 0 | 860754 | 717.414 | 0 | 0 | 0 | 0 | 860754 | 717.414 | 847093 | 830151.5625
3057 | 2005-05-08 08:00 | 702 | 878 | 101 | 15.69 | 2.14 | 0 | 43.1989 | 98.7937 | 48.1259 | 0 | 702 | 586.042 | 106.192 | 6.5772 | 586.042 | 99.3787 | 0.034331 | 571.446 | 95.7008 | 0.025869 | 647.157 | 647.149 | 1453330 | 33.3066 | 1428700 | 1377730 | 1342970 | 0 | 0 | 1328830 | 704.142 | 0 | 0 | 0 | 0 | 1328830 | 704.142 | 1306970 | 1280829.25
3058 | 2005-05-08 09:00 | 869 | 927 | 109 | 17.22 | 3.29 | 0 | 55.1431 | 111.008 | 33.8712 | 0 | 869 | 768.993 | 114.992 | 8.1418 | 768.993 | 107.614 | 0.042498 | 761.134 | 103.631 | 0.032023 | 838.854 | 838.849 | 1883840 | 38.376 | 1879020 | 1772880 | 1728010 | 0 | 0 | 1704220 | 695.892 | 0 | 0 | 0 | 0 | 1704220 | 695.892 | 1672570 | 1639115.75
3059 | 2005-05-08 10:00 | 972 | 933 | 122 | 18.75 | 3.29 | 0 | 65.8047 | 130.785 | 19.976 | 0 | 972 | 875.796 | 127.799 | 9.1069 | 875.796 | 119.599 | 0.047535 | 872.992 | 115.173 | 0.035819 | 958.555 | 958.547 | 2152660 | 42.9248 | 2161860 | 1999230 | 1949110 | 0 | 0 | 1917770 | 682.574 | 0 | 0 | 0 | 0 | 1917770 | 682.574 | 1878890 | 1841316.625
3060 | 2005-05-08 11:00 | 1033 | 959 | 121 | 19.88 | 3.29 | 0 | 72.3677 | 167.418 | 8.6333 | 0 | 1033 | 946.115 | 126.406 | 9.6784 | 946.115 | 118.295 | 0.050518 | 945.573 | 113.917 | 0.038066 | 1027.74 | 1027.74 | 2308030 | 45.7998 | 2325680 | 2123220 | 2072240 | 0 | 0 | 2035980 | 674.253 | 758.343 | 0 | 0 | 0 | 2035180 | 676.467 | 1991790 | 1951952.25
3061 | 2005-05-08 12:00 | 1005 | 935 | 127 | 21.01 | 7.46 | 0 | 70.1202 | 212.522 | 13.2265 | 0 | 1005 | 908.871 | 132.472 | 9.4161 | 908.871 | 123.972 | 0.049149 | 907.633 | 119.384 | 0.037035 | 996.242 | 996.239 | 2237310 | 40.1902 | 2251080 | 2108370 | 2053790 | 0 | 0 | 2020160 | 693.924 | 0 | 0 | 0 | 0 | 2020160 | 693.924 | 1977400 | 1937851.875
3062 | 2005-05-08 13:00 | 939 | 942 | 115 | 22.15 | 7.46 | 0 | 61.0676 | 240.041 | 26.4538 | 0 | 939 | 842.927 | 120.973 | 8.7977 | 842.927 | 113.211 | 0.045921 | 837.998 | 109.021 | 0.034602 | 918.642 | 918.638 | 2063030 | 39.8362 | 2067460 | 1938760 | 1888800 | 0 | 0 | 1860100 | 691.709 | 0 | 0 | 0 | 0 | 1860100 | 691.709 | 1823230 | 1786764.375
3063 | 2005-05-08 14:00 | 795 | 902 | 108 | 22.03 | 7.46 | 0 | 49.6257 | 255.398 | 40.5826 | 0 | 795 | 684.872 | 113.704 | 7.4485 | 684.872 | 106.409 | 0.038879 | 674.027 | 102.471 | 0.029296 | 753.231 | 753.224 | 1691560 | 36.5316 | 1677380 | 1595230 | 1555530 | 0 | 0 | 1536310 | 698.343 | 0 | 0 | 0 | 0 | 1536310 | 698.343 | 1509810 | 1479609.25
3064 | 2005-05-08 15:00 | 618 | 862 | 94 | 21.92 | 6.58 | 0 | 37.4494 | 265.868 | 54.8817 | 0 | 618 | 495.74 | 99.3427 | 5.7902 | 495.74 | 92.9687 | 0.030223 | 477.439 | 89.5279 | 0.022773 | 549.98 | 549.976 | 1235100 | 33.1183 | 1202410 | 1160010 | 1130680 | 0 | 0 | 1120490 | 699.773 | 0 | 0 | 0 | 0 | 1120490 | 699.773 | 1103160 | 1081093.875
3065 | 2005-05-08 16:00 | 406 | 744 | 90 | 21.81 | 6.58 | 0 | 25.1113 | 274.402 | 69.1913 | 0 | 406 | 264.525 | 89.3066 | 3.8039 | 264.525 | 83.5766 | 0.019855 | 240.52 | 80.4835 | 0.014961 | 311.388 | 311.385 | 699291 | 28.1503 | 656503 | 647072 | 630689 | 0 | 0 | 627450 | 695.102 | 0 | 0 | 0 | 0 | 627450 | 695.102 | 618192 | 605828.5
3066 | 2005-05-08 17:00 | 172 | 445 | 72 | 21.05 | 6.58 | 0 | 12.9037 | 282.331 | 83.43 | 0 | 172 | 51.2364 | 62.9162 | 1.6115 | 51.2364 | 58.8793 | 0.0084115 | 31.408 | 56.7003 | 0.0063383 | 85.4712 | 85.4674 | 191938 | 22.7902 | 162627 | 164448 | 160195 | 0 | 0 | 159960 | 657.64 | 0 | 0 | 0 | -5.0277 | 159965 | 660.197 | 155419 | 152310.4062
3067 | 2005-05-08 18:00 | 15 | 137 | 7 | 20.28 | 9.21 | 0 | 1.0643 | 290.452 | 90 | 0 | 15 | 0 | 5.2878 | 0.14054 | 0 | 4.9486 | 0.00073356 | 0 | 4.7654 | 0.00055276 | 4.623 | 4.6228 | 10381.8 | 20.3598 | 4436.79 | 4499.16 | 4426.34 | 0 | 0 | 4426.01 | 484.161 | 0 | 0 | 0 | 4426.01 | 0 | 660 | 0 | 0
3068 | 2005-05-08 19:00 | 0 | 0 | 0 | 19.52 | 9.21 | 0
3069 | 2005-05-08 20:00 | 0 | 0 | 0 | 18.36 | 9.21 | 0
3070 | 2005-05-08 21:00 | 0 | 0 | 0 | 17.2 | 9.03 | 0
3071 | 2005-05-08 22:00 | 0 | 0 | 0 | 16.05 | 9.03 | 0
3072 | 2005-05-08 23:00 | 0 | 0 | 0 | 15.27 | 9.03 | 0
3073 | 2005-05-09 | 0 | 0 | 0 | 14.5 | 10.26 | 0
3074 | 2005-05-09 01:00 | 0 | 0 | 0 | 13.73 | 10.26 | 0
3075 | 2005-05-09 02:00 | 0 | 0 | 0 | 13.26 | 10.26 | 0
3076 | 2005-05-09 03:00 | 0 | 0 | 0 | 12.79 | 12.09 | 0
3077 | 2005-05-09 04:00 | 0 | 10 | 0 | 12.32 | 12.09 | 0
3078 | 2005-05-09 05:00 | 67 | 203 | 43 | 12.62 | 12.09 | 0 | 6.6679 | 73.3457 | 90 | 0 | 67 | 0 | 32.9038 | 0.62774 | 0 | 30.7927 | 0.0032766 | 0 | 29.653 | 0.002469 | 28.7658 | 28.7655 | 64600.1 | 13.0367 | 48028.9 | 51114.4 | 49860.8 | 0 | 0 | 49836.6 | 637.976 | 0 | 0 | 0 | 619.215 | 49217.4 | 660 | 47492.5 | 46542.6562
3079 | 2005-05-09 06:00 | 291 | 572 | 107 | 12.92 | 10.4 | 0 | 18.718 | 81.2629 | 76.7004 | 0 | 291 | 131.899 | 98.8711 | 2.7264 | 125.34 | 92.5274 | 0.014231 | 104.364 | 89.103 | 0.010723 | 187.673 | 187.671 | 421471 | 15.9296 | 381990 | 398161 | 375012 | 0 | 0 | 373928 | 718.715 | 0 | 0 | 0 | 0 | 373928 | 718.715 | 366495 | 359164.7188
3080 | 2005-05-09 07:00 | 474 | 692 | 117 | 13.22 | 10.4 | 0 | 31.0261 | 89.321 | 62.4291 | 0 | 474 | 320.58 | 118.518 | 4.441 | 320.58 | 110.914 | 0.023181 | 301.977 | 106.809 | 0.017467 | 396.539 | 396.534 | 890514 | 19.579 | 849372 | 869553 | 846118 | 0 | 0 | 840907 | 734.311 | 0 | 0 | 0 | 0 | 840907 | 734.311 | 826851 | 810313.8125
3081 | 2005-05-09 08:00 | 663 | 678 | 198 | 14.12 | 10.4 | 0 | 43.3472 | 98.4897 | 48.1273 | 0 | 663 | 452.169 | 203.863 | 6.2118 | 452.169 | 190.783 | 0.032424 | 440.906 | 183.722 | 0.024432 | 605.913 | 605.909 | 1360720 | 23.8367 | 1332470 | 1338920 | 1301680 | 0 | 0 | 1289430 | 734.356 | 0 | 0 | 0 | 0 | 1289430 | 734.356 | 1267020 | 1241677.5
3082 | 2005-05-09 09:00 | 577 | 231 | 387 | 15.03 | 10.27 | 0 | 55.3092 | 110.643 | 33.9014 | 0 | 577 | 191.794 | 379.614 | 5.406 | 191.794 | 355.258 | 0.028218 | 189.83 | 342.11 | 0.021263 | 516.002 | 515.981 | 1158760 | 23.3704 | 1123710 | 1131470 | 1098800 | 0 | 0 | 1090020 | 732.791 | 0 | 0 | 0 | 0 | 1090020 | 732.791 | 1071650 | 1050216
3083 | 2005-05-09 10:00 | 687 | 290 | 422 | 15.93 | 10.27 | 0 | 66.0126 | 130.378 | 20.0594 | 0 | 687 | 272.455 | 427.39 | 6.4367 | 272.455 | 399.968 | 0.033597 | 271.575 | 385.165 | 0.025316 | 637.063 | 637.046 | 1430640 | 26.2274 | 1405110 | 1397580 | 1359990 | 0 | 0 | 1346430 | 728.554 | 0 | 0 | 0 | 0 | 1346430 | 728.554 | 1323110 | 1296644.625
3084 | 2005-05-09 11:00 | 925 | 615 | 339 | 16.17 | 10.27 | 0 | 72.6306 | 167.286 | 8.866 | 0 | 925 | 606.662 | 356.359 | 8.6665 | 606.662 | 333.495 | 0.045236 | 606.295 | 321.152 | 0.034086 | 899.657 | 899.645 | 2020380 | 30.7121 | 2022570 | 1974250 | 1921270 | 0 | 0 | 1894030 | 723.058 | 0 | 0 | 0 | 0 | 1894030 | 723.058 | 1855630 | 1818515.625
3085 | 2005-05-09 12:00 | 977 | 842 | 185 | 16.4 | 14.61 | 0 | 70.3499 | 212.917 | 13.3869 | 0 | 977 | 818.125 | 197.952 | 9.1537 | 818.125 | 185.251 | 0.047779 | 816.982 | 178.395 | 0.036003 | 965.551 | 965.536 | 2168350 | 28.4757 | 2178400 | 2146890 | 2089520 | 0 | 0 | 2058160 | 731.684 | 14579.8 | 0 | 0 | 0 | 2043670 | 745.517 | 1999590 | 1959602.25
3086 | 2005-05-09 13:00 | 894 | 849 | 150 | 16.63 | 14.61 | 0 | 61.2352 | 240.467 | 26.5278 | 0 | 894 | 759.375 | 161.604 | 8.3761 | 759.375 | 151.235 | 0.04372 | 754.907 | 145.638 | 0.032944 | 873.56 | 873.551 | 1961770 | 27.5553 | 1960920 | 1939890 | 1887790 | 0 | 0 | 1862200 | 733.471 | 0 | 0 | 0 | 0 | 1862200 | 733.471 | 1824710 | 1788220.625
3087 | 2005-05-09 14:00 | 763 | 725 | 210 | 16.44 | 14.61 | 0 | 49.7622 | 255.749 | 40.6194 | 0 | 763 | 549.871 | 219.332 | 7.1487 | 549.871 | 205.259 | 0.037314 | 541.144 | 197.662 | 0.028117 | 716.669 | 716.657 | 1609430 | 25.4031 | 1591490 | 1588620 | 1546520 | 0 | 0 | 1529250 | 733.644 | 0 | 0 | 0 | 0 | 1529250 | 733.644 | 1501690 | 1471653.125
3088 | 2005-05-09 15:00 | 437 | 246 | 287 | 16.25 | 11.84 | 0 | 37.5749 | 266.162 | 54.8944 | 0 | 437 | 141.461 | 273.757 | 4.0944 | 141.461 | 256.193 | 0.021371 | 136.235 | 246.711 | 0.016104 | 371.473 | 371.459 | 834202 | 21.7112 | 792329 | 803814 | 781735 | 0 | 0 | 777193 | 726.185 | 0 | 0 | 0 | 0 | 777193 | 726.185 | 764518 | 749227.4375
3089 | 2005-05-09 16:00 | 382 | 568 | 139 | 16.06 | 11.84 | 0 | 25.2371 | 274.659 | 69.184 | 0 | 382 | 202.536 | 133.123 | 3.579 | 202.536 | 124.582 | 0.018681 | 184.166 | 119.971 | 0.014077 | 295.027 | 295.022 | 662545 | 20.3974 | 619753 | 632622 | 615388 | 0 | 0 | 612519 | 720.505 | 0 | 0 | 0 | 0 | 612519 | 720.505 | 602703 | 590648.8125
3090 | 2005-05-09 17:00 | 180 | 512 | 64 | 15.59 | 11.84 | 0 | 13.0372 | 282.565 | 83.4034 | 0 | 180 | 59.0726 | 57.0654 | 1.6865 | 59.0726 | 53.4039 | 0.0088027 | 36.3151 | 51.4275 | 0.0066331 | 85.1168 | 85.1146 | 191145 | 16.8414 | 161890 | 168564 | 164198 | 0 | 0 | 163966 | 678.348 | 0 | 0 | 0 | 0 | 163966 | 678.348 | 159078 | 155896.4531
3091 | 2005-05-09 18:00 | 16 | 161 | 6 | 15.11 | 10.65 | 0 | 1.2116 | 290.671 | 90 | 0 | 16 | 0 | 4.7231 | 0.14991 | 0 | 4.4201 | 0.00078247 | 0 | 4.2565 | 0.0005896 | 4.1294 | 4.129 | 9272.67 | 15.1752 | 3695.22 | 3777.07 | 3722.25 | 0 | 0 | 3722.01 | 483.888 | 0 | 0 | 0 | 3722.01 | 0 | 660 | 0 | 0
3092 | 2005-05-09 19:00 | 0 | 0 | 0 | 14.64 | 10.65 | 0
3093 | 2005-05-09 20:00 | 0 | 0 | 0 | 13.66 | 10.65 | 0
3094 | 2005-05-09 21:00 | 0 | 0 | 0 | 12.68 | 7.9 | 0
3095 | 2005-05-09 22:00 | 0 | 0 | 0 | 11.7 | 7.9 | 0
3096 | 2005-05-09 23:00 | 0 | 0 | 0 | 10.92 | 7.9 | 0
3097 | 2005-05-10 | 0 | 0 | 0 | 10.14 | 9.64 | 0
3098 | 2005-05-10 01:00 | 0 | 0 | 0 | 9.35 | 9.64 | 0
3099 | 2005-05-10 02:00 | 0 | 0 | 0 | 8.62 | 9.64 | 0
3100 | 2005-05-10 03:00 | 0 | 0 | 0 | 7.89 | 8.06 | 0
3101 | 2005-05-10 04:00 | 0 | 18 | 0 | 7.16 | 8.06 | 0
3102 | 2005-05-10 05:00 | 79 | 307 | 42 | 7.54 | 8.06 | 0 | 6.8225 | 73.1326 | 90 | 0 | 79 | 0 | 32.0171 | 0.74017 | 0 | 29.9628 | 0.0038634 | 0 | 28.8539 | 0.0029112 | 27.9911 | 27.9906 | 62859.9 | 8.0589 | 46539.3 | 50746 | 49426.4 | 0 | 0 | 49403.8 | 654.23 | 0 | 0 | 0 | 30.974 | 49372.8 | 660 | 47642.9 | 46690.0625
3103 | 2005-05-10 06:00 | 294 | 658 | 81 | 7.92 | 8.29 | 0 | 18.8619 | 81.0317 | 76.6643 | 0 | 294 | 151.969 | 76.628 | 2.7546 | 144.83 | 71.7114 | 0.014378 | 120.676 | 69.0575 | 0.010834 | 184.052 | 184.017 | 413265 | 11.2823 | 374073 | 397967 | 371660 | 0 | 0 | 370633 | 734.25 | 0 | 0 | 0 | 0 | 370633 | 734.25 | 362771 | 355515.7188
3104 | 2005-05-10 07:00 | 512 | 820 | 87 | 8.3 | 8.29 | 0 | 31.1654 | 89.0623 | 62.4123 | 0 | 512 | 380.321 | 89.9032 | 4.797 | 380.321 | 84.1348 | 0.025039 | 358.275 | 81.021 | 0.018867 | 426.135 | 426.133 | 956985 | 16.0862 | 916977 | 952489 | 926974 | 0 | 0 | 920968 | 748.895 | 0 | 0 | 0 | 0 | 920968 | 748.895 | 904939 | 886840.625
3105 | 2005-05-10 08:00 | 712 | 891 | 99 | 9.59 | 8.29 | 0 | 43.4902 | 98.1883 | 48.1319 | 0 | 712 | 594.462 | 103.96 | 6.6709 | 594.462 | 97.29 | 0.03482 | 579.651 | 93.6894 | 0.026237 | 653.165 | 653.159 | 1466830 | 21.5244 | 1442750 | 1463730 | 1424580 | 0 | 0 | 1410270 | 743.173 | 0 | 0 | 0 | 0 | 1410270 | 743.173 | 1384930 | 1357234.375
3106 | 2005-05-10 09:00 | 873 | 927 | 110 | 10.89 | 6.97 | 0 | 55.4695 | 110.28 | 33.9349 | 0 | 873 | 768.416 | 115.692 | 8.1793 | 768.416 | 108.269 | 0.042693 | 760.528 | 104.262 | 0.03217 | 838.878 | 838.872 | 1883900 | 27.5509 | 1879090 | 1858790 | 1807810 | 0 | 0 | 1784270 | 732.778 | 0 | 0 | 0 | 0 | 1784270 | 732.778 | 1749250 | 1714266.375
3107 | 2005-05-10 10:00 | 986 | 950 | 118 | 12.18 | 6.97 | 0 | 66.2142 | 129.968 | 20.1462 | 0 | 986 | 890.535 | 123.504 | 9.238 | 890.535 | 115.58 | 0.048219 | 887.633 | 111.302 | 0.036334 | 969.003 | 968.992 | 2176100 | 31.4252 | 2186560 | 2128040 | 2071040 | 0 | 0 | 2039390 | 722.556 | 1650 | 0 | 0 | 0 | 2037670 | 724.627 | 1994360 | 1954475.125
3108 | 2005-05-10 11:00 | 1037 | 959 | 122 | 13.4 | 6.97 | 0 | 72.8881 | 167.146 | 9.0971 | 0 | 1037 | 945.339 | 127.015 | 9.7159 | 945.339 | 118.866 | 0.050714 | 944.737 | 114.466 | 0.038214 | 1027.46 | 1027.46 | 2307410 | 33.8064 | 2325020 | 2240030 | 2178840 | 0 | 0 | 2143250 | 715.876 | 96058.2 | 0 | 0 | 0 | 2044860 | 752.288 | 1999980 | 1959976.125
3109 | 2005-05-10 12:00 | 1021 | 956 | 121 | 14.62 | 6.13 | 0 | 70.5756 | 213.307 | 13.5458 | 0 | 1021 | 927.773 | 126.203 | 9.566 | 927.773 | 118.105 | 0.049931 | 926.445 | 113.734 | 0.037624 | 1009.01 | 1009.01 | 2265960 | 35.7662 | 2281300 | 2179120 | 2122270 | 0 | 0 | 2087720 | 707.736 | 42507.3 | 0 | 0 | 0 | 2043450 | 733.55 | 1999980 | 1959977.25
3110 | 2005-05-10 13:00 | 941 | 942 | 115 | 15.85 | 6.13 | 0 | 61.4 | 240.887 | 26.6006 | 0 | 941 | 841.209 | 120.656 | 8.8164 | 841.209 | 112.915 | 0.046019 | 836.23 | 108.736 | 0.034676 | 916.651 | 916.646 | 2058550 | 35.0606 | 2062740 | 1975880 | 1924890 | 0 | 0 | 1896420 | 708.223 | 0 | 0 | 0 | 0 | 1896420 | 708.223 | 1858080 | 1820922.5
3111 | 2005-05-10 14:00 | 804 | 913 | 106 | 16.01 | 6.13 | 0 | 49.897 | 256.094 | 40.6548 | 0 | 804 | 692.307 | 111.443 | 7.5328 | 692.307 | 104.292 | 0.039319 | 681.294 | 100.433 | 0.029628 | 758.304 | 758.295 | 1702940 | 31.9019 | 1689300 | 1639890 | 1597530 | 0 | 0 | 1578120 | 713.703 | 0 | 0 | 0 | 0 | 1578120 | 713.703 | 1549850 | 1518852.375
3112 | 2005-05-10 15:00 | 621 | 862 | 94 | 16.17 | 10.1 | 0 | 37.6993 | 266.45 | 54.9055 | 0 | 621 | 495.466 | 99.0378 | 5.8183 | 495.466 | 92.6833 | 0.03037 | 477.15 | 89.2532 | 0.022884 | 549.433 | 549.435 | 1233890 | 25.144 | 1201160 | 1200290 | 1166350 | 0 | 0 | 1156350 | 728.956 | 0 | 0 | 0 | 0 | 1156350 | 728.956 | 1136870 | 1114135.625
3113 | 2005-05-10 16:00 | 401 | 732 | 87 | 16.32 | 10.1 | 0 | 25.362 | 274.911 | 69.1752 | 0 | 401 | 260.615 | 86.1204 | 3.7571 | 260.615 | 80.5947 | 0.019611 | 236.992 | 77.612 | 0.014777 | 305.18 | 305.174 | 685343 | 21.3045 | 642538 | 653217 | 637220 | 0 | 0 | 634109 | 716.493 | 0 | 0 | 0 | 0 | 634109 | 716.493 | 624074 | 611592.6875
3114 | 2005-05-10 17:00 | 178 | 488 | 66 | 16.02 | 10.1 | 0 | 13.1698 | 282.794 | 83.3754 | 0 | 178 | 56.7101 | 58.8167 | 1.6677 | 56.7101 | 55.0429 | 0.0087049 | 34.9667 | 53.0058 | 0.0065594 | 85.3397 | 85.3354 | 191642 | 17.4138 | 162352 | 168577 | 164242 | 0 | 0 | 164010 | 678.828 | 0 | 0 | 0 | 0 | 164010 | 678.828 | 159115 | 155932.3438
3115 | 2005-05-10 18:00 | 16 | 157 | 6 | 15.71 | 8.78 | 0 | 1.3578 | 290.886 | 90 | 0 | 16 | 0 | 4.6856 | 0.14991 | 0 | 4.385 | 0.00078247 | 0 | 4.2227 | 0.0005896 | 4.0966 | 4.0963 | 9199.3 | 15.7826 | 3647.07 | 3722.2 | 3668.59 | 0 | 0 | 3668.36 | 481.047 | 0 | 0 | 0 | 3668.36 | 0 | 660 | 0 | 0
3116 | 2005-05-10 19:00 | 0 | 0 | 0 | 15.4 | 8.78 | 0
3117 | 2005-05-10 20:00 | 0 | 0 | 0 | 14.33 | 8.78 | 0
3118 | 2005-05-10 21:00 | 0 | 0 | 0 | 13.26 | 8 | 0
3119 | 2005-05-10 22:00 | 0 | 0 | 0 | 12.19 | 8 | 0
3120 | 2005-05-10 23:00 | 0 | 0 | 0 | 11.63 | 8 | 0
3121 | 2005-05-11 | 0 | 0 | 0 | 11.06 | 8.71 | 0
3122 | 2005-05-11 01:00 | 0 | 0 | 0 | 10.49 | 8.71 | 0
3123 | 2005-05-11 02:00 | 0 | 0 | 0 | 9.83 | 8.71 | 0
3124 | 2005-05-11 03:00 | 0 | 0 | 0 | 9.17 | 5.85 | 0
3125 | 2005-05-11 04:00 | 1 | 20 | 1 | 8.52 | 5.85 | 0 | -4.5403 | 64.4864 | 90 | 0 | 1 | 0 | 1.0023 | 0.0093692 | 0 | 0.93795 | 0 | 0 | 0.90324 | 0 | 0.87614 | 0.87608 | 1967.46 | 8.5387 | 187.525 | 183.879 | 183.006 | 0 | 0 | 182.998 | 129.817 | 0 | 0 | 0 | 182.998 | 0 | 660 | 0 | 0
3126 | 2005-05-11 05:00 | 81 | 305 | 43 | 9.06 | 5.85 | 0 | 6.9723 | 72.9222 | 90 | 0 | 81 | 0 | 32.7494 | 0.75891 | 0 | 30.6482 | 0.0039612 | 0 | 29.5139 | 0.0029849 | 28.6314 | 28.6298 | 64295.4 | 9.6709 | 47767.4 | 51681.1 | 50406.3 | 0 | 0 | 50382.4 | 649.62 | 0 | 0 | 0 | 112.393 | 50270 | 660 | 48511.4 | 47541.1484
3127 | 2005-05-11 06:00 | 296 | 659 | 81 | 9.61 | 2.28 | 0 | 19.001 | 80.8034 | 76.6313 | 0 | 296 | 152.684 | 76.5034 | 2.7733 | 145.965 | 71.5948 | 0.014476 | 121.699 | 68.9451 | 0.010908 | 184.935 | 184.948 | 415355 | 14.5978 | 376092 | 394279 | 368026 | 0 | 0 | 366985 | 722.407 | 0 | 0 | 0 | 0 | 366985 | 722.407 | 359452 | 352262.625
3128 | 2005-05-11 07:00 | 508 | 806 | 89 | 10.16 | 2.28 | 0 | 31.2997 | 88.8065 | 62.3985 | 0 | 508 | 373.677 | 91.7385 | 4.7596 | 373.677 | 85.8524 | 0.024843 | 352.035 | 82.6751 | 0.01872 | 421.687 | 421.682 | 946988 | 21.5323 | 906794 | 920453 | 895142 | 0 | 0 | 889247 | 730.244 | 0 | 0 | 0 | 0 | 889247 | 730.244 | 874563 | 857072.125
3129 | 2005-05-11 08:00 | 714 | 891 | 99 | 11.89 | 2.28 | 0 | 43.6279 | 97.8897 | 48.1396 | 0 | 714 | 594.807 | 103.836 | 6.6896 | 594.807 | 97.1735 | 0.034918 | 579.981 | 93.5772 | 0.026311 | 653.377 | 653.37 | 1467300 | 29.5106 | 1443230 | 1415270 | 1378190 | 0 | 0 | 1363820 | 717.3 | 0 | 0 | 0 | 0 | 1363820 | 717.3 | 1340620 | 1313810.125
3130 | 2005-05-11 09:00 | 876 | 929 | 110 | 13.62 | 2.43 | 0 | 55.6239 | 109.919 | 33.9716 | 0 | 876 | 769.68 | 115.549 | 8.2074 | 769.68 | 108.135 | 0.04284 | 761.76 | 104.133 | 0.032281 | 839.947 | 839.944 | 1886300 | 36.0471 | 1881600 | 1793920 | 1746700 | 0 | 0 | 1722860 | 703.038 | 0 | 0 | 0 | 0 | 1722860 | 703.038 | 1690420 | 1656614.875
3131 | 2005-05-11 10:00 | 987 | 951 | 116 | 15.36 | 2.43 | 0 | 66.4095 | 129.556 | 20.2361 | 0 | 987 | 891.763 | 121.364 | 9.2474 | 891.763 | 113.577 | 0.048268 | 888.83 | 109.373 | 0.036371 | 968.292 | 968.291 | 2174540 | 41.2141 | 2184920 | 2036490 | 1985330 | 0 | 0 | 1953580 | 690.47 | 0 | 0 | 0 | 0 | 1953580 | 690.47 | 1913330 | 1875060.5
3132 | 2005-05-11 11:00 | 1031 | 949 | 125 | 16.65 | 2.43 | 0 | 73.1402 | 166.997 | 9.3262 | 0 | 1031 | 934.177 | 129.772 | 9.6597 | 934.177 | 121.446 | 0.05042 | 933.552 | 116.951 | 0.037993 | 1019.02 | 1019.02 | 2288450 | 43.8586 | 2305020 | 2123220 | 2071700 | 0 | 0 | 2036250 | 681.773 | 201.523 | 0 | 0 | 0 | 2036030 | 683.186 | 1992620 | 1952771.75
3133 | 2005-05-11 12:00 | 1022 | 956 | 121 | 17.94 | 2.98 | 0 | 70.7972 | 213.692 | 13.7029 | 0 | 1022 | 926.929 | 126.027 | 9.5753 | 926.929 | 117.941 | 0.04998 | 925.571 | 113.576 | 0.037661 | 1008.01 | 1008.01 | 2263730 | 43.889 | 2278940 | 2098770 | 2048790 | 0 | 0 | 2014100 | 681.308 | 0 | 0 | 0 | 0 | 2014100 | 681.308 | 1971550 | 1932117.875
3134 | 2005-05-11 13:00 | 943 | 942 | 115 | 19.23 | 2.98 | 0 | 61.562 | 241.301 | 26.6721 | 0 | 943 | 841.425 | 120.502 | 8.8352 | 841.425 | 112.771 | 0.046117 | 836.415 | 108.597 | 0.03475 | 916.696 | 916.69 | 2058660 | 42.8283 | 2062850 | 1908030 | 1861100 | 0 | 0 | 1832530 | 682.723 | 0 | 0 | 0 | 0 | 1832530 | 682.723 | 1796760 | 1760829
3135 | 2005-05-11 14:00 | 801 | 904 | 108 | 19.47 | 2.98 | 0 | 50.03 | 256.433 | 40.6886 | 0 | 801 | 685.659 | 113.283 | 7.5047 | 685.659 | 106.014 | 0.039172 | 674.73 | 102.091 | 0.029517 | 753.545 | 753.538 | 1692260 | 38.8683 | 1678120 | 1579020 | 1538710 | 0 | 0 | 1519480 | 690.492 | 0 | 0 | 0 | 0 | 1519480 | 690.492 | 1493760 | 1463885.375
3136 | 2005-05-11 15:00 | 623 | 821 | 119 | 19.72 | 2.75 | 0 | 37.8224 | 266.733 | 54.9151 | 0 | 623 | 472.417 | 123.561 | 5.837 | 472.417 | 115.633 | 0.030467 | 454.943 | 111.353 | 0.022958 | 549.33 | 549.323 | 1233640 | 34.0786 | 1200900 | 1153470 | 1124350 | 0 | 0 | 1114170 | 696.508 | 0 | 0 | 0 | 0 | 1114170 | 696.508 | 1097120 | 1075176.625
3137 | 2005-05-11 16:00 | 388 | 694 | 89 | 19.97 | 2.75 | 0 | 25.4859 | 275.158 | 69.1649 | 0 | 388 | 247.156 | 87.8928 | 3.6353 | 247.156 | 82.2534 | 0.018975 | 224.769 | 79.2093 | 0.014298 | 294.873 | 294.87 | 662206 | 27.6775 | 619412 | 611798 | 595711 | 0 | 0 | 592830 | 696.154 | 0 | 0 | 0 | 0 | 592830 | 696.154 | 584011 | 572330.8125
3138 | 2005-05-11 17:00 | 180 | 500 | 64 | 19.75 | 2.75 | 0 | 13.3015 | 283.018 | 83.346 | 0 | 180 | 58.4219 | 56.8386 | 1.6865 | 58.4219 | 53.1917 | 0.0088027 | 36.1338 | 51.2231 | 0.0066331 | 84.7426 | 84.7409 | 190307 | 21.965 | 161112 | 163593 | 159362 | 0 | 0 | 159132 | 661.718 | 0 | 0 | 0 | -3.4489 | 159136 | 662.008 | 154579 | 151487.7344
3139 | 2005-05-11 18:00 | 17 | 164 | 6 | 19.54 | 4.4 | 0 | 1.503 | 291.095 | 90 | 0 | 17 | 0 | 4.6506 | 0.15928 | 0 | 4.3522 | 0.00083137 | 0 | 4.1911 | 0.00062646 | 4.066 | 4.0657 | 9130.55 | 19.6353 | 3601.91 | 3647.25 | 3596.09 | 0 | 0 | 3595.86 | 468.889 | 0 | 0 | 0 | 3595.86 | 0 | 660 | 0 | 0
3140 | 2005-05-11 19:00 | 0 | 0 | 0 | 19.32 | 4.4 | 0
3141 | 2005-05-11 20:00 | 0 | 0 | 0 | 18.29 | 4.4 | 0
3142 | 2005-05-11 21:00 | 0 | 0 | 0 | 17.26 | 4.23 | 0
3143 | 2005-05-11 22:00 | 0 | 0 | 0 | 16.22 | 4.23 | 0
3144 | 2005-05-11 23:00 | 0 | 0 | 0 | 15.45 | 4.23 | 0
3145 | 2005-05-12 | 0 | 0 | 0 | 14.67 | 1.99 | 0
3146 | 2005-05-12 01:00 | 0 | 0 | 0 | 13.9 | 1.99 | 0
3147 | 2005-05-12 02:00 | 0 | 0 | 0 | 13.31 | 1.99 | 0
3148 | 2005-05-12 03:00 | 0 | 0 | 0 | 12.72 | 3.97 | 0
3149 | 2005-05-12 04:00 | 1 | 26 | 1 | 12.14 | 3.97 | 0 | -4.3793 | 64.2916 | 90 | 0 | 1 | 0 | 1.0021 | 0.0093692 | 0 | 0.93781 | 0 | 0 | 0.9031 | 0 | 0.87601 | 0.87597 | 1967.21 | 12.1611 | 187.48 | 184.638 | 183.77 | 0 | 0 | 183.762 | 129.89 | 0 | 0 | 0 | 183.762 | 0 | 660 | 0 | 0
3150 | 2005-05-12 05:00 | 87 | 363 | 41 | 12.55 | 3.97 | 0 | 7.1174 | 72.7145 | 90 | 0 | 87 | 0 | 32.4775 | 0.81512 | 0 | 30.3936 | 0.0042547 | 0 | 29.2688 | 0.003206 | 28.3938 | 28.3929 | 63763.1 | 13.2347 | 47311.8 | 50302.1 | 49048.4 | 0 | 0 | 49024.9 | 637.55 | 0 | 0 | 0 | 692.18 | 48332.7 | 660 | 46636.3 | 45703.5273
3151 | 2005-05-12 06:00 | 297 | 659 | 80 | 12.96 | 1.8 | 0 | 19.1353 | 80.578 | 76.6013 | 0 | 297 | 153.4 | 75.445 | 2.7827 | 147.08 | 70.6043 | 0.014524 | 122.698 | 67.9913 | 0.010944 | 184.979 | 184.971 | 415403 | 18.111 | 376124 | 388142 | 361805 | 0 | 0 | 360766 | 710.232 | 0 | 0 | 0 | 0 | 360766 | 710.232 | 353551 | 346479.6562
3152 | 2005-05-12 07:00 | 497 | 744 | 109 | 13.37 | 1.8 | 0 | 31.4291 | 88.5538 | 62.3877 | 0 | 497 | 344.875 | 110.263 | 4.6565 | 344.875 | 103.189 | 0.024305 | 324.915 | 99.3696 | 0.018315 | 411.573 | 411.571 | 924287 | 24.8312 | 883691 | 884228 | 859401 | 0 | 0 | 853814 | 719.965 | 0 | 0 | 0 | 0 | 853814 | 719.965 | 840154 | 823351
3153 | 2005-05-12 08:00 | 700 | 858 | 107 | 15.4 | 1.8 | 0 | 43.7603 | 97.5941 | 48.1503 | 0 | 700 | 572.025 | 113.544 | 6.5584 | 572.025 | 106.258 | 0.034233 | 557.758 | 102.326 | 0.025795 | 640.306 | 640.305 | 1437960 | 33.2309 | 1412710 | 1362720 | 1329420 | 0 | 0 | 1315540 | 703.473 | 0 | 0 | 0 | 0 | 1315540 | 703.473 | 1293990 | 1268108.375
3154 | 2005-05-12 09:00 | 858 | 892 | 121 | 17.42 | 2.35 | 0 | 55.7725 | 109.559 | 34.0113 | 0 | 858 | 738.887 | 126.23 | 8.0388 | 738.887 | 118.131 | 0.04196 | 731.263 | 113.759 | 0.031618 | 819.702 | 819.697 | 1840830 | 39.4234 | 1833860 | 1721860 | 1678480 | 0 | 0 | 1655710 | 691.117 | 0 | 0 | 0 | 0 | 1655710 | 691.117 | 1625760 | 1593240.375
3155 | 2005-05-12 10:00 | 986 | 903 | 158 | 19.44 | 2.35 | 0 | 66.5984 | 129.142 | 20.3289 | 0 | 986 | 846.018 | 161.826 | 9.238 | 846.018 | 151.443 | 0.048219 | 843.208 | 145.838 | 0.036334 | 959.41 | 959.402 | 2154570 | 45.1936 | 2163870 | 1980160 | 1933300 | 0 | 0 | 1901840 | 675.597 | 0 | 0 | 0 | 0 | 1901840 | 675.597 | 1863630 | 1826352.625
3156 | 2005-05-12 11:00 | 998 | 847 | 188 | 20.83 | 2.35 | 0 | 73.3868 | 166.84 | 9.553 | 0 | 998 | 833.563 | 200.365 | 9.3505 | 833.563 | 187.509 | 0.048806 | 832.977 | 180.569 | 0.036777 | 983.176 | 983.172 | 2207960 | 47.2216 | 2220140 | 2012750 | 1963870 | 0 | 0 | 1930860 | 669.523 | 0 | 0 | 0 | 0 | 1930860 | 669.523 | 1891580 | 1853749.125
3157 | 2005-05-12 12:00 | 972 | 825 | 193 | 22.21 | 3.73 | 0 | 71.0146 | 214.073 | 13.858 | 0 | 972 | 799.835 | 204.922 | 9.1069 | 799.835 | 191.774 | 0.047535 | 798.636 | 184.676 | 0.035819 | 953.848 | 953.836 | 2142070 | 45.578 | 2150700 | 1964540 | 1915630 | 0 | 0 | 1884600 | 674.031 | 0 | 0 | 0 | 0 | 1884600 | 674.031 | 1847050 | 1810107.375
3158 | 2005-05-12 13:00 | 944 | 893 | 158 | 23.6 | 3.73 | 0 | 61.7212 | 241.708 | 26.7421 | 0 | 944 | 797.057 | 168.896 | 8.8445 | 797.057 | 158.059 | 0.046165 | 792.284 | 152.21 | 0.034787 | 916.193 | 916.186 | 2057520 | 46.0456 | 2061660 | 1878580 | 1834890 | 0 | 0 | 1806140 | 671.199 | 0 | 0 | 0 | 0 | 1806140 | 671.199 | 1771520 | 1736086.25
3159 | 2005-05-12 14:00 | 803 | 822 | 172 | 24.03 | 3.73 | 0 | 50.1613 | 256.765 | 40.721 | 0 | 803 | 622.819 | 179.222 | 7.5235 | 622.819 | 167.723 | 0.03927 | 612.871 | 161.515 | 0.029591 | 751.184 | 751.178 | 1686960 | 42.4331 | 1672570 | 1548090 | 1510290 | 0 | 0 | 1491110 | 678.23 | 0 | 0 | 0 | 0 | 1491110 | 678.23 | 1466640 | 1437307.25
3160 | 2005-05-12 15:00 | 543 | 531 | 216 | 24.46 | 2.14 | 0 | 37.9443 | 267.009 | 54.9232 | 0 | 543 | 305.611 | 213.779 | 5.0875 | 305.611 | 200.063 | 0.026555 | 294.301 | 192.658 | 0.02001 | 472.37 | 472.354 | 1060790 | 37.3184 | 1023070 | 967415 | 943721 | 0 | 0 | 936205 | 680.248 | 0 | 0 | 0 | 0 | 936205 | 680.248 | 923087 | 904625.0625
3161 | 2005-05-12 16:00 | 406 | 693 | 106 | 24.89 | 2.14 | 0 | 25.6087 | 275.398 | 69.153 | 0 | 406 | 247.007 | 103.93 | 3.8039 | 247.007 | 97.2621 | 0.019855 | 224.653 | 93.6625 | 0.014961 | 308.78 | 308.775 | 693432 | 33.2954 | 650636 | 625956 | 610411 | 0 | 0 | 607230 | 678.159 | 0 | 0 | 0 | 0 | 607230 | 678.159 | 598784 | 586808.5
3162 | 2005-05-12 17:00 | 188 | 529 | 64 | 24.69 | 2.14 | 0 | 13.4321 | 283.236 | 83.3151 | 0 | 188 | 62.1403 | 56.7311 | 1.7614 | 62.1403 | 53.0912 | 0.009194 | 38.5569 | 51.1263 | 0.0069279 | 86.9995 | 86.9961 | 195372 | 27.0582 | 165816 | 164069 | 160000 | 0 | 0 | 159756 | 643.855 | 0 | 0 | 0 | 1174.2 | 158582 | 660 | 154065 | 150983.3906
3163 | 2005-05-12 18:00 | 18 | 177 | 6 | 24.5 | 4.06 | 0 | 1.6469 | 291.298 | 90 | 0 | 18 | 0 | 4.6178 | 0.16865 | 0 | 4.3215 | 0.00088028 | 0 | 4.1615 | 0.00066331 | 4.0373 | 4.0371 | 9066.27 | 24.5968 | 3559.91 | 3563.37 | 3512.86 | 0 | 0 | 3512.62 | 453.614 | 0 | 0 | 0 | 3512.62 | 0 | 660 | 0 | 0
3164 | 2005-05-12 19:00 | 0 | 0 | 0 | 24.3 | 4.06 | 0
3165 | 2005-05-12 20:00 | 0 | 0 | 0 | 23.38 | 4.06 | 0
3166 | 2005-05-12 21:00 | 0 | 0 | 0 | 22.47 | 3.38 | 0
3167 | 2005-05-12 22:00 | 0 | 0 | 0 | 21.55 | 3.38 | 0
3168 | 2005-05-12 23:00 | 0 | 0 | 0 | 20.61 | 3.38 | 0
3169 | 2005-05-13 | 0 | 0 | 0 | 19.67 | 1.76 | 0
3170 | 2005-05-13 01:00 | 0 | 0 | 0 | 18.74 | 1.76 | 0
3171 | 2005-05-13 02:00 | 0 | 0 | 0 | 17.97 | 1.76 | 0
3172 | 2005-05-13 03:00 | 0 | 0 | 0 | 17.2 | 1.11 | 0
3173 | 2005-05-13 04:00 | 1 | 29 | 1 | 16.44 | 1.11 | 0 | -4.2233 | 64.0995 | 90 | 0 | 1 | 0 | 1.002 | 0.0093692 | 0 | 0.93768 | 0 | 0 | 0.90297 | 0 | 0.87589 | 0.87585 | 1966.95 | 16.4655 | 187.44 | 185.554 | 184.676 | 0 | 0 | 184.668 | 130.068 | 0 | 0 | 0 | 184.668 | 0 | 660 | 0 | 0
3174 | 2005-05-13 05:00 | 89 | 364 | 42 | 16.42 | 1.11 | 0 | 7.2576 | 72.5097 | 90 | 0 | 89 | 0 | 33.2846 | 0.83386 | 0 | 31.149 | 0.0043525 | 0 | 29.9962 | 0.0032797 | 29.0995 | 29.0985 | 65348 | 17.2687 | 48670 | 50701.1 | 49426.4 | 0 | 0 | 49401.5 | 624.337 | 0 | 0 | 0 | 1988.38 | 47413.2 | 660 | 45746.4 | 44831.4375
3175 | 2005-05-13 06:00 | 287 | 628 | 79 | 16.41 | 2.27 | 0 | 19.2646 | 80.3557 | 76.5744 | 0 | 287 | 146.376 | 74.3893 | 2.689 | 140.691 | 69.6164 | 0.014035 | 117.428 | 67.0399 | 0.010576 | 178.944 | 178.936 | 401850 | 21.2389 | 362915 | 369228 | 345082 | 0 | 0 | 344101 | 696.771 | 0 | 0 | 0 | 0 | 344101 | 696.771 | 337212 | 330467.5312
3176 | 2005-05-13 07:00 | 513 | 775 | 107 | 16.4 | 2.27 | 0 | 31.5534 | 88.3043 | 62.3799 | 0 | 513 | 359.693 | 108.161 | 4.8064 | 359.693 | 101.221 | 0.025088 | 338.885 | 97.475 | 0.018904 | 423.287 | 423.283 | 950584 | 27.8231 | 910457 | 899011 | 875782 | 0 | 0 | 869798 | 708.787 | 0 | 0 | 0 | 0 | 869798 | 708.787 | 856369 | 839241.4375
3177 | 2005-05-13 08:00 | 717 | 891 | 99 | 18.57 | 2.27 | 0 | 43.8873 | 97.3018 | 48.1639 | 0 | 717 | 594.608 | 103.594 | 6.7177 | 594.608 | 96.9472 | 0.035064 | 579.765 | 93.3593 | 0.026422 | 652.956 | 652.953 | 1466360 | 36.1911 | 1442260 | 1372890 | 1338320 | 0 | 0 | 1323930 | 695.471 | 0 | 0 | 0 | 0 | 1323930 | 695.471 | 1302550 | 1276503.125
3178 | 2005-05-13 09:00 | 860 | 829 | 174 | 20.74 | 3.43 | 0 | 55.9152 | 109.202 | 34.0538 | 0 | 860 | 686.251 | 182.88 | 8.0575 | 686.251 | 171.146 | 0.042058 | 679.149 | 164.812 | 0.031691 | 818.673 | 818.662 | 1838500 | 41.1969 | 1831420 | 1705680 | 1661950 | 0 | 0 | 1639290 | 685.919 | 0 | 0 | 0 | 0 | 1639290 | 685.919 | 1610010 | 1577809.125
3179 | 2005-05-13 10:00 | 887 | 635 | 304 | 22.91 | 3.43 | 0 | 66.7809 | 128.726 | 20.4242 | 0 | 887 | 594.502 | 316.888 | 8.3105 | 594.502 | 296.556 | 0.043378 | 592.508 | 285.58 | 0.032686 | 851.777 | 851.769 | 1912870 | 44.1942 | 1909520 | 1754240 | 1709180 | 0 | 0 | 1684560 | 676.201 | 0 | 0 | 0 | 0 | 1684560 | 676.201 | 1654060 | 1620982.125
3180 | 2005-05-13 11:00 | 962 | 711 | 281 | 24.13 | 3.43 | 0 | 73.6278 | 166.674 | 9.777 | 0 | 962 | 699.472 | 298.005 | 9.0132 | 699.472 | 278.884 | 0.047046 | 698.957 | 268.563 | 0.03545 | 938.528 | 938.526 | 2107690 | 47.5821 | 2114490 | 1913080 | 1869940 | 0 | 0 | 1839770 | 667.247 | 0 | 0 | 0 | 0 | 1839770 | 667.247 | 1803970 | 1767893.375
3181 | 2005-05-13 12:00 | 766 | 378 | 409 | 25.34 | 4.93 | 0 | 71.2278 | 214.447 | 14.0108 | 0 | 766 | 365.84 | 414.98 | 7.1768 | 365.84 | 388.354 | 0.037461 | 365.279 | 373.981 | 0.028227 | 717.11 | 717.094 | 1610410 | 41.5812 | 1592530 | 1479440 | 1442500 | 0 | 0 | 1425030 | 679.338 | 0 | 0 | 0 | 0 | 1425030 | 679.338 | 1402080 | 1374039.625
3182 | 2005-05-13 13:00 | 589 | 208 | 406 | 26.55 | 4.93 | 0 | 61.8776 | 242.107 | 26.8104 | 0 | 589 | 185.191 | 399.741 | 5.5185 | 185.191 | 374.093 | 0.028805 | 184.076 | 360.248 | 0.021705 | 528.016 | 527.997 | 1185750 | 38.5084 | 1151510 | 1083400 | 1056210 | 0 | 0 | 1046800 | 679.955 | 0 | 0 | 0 | 0 | 1046800 | 679.955 | 1031910 | 1011267
3183 | 2005-05-13 14:00 | 746 | 634 | 258 | 26.77 | 4.93 | 0 | 50.2907 | 257.09 | 40.7517 | 0 | 746 | 480.546 | 263.448 | 6.9894 | 480.546 | 246.545 | 0.036483 | 472.856 | 237.421 | 0.02749 | 688.995 | 688.99 | 1547300 | 42.3746 | 1526620 | 1412650 | 1377720 | 0 | 0 | 1361540 | 674.788 | 0 | 0 | 0 | 0 | 1361540 | 674.788 | 1340250 | 1313441.25
3184 | 2005-05-13 15:00 | 528 | 563 | 181 | 26.98 | 1.85 | 0 | 38.065 | 267.279 | 54.9296 | 0 | 528 | 323.378 | 180.375 | 4.947 | 323.378 | 168.802 | 0.025821 | 311.407 | 162.555 | 0.019457 | 459.762 | 459.751 | 1032480 | 39.7402 | 994080 | 929110 | 905750 | 0 | 0 | 898631 | 671.245 | 0 | 0 | 0 | 0 | 898631 | 671.245 | 886443 | 868714.25
3185 | 2005-05-13 16:00 | 348 | 528 | 118 | 27.2 | 1.85 | 0 | 25.7306 | 275.634 | 69.1396 | 0 | 348 | 188.651 | 115.083 | 3.2605 | 188.651 | 107.699 | 0.017019 | 171.595 | 103.713 | 0.012824 | 267.061 | 267.057 | 599742 | 34.612 | 557198 | 532352 | 519765 | 0 | 0 | 517379 | 667.444 | 0 | 0 | 0 | 0 | 517379 | 667.444 | 510207 | 500002.9375
3186 | 2005-05-13 17:00 | 184 | 362 | 99 | 26.86 | 1.85 | 0 | 13.5618 | 283.449 | 83.2828 | 0 | 184 | 42.3995 | 85.8026 | 1.7239 | 42.3995 | 80.2974 | 0.0089984 | 26.3953 | 77.3256 | 0.0067805 | 100.616 | 100.613 | 225952 | 29.6525 | 194385 | 189810 | 185138 | 0 | 0 | 184809 | 641.994 | 0 | 0 | 0 | 1870.49 | 182939 | 660 | 177995 | 174435.2656
3187 | 2005-05-13 18:00 | 19 | 123 | 10 | 26.53 | 4.93 | 0 | 1.7896 | 291.496 | 90 | 0 | 19 | 0 | 7.6648 | 0.17802 | 0 | 7.173 | 0.00092918 | 0 | 6.9075 | 0.00070016 | 6.701 | 6.7004 | 15047.5 | 26.6818 | 7736.05 | 7677.17 | 7533 | 0 | 0 | 7532.11 | 502.352 | 0 | 0 | 0 | 7532.11 | 0 | 660 | 0 | 0
3188 | 2005-05-13 19:00 | 0 | 0 | 0 | 26.19 | 4.93 | 0
3189 | 2005-05-13 20:00 | 0 | 0 | 0 | 25.05 | 4.93 | 0
3190 | 2005-05-13 21:00 | 0 | 0 | 0 | 23.91 | 4.2 | 0
3191 | 2005-05-13 22:00 | 0 | 0 | 0 | 22.77 | 4.2 | 0
3192 | 2005-05-13 23:00 | 0 | 0 | 0 | 21.9 | 4.2 | 0
3193 | 2005-05-14 | 0 | 0 | 0 | 21.03 | 3.53 | 0
3194 | 2005-05-14 01:00 | 0 | 0 | 0 | 20.15 | 3.53 | 0
3195 | 2005-05-14 02:00 | 0 | 0 | 0 | 19.27 | 3.53 | 0
3196 | 2005-05-14 03:00 | 0 | 0 | 0 | 18.38 | 3.31 | 0
3197 | 2005-05-14 04:00 | 1 | 20 | 1 | 17.5 | 3.31 | 0 | -4.0722 | 63.9101 | 90 | 0 | 1 | 0 | 1.0018 | 0.0093692 | 0 | 0.93755 | 0 | 0 | 0.90285 | 0 | 0.87576 | 0.87571 | 1966.63 | 17.5221 | 187.359 | 185.708 | 184.844 | 0 | 0 | 184.836 | 130.124 | 0 | 0 | 0 | 184.836 | 0 | 660 | 0 | 0
3198 | 2005-05-14 05:00 | 79 | 240 | 47 | 17.61 | 3.31 | 0 | 7.3929 | 72.3079 | 90 | 0 | 79 | 0 | 35.7572 | 0.74017 | 0 | 33.463 | 0.0038634 | 0 | 32.2245 | 0.0029112 | 31.2606 | 31.2587 | 70199.1 | 18.3973 | 52843 | 54724.5 | 53399.4 | 0 | 0 | 53370.3 | 624.01 | 0 | 0 | 0 | 2230.83 | 51139.5 | 660 | 49353.2 | 48366.0938
3199 | 2005-05-14 06:00 | 300 | 617 | 95 | 17.72 | 1.37 | 0 | 19.3891 | 80.1365 | 76.5505 | 0 | 300 | 143.624 | 89.1925 | 2.8108 | 138.383 | 83.4697 | 0.014671 | 115.554 | 80.3806 | 0.011055 | 190.067 | 190.068 | 426846 | 23.1677 | 387195 | 390379 | 365602 | 0 | 0 | 364487 | 691.605 | 0 | 0 | 0 | 0 | 364487 | 691.605 | 357789 | 350633.0938
3200 | 2005-05-14 07:00 | 515 | 812 | 88 | 17.84 | 1.37 | 0 | 31.6727 | 88.0581 | 62.375 | 0 | 515 | 377.082 | 90.3694 | 4.8251 | 377.082 | 84.5712 | 0.025186 | 355.274 | 81.4412 | 0.018978 | 423.632 | 423.629 | 951361 | 29.982 | 911248 | 891070 | 868208 | 0 | 0 | 862202 | 701.528 | 0 | 0 | 0 | 0 | 862202 | 701.528 | 849203 | 832218.5625
3201 | 2005-05-14 08:00 | 720 | 846 | 132 | 19.84 | 1.37 | 0 | 44.0091 | 97.0129 | 48.1803 | 0 | 720 | 564.317 | 137.963 | 6.7458 | 564.317 | 129.111 | 0.035211 | 550.217 | 124.333 | 0.026532 | 654.339 | 654.328 | 1469450 | 38.5942 | 1445480 | 1360890 | 1326210 | 0 | 0 | 1311780 | 687.966 | 0 | 0 | 0 | 0 | 1311780 | 687.966 | 1291010 | 1265188.875
3202 | 2005-05-14 09:00 | 856 | 844 | 156 | 21.85 | 3.05 | 0 | 56.0521 | 108.848 | 34.0991 | 0 | 856 | 698.754 | 165.15 | 8.02 | 698.754 | 154.554 | 0.041862 | 691.5 | 148.834 | 0.031544 | 815.154 | 815.152 | 1830620 | 42.7373 | 1823150 | 1685870 | 1644160 | 0 | 0 | 1621680 | 681.202 | 0 | 0 | 0 | 0 | 1621680 | 681.202 | 1593110 | 1561250.5
3203 | 2005-05-14 10:00 | 991 | 950 | 118 | 23.85 | 3.05 | 0 | 66.9569 | 128.308 | 20.5219 | 0 | 991 | 888.49 | 122.866 | 9.2849 | 888.49 | 114.983 | 0.048464 | 885.48 | 110.728 | 0.036519 | 966.357 | 966.348 | 2170170 | 48.6116 | 2180320 | 1963440 | 1917020 | 0 | 0 | 1885010 | 664.284 | 0 | 0 | 0 | 0 | 1885010 | 664.284 | 1847550 | 1810595.375
3204 | 2005-05-14 11:00 | 1041 | 958 | 123 | 25.21 | 3.05 | 0 | 73.8631 | 166.499 | 9.9982 | 0 | 1041 | 941.139 | 127.278 | 9.7534 | 941.139 | 119.111 | 0.050909 | 940.413 | 114.703 | 0.038361 | 1023.5 | 1023.5 | 2298510 | 51.4359 | 2315630 | 2058220 | 2013200 | 0 | 0 | 1977010 | 654.679 | 0 | 0 | 0 | 1137.04 | 1975870 | 659.999 | 1934850 | 1896154.25
3205 | 2005-05-14 12:00 | 1024 | 955 | 120 | 26.58 | 0.88 | 0 | 71.4369 | 214.816 | 14.1612 | 0 | 1024 | 924.634 | 124.539 | 9.5941 | 924.634 | 116.548 | 0.050078 | 923.185 | 112.235 | 0.037735 | 1004.39 | 1004.39 | 2255600 | 56.3324 | 2270370 | 1969550 | 1927380 | 0 | 0 | 1892470 | 638.392 | 0 | 0 | 0 | 25393.5 | 1867080 | 660 | 1830350 | 1793742.5
3206 | 2005-05-14 13:00 | 945 | 942 | 114 | 27.94 | 0.88 | 0 | 62.0313 | 242.499 | 26.8771 | 0 | 945 | 839.256 | 119.073 | 8.8539 | 839.256 | 111.433 | 0.046214 | 834.174 | 107.309 | 0.034824 | 913.273 | 913.267 | 2050970 | 54.9932 | 2054770 | 1792680 | 1751980 | 0 | 0 | 1723340 | 641.549 | 0 | 0 | 0 | 17647.2 | 1705700 | 660 | 1674900 | 1641398.625
3207 | 2005-05-14 14:00 | 810 | 913 | 106 | 28.29 | 0.88 | 0 | 50.4184 | 257.408 | 40.7807 | 0 | 810 | 691.666 | 110.919 | 7.5891 | 691.666 | 103.803 | 0.039612 | 680.578 | 99.9609 | 0.029849 | 757.151 | 757.142 | 1700340 | 50.7184 | 1686580 | 1500210 | 1465590 | 0 | 0 | 1445930 | 649.985 | 0 | 0 | 0 | 3660.24 | 1442270 | 659.999 | 1419690 | 1391294.875
3208 | 2005-05-14 15:00 | 629 | 863 | 95 | 28.64 | 0.94 | 0 | 38.1844 | 267.543 | 54.9343 | 0 | 629 | 496.269 | 99.4681 | 5.8932 | 496.269 | 93.086 | 0.030761 | 477.892 | 89.641 | 0.023179 | 550.53 | 550.527 | 1236340 | 44.8822 | 1203690 | 1098750 | 1071770 | 0 | 0 | 1061560 | 662.205 | 0 | 0 | 0 | -3.6898 | 1061560 | 662.672 | 1047240 | 1026292.125
3209 | 2005-05-14 16:00 | 407 | 732 | 87 | 28.98 | 0.94 | 0 | 25.8514 | 275.863 | 69.1246 | 0 | 407 | 261.508 | 85.5644 | 3.8133 | 261.508 | 80.0744 | 0.019904 | 237.889 | 77.1109 | 0.014998 | 305.565 | 305.561 | 686211 | 37.995 | 643408 | 605007 | 590414 | 0 | 0 | 587292 | 662.731 | 0 | 0 | 0 | -5.0812 | 587297 | 662.837 | 579539 | 567948.4375
3210 | 2005-05-14 17:00 | 182 | 480 | 68 | 28.63 | 0.94 | 0 | 13.6904 | 283.657 | 83.249 | 0 | 182 | 56.6226 | 60.2443 | 1.7052 | 56.6226 | 56.3789 | 0.0089006 | 35.37 | 54.2924 | 0.0067068 | 86.979 | 86.9769 | 195327 | 31.1961 | 165775 | 160509 | 156740 | 0 | 0 | 156495 | 629.119 | 0 | 0 | 0 | 5042.33 | 151452 | 660 | 147074 | 144132.0781
3211 | 2005-05-14 18:00 | 19 | 167 | 7 | 28.27 | 3.59 | 0 | 1.9311 | 291.689 | 90 | 0 | 19 | 0 | 5.4279 | 0.17802 | 0 | 5.0796 | 0.00092918 | 0 | 4.8916 | 0.00070016 | 4.7455 | 4.7451 | 10656.3 | 28.3873 | 4623.46 | 4569.32 | 4492.94 | 0 | 0 | 4492.57 | 464.505 | 0 | 0 | 0 | 4492.57 | 0 | 660 | 0 | 0
3212 | 2005-05-14 19:00 | 0 | 0 | 0 | 27.91 | 3.59 | 0
3213 | 2005-05-14 20:00 | 0 | 0 | 0 | 26.89 | 3.59 | 0
3214 | 2005-05-14 21:00 | 0 | 0 | 0 | 25.87 | 5.76 | 0
3215 | 2005-05-14 22:00 | 0 | 0 | 0 | 24.85 | 5.76 | 0
3216 | 2005-05-14 23:00 | 0 | 0 | 0 | 23.81 | 5.76 | 0
3217 | 2005-05-15 | 0 | 0 | 0 | 22.76 | 4.15 | 0
3218 | 2005-05-15 01:00 | 0 | 0 | 0 | 21.72 | 4.15 | 0
3219 | 2005-05-15 02:00 | 0 | 0 | 0 | 20.7 | 4.15 | 0
3220 | 2005-05-15 03:00 | 0 | 0 | 0 | 19.67 | 3.66 | 0
3221 | 2005-05-15 04:00 | 1 | 30 | 0 | 18.65 | 3.66 | 0 | -3.9261 | 63.7236 | 90 | 0 | 1 | 0 | 0 | 0.0093692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.65 | 0 | 0 | 0 | 0 | 0 | 0 | 660 | 0 | 0 | 0 | 0 | 0 | 660 | 0 | 0
3222 | 2005-05-15 05:00 | 90 | 333 | 45 | 18.79 | 3.66 | 0 | 7.5234 | 72.1091 | 90 | 0 | 90 | 0 | 35.9111 | 0.84323 | 0 | 33.607 | 0.0044014 | 0 | 32.3632 | 0.0033165 | 31.3955 | 31.3932 | 70501.1 | 19.5627 | 53103.5 | 54662.7 | 53407.5 | 0 | 0 | 53378.1 | 619.771 | 0 | 0 | 0 | 2901.57 | 50476.5 | 660 | 48711.3 | 47737.1094
3223 | 2005-05-15 06:00 | 305 | 665 | 82 | 18.94 | 2.29 | 0 | 19.5087 | 79.9205 | 76.5295 | 0 | 305 | 155.551 | 76.952 | 2.8576 | 150.27 | 72.0146 | 0.014916 | 125.529 | 69.3494 | 0.011239 | 189.043 | 189.031 | 424520 | 24.0346 | 384950 | 386543 | 360376 | 0 | 0 | 359284 | 689.772 | 0 | 0 | 0 | 0 | 359284 | 689.772 | 352626 | 345573.6875
3224 | 2005-05-15 07:00 | 521 | 823 | 87 | 19.08 | 2.29 | 0 | 31.7869 | 87.8154 | 62.3729 | 0 | 521 | 382.055 | 89.2637 | 4.8814 | 382.055 | 83.5364 | 0.025479 | 359.963 | 80.4448 | 0.019199 | 427.214 | 427.209 | 959402 | 30.5937 | 919441 | 896613 | 872956 | 0 | 0 | 866864 | 699.755 | 0 | 0 | 0 | 0 | 866864 | 699.755 | 853872 | 836794.625
3225 | 2005-05-15 08:00 | 712 | 875 | 103 | 21.26 | 2.29 | 0 | 44.1255 | 96.7276 | 48.1995 | 0 | 712 | 583.028 | 107.28 | 6.6709 | 583.028 | 100.397 | 0.03482 | 568.443 | 96.6814 | 0.026237 | 645.197 | 645.19 | 1448930 | 38.6485 | 1424120 | 1340380 | 1307070 | 0 | 0 | 1293020 | 687.547 | 0 | 0 | 0 | 0 | 1293020 | 687.547 | 1272680 | 1247221.875
3226 | 2005-05-15 09:00 | 857 | 881 | 125 | 23.45 | 3.53 | 0 | 56.1831 | 108.497 | 34.147 | 0 | 857 | 729.163 | 129.682 | 8.0294 | 729.163 | 121.361 | 0.041911 | 721.568 | 116.87 | 0.031581 | 813.315 | 813.309 | 1826490 | 43.6395 | 1818800 | 1674790 | 1636240 | 0 | 0 | 1613700 | 677.08 | 0 | 0 | 0 | 0 | 1613700 | 677.08 | 1585510 | 1553799.125
3227 | 2005-05-15 10:00 | 976 | 924 | 126 | 25.63 | 3.53 | 0 | 67.1264 | 127.89 | 20.6216 | 0 | 976 | 863.434 | 130.542 | 9.1444 | 863.434 | 122.166 | 0.047731 | 860.479 | 117.645 | 0.035966 | 948.815 | 948.812 | 2130790 | 49.1832 | 2138820 | 1920560 | 1876000 | 0 | 0 | 1845170 | 662.181 | 0 | 0 | 0 | -13.6894 | 1845190 | 662.499 | 1809260 | 1773073.5
3228 | 2005-05-15 11:00 | 1042 | 958 | 123 | 26.82 | 3.53 | 0 | 74.0926 | 166.314 | 10.2162 | 0 | 1042 | 940.443 | 127.106 | 9.7627 | 940.443 | 118.951 | 0.050958 | 939.685 | 114.549 | 0.038398 | 1022.64 | 1022.64 | 2296580 | 52.2058 | 2313600 | 2048730 | 2000870 | 0 | 0 | 1964980 | 653.714 | 0 | 0 | 0 | 2136.31 | 1962850 | 660 | 1922360 | 1883908.625
3229 | 2005-05-15 12:00 | 1026 | 955 | 121 | 28.01 | 5.96 | 0 | 71.6418 | 215.179 | 14.3088 | 0 | 1026 | 923.948 | 125.356 | 9.6128 | 923.948 | 117.313 | 0.050176 | 922.469 | 112.971 | 0.037808 | 1004.41 | 1004.41 | 2255630 | 49.2912 | 2270410 | 2038690 | 1991380 | 0 | 0 | 1956770 | 662.962 | 0 | 0 | 0 | -0.55978 | 1956770 | 662.964 | 1916510 | 1878181.75
3230 | 2005-05-15 13:00 | 947 | 942 | 114 | 29.21 | 5.96 | 0 | 62.1823 | 242.883 | 26.9418 | 0 | 947 | 839.621 | 118.933 | 8.8727 | 839.621 | 111.302 | 0.046312 | 834.51 | 107.183 | 0.034897 | 913.477 | 913.473 | 2051430 | 48.5645 | 2055240 | 1850510 | 1805740 | 0 | 0 | 1777260 | 663.933 | 0 | 0 | 0 | -11.6902 | 1777280 | 663.971 | 1743830 | 1708956.125
3231 | 2005-05-15 14:00 | 812 | 913 | 107 | 29.43 | 5.96 | 0 | 50.5444 | 257.718 | 40.8079 | 0 | 812 | 691.11 | 111.78 | 7.6078 | 691.11 | 104.608 | 0.03971 | 680.012 | 100.737 | 0.029922 | 757.355 | 757.354 | 1700830 | 45.4767 | 1687090 | 1539390 | 1502470 | 0 | 0 | 1483010 | 669.352 | 0 | 0 | 0 | 0 | 1483010 | 669.352 | 1459070 | 1429889
3232 | 2005-05-15 15:00 | 631 | 822 | 121 | 29.65 | 6.09 | 0 | 38.3026 | 267.801 | 54.9374 | 0 | 631 | 472.69 | 124.876 | 5.912 | 472.69 | 116.863 | 0.030859 | 455.183 | 112.538 | 0.023252 | 550.713 | 550.708 | 1236750 | 41.2211 | 1204110 | 1118780 | 1092000 | 0 | 0 | 1081710 | 672.599 | 0 | 0 | 0 | 0 | 1081710 | 672.599 | 1066500 | 1045165.4375
3233 | 2005-05-15 16:00 | 388 | 636 | 109 | 29.87 | 6.09 | 0 | 25.9712 | 276.086 | 69.1081 | 0 | 388 | 227.195 | 106.322 | 3.6353 | 227.195 | 99.5003 | 0.018975 | 206.699 | 95.8179 | 0.014298 | 293.456 | 293.452 | 659020 | 36.0358 | 616232 | 584944 | 571283 | 0 | 0 | 568392 | 666.298 | 0 | 0 | 0 | 0 | 568392 | 666.298 | 560720 | 549505.3125
3234 | 2005-05-15 17:00 | 192 | 478 | 77 | 29.09 | 6.09 | 0 | 13.8179 | 283.858 | 83.214 | 0 | 192 | 56.8952 | 68.5714 | 1.7989 | 56.8952 | 64.1718 | 0.0093896 | 35.6649 | 61.7968 | 0.0070753 | 94.5447 | 94.5436 | 212321 | 31.0765 | 181617 | 176001 | 171749 | 0 | 0 | 171459 | 634.341 | 0 | 0 | 0 | 3902.93 | 167556 | 660 | 162874 | 159616.2969
3235 | 2005-05-15 18:00 | 20 | 169 | 8 | 28.3 | 6.98 | 0 | 2.0712 | 291.876 | 90 | 0 | 20 | 0 | 6.2833 | 0.18738 | 0 | 5.8802 | 0.00097808 | 0 | 5.6625 | 0.00073701 | 5.4934 | 5.4931 | 12336.1 | 28.409 | 5789.34 | 5710.32 | 5604.9 | 0 | 0 | 5604.36 | 480.891 | 0 | 0 | 0 | 5604.36 | 0 | 660 | 0 | 0
3236 | 2005-05-15 19:00 | 0 | 0 | 0 | 27.52 | 6.98 | 0
3237 | 2005-05-15 20:00 | 0 | 0 | 0 | 26.33 | 6.98 | 0
3238 | 2005-05-15 21:00 | 0 | 0 | 0 | 25.14 | 8.57 | 0
3239 | 2005-05-15 22:00 | 0 | 0 | 0 | 23.95 | 8.57 | 0
3240 | 2005-05-15 23:00 | 0 | 0 | 0 | 22.93 | 8.57 | 0
3241 | 2005-05-16 | 0 | 0 | 0 | 21.9 | 9.36 | 0
3242 | 2005-05-16 01:00 | 0 | 0 | 0 | 20.87 | 9.36 | 0
3243 | 2005-05-16 02:00 | 0 | 0 | 0 | 20.15 | 9.36 | 0
3244 | 2005-05-16 03:00 | 0 | 0 | 0 | 19.42 | 9.69 | 0
3245 | 2005-05-16 04:00 | 0 | 0 | 0 | 18.69 | 9.69 | 0
3246 | 2005-05-16 05:00 | 16 | 0 | 16 | 19.06 | 9.69 | 0 | 7.6489 | 71.9133 | 90 | 0 | 16 | 0 | 15.387 | 0.14991 | 0 | 14.3997 | 0.00078247 | 0 | 13.8668 | 0.0005896 | 13.4514 | 13.4513 | 30208.2 | 19.2853 | 19409.8 | 19997.3 | 19555.7 | 0 | 0 | 19551 | 570.829 | 0 | 0 | 0 | 6868.28 | 12682.7 | 660 | 12210.4 | 11966.2236
3247 | 2005-05-16 06:00 | 118 | 8 | 115 | 19.42 | 8.29 | 0 | 19.6234 | 79.7079 | 76.5116 | 0 | 118 | 2.0836 | 104.332 | 1.1056 | 2.0179 | 97.6375 | 0.0057707 | 1.6863 | 94.024 | 0.0043483 | 92.8432 | 92.8385 | 208492 | 21.1163 | 178048 | 181525 | 176567 | 0 | 0 | 176291 | 668.887 | 0 | 0 | 0 | 0 | 176291 | 668.887 | 171318 | 167891.4062
3248 | 2005-05-16 07:00 | 252 | 34 | 234 | 19.79 | 8.29 | 0 | 31.8962 | 87.5763 | 62.3737 | 0 | 252 | 15.7966 | 238.305 | 2.361 | 15.7966 | 223.015 | 0.012324 | 14.8832 | 214.761 | 0.0092863 | 222.764 | 222.746 | 500230 | 23.86 | 458854 | 461255 | 448677 | 0 | 0 | 447049 | 697.781 | 0 | 0 | 0 | 0 | 447049 | 697.781 | 439728 | 430933.9062
3249 | 2005-05-16 08:00 | 363 | 77 | 309 | 20.32 | 8.29 | 0 | 44.2366 | 96.4462 | 48.2213 | 0 | 363 | 51.572 | 317.617 | 3.401 | 51.572 | 297.239 | 0.017752 | 50.2803 | 286.238 | 0.013377 | 326.436 | 326.411 | 733034 | 26.2841 | 690369 | 686298 | 668436 | 0 | 0 | 664889 | 703.47 | 0 | 0 | 0 | 0 | 664889 | 703.47 | 654800 | 641704.3125
3250 | 2005-05-16 09:00 | 666 | 338 | 385 | 20.86 | 10.2 | 0 | 56.3083 | 108.15 | 34.1974 | 0 | 666 | 279.336 | 382.037 | 6.2399 | 279.336 | 357.525 | 0.03257 | 276.416 | 344.293 | 0.024542 | 602.112 | 602.109 | 1352190 | 30.6344 | 1323630 | 1291480 | 1255320 | 0 | 0 | 1243250 | 712.776 | 0 | 0 | 0 | 0 | 1243250 | 712.776 | 1222790 | 1198336.875
3251 | 2005-05-16 10:00 | 937 | 739 | 256 | 21.39 | 10.2 | 0 | 67.2895 | 127.471 | 20.7231 | 0 | 937 | 690.475 | 270.155 | 8.779 | 690.475 | 252.822 | 0.045823 | 688.087 | 243.465 | 0.034529 | 903.638 | 903.629 | 2029310 | 36.0591 | 2031970 | 1937850 | 1888360 | 0 | 0 | 1860650 | 704.286 | 0 | 0 | 0 | 0 | 1860650 | 704.286 | 1823600 | 1787125.625
3252 | 2005-05-16 11:00 | 578 | 145 | 439 | 21.65 | 10.2 | 0 | 74.3163 | 166.121 | 10.4308 | 0 | 578 | 141.989 | 436.34 | 5.4154 | 141.989 | 408.343 | 0.028267 | 141.87 | 393.231 | 0.021299 | 519.069 | 519.064 | 1165690 | 30.0762 | 1130860 | 1105800 | 1076340 | 0 | 0 | 1067310 | 707.588 | 0 | 0 | 0 | 0 | 1067310 | 707.588 | 1050630 | 1029619.375
3253 | 2005-05-16 12:00 | 455 | 55 | 403 | 21.91 | 13.36 | 0 | 71.8425 | 215.534 | 14.4535 | 0 | 455 | 52.9931 | 419.821 | 4.263 | 52.9931 | 392.884 | 0.022251 | 52.9065 | 378.344 | 0.016767 | 418.329 | 418.309 | 939417 | 27.5326 | 899123 | 888988 | 864153 | 0 | 0 | 858348 | 709.311 | 0 | 0 | 0 | 0 | 858348 | 709.311 | 845073 | 828171.9375
3254 | 2005-05-16 13:00 | 257 | 5 | 253 | 22.17 | 13.36 | 0 | 62.3305 | 243.258 | 27.0046 | 0 | 257 | 4.0241 | 236.415 | 2.4079 | 4.0241 | 221.246 | 0.012568 | 3.9994 | 213.058 | 0.0094705 | 210.554 | 210.54 | 472822 | 24.9999 | 431945 | 431917 | 419779 | 0 | 0 | 418327 | 691.478 | 0 | 0 | 0 | 0 | 418327 | 691.478 | 411552 | 403320.8125
3255 | 2005-05-16 14:00 | 173 | 0 | 173 | 21.81 | 13.36 | 0 | 50.6686 | 258.022 | 40.8333 | 0 | 173 | 0 | 160.492 | 1.6209 | 0 | 150.194 | 0.0084604 | 0 | 144.636 | 0.0063751 | 140.303 | 140.294 | 315065 | 23.6957 | 278934 | 280695 | 273047 | 0 | 0 | 272409 | 679.527 | 0 | 0 | 0 | 0 | 272409 | 679.527 | 266069 | 260747.9688
3256 | 2005-05-16 15:00 | 578 | 496 | 270 | 21.45 | 13.08 | 0 | 38.4195 | 268.051 | 54.9388 | 0 | 578 | 284.723 | 262.877 | 5.4154 | 284.723 | 246.011 | 0.028267 | 274.177 | 236.906 | 0.021299 | 495.771 | 495.763 | 1113360 | 28.2235 | 1077010 | 1061830 | 1032910 | 0 | 0 | 1024730 | 713.81 | 0 | 0 | 0 | 0 | 1024730 | 713.81 | 1008570 | 988395.5
3257 | 2005-05-16 16:00 | 322 | 337 | 174 | 21.09 | 13.08 | 0 | 26.0898 | 276.304 | 69.0901 | 0 | 322 | 120.108 | 162.174 | 3.0169 | 120.108 | 151.769 | 0.015747 | 109.287 | 146.152 | 0.011866 | 247.787 | 247.783 | 556458 | 24.4754 | 514301 | 515521 | 501491 | 0 | 0 | 499467 | 699.736 | 0 | 0 | 0 | 0 | 499467 | 699.736 | 491482 | 481652.2188
3258 | 2005-05-16 17:00 | 188 | 365 | 100 | 20.38 | 13.08 | 0 | 13.9442 | 284.054 | 83.1775 | 0 | 188 | 43.3811 | 86.4077 | 1.7614 | 43.3811 | 80.8636 | 0.009194 | 27.2911 | 77.8709 | 0.0069279 | 102.014 | 102.009 | 229087 | 21.7737 | 197328 | 200507 | 195465 | 0 | 0 | 195129 | 670.799 | 0 | 0 | 0 | 0 | 195129 | 670.799 | 189814 | 186017.5781
3259 | 2005-05-16 18:00 | 20 | 131 | 11 | 19.67 | 11.58 | 0 | 2.2099 | 292.057 | 90 | 0 | 20 | 0 | 8.3697 | 0.18738 | 0 | 7.8327 | 0.00097808 | 0 | 7.5428 | 0.00073701 | 7.3173 | 7.3169 | 16431.9 | 19.7793 | 8753.92 | 8961.38 | 8786.37 | 0 | 0 | 8785.29 | 531.703 | 0 | 0 | 0 | 8752.32 | 32.968 | 660 | 31.7153 | 31.081
3260 | 2005-05-16 19:00 | 0 | 0 | 0 | 18.97 | 11.58 | 0
3261 | 2005-05-16 20:00 | 0 | 0 | 0 | 17.93 | 11.58 | 0
3262 | 2005-05-16 21:00 | 0 | 0 | 0 | 16.88 | 9.68 | 0
3263 | 2005-05-16 22:00 | 0 | 0 | 0 | 15.85 | 9.68 | 0
3264 | 2005-05-16 23:00 | 0 | 0 | 0 | 15.08 | 9.68 | 0
3265 | 2005-05-17 | 0 | 0 | 0 | 14.32 | 10.04 | 0
3266 | 2005-05-17 01:00 | 0 | 0 | 0 | 13.56 | 10.04 | 0
3267 | 2005-05-17 02:00 | 0 | 0 | 0 | 12.9 | 10.04 | 0
3268 | 2005-05-17 03:00 | 0 | 0 | 0 | 12.23 | 4.02 | 0
3269 | 2005-05-17 04:00 | 1 | 20 | 1 | 11.57 | 4.02 | 0 | -3.6491 | 63.3591 | 90 | 0 | 1 | 0 | 1.0014 | 0.0093692 | 0 | 0.93719 | 0 | 0 | 0.9025 | 0 | 0.87543 | 0.87537 | 1965.85 | 11.591 | 187.224 | 184.26 | 183.384 | 0 | 0 | 183.376 | 129.85 | 0 | 0 | 0 | 183.376 | 0 | 660 | 0 | 0
3270 | 2005-05-17 05:00 | 81 | 194 | 54 | 11.98 | 4.02 | 0 | 7.7695 | 71.7208 | 90 | 0 | 81 | 0 | 42.3296 | 0.75891 | 0 | 39.6137 | 0.0039612 | 0 | 38.1476 | 0.0029849 | 37.0061 | 37.0044 | 83102.6 | 12.8695 | 64053.9 | 68188.7 | 66449.4 | 0 | 0 | 66408.5 | 654.189 | 0 | 0 | 0 | 85.4959 | 66323 | 660 | 64066.7 | 62785.3672
3271 | 2005-05-17 06:00 | 152 | 52 | 134 | 12.39 | 1.89 | 0 | 19.7332 | 79.4987 | 76.4965 | 0 | 152 | 12.4484 | 134.627 | 1.4241 | 12.0817 | 125.989 | 0.0074334 | 10.0987 | 121.326 | 0.0056013 | 127.488 | 127.482 | 286294 | 15.9187 | 251457 | 262570 | 254915 | 0 | 0 | 254394 | 701.956 | 0 | 0 | 0 | 0 | 254394 | 701.956 | 247713 | 242759
3272 | 2005-05-17 07:00 | 161 | 8 | 157 | 12.8 | 1.89 | 0 | 32.0004 | 87.341 | 62.3772 | 0 | 161 | 3.4997 | 144.515 | 1.5084 | 3.4997 | 135.243 | 0.0078736 | 3.2973 | 130.237 | 0.0059329 | 129.534 | 129.524 | 290878 | 16.3853 | 255822 | 266537 | 259111 | 0 | 0 | 258570 | 699.916 | 0 | 0 | 0 | 0 | 258570 | 699.916 | 251891 | 246853.5469
3273 | 2005-05-17 08:00 | 502 | 246 | 330 | 14.5 | 1.89 | 0 | 44.3424 | 96.1687 | 48.2458 | 0 | 502 | 163.877 | 316.13 | 4.7034 | 163.877 | 295.847 | 0.02455 | 159.767 | 284.898 | 0.018499 | 431.343 | 431.325 | 968646 | 26.4392 | 928884 | 922846 | 898021 | 0 | 0 | 891848 | 715.235 | 0 | 0 | 0 | 0 | 891848 | 715.235 | 877791 | 860235.5
3274 | 2005-05-17 09:00 | 866 | 794 | 205 | 16.21 | 1.94 | 0 | 56.4277 | 107.806 | 34.25 | 0 | 866 | 655.765 | 215.355 | 8.1137 | 655.765 | 201.538 | 0.042351 | 648.886 | 194.079 | 0.031912 | 817.707 | 817.695 | 1836340 | 38.7685 | 1829150 | 1722520 | 1680470 | 0 | 0 | 1657640 | 691.426 | 0 | 0 | 0 | 0 | 1657640 | 691.426 | 1627610 | 1595058
3275 | 2005-05-17 10:00 | 982 | 930 | 124 | 17.91 | 1.94 | 0 | 67.446 | 127.053 | 20.8262 | 0 | 982 | 868.354 | 128.287 | 9.2006 | 868.354 | 120.056 | 0.048024 | 865.319 | 115.613 | 0.036187 | 951.539 | 951.532 | 2136900 | 44.1608 | 2145250 | 1972460 | 1924780 | 0 | 0 | 1893850 | 678.1 | 0 | 0 | 0 | 0 | 1893850 | 678.1 | 1855910 | 1818787.125
3276 | 2005-05-17 11:00 | 1044 | 912 | 167 | 19.25 | 1.94 | 0 | 74.5339 | 165.919 | 10.6417 | 0 | 1044 | 894.301 | 168.68 | 9.7815 | 894.301 | 157.857 | 0.051056 | 893.518 | 152.015 | 0.038472 | 1014.2 | 1014.2 | 2277630 | 47.2296 | 2293610 | 2079720 | 2029840 | 0 | 0 | 1994680 | 669.997 | 0 | 0 | 0 | 0 | 1994680 | 669.997 | 1952900 | 1913838
3277 | 2005-05-17 12:00 | 961 | 690 | 306 | 20.59 | 3.25 | 0 | 72.039 | 215.882 | 14.5951 | 0 | 961 | 666.336 | 319.395 | 9.0038 | 666.336 | 298.902 | 0.046997 | 665.226 | 287.84 | 0.035413 | 924.508 | 924.496 | 2076180 | 43.9678 | 2081300 | 1915040 | 1868270 | 0 | 0 | 1839030 | 677.797 | 0 | 0 | 0 | 0 | 1839030 | 677.797 | 1803110 | 1767043.125
3278 | 2005-05-17 13:00 | 164 | 4 | 160 | 21.93 | 3.25 | 0 | 62.476 | 243.626 | 27.0653 | 0 | 164 | 4.0166 | 148.73 | 1.5366 | 4.0166 | 139.187 | 0.0080203 | 3.9919 | 134.036 | 0.0060434 | 133.892 | 133.88 | 300661 | 25.3154 | 265157 | 264725 | 257470 | 0 | 0 | 256890 | 671.734 | 0 | 0 | 0 | 0 | 256890 | 671.734 | 250835 | 245818.5469
3279 | 2005-05-17 14:00 | 342 | 76 | 283 | 22.43 | 3.25 | 0 | 50.7911 | 258.317 | 40.8568 | 0 | 342 | 57.5914 | 287.286 | 3.2043 | 57.5914 | 268.853 | 0.016725 | 56.6637 | 258.903 | 0.012603 | 306.112 | 306.108 | 687441 | 30.1706 | 644663 | 629405 | 612567 | 0 | 0 | 609448 | 687.088 | 0 | 0 | 0 | 0 | 609448 | 687.088 | 600699 | 588685.4375
3280 | 2005-05-17 15:00 | 607 | 550 | 264 | 22.93 | 4.9 | 0 | 38.5351 | 268.296 | 54.9384 | 0 | 607 | 316.277 | 257.151 | 5.6871 | 316.277 | 240.652 | 0.029685 | 304.562 | 231.746 | 0.022368 | 520.24 | 520.223 | 1168290 | 34.7353 | 1133510 | 1085280 | 1057670 | 0 | 0 | 1048560 | 692.601 | 0 | 0 | 0 | 0 | 1048560 | 692.601 | 1032990 | 1012334.0625
3281 | 2005-05-17 16:00 | 270 | 166 | 197 | 23.43 | 4.9 | 0 | 26.2073 | 276.515 | 69.0704 | 0 | 270 | 59.0486 | 181.18 | 2.5297 | 59.0486 | 169.555 | 0.013204 | 53.736 | 163.28 | 0.0099496 | 210.515 | 210.509 | 472749 | 28.207 | 431863 | 425309 | 414719 | 0 | 0 | 413261 | 682.231 | 0 | 0 | 0 | 0 | 413261 | 682.231 | 406830 | 398692.9062
3282 | 2005-05-17 17:00 | 124 | 81 | 104 | 22.83 | 4.9 | 0 | 14.0693 | 284.245 | 83.1398 | 0 | 124 | 9.8272 | 89.9892 | 1.1618 | 9.8272 | 84.2153 | 0.0060641 | 6.205 | 81.0986 | 0.0045694 | 84.6889 | 84.6835 | 190178 | 24.7517 | 160998 | 161195 | 157180 | 0 | 0 | 156948 | 650.609 | 0 | 0 | 0 | 381.655 | 156567 | 660 | 152088 | 149046.4062
3283 | 2005-05-17 18:00 | 14 | 30 | 12 | 22.24 | 7.99 | 0 | 2.3471 | 292.233 | 90 | 0 | 14 | 0 | 10.6594 | 0.13117 | 0 | 9.9754 | 0.00068466 | 0 | 9.6062 | 0.0005159 | 9.3186 | 9.318 | 20926 | 22.4135 | 12139.8 | 12296.8 | 12047.3 | 0 | 0 | 12045.4 | 538.714 | 0 | 0 | 0 | 11232.8 | 812.58 | 660 | 781.745 | 766.1098
3284 | 2005-05-17 19:00 | 0 | 0 | 0 | 21.65 | 7.99 | 0
3285 | 2005-05-17 20:00 | 0 | 0 | 0 | 20.64 | 7.99 | 0
3286 | 2005-05-17 21:00 | 0 | 0 | 0 | 19.64 | 7.13 | 0
3287 | 2005-05-17 22:00 | 0 | 0 | 0 | 18.63 | 7.13 | 0
3288 | 2005-05-17 23:00 | 0 | 0 | 0 | 17.86 | 7.13 | 0
3289 | 2005-05-18 | 0 | 0 | 0 | 17.09 | 9.33 | 0
3290 | 2005-05-18 01:00 | 0 | 0 | 0 | 16.31 | 9.33 | 0
3291 | 2005-05-18 02:00 | 0 | 0 | 0 | 15.91 | 9.33 | 0
3292 | 2005-05-18 03:00 | 0 | 0 | 0 | 15.51 | 7.31 | 0
3293 | 2005-05-18 04:00 | 2 | 40 | 1 | 15.11 | 7.31 | 0 | -3.5182 | 63.1813 | 90 | 0 | 2 | 0 | 0.69961 | 0.018738 | 0 | 0.65473 | 0 | 0 | 0.6305 | 0 | 0.61158 | 0.61152 | 1373.31 | 15.1219 | 91.474 | 90.4019 | 89.5912 | 0 | 0 | 89.5877 | 95.6419 | 0 | 0 | 0 | 89.5877 | 0 | 660 | 0 | 0
3294 | 2005-05-18 05:00 | 96 | 370 | 44 | 16.14 | 7.31 | 0 | 7.8851 | 71.5315 | 90 | 0 | 96 | 0 | 34.4466 | 0.89945 | 0 | 32.2365 | 0.0046948 | 0 | 31.0434 | 0.0035376 | 30.1156 | 30.1147 | 67629.7 | 16.7253 | 50629.8 | 52887.4 | 51563.4 | 0 | 0 | 51536.7 | 627.932 | 0 | 0 | 0 | 1606.39 | 49930.3 | 660 | 48182.5 | 47218.8828
3295 | 2005-05-18 06:00 | 302 | 652 | 80 | 17.18 | 5.74 | 0 | 19.8381 | 79.2931 | 76.4844 | 0 | 302 | 152.886 | 74.7421 | 2.8295 | 148.696 | 69.9465 | 0.014769 | 124.319 | 67.3578 | 0.011129 | 185.937 | 185.925 | 417544 | 21.1756 | 378111 | 384842 | 357510 | 0 | 0 | 356468 | 700.632 | 0 | 0 | 0 | 0 | 356468 | 700.632 | 349496 | 342506.3438
3296 | 2005-05-18 07:00 | 527 | 824 | 89 | 18.22 | 5.74 | 0 | 32.0996 | 87.1095 | 62.3834 | 0 | 527 | 382.082 | 90.8625 | 4.9376 | 382.082 | 85.0326 | 0.025773 | 359.974 | 81.8856 | 0.01942 | 428.623 | 428.619 | 962568 | 27.4312 | 922667 | 912699 | 888904 | 0 | 0 | 882774 | 710.903 | 0 | 0 | 0 | 0 | 882774 | 710.903 | 869051 | 851670.1875
3297 | 2005-05-18 08:00 | 717 | 877 | 103 | 20.24 | 5.74 | 0 | 44.4429 | 95.8955 | 48.2726 | 0 | 717 | 583.649 | 106.94 | 6.7177 | 583.649 | 100.078 | 0.035064 | 568.987 | 96.3747 | 0.026422 | 645.427 | 645.418 | 1449450 | 34.1103 | 1424650 | 1368940 | 1334480 | 0 | 0 | 1320390 | 701.201 | 0 | 0 | 0 | 0 | 1320390 | 701.201 | 1298840 | 1272863
3298 | 2005-05-18 09:00 | 885 | 929 | 110 | 22.27 | 3.01 | 0 | 56.5412 | 107.466 | 34.3049 | 0 | 885 | 767.352 | 114.629 | 8.2918 | 767.352 | 107.274 | 0.04328 | 759.273 | 103.304 | 0.032613 | 836.731 | 836.733 | 1879080 | 43.7672 | 1874030 | 1724890 | 1680630 | 0 | 0 | 1656870 | 677.237 | 0 | 0 | 0 | 0 | 1656870 | 677.237 | 1627270 | 1594724.625
3299 | 2005-05-18 10:00 | 995 | 905 | 159 | 24.3 | 3.01 | 0 | 67.5959 | 126.635 | 20.9306 | 0 | 995 | 844.586 | 161.602 | 9.3224 | 844.586 | 151.233 | 0.04866 | 841.603 | 145.636 | 0.036666 | 957.657 | 957.647 | 2150630 | 48.9037 | 2159720 | 1942060 | 1900360 | 0 | 0 | 1868690 | 661.751 | 0 | 0 | 0 | -28.9921 | 1868720 | 662.452 | 1831900 | 1795257.375
3300 | 2005-05-18 11:00 | 1000 | 840 | 191 | 25.27 | 3.01 | 0 | 74.7456 | 165.707 | 10.8488 | 0 | 1000 | 823.557 | 201.698 | 9.3692 | 823.557 | 188.757 | 0.048904 | 822.808 | 181.771 | 0.03685 | 974.477 | 974.463 | 2188400 | 50.3057 | 2199530 | 1964860 | 1919950 | 0 | 0 | 1887300 | 658.223 | 0 | 0 | 0 | 165.855 | 1887130 | 660.774 | 1849620 | 1812628.875
3301 | 2005-05-18 12:00 | 1029 | 909 | 165 | 26.24 | 4.45 | 0 | 72.2312 | 216.222 | 14.7334 | 0 | 1029 | 877.449 | 166.866 | 9.6409 | 877.449 | 156.159 | 0.050322 | 875.958 | 150.38 | 0.037919 | 995.585 | 995.576 | 2235800 | 49.5054 | 2249500 | 2017640 | 1968690 | 0 | 0 | 1934920 | 663.218 | 0 | 0 | 0 | 0 | 1934920 | 663.218 | 1895520 | 1857612
3302 | 2005-05-18 13:00 | 950 | 942 | 114 | 27.22 | 4.45 | 0 | 62.6189 | 243.984 | 27.1239 | 0 | 950 | 837.936 | 118.532 | 8.9008 | 837.936 | 110.927 | 0.046459 | 832.759 | 106.822 | 0.035008 | 911.427 | 911.42 | 2046820 | 48.5188 | 2050390 | 1846470 | 1803040 | 0 | 0 | 1774580 | 663.13 | 0 | 0 | 0 | -11.7548 | 1774590 | 663.179 | 1741260 | 1706433.25
3303 | 2005-05-18 14:00 | 793 | 837 | 143 | 27.44 | 4.45 | 0 | 50.9118 | 258.605 | 40.8784 | 0 | 793 | 633.188 | 150.051 | 7.4298 | 633.188 | 140.423 | 0.038781 | 622.975 | 135.226 | 0.029222 | 735.484 | 735.476 | 1651700 | 44.6272 | 1635670 | 1498180 | 1464240 | 0 | 0 | 1445700 | 668.886 | 0 | 0 | 0 | 0 | 1445700 | 668.886 | 1422680 | 1394225.75
3304 | 2005-05-18 15:00 | 635 | 822 | 121 | 27.67 | 5.29 | 0 | 38.6494 | 268.533 | 54.9364 | 0 | 635 | 472.795 | 124.447 | 5.9495 | 472.795 | 116.462 | 0.031054 | 455.286 | 112.152 | 0.0234 | 550.437 | 550.434 | 1236130 | 39.8485 | 1203480 | 1125480 | 1098220 | 0 | 0 | 1087990 | 677.72 | 0 | 0 | 0 | 0 | 1087990 | 677.72 | 1072390 | 1050941.25
3305 | 2005-05-18 16:00 | 408 | 720 | 88 | 27.89 | 5.29 | 0 | 26.3236 | 276.721 | 69.0493 | 0 | 408 | 258.029 | 86.0288 | 3.8226 | 258.029 | 80.509 | 0.019953 | 234.849 | 77.5294 | 0.015035 | 303.022 | 303.017 | 680498 | 34.5943 | 637693 | 609657 | 594637 | 0 | 0 | 591572 | 673.559 | 0 | 0 | 0 | 0 | 591572 | 673.559 | 583447 | 571778.125
3306 | 2005-05-18 17:00 | 200 | 538 | 67 | 27.18 | 5.29 | 0 | 14.1931 | 284.429 | 83.1008 | 0 | 200 | 65.1594 | 58.9388 | 1.8738 | 65.1594 | 55.1572 | 0.0097808 | 41.2956 | 53.1159 | 0.0073701 | 91.5863 | 91.5826 | 205670 | 29.2063 | 175406 | 171647 | 167628 | 0 | 0 | 167355 | 638.934 | 0 | 0 | 0 | 2394.61 | 164960 | 660 | 160325 | 157118.125
3307 | 2005-05-18 18:00 | 23 | 200 | 8 | 26.46 | 7.33 | 0 | 2.4828 | 292.402 | 90 | 0 | 23 | 0 | 6.1624 | 0.21549 | 0 | 5.767 | 0.0011248 | 0 | 5.5535 | 0.00084756 | 5.3878 | 5.3876 | 12099.1 | 26.5646 | 5622.79 | 5588.53 | 5486.75 | 0 | 0 | 5486.24 | 484.137 | 0 | 0 | 0 | 5486.24 | 0 | 660 | 0 | 0
3308 | 2005-05-18 19:00 | 0 | 0 | 0 | 25.74 | 7.33 | 0
3309 | 2005-05-18 20:00 | 0 | 0 | 0 | 24.58 | 7.33 | 0
3310 | 2005-05-18 21:00 | 0 | 0 | 0 | 23.42 | 5.89 | 0
3311 | 2005-05-18 22:00 | 0 | 0 | 0 | 22.27 | 5.89 | 0
3312 | 2005-05-18 23:00 | 0 | 0 | 0 | 21.38 | 5.89 | 0
3313 | 2005-05-19 | 0 | 0 | 0 | 20.5 | 6.97 | 0
3314 | 2005-05-19 01:00 | 0 | 0 | 0 | 19.62 | 6.97 | 0
3315 | 2005-05-19 02:00 | 0 | 0 | 0 | 18.79 | 6.97 | 0
3316 | 2005-05-19 03:00 | 0 | 0 | 0 | 17.95 | 9.51 | 0
3317 | 2005-05-19 04:00 | 2 | 46 | 1 | 17.12 | 9.51 | 0 | -3.3924 | 63.0065 | 90 | 0 | 2 | 0 | 0.69871 | 0.018738 | 0 | 0.65388 | 0 | 0 | 0.62968 | 0 | 0.61079 | 0.61078 | 1371.67 | 17.1303 | 91.2678 | 90.4156 | 89.7044 | 0 | 0 | 89.7009 | 94.7488 | 0 | 0 | 0 | 89.7009 | 0 | 660 | 0 | 0
3318 | 2005-05-19 05:00 | 103 | 404 | 46 | 17.57 | 9.51 | 0 | 7.9957 | 71.3456 | 90 | 0 | 103 | 0 | 36.2617 | 0.96503 | 0 | 33.9351 | 0.0050371 | 0 | 32.6792 | 0.0037956 | 31.7025 | 31.7011 | 71192.4 | 18.1069 | 53700.6 | 55696.3 | 54341.5 | 0 | 0 | 54311.6 | 626.172 | 0 | 0 | 0 | 2028.49 | 52283.1 | 660 | 50460.4 | 49451.1914
3319 | 2005-05-19 06:00 | 308 | 688 | 73 | 18.02 | 4.27 | 0 | 19.938 | 79.0912 | 76.4751 | 0 | 308 | 161.169 | 68.1197 | 2.8857 | 157.064 | 63.749 | 0.015062 | 131.338 | 61.3897 | 0.01135 | 186.956 | 186.953 | 419855 | 22.4406 | 380367 | 384851 | 356761 | 0 | 0 | 355710 | 696.48 | 0 | 0 | 0 | 0 | 355710 | 696.48 | 348858 | 341881.1875
3320 | 2005-05-19 07:00 | 529 | 785 | 110 | 18.47 | 4.27 | 0 | 32.1939 | 86.8821 | 62.3923 | 0 | 529 | 364.445 | 110.142 | 4.9563 | 364.445 | 103.075 | 0.02587 | 343.346 | 99.2604 | 0.019494 | 429.347 | 429.345 | 964199 | 28.6221 | 924333 | 909472 | 885715 | 0 | 0 | 879563 | 706.728 | 0 | 0 | 0 | 0 | 879563 | 706.728 | 866074 | 848752.5
3321 | 2005-05-19 08:00 | 703 | 808 | 136 | 20.47 | 4.27 | 0 | 44.5382 | 95.6267 | 48.3019 | 0 | 703 | 537.753 | 141.029 | 6.5866 | 537.753 | 131.98 | 0.03438 | 524.22 | 127.096 | 0.025906 | 631.801 | 631.797 | 1418850 | 35.4093 | 1392840 | 1330430 | 1296840 | 0 | 0 | 1283370 | 697.066 | 0 | 0 | 0 | 0 | 1283370 | 697.066 | 1262800 | 1237546.75
3322 | 2005-05-19 09:00 | 886 | 928 | 111 | 22.46 | 4.4 | 0 | 56.649 | 107.13 | 34.3617 | 0 | 886 | 765.882 | 115.492 | 8.3011 | 765.882 | 108.081 | 0.043329 | 757.786 | 104.081 | 0.032649 | 836.043 | 836.036 | 1877520 | 42.0612 | 1872380 | 1737130 | 1692930 | 0 | 0 | 1669260 | 683.433 | 0 | 0 | 0 | 0 | 1669260 | 683.433 | 1639080 | 1606293.875
3323 | 2005-05-19 10:00 | 996 | 949 | 119 | 24.46 | 4.4 | 0 | 67.7393 | 126.218 | 21.036 | 0 | 996 | 884.472 | 123.125 | 9.3317 | 884.472 | 115.225 | 0.048709 | 881.314 | 110.961 | 0.036703 | 962.542 | 962.539 | 2161630 | 47.0271 | 2171310 | 1970060 | 1920550 | 0 | 0 | 1889140 | 671.484 | 0 | 0 | 0 | 0 | 1889140 | 671.484 | 1851440 | 1814415.125
3324 | 2005-05-19 11:00 | 1045 | 957 | 123 | 25.67 | 4.4 | 0 | 74.9511 | 165.486 | 11.0519 | 0 | 1045 | 937.037 | 126.459 | 9.7908 | 937.037 | 118.345 | 0.051105 | 936.151 | 113.965 | 0.038509 | 1018.65 | 1018.65 | 2287630 | 49.5526 | 2304150 | 2066580 | 2020820 | 0 | 0 | 1985010 | 660.788 | 0 | 0 | 0 | -50.5797 | 1985060 | 661.395 | 1943670 | 1904796.125
3325 | 2005-05-19 12:00 | 1029 | 954 | 121 | 26.89 | 3.68 | 0 | 72.4192 | 216.554 | 14.8682 | 0 | 1029 | 920.598 | 124.742 | 9.6409 | 920.598 | 116.738 | 0.050322 | 919.004 | 112.418 | 0.037919 | 1000.52 | 1000.51 | 2246890 | 51.4823 | 2261190 | 2008980 | 1962210 | 0 | 0 | 1928060 | 656.982 | 0 | 0 | 0 | 1076 | 1926980 | 660 | 1887920 | 1850162.5
3326 | 2005-05-19 13:00 | 951 | 942 | 114 | 28.11 | 3.68 | 0 | 62.759 | 244.334 | 27.1801 | 0 | 951 | 837.457 | 118.406 | 8.9101 | 837.457 | 110.808 | 0.046508 | 832.26 | 106.707 | 0.035045 | 910.832 | 910.826 | 2045480 | 50.4979 | 2048990 | 1827670 | 1786290 | 0 | 0 | 1757780 | 655.911 | 0 | 0 | 0 | 685.19 | 1757090 | 660.057 | 1724460 | 1689969.75
3327 | 2005-05-19 14:00 | 816 | 914 | 105 | 28.67 | 3.68 | 0 | 51.0308 | 258.885 | 40.898 | 0 | 816 | 691.24 | 109.352 | 7.6453 | 691.24 | 102.336 | 0.039906 | 680.078 | 98.5483 | 0.03007 | 755.296 | 755.294 | 1696200 | 47.2349 | 1682240 | 1522030 | 1485700 | 0 | 0 | 1466140 | 660.719 | 0 | 0 | 0 | -49.4389 | 1466190 | 661.162 | 1442980 | 1414118.625
3328 | 2005-05-19 15:00 | 637 | 864 | 96 | 29.23 | 5.71 | 0 | 38.7624 | 268.764 | 54.9325 | 0 | 637 | 496.455 | 99.8307 | 5.9682 | 496.455 | 93.4254 | 0.031152 | 478.074 | 89.9678 | 0.023474 | 551.023 | 551.017 | 1237440 | 41.0946 | 1204830 | 1120120 | 1092140 | 0 | 0 | 1081880 | 673.251 | 0 | 0 | 0 | 0 | 1081880 | 673.251 | 1066630 | 1045296.8125
3329 | 2005-05-19 16:00 | 417 | 751 | 82 | 29.79 | 5.71 | 0 | 26.4387 | 276.92 | 69.0266 | 0 | 417 | 269.31 | 81.569 | 3.907 | 269.31 | 76.3354 | 0.020393 | 245.156 | 73.5102 | 0.015367 | 309.121 | 309.118 | 694200 | 36.446 | 651403 | 617254 | 602846 | 0 | 0 | 599641 | 667.493 | 0 | 0 | 0 | 0 | 599641 | 667.493 | 591614 | 579782.1875
3330 | 2005-05-19 17:00 | 202 | 543 | 67 | 29.07 | 5.71 | 0 | 14.3156 | 284.608 | 83.0605 | 0 | 202 | 65.966 | 58.8554 | 1.8926 | 65.966 | 55.0791 | 0.0098786 | 41.9654 | 53.0406 | 0.0074438 | 92.1631 | 92.1611 | 206971 | 31.0544 | 176620 | 171167 | 167128 | 0 | 0 | 166851 | 632.295 | 0 | 0 | 0 | 4184.38 | 162667 | 660 | 158073 | 154912
3331 | 2005-05-19 18:00 | 23 | 206 | 8 | 28.34 | 7.67 | 0 | 2.6168 | 292.567 | 90 | 0 | 23 | 0 | 6.1266 | 0.21549 | 0 | 5.7335 | 0.0011248 | 0 | 5.5213 | 0.00084756 | 5.3565 | 5.3561 | 12028.4 | 28.4418 | 5573.05 | 5497.86 | 5399.87 | 0 | 0 | 5399.37 | 477.813 | 0 | 0 | 0 | 5399.37 | 0 | 660 | 0 | 0
3332 | 2005-05-19 19:00 | 0 | 0 | 0 | 27.62 | 7.67 | 0
3333 | 2005-05-19 20:00 | 0 | 0 | 0 | 26.42 | 7.67 | 0
3334 | 2005-05-19 21:00 | 0 | 0 | 0 | 25.23 | 7.15 | 0
3335 | 2005-05-19 22:00 | 0 | 0 | 0 | 24.04 | 7.15 | 0
3336 | 2005-05-19 23:00 | 0 | 0 | 0 | 23.1 | 7.15 | 0
3337 | 2005-05-20 | 0 | 0 | 0 | 22.16 | 6.93 | 0
3338 | 2005-05-20 01:00 | 0 | 0 | 0 | 21.22 | 6.93 | 0
3339 | 2005-05-20 02:00 | 0 | 0 | 0 | 20.32 | 6.93 | 0
3340 | 2005-05-20 03:00 | 0 | 0 | 0 | 19.42 | 8.58 | 0
3341 | 2005-05-20 04:00 | 2 | 49 | 1 | 18.52 | 8.58 | 0 | -3.2717 | 62.8349 | 90 | 0 | 2 | 0 | 0.69784 | 0.018738 | 0 | 0.65307 | 0 | 0 | 0.6289 | 0 | 0.61003 | 0.60999 | 1369.89 | 18.5309 | 91.0197 | 90.3215 | 89.6207 | 0 | 0 | 89.6171 | 94.7079 | 0 | 0 | 0 | 89.6171 | 0 | 660 | 0 | 0
3342 | 2005-05-20 05:00 | 104 | 408 | 45 | 18.92 | 8.58 | 0 | 8.1014 | 71.1632 | 90 | 0 | 104 | 0 | 35.1472 | 0.9744 | 0 | 32.8921 | 0.005086 | 0 | 31.6748 | 0.0038324 | 30.7283 | 30.7263 | 69003.7 | 19.4713 | 51812.5 | 53360.2 | 52086.2 | 0 | 0 | 52058.1 | 618.875 | 0 | 0 | 0 | 2923.89 | 49134.2 | 660 | 47412 | 46463.7656
3343 | 2005-05-20 06:00 | 314 | 703 | 73 | 19.32 | 4.14 | 0 | 20.033 | 78.893 | 76.4686 | 0 | 314 | 164.609 | 68.0158 | 2.9419 | 160.759 | 63.6518 | 0.015356 | 134.443 | 61.2961 | 0.011571 | 189.879 | 189.869 | 426404 | 23.848 | 386734 | 388723 | 360565 | 0 | 0 | 359448 | 681.768 | 0 | 0 | 0 | 1382.01 | 358066 | 685.252 | 351547 | 344515.9375
3344 | 2005-05-20 07:00 | 530 | 826 | 88 | 19.72 | 4.14 | 0 | 32.2831 | 86.6589 | 62.4037 | 0 | 530 | 383.356 | 89.6556 | 4.9657 | 383.356 | 83.9031 | 0.025919 | 361.146 | 80.7979 | 0.019531 | 428.705 | 428.702 | 962755 | 29.9436 | 922860 | 902630 | 879328 | 0 | 0 | 873178 | 701.621 | 0 | 0 | 0 | 0 | 873178 | 701.621 | 860009 | 842809.1875
3345 | 2005-05-20 08:00 | 727 | 892 | 100 | 21.93 | 4.14 | 0 | 44.6283 | 95.3625 | 48.3335 | 0 | 727 | 593.343 | 103.803 | 6.8114 | 593.343 | 97.1429 | 0.035553 | 578.384 | 93.5477 | 0.02679 | 651.799 | 651.795 | 1463760 | 37.474 | 1439550 | 1362340 | 1328240 | 0 | 0 | 1313840 | 690.116 | 0 | 0 | 0 | 0 | 1313840 | 690.116 | 1292920 | 1267066.25
3346 | 2005-05-20 09:00 | 887 | 928 | 111 | 24.14 | 4.27 | 0 | 56.7511 | 106.799 | 34.4205 | 0 | 887 | 765.436 | 115.375 | 8.3105 | 765.436 | 107.972 | 0.043378 | 757.313 | 103.976 | 0.032686 | 835.482 | 835.472 | 1876260 | 43.8953 | 1871060 | 1721150 | 1678580 | 0 | 0 | 1654830 | 676.472 | 0 | 0 | 0 | 0 | 1654830 | 676.472 | 1625320 | 1592814.5
3347 | 2005-05-20 10:00 | 997 | 949 | 119 | 26.36 | 4.27 | 0 | 67.8762 | 125.803 | 21.1424 | 0 | 997 | 883.985 | 122.992 | 9.3411 | 883.985 | 115.1 | 0.048757 | 880.796 | 110.84 | 0.03674 | 961.922 | 961.92 | 2160230 | 49.1052 | 2169840 | 1949380 | 1903210 | 0 | 0 | 1871620 | 663.257 | 0 | 0 | 0 | -60.2556 | 1871680 | 663.607 | 1834740 | 1798040.375
3348 | 2005-05-20 11:00 | 1019 | 875 | 175 | 27.62 | 4.27 | 0 | 75.1504 | 165.257 | 11.2508 | 0 | 1019 | 856.382 | 185.602 | 9.5472 | 856.382 | 173.693 | 0.049833 | 855.543 | 167.265 | 0.037551 | 992.16 | 992.148 | 2228110 | 51.08 | 2241390 | 1995140 | 1948710 | 0 | 0 | 1915040 | 657.837 | 0 | 0 | 0 | 823.409 | 1914220 | 660.682 | 1875650 | 1838141.375
3349 | 2005-05-20 12:00 | 1025 | 948 | 122 | 28.89 | 4.77 | 0 | 72.6029 | 216.876 | 14.9994 | 0 | 1025 | 914.046 | 125.569 | 9.6035 | 914.046 | 117.513 | 0.050127 | 912.434 | 113.164 | 0.037772 | 994.866 | 994.863 | 2234210 | 51.6582 | 2247820 | 1995360 | 1951890 | 0 | 0 | 1917700 | 653.409 | 0 | 0 | 0 | 1917.65 | 1915790 | 660 | 1877170 | 1839624.25
3350 | 2005-05-20 13:00 | 952 | 941 | 115 | 30.15 | 4.77 | 0 | 62.8965 | 244.674 | 27.2339 | 0 | 952 | 836.023 | 119.262 | 8.9195 | 836.023 | 111.61 | 0.046557 | 830.811 | 107.479 | 0.035082 | 910.176 | 910.168 | 2044010 | 50.9799 | 2047440 | 1822040 | 1781680 | 0 | 0 | 1753070 | 653.243 | 0 | 0 | 0 | 1710.74 | 1751350 | 660 | 1718930 | 1684551.625
3351 | 2005-05-20 14:00 | 818 | 914 | 106 | 30.49 | 4.77 | 0 | 51.148 | 259.157 | 40.9156 | 0 | 818 | 690.886 | 110.226 | 7.664 | 690.886 | 103.153 | 0.040004 | 679.718 | 99.3356 | 0.030144 | 755.711 | 755.706 | 1697130 | 47.7849 | 1683210 | 1518880 | 1482970 | 0 | 0 | 1463500 | 660.926 | 0 | 0 | 0 | -6.1183 | 1463510 | 661.412 | 1440350 | 1411547.75
3352 | 2005-05-20 15:00 | 633 | 855 | 96 | 30.84 | 7.33 | 0 | 38.874 | 268.988 | 54.9269 | 0 | 633 | 491.661 | 99.7155 | 5.9307 | 491.661 | 93.3176 | 0.030956 | 473.463 | 89.864 | 0.023326 | 546.45 | 546.441 | 1227160 | 41.4474 | 1194220 | 1108340 | 1081480 | 0 | 0 | 1071360 | 670.898 | 0 | 0 | 0 | 0 | 1071360 | 670.898 | 1056430 | 1035300.5625
3353 | 2005-05-20 16:00 | 424 | 699 | 111 | 31.18 | 7.33 | 0 | 26.5526 | 277.113 | 69.0025 | 0 | 424 | 250.899 | 107.552 | 3.9726 | 250.899 | 100.651 | 0.020735 | 228.434 | 96.9262 | 0.015624 | 315.615 | 315.612 | 708782 | 37.3066 | 666014 | 628524 | 612904 | 0 | 0 | 609567 | 665.197 | 0 | 0 | 0 | 0 | 609567 | 665.197 | 601484 | 589454.625
3354 | 2005-05-20 17:00 | 184 | 323 | 103 | 30 | 7.33 | 0 | 14.4367 | 284.78 | 83.019 | 0 | 184 | 39.4881 | 88.7799 | 1.7239 | 39.4881 | 83.0836 | 0.0089984 | 25.2177 | 80.0087 | 0.0067805 | 102.076 | 102.073 | 229229 | 31.9814 | 197463 | 190490 | 185818 | 0 | 0 | 185478 | 634.473 | 0 | 0 | 0 | 4077.86 | 181400 | 660 | 176482 | 172952.125
3355 | 2005-05-20 18:00 | 21 | 124 | 12 | 28.82 | 7.79 | 0 | 2.7492 | 292.725 | 90 | 0 | 21 | 0 | 9.0123 | 0.19675 | 0 | 8.4341 | 0.001027 | 0 | 8.122 | 0.00077386 | 7.8791 | 7.8787 | 17693.6 | 28.9686 | 9692.77 | 9504.84 | 9326.32 | 0 | 0 | 9324.97 | 505.106 | 0 | 0 | 0 | 9324.97 | 0 | 660 | 0 | 0
3356 | 2005-05-20 19:00 | 0 | 0 | 0 | 27.64 | 7.79 | 0
3357 | 2005-05-20 20:00 | 0 | 0 | 0 | 26.48 | 7.79 | 0
3358 | 2005-05-20 21:00 | 0 | 0 | 0 | 25.32 | 7.4 | 0
3359 | 2005-05-20 22:00 | 0 | 0 | 0 | 24.15 | 7.4 | 0
3360 | 2005-05-20 23:00 | 0 | 0 | 0 | 23.08 | 7.4 | 0
3361 | 2005-05-21 | 0 | 0 | 0 | 22.01 | 7.66 | 0
3362 | 2005-05-21 01:00 | 0 | 0 | 0 | 20.95 | 7.66 | 0
3363 | 2005-05-21 02:00 | 0 | 0 | 0 | 19.99 | 7.66 | 0
3364 | 2005-05-21 03:00 | 0 | 0 | 0 | 19.03 | 7.67 | 0
3365 | 2005-05-21 04:00 | 2 | 48 | 1 | 18.08 | 7.67 | 0 | -3.1562 | 62.6665 | 90 | 0 | 2 | 0 | 0.69701 | 0.018738 | 0 | 0.65229 | 0 | 0 | 0.62815 | 0 | 0.60931 | 0.60925 | 1368.23 | 18.0916 | 90.8007 | 90.0564 | 89.3537 | 0 | 0 | 89.3501 | 94.597 | 0 | 0 | 0 | 89.3501 | 0 | 660 | 0 | 0
3366 | 2005-05-21 05:00 | 102 | 386 | 46 | 18.37 | 7.67 | 0 | 8.2021 | 70.9843 | 90 | 0 | 102 | 0 | 35.9922 | 0.95566 | 0 | 33.6829 | 0.0049882 | 0 | 32.4363 | 0.0037587 | 31.4668 | 31.4674 | 70667.6 | 18.9678 | 53248 | 54981.4 | 53592.5 | 0 | 0 | 53563.1 | 622.019 | 0 | 0 | 0 | 2466.36 | 51096.7 | 660 | 49311.7 | 48325.4883
3367 | 2005-05-21 06:00 | 315 | 670 | 84 | 18.67 | 3.61 | 0 | 20.1232 | 78.6987 | 76.4649 | 0 | 315 | 157.144 | 78.1268 | 2.9513 | 153.749 | 73.1141 | 0.015405 | 128.59 | 70.4082 | 0.011608 | 193.039 | 193.038 | 433521 | 23.4367 | 393638 | 396436 | 371755 | 0 | 0 | 370566 | 680.335 | 0 | 0 | 0 | 3418.66 | 367147 | 685.96 | 360638 | 353425
3368 | 2005-05-21 07:00 | 529 | 822 | 89 | 18.96 | 3.61 | 0 | 32.3674 | 86.44 | 62.4176 | 0 | 529 | 380.558 | 90.5206 | 4.9563 | 380.558 | 84.7126 | 0.02587 | 358.491 | 81.5775 | 0.019494 | 426.886 | 426.879 | 958665 | 29.5011 | 918691 | 900342 | 877488 | 0 | 0 | 871401 | 703.923 | 0 | 0 | 0 | 0 | 871401 | 703.923 | 858159 | 840995.5
3369 | 2005-05-21 08:00 | 727 | 892 | 99 | 21.2 | 3.61 | 0 | 44.7132 | 95.1031 | 48.3672 | 0 | 727 | 593.006 | 102.727 | 6.8114 | 593.006 | 96.1358 | 0.035553 | 578.026 | 92.5779 | 0.02679 | 650.512 | 650.506 | 1460870 | 37.2632 | 1436540 | 1360780 | 1325520 | 0 | 0 | 1311240 | 691.243 | 0 | 0 | 0 | 0 | 1311240 | 691.243 | 1290340 | 1264531.625
3370 | 2005-05-21 09:00 | 888 | 928 | 111 | 23.45 | 1.29 | 0 | 56.8475 | 106.473 | 34.4809 | 0 | 888 | 765.025 | 115.261 | 8.3199 | 765.025 | 107.866 | 0.043427 | 756.873 | 103.874 | 0.032723 | 834.956 | 834.949 | 1875080 | 47.5101 | 1869820 | 1690750 | 1650790 | 0 | 0 | 1627020 | 665.323 | 0 | 0 | 0 | 0 | 1627020 | 665.323 | 1598760 | 1566785.25
3371 | 2005-05-21 10:00 | 997 | 949 | 118 | 25.69 | 1.29 | 0 | 68.0065 | 125.39 | 21.2493 | 0 | 997 | 883.537 | 121.886 | 9.3411 | 883.537 | 114.066 | 0.048757 | 880.315 | 109.844 | 0.03674 | 960.49 | 960.484 | 2157010 | 53.3676 | 2166440 | 1906380 | 1865280 | 0 | 0 | 1833500 | 647.831 | 0 | 0 | 0 | 8284.55 | 1825210 | 660 | 1790070 | 1754271.5
3372 | 2005-05-21 11:00 | 1046 | 957 | 122 | 27.48 | 1.29 | 0 | 75.3434 | 165.018 | 11.4453 | 0 | 1046 | 936.086 | 125.19 | 9.8002 | 936.086 | 117.157 | 0.051154 | 935.137 | 112.821 | 0.038545 | 1016.56 | 1016.55 | 2282920 | 56.7733 | 2299190 | 1990420 | 1946740 | 0 | 0 | 1911090 | 637.704 | 0 | 0 | 0 | 27718.2 | 1883380 | 660 | 1846020 | 1809100.375
3373 | 2005-05-21 12:00 | 1027 | 949 | 122 | 29.27 | 2.42 | 0 | 72.7823 | 217.189 | 15.1268 | 0 | 1027 | 914.63 | 125.428 | 9.6222 | 914.63 | 117.38 | 0.050225 | 912.988 | 113.036 | 0.037845 | 995.28 | 995.273 | 2235130 | 55.8622 | 2248780 | 1955290 | 1910810 | 0 | 0 | 1876820 | 641.488 | 0 | 0 | 0 | 20453.3 | 1856370 | 660 | 1820050 | 1783649.375
3374 | 2005-05-21 13:00 | 953 | 940 | 116 | 31.06 | 2.42 | 0 | 63.0313 | 245.005 | 27.2852 | 0 | 953 | 834.634 | 120.118 | 8.9289 | 834.634 | 112.411 | 0.046606 | 829.409 | 108.251 | 0.035118 | 909.565 | 909.557 | 2042630 | 55.362 | 2045980 | 1781730 | 1742330 | 0 | 0 | 1713830 | 639.704 | 0 | 0 | 0 | 20489.8 | 1693340 | 660 | 1662970 | 1629712.125
3375 | 2005-05-21 14:00 | 815 | 907 | 108 | 31.9 | 2.42 | 0 | 51.2635 | 259.421 | 40.9311 | 0 | 815 | 684.764 | 112.077 | 7.6359 | 684.764 | 104.886 | 0.039857 | 673.683 | 101.004 | 0.030033 | 751.476 | 751.472 | 1687610 | 51.9782 | 1673250 | 1479040 | 1444540 | 0 | 0 | 1425230 | 646.25 | 0 | 0 | 0 | 7663.18 | 1417560 | 660 | 1395580 | 1367671.5
3376 | 2005-05-21 15:00 | 640 | 865 | 96 | 32.75 | 2.26 | 0 | 38.9842 | 269.204 | 54.9195 | 0 | 640 | 496.977 | 99.6042 | 5.9963 | 496.977 | 93.2134 | 0.031299 | 478.589 | 89.7637 | 0.023584 | 551.325 | 551.324 | 1238140 | 47.6384 | 1205550 | 1085640 | 1060510 | 0 | 0 | 1050200 | 651.595 | 0 | 0 | 0 | 2556.81 | 1047640 | 660 | 1033720 | 1013048.125
3377 | 2005-05-21 16:00 | 416 | 740 | 83 | 33.6 | 2.26 | 0 | 26.6651 | 277.299 | 68.9768 | 0 | 416 | 266.197 | 82.3483 | 3.8976 | 266.197 | 77.0647 | 0.020344 | 242.406 | 74.2126 | 0.01533 | 307.135 | 307.131 | 689736 | 41.894 | 646935 | 596617 | 582987 | 0 | 0 | 579795 | 647.412 | 0 | 0 | 0 | 2529.81 | 577265 | 660 | 569695 | 558300.875
3378 | 2005-05-21 17:00 | 201 | 525 | 68 | 33.17 | 2.26 | 0 | 14.5564 | 284.947 | 82.9763 | 0 | 201 | 64.7079 | 59.6224 | 1.8832 | 64.7079 | 55.7969 | 0.0098297 | 41.4844 | 53.7319 | 0.0074069 | 92.367 | 92.3651 | 207429 | 35.6643 | 177047 | 167383 | 163678 | 0 | 0 | 163399 | 616.637 | 0 | 0 | 0 | 11857.2 | 151542 | 660 | 147161 | 144218
3379 | 2005-05-21 18:00 | 24 | 205 | 8 | 32.74 | 4.21 | 0 | 2.8799 | 292.878 | 90 | 0 | 24 | 0 | 6.0611 | 0.22486 | 0 | 5.6722 | 0.0011737 | 0 | 5.4622 | 0.00088441 | 5.2992 | 5.2991 | 11900.5 | 32.8658 | 5483.69 | 5310.56 | 5207.61 | 0 | 0 | 5207.12 | 465.611 | 0 | 0 | 0 | 5207.12 | 0 | 660 | 0 | 0
3380 | 2005-05-21 19:00 | 0 | 0 | 0 | 32.3 | 4.21 | 0
3381 | 2005-05-21 20:00 | 0 | 0 | 0 | 30.76 | 4.21 | 0
3382 | 2005-05-21 21:00 | 0 | 0 | 0 | 29.22 | 5.62 | 0
3383 | 2005-05-21 22:00 | 0 | 0 | 0 | 27.68 | 5.62 | 0
3384 | 2005-05-21 23:00 | 0 | 0 | 0 | 26.36 | 5.62 | 0
3385 | 2005-05-22 | 0 | 0 | 0 | 25.03 | 6.31 | 0
3386 | 2005-05-22 01:00 | 0 | 0 | 0 | 23.71 | 6.31 | 0
3387 | 2005-05-22 02:00 | 0 | 0 | 0 | 22.95 | 6.31 | 0
3388 | 2005-05-22 03:00 | 0 | 0 | 0 | 22.2 | 3.59 | 0
3389 | 2005-05-22 04:00 | 2 | 55 | 1 | 21.45 | 3.59 | 0 | -3.0459 | 62.5014 | 90 | 0 | 2 | 0 | 0.69622 | 0.018738 | 0 | 0.65155 | 0 | 0 | 0.62744 | 0 | 0.60861 | 0.60858 | 1366.72 | 21.465 | 90.6025 | 90.2228 | 89.5396 | 0 | 0 | 89.536 | 94.483 | 0 | 0 | 0 | 89.536 | 0 | 660 | 0 | 0
3390 | 2005-05-22 05:00 | 110 | 427 | 47 | 21.59 | 3.59 | 0 | 8.2978 | 70.809 | 90 | 0 | 110 | 0 | 36.8445 | 1.0306 | 0 | 34.4804 | 0.0053795 | 0 | 33.2043 | 0.0040535 | 32.2122 | 32.2119 | 72339.8 | 22.3865 | 54692.8 | 55466 | 54100.3 | 0 | 0 | 54069.3 | 611.478 | 0 | 0 | 0 | 4663.54 | 49405.8 | 660 | 47674.8 | 46721.3359
3391 | 2005-05-22 06:00 | 317 | 703 | 73 | 21.73 | 1.16 | 0 | 20.2084 | 78.5085 | 76.4639 | 0 | 317 | 165.328 | 67.8135 | 2.97 | 162.064 | 63.4625 | 0.015503 | 135.547 | 61.1138 | 0.011681 | 190.772 | 190.757 | 428402 | 27.2752 | 388652 | 384332 | 361534 | 0 | 0 | 360362 | 665.966 | 0 | 0 | 0 | 6636.57 | 353726 | 675.933 | 347437 | 340487.9375
3392 | 2005-05-22 07:00 | 532 | 826 | 88 | 21.87 | 1.16 | 0 | 32.4468 | 86.2256 | 62.4339 | 0 | 532 | 382.972 | 89.4362 | 4.9844 | 382.972 | 83.6979 | 0.026017 | 360.742 | 80.6003 | 0.019604 | 428.121 | 428.117 | 961444 | 34.315 | 921522 | 883370 | 861264 | 0 | 0 | 855118 | 687.217 | 0 | 0 | 0 | 0 | 855118 | 687.217 | 842838 | 825981.0625
3393 | 2005-05-22 08:00 | 706 | 809 | 136 | 24.25 | 1.16 | 0 | 44.7929 | 94.8488 | 48.4031 | 0 | 706 | 537.105 | 140.57 | 6.6147 | 537.105 | 131.551 | 0.034526 | 523.509 | 126.683 | 0.026016 | 630.711 | 630.702 | 1416400 | 42.584 | 1390290 | 1284440 | 1252640 | 0 | 0 | 1239170 | 672.923 | 0 | 0 | 0 | 0 | 1239170 | 672.923 | 1220670 | 1196256.125
3394 | 2005-05-22 09:00 | 881 | 916 | 114 | 26.63 | 0.76 | 0 | 56.9382 | 106.153 | 34.5429 | 0 | 881 | 753.839 | 118.082 | 8.2543 | 753.839 | 110.506 | 0.043085 | 745.772 | 106.416 | 0.032465 | 826.653 | 826.647 | 1856440 | 51.3163 | 1850250 | 1642310 | 1604750 | 0 | 0 | 1581240 | 650.344 | 0 | 0 | 0 | 3467.68 | 1577770 | 660 | 1551300 | 1520273.875
3395 | 2005-05-22 10:00 | 995 | 945 | 119 | 29.01 | 0.76 | 0 | 68.1303 | 124.979 | 21.3565 | 0 | 995 | 879.114 | 122.736 | 9.3224 | 879.114 | 114.861 | 0.04866 | 875.873 | 110.61 | 0.036666 | 956.924 | 956.92 | 2149010 | 57.5867 | 2158010 | 1859320 | 1816970 | 0 | 0 | 1785480 | 634.141 | 0 | 0 | 0 | 36087.1 | 1749400 | 660 | 1717040 | 1682700.5
3396 | 2005-05-22 11:00 | 1047 | 956 | 123 | 30.61 | 0.76 | 0 | 75.5301 | 164.771 | 11.6354 | 0 | 1047 | 934.661 | 126.015 | 9.8096 | 934.661 | 117.929 | 0.051203 | 933.681 | 113.565 | 0.038582 | 1015.87 | 1015.86 | 2281370 | 60.9468 | 2297560 | 1947270 | 1904250 | 0 | 0 | 1868650 | 623.831 | 0 | 0 | 0 | 73747.1 | 1794900 | 660 | 1760890 | 1725671.75
3397 | 2005-05-22 12:00 | 1032 | 954 | 121 | 32.21 | 3.74 | 0 | 72.9573 | 217.492 | 15.2503 | 0 | 1032 | 919.289 | 124.32 | 9.669 | 919.289 | 116.343 | 0.050469 | 917.611 | 112.037 | 0.03803 | 998.796 | 998.788 | 2243030 | 56.6632 | 2257120 | 1954840 | 1912390 | 0 | 0 | 1877950 | 637.367 | 0 | 0 | 0 | 27408.4 | 1850540 | 660 | 1814440 | 1778154.25
3398 | 2005-05-22 13:00 | 948 | 933 | 116 | 33.81 | 3.74 | 0 | 63.1635 | 245.325 | 27.334 | 0 | 948 | 828.313 | 120 | 8.882 | 828.313 | 112.301 | 0.046361 | 823.108 | 108.144 | 0.034934 | 903.349 | 903.344 | 2028680 | 55.9264 | 2031300 | 1763850 | 1724990 | 0 | 0 | 1696830 | 637.105 | 0 | 0 | 0 | 25001.4 | 1671830 | 660 | 1642200 | 1609360.75
3399 | 2005-05-22 14:00 | 793 | 860 | 121 | 34.24 | 3.74 | 0 | 51.3772 | 259.677 | 40.9445 | 0 | 793 | 649.7 | 124.567 | 7.4298 | 649.7 | 116.575 | 0.038781 | 639.178 | 112.261 | 0.029222 | 728.923 | 728.92 | 1636970 | 52.086 | 1620270 | 1431020 | 1398740 | 0 | 0 | 1380420 | 642.828 | 0 | 0 | 0 | 9704.49 | 1370720 | 660 | 1349850 | 1322853
3400 | 2005-05-22 15:00 | 617 | 786 | 121 | 34.67 | 4.48 | 0 | 39.0931 | 269.414 | 54.9103 | 0 | 617 | 452.168 | 123.935 | 5.7808 | 452.168 | 115.983 | 0.030174 | 435.448 | 111.691 | 0.022737 | 530.747 | 530.739 | 1191900 | 47.0485 | 1157840 | 1045400 | 1020390 | 0 | 0 | 1010830 | 651.039 | 0 | 0 | 0 | 1962.56 | 1008870 | 660 | 995700 | 975786.1875
3401 | 2005-05-22 16:00 | 429 | 702 | 112 | 35.1 | 4.48 | 0 | 26.7764 | 277.479 | 68.9496 | 0 | 429 | 252.742 | 108.261 | 4.0194 | 252.742 | 101.315 | 0.02098 | 230.197 | 97.5651 | 0.015809 | 317.945 | 317.942 | 714020 | 42.5154 | 671267 | 617284 | 602240 | 0 | 0 | 598856 | 648.814 | 0 | 0 | 0 | 2585.97 | 596270 | 660 | 588508 | 576737.3125
3402 | 2005-05-22 17:00 | 181 | 296 | 106 | 33.92 | 4.48 | 0 | 14.6747 | 285.108 | 82.9325 | 0 | 181 | 36.4265 | 91.1932 | 1.6958 | 36.4265 | 85.3421 | 0.0088517 | 23.445 | 82.1836 | 0.0066699 | 102.466 | 102.462 | 230104 | 36.3097 | 198284 | 186903 | 182472 | 0 | 0 | 182128 | 618.798 | 0 | 0 | 0 | 11298.5 | 170830 | 660 | 166090 | 162767.875
3403 | 2005-05-22 18:00 | 22 | 117 | 13 | 32.73 | 7.92 | 0 | 3.0088 | 293.024 | 90 | 0 | 22 | 0 | 9.9786 | 0.20612 | 0 | 9.3383 | 0.0010759 | 0 | 8.9927 | 0.00081071 | 8.7237 | 8.7231 | 19590 | 32.8931 | 11121.8 | 10673.3 | 10471.3 | 0 | 0 | 10469.5 | 497.736 | 0 | 0 | 0 | 10469.5 | 0 | 660 | 0 | 0
3404 | 2005-05-22 19:00 | 0 | 0 | 0 | 31.55 | 7.92 | 0
3405 | 2005-05-22 20:00 | 0 | 0 | 0 | 29.98 | 7.92 | 0
3406 | 2005-05-22 21:00 | 0 | 0 | 0 | 28.41 | 5.96 | 0
3407 | 2005-05-22 22:00 | 0 | 0 | 0 | 26.84 | 5.96 | 0
3408 | 2005-05-22 23:00 | 0 | 0 | 0 | 25.66 | 5.96 | 0
3409 | 2005-05-23 | 0 | 0 | 0 | 24.48 | 7.15 | 0
3410 | 2005-05-23 01:00 | 0 | 0 | 0 | 23.31 | 7.15 | 0
3411 | 2005-05-23 02:00 | 0 | 0 | 0 | 22.35 | 7.15 | 0
3412 | 2005-05-23 03:00 | 0 | 0 | 0 | 21.4 | 8.22 | 0
3413 | 2005-05-23 04:00 | 3 | 56 | 2 | 20.44 | 8.22 | 0 | -2.9408 | 62.3397 | 90 | 0 | 3 | 0 | 1.5746 | 0.028108 | 0 | 1.4736 | 0 | 0 | 1.4191 | 0 | 1.3765 | 1.3764 | 3091.08 | 20.4653 | 461.655 | 459.286 | 457.175 | 0 | 0 | 457.155 | 203.486 | 0 | 0 | 0 | 457.155 | 0 | 660 | 0 | 0
3414 | 2005-05-23 05:00 | 109 | 421 | 47 | 20.85 | 8.22 | 0 | 8.3886 | 70.6374 | 90 | 0 | 109 | 0 | 36.7265 | 1.0212 | 0 | 34.37 | 0.0053305 | 0 | 33.098 | 0.0040167 | 32.109 | 32.1078 | 72106.3 | 21.4392 | 54490.6 | 55540 | 54173.4 | 0 | 0 | 54142.5 | 614.573 | 0 | 0 | 0 | 3952.64 | 50189.9 | 660 | 48433.9 | 47465.1914
3415 | 2005-05-23 06:00 | 315 | 696 | 73 | 21.26 | 4.04 | 0 | 20.2888 | 78.3223 | 76.4655 | 0 | 315 | 163.331 | 67.7151 | 2.9513 | 160.367 | 63.3704 | 0.015405 | 134.123 | 61.0251 | 0.011608 | 189.305 | 189.295 | 425117 | 25.804 | 385437 | 383871 | 362874 | 0 | 0 | 361706 | 668.753 | 0 | 0 | 0 | 7464.23 | 354242 | 678.791 | 347868 | 340910.75
3416 | 2005-05-23 07:00 | 532 | 824 | 89 | 21.66 | 4.04 | 0 | 32.5213 | 86.0158 | 62.4526 | 0 | 532 | 381.092 | 90.3048 | 4.9844 | 381.092 | 84.5107 | 0.026017 | 358.946 | 81.383 | 0.019604 | 427.138 | 427.133 | 959235 | 31.9133 | 919269 | 891073 | 868930 | 0 | 0 | 862795 | 694.189 | 0 | 0 | 0 | 0 | 862795 | 694.189 | 850104 | 833101.9375
3417 | 2005-05-23 08:00 | 730 | 891 | 101 | 23.83 | 4.04 | 0 | 44.8675 | 94.5996 | 48.4409 | 0 | 730 | 591.484 | 104.484 | 6.8395 | 591.484 | 97.78 | 0.0357 | 576.478 | 94.1612 | 0.026901 | 650.546 | 650.542 | 1460950 | 39.4462 | 1436620 | 1347250 | 1314090 | 0 | 0 | 1299780 | 684.506 | 0 | 0 | 0 | 0 | 1299780 | 684.506 | 1279430 | 1253840.125
3418 | 2005-05-23 09:00 | 889 | 928 | 111 | 26 | 3.83 | 0 | 57.0232 | 105.838 | 34.6064 | 0 | 889 | 763.33 | 115.044 | 8.3292 | 763.33 | 107.663 | 0.043476 | 755.125 | 103.678 | 0.03276 | 833.071 | 833.068 | 1870860 | 46.2755 | 1865380 | 1696750 | 1656430 | 0 | 0 | 1632740 | 668.654 | 0 | 0 | 0 | 0 | 1632740 | 668.654 | 1604190 | 1572106.375
3419 | 2005-05-23 10:00 | 999 | 948 | 119 | 28.16 | 3.83 | 0 | 68.2476 | 124.573 | 21.464 | 0 | 999 | 881.756 | 122.614 | 9.3598 | 881.756 | 114.746 | 0.048855 | 878.471 | 110.5 | 0.036813 | 959.337 | 959.33 | 2154410 | 51.5085 | 2163700 | 1921420 | 1875490 | 0 | 0 | 1844050 | 654.823 | 0 | 0 | 0 | 1401.04 | 1842640 | 660 | 1806850 | 1770710.625
3420 | 2005-05-23 11:00 | 1047 | 956 | 122 | 29.69 | 3.83 | 0 | 75.7103 | 164.516 | 11.8208 | 0 | 1047 | 934.29 | 124.908 | 9.8096 | 934.29 | 116.894 | 0.051203 | 933.278 | 112.568 | 0.038582 | 1014.51 | 1014.5 | 2278330 | 54.3814 | 2294350 | 2010040 | 1962200 | 0 | 0 | 1926990 | 647.332 | 0 | 0 | 0 | 9820.97 | 1917170 | 660 | 1878500 | 1840926.625
3421 | 2005-05-23 12:00 | 1032 | 954 | 120 | 31.21 | 5.74 | 0 | 73.1281 | 217.785 | 15.3697 | 0 | 1032 | 918.938 | 123.217 | 9.669 | 918.938 | 115.311 | 0.050469 | 917.233 | 111.043 | 0.03803 | 997.465 | 997.464 | 2240050 | 52.646 | 2253980 | 1991310 | 1948470 | 0 | 0 | 1914000 | 649.505 | 0 | 0 | 0 | 4748.28 | 1909250 | 660 | 1870890 | 1833470.25
3422 | 2005-05-23 13:00 | 956 | 940 | 117 | 32.74 | 5.74 | 0 | 63.293 | 245.636 | 27.3801 | 0 | 956 | 833.983 | 120.86 | 8.957 | 833.983 | 113.105 | 0.046752 | 828.722 | 108.919 | 0.035229 | 909.547 | 909.542 | 2042600 | 52.2865 | 2045950 | 1809150 | 1767540 | 0 | 0 | 1739180 | 650.725 | 0 | 0 | 0 | 4448.25 | 1734730 | 660 | 1702910 | 1668847
3423 | 2005-05-23 14:00 | 819 | 910 | 107 | 32.75 | 5.74 | 0 | 51.4891 | 259.924 | 40.9557 | 0 | 819 | 687.184 | 110.898 | 7.6734 | 687.184 | 103.783 | 0.040052 | 676.047 | 99.942 | 0.03018 | 752.739 | 752.733 | 1690450 | 48.9266 | 1676220 | 1504180 | 1470070 | 0 | 0 | 1450630 | 655.66 | 0 | 0 | 0 | 535.045 | 1450100 | 660 | 1427330 | 1398783
3424 | 2005-05-23 15:00 | 642 | 865 | 95 | 32.76 | 7.41 | 0 | 39.2005 | 269.616 | 54.8994 | 0 | 642 | 497.65 | 97.7947 | 6.015 | 497.65 | 91.52 | 0.031397 | 479.259 | 88.1329 | 0.023658 | 550.393 | 550.391 | 1236040 | 43.3901 | 1203380 | 1106540 | 1079930 | 0 | 0 | 1069670 | 665.702 | 0 | 0 | 0 | 0 | 1069670 | 665.702 | 1055030 | 1033931.375
3425 | 2005-05-23 16:00 | 432 | 750 | 92 | 32.78 | 7.41 | 0 | 26.8862 | 277.653 | 68.921 | 0 | 432 | 270.405 | 89.304 | 4.0475 | 270.405 | 83.5741 | 0.021127 | 246.333 | 80.481 | 0.015919 | 317.025 | 317.02 | 711945 | 38.9028 | 669184 | 626595 | 611240 | 0 | 0 | 607881 | 661.088 | 0 | 0 | 0 | -5.2365 | 607887 | 661.37 | 599942 | 587943.625
3426 | 2005-05-23 17:00 | 203 | 516 | 71 | 31.85 | 7.41 | 0 | 14.7914 | 285.262 | 82.8875 | 0 | 203 | 64.0183 | 62.2481 | 1.902 | 64.0183 | 58.2541 | 0.0099275 | 41.3673 | 56.0982 | 0.0074806 | 94.5487 | 94.5463 | 212327 | 33.676 | 181622 | 173587 | 169671 | 0 | 0 | 169379 | 624.215 | 0 | 0 | 0 | 7689.98 | 161689 | 660 | 157113 | 153971.0938
3427 | 2005-05-23 18:00 | 25 | 208 | 9 | 30.93 | 8.2 | 0 | 3.1357 | 293.165 | 90 | 0 | 25 | 0 | 6.8575 | 0.23423 | 0 | 6.4175 | 0.0012226 | 0 | 6.18 | 0.00092126 | 5.9955 | 5.9953 | 13463.9 | 31.0402 | 6590.7 | 6418.06 | 6293.63 | 0 | 0 | 6292.95 | 482.207 | 0 | 0 | 0 | 6292.95 | 0 | 660 | 0 | 0
3428 | 2005-05-23 19:00 | 0 | 0 | 0 | 30.01 | 8.2 | 0
3429 | 2005-05-23 20:00 | 0 | 0 | 0 | 28.59 | 8.2 | 0
3430 | 2005-05-23 21:00 | 0 | 0 | 0 | 27.18 | 8.77 | 0
3431 | 2005-05-23 22:00 | 0 | 0 | 0 | 25.76 | 8.77 | 0
3432 | 2005-05-23 23:00 | 0 | 0 | 0 | 24.72 | 8.77 | 0
3433 | 2005-05-24 | 0 | 0 | 0 | 23.67 | 9.51 | 0
3434 | 2005-05-24 01:00 | 0 | 0 | 0 | 22.62 | 9.51 | 0
3435 | 2005-05-24 02:00 | 0 | 0 | 0 | 21.8 | 9.51 | 0
3436 | 2005-05-24 03:00 | 0 | 0 | 0 | 20.98 | 8.29 | 0
3437 | 2005-05-24 04:00 | 2 | 48 | 1 | 20.15 | 8.29 | 0 | -2.8409 | 62.1813 | 90 | 0 | 2 | 0 | 0.69475 | 0.018738 | 0 | 0.65017 | 0 | 0 | 0.62611 | 0 | 0.60733 | 0.60728 | 1363.79 | 20.1611 | 90.2074 | 89.6898 | 89.0096 | 0 | 0 | 89.0061 | 94.3028 | 0 | 0 | 0 | 89.0061 | 0 | 660 | 0 | 0
3438 | 2005-05-24 05:00 | 102 | 347 | 50 | 20.5 | 8.29 | 0 | 8.4743 | 70.4696 | 90 | 0 | 102 | 0 | 37.5833 | 0.95566 | 0 | 35.1719 | 0.0049882 | 0 | 33.8702 | 0.0037587 | 32.8577 | 32.8557 | 73785.4 | 21.1003 | 55943.6 | 57121.4 | 55746.7 | 0 | 0 | 55714.2 | 616.543 | 0 | 0 | 0 | 3599.58 | 52114.7 | 660 | 50297.3 | 49291.3555
3439 | 2005-05-24 06:00 | 310 | 654 | 82 | 20.86 | 2.16 | 0 | 20.3642 | 78.1403 | 76.4698 | 0 | 310 | 153.288 | 75.9545 | 2.9045 | 150.736 | 71.0811 | 0.01516 | 126.058 | 68.4505 | 0.011424 | 188.684 | 188.678 | 423729 | 25.9893 | 384055 | 382159 | 362592 | 0 | 0 | 361423 | 667.671 | 0 | 0 | 0 | 4950.22 | 356472 | 678.884 | 350081 | 343079.4375
3440 | 2005-05-24 07:00 | 525 | 805 | 91 | 21.21 | 2.16 | 0 | 32.5909 | 85.8107 | 62.4735 | 0 | 525 | 372.379 | 92.1457 | 4.9188 | 372.379 | 86.2335 | 0.025675 | 350.711 | 83.042 | 0.019346 | 420.759 | 420.754 | 944907 | 32.6484 | 904672 | 873907 | 852066 | 0 | 0 | 846143 | 692.514 | 0 | 0 | 0 | 0 | 846143 | 692.514 | 833768 | 817092.1875
3441 | 2005-05-24 08:00 | 726 | 884 | 102 | 23.36 | 2.16 | 0 | 44.9371 | 94.3559 | 48.4806 | 0 | 726 | 585.61 | 105.362 | 6.8021 | 585.61 | 98.602 | 0.035504 | 570.718 | 94.9528 | 0.026753 | 645.727 | 645.723 | 1450130 | 40.9143 | 1425370 | 1327480 | 1294760 | 0 | 0 | 1280640 | 678.886 | 0 | 0 | 0 | 0 | 1280640 | 678.886 | 1260960 | 1235742.875
3442 | 2005-05-24 09:00 | 890 | 928 | 111 | 25.51 | 3.63 | 0 | 57.1028 | 105.529 | 34.6712 | 0 | 890 | 763.028 | 114.94 | 8.3386 | 763.028 | 107.566 | 0.043525 | 754.791 | 103.585 | 0.032797 | 832.656 | 832.651 | 1869920 | 46.0439 | 1864400 | 1697700 | 1656800 | 0 | 0 | 1633270 | 671.147 | 0 | 0 | 0 | 0 | 1633270 | 671.147 | 1604630 | 1572534.75
3443 | 2005-05-24 10:00 | 989 | 933 | 123 | 27.66 | 3.63 | 0 | 68.3584 | 124.17 | 21.5714 | 0 | 989 | 866.42 | 126.376 | 9.2662 | 866.42 | 118.267 | 0.048366 | 863.158 | 113.89 | 0.036445 | 947.772 | 947.761 | 2128430 | 51.0326 | 2136330 | 1901290 | 1856390 | 0 | 0 | 1825670 | 655.891 | 0 | 0 | 0 | 836.02 | 1824830 | 659.999 | 1789710 | 1753914.125
3444 | 2005-05-24 11:00 | 1048 | 956 | 123 | 28.84 | 3.63 | 0 | 75.884 | 164.252 | 12.0014 | 0 | 1048 | 932.953 | 125.739 | 9.8189 | 932.953 | 117.672 | 0.051252 | 931.911 | 113.317 | 0.038619 | 1013.91 | 1013.91 | 2276980 | 53.8438 | 2292920 | 2014090 | 1968130 | 0 | 0 | 1932830 | 647.785 | 0 | 0 | 0 | 8153.98 | 1924670 | 660 | 1885700 | 1847990.375
3445 | 2005-05-24 12:00 | 1033 | 953 | 122 | 30.02 | 4.2 | 0 | 73.2945 | 218.066 | 15.485 | 0 | 1033 | 916.617 | 125.026 | 9.6784 | 916.617 | 117.004 | 0.050518 | 914.891 | 112.673 | 0.038066 | 996.774 | 996.766 | 2238480 | 53.6975 | 2252330 | 1979560 | 1934580 | 0 | 0 | 1900400 | 648.151 | 0 | 0 | 0 | 8068.82 | 1892340 | 660 | 1854630 | 1817540.375
3446 | 2005-05-24 13:00 | 956 | 940 | 116 | 31.2 | 4.2 | 0 | 63.4199 | 245.936 | 27.4235 | 0 | 956 | 833.723 | 119.773 | 8.957 | 833.723 | 112.089 | 0.046752 | 828.445 | 107.94 | 0.035229 | 908.328 | 908.325 | 2039870 | 52.7766 | 2043070 | 1802210 | 1763370 | 0 | 0 | 1734900 | 647.844 | 0 | 0 | 0 | 7191.45 | 1727710 | 660 | 1696130 | 1662210.25
3447 | 2005-05-24 14:00 | 822 | 913 | 107 | 31.5 | 4.2 | 0 | 51.5992 | 260.162 | 40.9648 | 0 | 822 | 688.932 | 110.803 | 7.7015 | 688.932 | 103.693 | 0.040199 | 677.761 | 99.8558 | 0.030291 | 754.317 | 754.31 | 1693990 | 49.4181 | 1679930 | 1503900 | 1470470 | 0 | 0 | 1450860 | 653.062 | 0 | 0 | 0 | 1344.59 | 1449520 | 660 | 1426760 | 1398227.375
3448 | 2005-05-24 15:00 | 644 | 866 | 95 | 31.81 | 6.1 | 0 | 39.3065 | 269.811 | 54.8866 | 0 | 644 | 498.498 | 97.715 | 6.0338 | 498.498 | 91.4454 | 0.031494 | 480.09 | 88.0611 | 0.023732 | 551.129 | 551.124 | 1237690 | 43.3825 | 1205090 | 1108130 | 1081590 | 0 | 0 | 1071290 | 665.232 | 0 | 0 | 0 | 0 | 1071290 | 665.232 | 1056650 | 1035513.0625
3449 | 2005-05-24 16:00 | 437 | 754 | 94 | 32.11 | 6.1 | 0 | 26.9946 | 277.82 | 68.891 | 0 | 437 | 272.147 | 91.1035 | 4.0944 | 272.147 | 85.2582 | 0.021371 | 247.971 | 82.1028 | 0.016104 | 320.187 | 320.179 | 719039 | 38.8331 | 676299 | 633511 | 618304 | 0 | 0 | 614877 | 662.232 | 0 | 0 | 0 | 0.47876 | 614876 | 662.277 | 606813 | 594676.4375
3450 | 2005-05-24 17:00 | 205 | 486 | 79 | 31.36 | 6.1 | 0 | 14.9064 | 285.411 | 82.8416 | 0 | 205 | 61.0371 | 69.608 | 1.9207 | 61.0371 | 65.1418 | 0.010025 | 39.5984 | 62.731 | 0.0075543 | 99.2668 | 99.265 | 222923 | 33.4444 | 191542 | 183331 | 178919 | 0 | 0 | 178598 | 627.467 | 0 | 0 | 0 | 6433.21 | 172164 | 660 | 167401 | 164052.6406
3451 | 2005-05-24 18:00 | 26 | 199 | 10 | 30.62 | 7.48 | 0 | 3.2607 | 293.3 | 90 | 0 | 26 | 0 | 7.6958 | 0.2436 | 0 | 7.202 | 0.0012715 | 0 | 6.9355 | 0.00095811 | 6.7284 | 6.7281 | 15109.5 | 30.7494 | 7781.49 | 7575.01 | 7431.15 | 0 | 0 | 7430.24 | 489.349 | 0 | 0 | 0 | 7430.24 | 0 | 660 | 0 | 0
3452 | 2005-05-24 19:00 | 0 | 0 | 0 | 29.87 | 7.48 | 0
3453 | 2005-05-24 20:00 | 0 | 0 | 0 | 28.58 | 7.48 | 0
3454 | 2005-05-24 21:00 | 0 | 0 | 0 | 27.29 | 7.41 | 0
3455 | 2005-05-24 22:00 | 0 | 0 | 0 | 26 | 7.41 | 0
3456 | 2005-05-24 23:00 | 0 | 0 | 0 | 24.87 | 7.41 | 0
3457 | 2005-05-25 | 0 | 0 | 0 | 23.74 | 7.74 | 0
3458 | 2005-05-25 01:00 | 0 | 0 | 0 | 22.61 | 7.74 | 0
3459 | 2005-05-25 02:00 | 0 | 0 | 0 | 21.93 | 7.74 | 0
3460 | 2005-05-25 03:00 | 0 | 0 | 0 | 21.24 | 4 | 0
3461 | 2005-05-25 04:00 | 3 | 53 | 2 | 20.56 | 4 | 0 | -2.7461 | 62.0265 | 90 | 0 | 3 | 0 | 1.5723 | 0.028108 | 0 | 1.4714 | 0 | 0 | 1.417 | 0 | 1.3745 | 1.3744 | 3086.56 | 20.5931 | 460.328 | 458.034 | 455.924 | 0 | 0 | 455.904 | 203.21 | 0 | 0 | 0 | 455.904 | 0 | 660 | 0 | 0
3462 | 2005-05-25 05:00 | 106 | 374 | 49 | 20.77 | 4 | 0 | 8.5551 | 70.3056 | 90 | 0 | 106 | 0 | 38.4627 | 0.99314 | 0 | 35.9949 | 0.0051838 | 0 | 34.6628 | 0.0039061 | 33.6267 | 33.6238 | 75510.4 | 21.5793 | 57439.4 | 58499.9 | 57097.9 | 0 | 0 | 57063.9 | 616.762 | 0 | 0 | 0 | 3805.9 | 53258 | 660 | 51404.4 | 50376.3633
3463 | 2005-05-25 06:00 | 321 | 674 | 85 | 20.99 | 2.29 | 0 | 20.4349 | 77.9627 | 76.4767 | 0 | 321 | 158.062 | 78.6299 | 3.0075 | 155.679 | 73.5849 | 0.015698 | 130.176 | 70.8615 | 0.011829 | 195.017 | 195.022 | 437973 | 26.246 | 397939 | 395500 | 375165 | 0 | 0 | 373913 | 667.847 | 0 | 0 | 0 | 2538.99 | 371374 | 678.049 | 365064 | 357762.2812
3464 | 2005-05-25 07:00 | 536 | 827 | 89 | 21.2 | 2.29 | 0 | 32.6556 | 85.6104 | 62.4967 | 0 | 536 | 382.559 | 90.0992 | 5.0219 | 382.559 | 84.3182 | 0.026213 | 360.267 | 81.1977 | 0.019752 | 428.24 | 428.234 | 961703 | 32.7413 | 921784 | 890107 | 869508 | 0 | 0 | 863321 | 691.692 | 0 | 0 | 0 | 0 | 863321 | 691.692 | 850730 | 833715
3465 | 2005-05-25 08:00 | 731 | 891 | 101 | 23.34 | 2.29 | 0 | 45.0016 | 94.1178 | 48.522 | 0 | 731 | 590.091 | 104.301 | 6.8489 | 590.091 | 97.609 | 0.035749 | 575.049 | 93.9966 | 0.026938 | 649.001 | 648.993 | 1457480 | 40.8309 | 1433010 | 1335170 | 1302920 | 0 | 0 | 1288640 | 679.507 | 0 | 0 | 0 | 0 | 1288640 | 679.507 | 1268760 | 1243384.25
3466 | 2005-05-25 09:00 | 890 | 927 | 111 | 25.48 | 2.22 | 0 | 57.1768 | 105.226 | 34.737 | 0 | 890 | 761.785 | 114.84 | 8.3386 | 761.785 | 107.472 | 0.043525 | 753.524 | 103.494 | 0.032797 | 831.34 | 831.334 | 1866960 | 47.99 | 1861290 | 1679140 | 1638260 | 0 | 0 | 1614710 | 662.962 | 0 | 0 | 0 | 0 | 1614710 | 662.962 | 1586930 | 1555193
3467 | 2005-05-25 10:00 | 1000 | 948 | 119 | 27.61 | 2.22 | 0 | 68.4628 | 123.771 | 21.6785 | 0 | 1000 | 880.14 | 122.381 | 9.3692 | 880.14 | 114.529 | 0.048904 | 876.79 | 110.291 | 0.03685 | 957.504 | 957.497 | 2150300 | 53.5361 | 2159370 | 1898560 | 1855300 | 0 | 0 | 1823950 | 649.301 | 0 | 0 | 0 | 8309.99 | 1815640 | 660 | 1780860 | 1745238.375
3468 | 2005-05-25 11:00 | 1048 | 956 | 122 | 29.04 | 2.22 | 0 | 76.0512 | 163.98 | 12.1772 | 0 | 1048 | 932.668 | 124.644 | 9.8189 | 932.668 | 116.646 | 0.051252 | 931.594 | 112.329 | 0.038619 | 1012.64 | 1012.64 | 2274130 | 56.4591 | 2289910 | 1985490 | 1943790 | 0 | 0 | 1908230 | 637.545 | 0 | 0 | 0 | 26362.6 | 1881870 | 660 | 1844570 | 1807682.125
3469 | 2005-05-25 12:00 | 1034 | 953 | 122 | 30.47 | 2.25 | 0 | 73.4565 | 218.336 | 15.5959 | 0 | 1034 | 916.355 | 124.899 | 9.6878 | 916.355 | 116.886 | 0.050567 | 914.604 | 112.56 | 0.038103 | 996.386 | 996.383 | 2237620 | 57.3951 | 2251420 | 1942610 | 1900250 | 0 | 0 | 1866000 | 635.245 | 0 | 0 | 0 | 34072.2 | 1831930 | 660 | 1796540 | 1760606.875
3470 | 2005-05-25 13:00 | 952 | 935 | 115 | 31.89 | 2.25 | 0 | 63.5441 | 246.225 | 27.4641 | 0 | 952 | 829.542 | 118.691 | 8.9195 | 829.542 | 111.076 | 0.046557 | 824.274 | 106.965 | 0.035082 | 903.336 | 903.329 | 2028640 | 56.3005 | 2031270 | 1760440 | 1720830 | 0 | 0 | 1692720 | 636.343 | 0 | 0 | 0 | 27406 | 1665310 | 660 | 1635910 | 1603195.75
3471 | 2005-05-25 14:00 | 822 | 911 | 107 | 31.88 | 2.25 | 0 | 51.7075 | 260.392 | 40.9716 | 0 | 822 | 687.831 | 110.71 | 7.7015 | 687.831 | 103.607 | 0.040199 | 676.673 | 99.7725 | 0.030291 | 753.181 | 753.174 | 1691430 | 52.2329 | 1677250 | 1480730 | 1447530 | 0 | 0 | 1428030 | 644.825 | 0 | 0 | 0 | 9154.09 | 1418880 | 659.999 | 1396860 | 1368927.625
3472 | 2005-05-25 15:00 | 638 | 851 | 97 | 31.86 | 4.15 | 0 | 39.411 | 269.999 | 54.8721 | 0 | 638 | 490.319 | 100.186 | 5.9776 | 490.319 | 93.7577 | 0.031201 | 472.229 | 90.2878 | 0.023511 | 545.664 | 545.661 | 1225410 | 44.8644 | 1192410 | 1088510 | 1062320 | 0 | 0 | 1052250 | 660.814 | 0 | 0 | 0 | -8.2755 | 1052260 | 661.19 | 1038190 | 1017423.5
3473 | 2005-05-25 16:00 | 426 | 753 | 82 | 31.85 | 4.15 | 0 | 27.1016 | 277.98 | 68.8596 | 0 | 426 | 272.331 | 81.0673 | 3.9913 | 272.331 | 75.8659 | 0.020833 | 248.192 | 73.0582 | 0.015698 | 311.628 | 311.625 | 699831 | 39.2768 | 657043 | 614013 | 600256 | 0 | 0 | 596986 | 658.287 | 0 | 0 | 0 | 63.5917 | 596923 | 660 | 589153 | 577369.875
3474 | 2005-05-25 17:00 | 208 | 528 | 70 | 31.68 | 4.15 | 0 | 15.0199 | 285.553 | 82.7946 | 0 | 208 | 66.79 | 61.1946 | 1.9488 | 66.79 | 57.2682 | 0.010172 | 43.5043 | 55.1488 | 0.0076649 | 95.701 | 95.6972 | 214912 | 33.9607 | 184038 | 175637 | 171714 | 0 | 0 | 171414 | 623.82 | 0 | 0 | 0 | 8040.48 | 163374 | 660 | 158767 | 155591.8906
3475 | 2005-05-25 18:00 | 27 | 219 | 9 | 31.51 | 5.45 | 0 | 3.3837 | 293.429 | 90 | 0 | 27 | 0 | 6.7927 | 0.25297 | 0 | 6.3568 | 0.0013204 | 0 | 6.1216 | 0.00099496 | 5.9389 | 5.9386 | 13336.5 | 31.64 | 6499.59 | 6312.92 | 6190.54 | 0 | 0 | 6189.88 | 478.788 | 0 | 0 | 0 | 6189.88 | 0 | 660 | 0 | 0
3476 | 2005-05-25 19:00 | 0 | 0 | 0 | 31.34 | 5.45 | 0
3477 | 2005-05-25 20:00 | 0 | 0 | 0 | 30.05 | 5.45 | 0
3478 | 2005-05-25 21:00 | 0 | 0 | 0 | 28.76 | 3.68 | 0
3479 | 2005-05-25 22:00 | 0 | 0 | 0 | 27.46 | 3.68 | 0
3480 | 2005-05-25 23:00 | 0 | 0 | 0 | 26.28 | 3.68 | 0
3481 | 2005-05-26 | 0 | 0 | 0 | 25.1 | 4.45 | 0
3482 | 2005-05-26 01:00 | 0 | 0 | 0 | 23.92 | 4.45 | 0
3483 | 2005-05-26 02:00 | 0 | 0 | 0 | 22.85 | 4.45 | 0
3484 | 2005-05-26 03:00 | 0 | 0 | 0 | 21.77 | 2.14 | 0
3485 | 2005-05-26 04:00 | 3 | 58 | 1 | 20.69 | 2.14 | 0 | -2.6566 | 61.8753 | 90 | 0 | 3 | 0 | 0.72781 | 0.028108 | 0 | 0.68111 | 0 | 0 | 0.6559 | 0 | 0.63622 | 0.63616 | 1428.65 | 20.7073 | 98.9835 | 98.4802 | 97.8038 | 0 | 0 | 97.7998 | 98.1077 | 0 | 0 | 0 | 97.7998 | 0 | 660 | 0 | 0
3486 | 2005-05-26 05:00 | 108 | 396 | 48 | 20.99 | 2.14 | 0 | 8.6309 | 70.1457 | 90 | 0 | 108 | 0 | 37.3866 | 1.0119 | 0 | 34.9878 | 0.0052816 | 0 | 33.6929 | 0.0039798 | 32.686 | 32.685 | 73402 | 21.8797 | 55611.8 | 56549.1 | 55166.4 | 0 | 0 | 55134.4 | 614.068 | 0 | 0 | 0 | 4177.61 | 50956.8 | 660 | 49176.3 | 48192.7773
3487 | 2005-05-26 06:00 | 316 | 664 | 83 | 21.29 | 2.67 | 0 | 20.5007 | 77.7894 | 76.4861 | 0 | 316 | 155.468 | 76.679 | 2.9607 | 153.322 | 71.7591 | 0.015454 | 128.183 | 69.1034 | 0.011645 | 191.379 | 191.37 | 429769 | 26.3188 | 389923 | 387406 | 368002 | 0 | 0 | 366794 | 666.613 | 0 | 0 | 0 | 745.534 | 366048 | 676.605 | 359736 | 352541.5938
3488 | 2005-05-26 07:00 | 522 | 794 | 93 | 21.59 | 2.67 | 0 | 32.7156 | 85.4152 | 62.522 | 0 | 522 | 366.245 | 93.8816 | 4.8907 | 366.245 | 87.858 | 0.025528 | 344.87 | 84.6065 | 0.019236 | 416.611 | 416.607 | 935591 | 32.5376 | 895190 | 865166 | 843378 | 0 | 0 | 837570 | 692.657 | 0 | 0 | 0 | 0 | 837570 | 692.657 | 825314 | 808808.1875
3489 | 2005-05-26 08:00 | 727 | 884 | 101 | 23.91 | 2.67 | 0 | 45.0612 | 93.8854 | 48.5651 | 0 | 727 | 585.237 | 104.214 | 6.8114 | 585.237 | 97.5275 | 0.035553 | 570.281 | 93.918 | 0.02679 | 644.299 | 644.291 | 1446920 | 40.8406 | 1422020 | 1324820 | 1292660 | 0 | 0 | 1278580 | 679.245 | 0 | 0 | 0 | 0 | 1278580 | 679.245 | 1258930 | 1233751.25
3490 | 2005-05-26 09:00 | 891 | 927 | 112 | 26.24 | 4.22 | 0 | 57.2453 | 104.93 | 34.8039 | 0 | 891 | 760.581 | 115.718 | 8.348 | 760.581 | 108.294 | 0.043574 | 752.296 | 104.286 | 0.032834 | 830.916 | 830.918 | 1866020 | 45.9521 | 1860310 | 1694700 | 1652290 | 0 | 0 | 1628770 | 669.564 | 0 | 0 | 0 | 0 | 1628770 | 669.564 | 1600320 | 1568316.625
3491 | 2005-05-26 10:00 | 990 | 933 | 122 | 28.56 | 4.22 | 0 | 68.5608 | 123.378 | 21.7851 | 0 | 990 | 865.926 | 125.178 | 9.2755 | 865.926 | 117.146 | 0.048415 | 862.596 | 112.811 | 0.036482 | 946.18 | 946.172 | 2124860 | 51.0063 | 2132570 | 1898200 | 1858180 | 0 | 0 | 1827110 | 653.053 | 0 | 0 | 0 | 1586.29 | 1825520 | 660 | 1790370 | 1754565.875
3492 | 2005-05-26 11:00 | 1049 | 956 | 122 | 29.76 | 4.22 | 0 | 76.2117 | 163.7 | 12.348 | 0 | 1049 | 932.425 | 124.518 | 9.8283 | 932.425 | 116.528 | 0.0513 | 931.321 | 112.216 | 0.038656 | 1012.27 | 1012.26 | 2273280 | 53.7741 | 2289020 | 2011350 | 1966730 | 0 | 0 | 1931310 | 646.522 | 0 | 0 | 0 | 8383.95 | 1922930 | 660 | 1884030 | 1846344.75
3493 | 2005-05-26 12:00 | 1035 | 953 | 122 | 30.96 | 3.86 | 0 | 73.6141 | 218.593 | 15.7024 | 0 | 1035 | 916.137 | 124.777 | 9.6971 | 916.137 | 116.772 | 0.050616 | 914.362 | 112.45 | 0.03814 | 996.044 | 996.038 | 2236840 | 55.1541 | 2250590 | 1963830 | 1918200 | 0 | 0 | 1884190 | 643.589 | 0 | 0 | 0 | 15143.4 | 1869040 | 660 | 1832240 | 1795596.125
3494 | 2005-05-26 13:00 | 957 | 940 | 115 | 32.17 | 3.86 | 0 | 63.6657 | 246.504 | 27.5017 | 0 | 957 | 833.334 | 118.588 | 8.9663 | 833.334 | 110.979 | 0.046801 | 828.026 | 106.872 | 0.035266 | 906.885 | 906.878 | 2036620 | 54.1984 | 2039660 | 1786540 | 1746390 | 0 | 0 | 1718050 | 643.377 | 0 | 0 | 0 | 13259.2 | 1704790 | 660 | 1674020 | 1640541.625
3495 | 2005-05-26 14:00 | 825 | 913 | 107 | 32.13 | 3.86 | 0 | 51.8141 | 260.613 | 40.9763 | 0 | 825 | 689.657 | 110.621 | 7.7296 | 689.657 | 103.524 | 0.040346 | 678.466 | 99.6923 | 0.030402 | 754.843 | 754.838 | 1695180 | 50.4653 | 1681170 | 1497300 | 1464800 | 0 | 0 | 1445120 | 649.113 | 0 | 0 | 0 | 3535.55 | 1441580 | 660 | 1419020 | 1390642.625
3496 | 2005-05-26 15:00 | 647 | 865 | 96 | 32.1 | 3.98 | 0 | 39.514 | 270.179 | 54.8558 | 0 | 647 | 498.495 | 98.5277 | 6.0619 | 498.495 | 92.206 | 0.031641 | 480.12 | 88.7935 | 0.023842 | 551.87 | 551.867 | 1239350 | 45.3998 | 1206800 | 1098870 | 1073380 | 0 | 0 | 1063050 | 659.144 | 0 | 0 | 0 | 71.8479 | 1062980 | 660.307 | 1048740 | 1027765.6875
3497 | 2005-05-26 16:00 | 441 | 708 | 117 | 32.07 | 3.98 | 0 | 27.207 | 278.134 | 68.8268 | 0 | 441 | 255.957 | 112.533 | 4.1318 | 255.957 | 105.313 | 0.021567 | 233.323 | 101.416 | 0.016251 | 324.712 | 324.706 | 729205 | 39.8953 | 686502 | 639743 | 624513 | 0 | 0 | 620975 | 658.021 | 0 | 0 | 0 | 106.533 | 620868 | 660.05 | 612795 | 600539.5625
3498 | 2005-05-26 17:00 | 195 | 339 | 106 | 31.18 | 3.98 | 0 | 15.1316 | 285.689 | 82.7467 | 0 | 195 | 43.047 | 90.9548 | 1.827 | 43.047 | 85.119 | 0.0095363 | 28.1519 | 81.9688 | 0.0071858 | 106.824 | 106.818 | 239886 | 33.7543 | 207486 | 198321 | 193674 | 0 | 0 | 193299 | 630.034 | 0 | 0 | 0 | 6002.87 | 187296 | 660 | 182284 | 178638.375
3499 | 2005-05-26 18:00 | 26 | 142 | 14 | 30.3 | 6.31 | 0 | 3.5046 | 293.552 | 90 | 0 | 26 | 0 | 10.4147 | 0.2436 | 0 | 9.7465 | 0.0012715 | 0 | 9.3858 | 0.00095811 | 9.1051 | 9.1048 | 20447.1 | 30.4886 | 11774 | 11443 | 11222.3 | 0 | 0 | 11220.4 | 508.683 | 0 | 0 | 0 | 11220.4 | 0 | 660 | 0 | 0
3500 | 2005-05-26 19:00 | 0 | 0 | 0 | 29.41 | 6.31 | 0
3501 | 2005-05-26 20:00 | 0 | 0 | 0 | 28.36 | 6.31 | 0
3502 | 2005-05-26 21:00 | 0 | 0 | 0 | 27.3 | 3.09 | 0
3503 | 2005-05-26 22:00 | 0 | 0 | 0 | 26.25 | 3.09 | 0
3504 | 2005-05-26 23:00 | 0 | 0 | 0 | 25.29 | 3.09 | 0
3505 | 2005-05-27 | 0 | 0 | 0 | 24.33 | 4.4 | 0
3506 | 2005-05-27 01:00 | 0 | 0 | 0 | 23.37 | 4.4 | 0
3507 | 2005-05-27 02:00 | 0 | 0 | 0 | 22.7 | 4.4 | 0
3508 | 2005-05-27 03:00 | 0 | 0 | 0 | 22.03 | 0.49 | 0
3509 | 2005-05-27 04:00 | 3 | 49 | 2 | 21.36 | 0.49 | 0 | -2.5723 | 61.7276 | 90 | 0 | 3 | 0 | 1.5702 | 0.028108 | 0 | 1.4695 | 0 | 0 | 1.4151 | 0 | 1.3726 | 1.3726 | 3082.58 | 21.4017 | 459.19 | 457.324 | 455.164 | 0 | 0 | 455.144 | 203.04 | 0 | 0 | 0 | 455.144 | 0 | 660 | 0 | 0
3510 | 2005-05-27 05:00 | 101 | 325 | 51 | 21.67 | 0.49 | 0 | 8.7017 | 69.9898 | 90 | 0 | 101 | 0 | 38.2573 | 0.94629 | 0 | 35.8027 | 0.0049393 | 0 | 34.4776 | 0.0037219 | 33.4469 | 33.4455 | 75109.8 | 22.6872 | 57091.8 | 57805.2 | 56432.8 | 0 | 0 | 56399.1 | 612.455 | 0 | 0 | 0 | 4711.59 | 51687.5 | 660 | 49883.7 | 48886.0625
3511 | 2005-05-27 06:00 | 311 | 608 | 97 | 21.99 | 2.23 | 0 | 20.5617 | 77.6207 | 76.498 | 0 | 311 | 142.262 | 89.5244 | 2.9138 | 140.502 | 83.7803 | 0.015209 | 117.438 | 80.6797 | 0.01146 | 192.185 | 192.178 | 431587 | 27.1901 | 391671 | 387531 | 370318 | 0 | 0 | 369114 | 671.427 | 0 | 0 | 0 | 815.829 | 368298 | 676.007 | 362007 | 354767.0625
3512 | 2005-05-27 07:00 | 528 | 772 | 110 | 22.3 | 2.23 | 0 | 32.7708 | 85.2251 | 62.5493 | 0 | 528 | 355.993 | 109.069 | 4.947 | 355.993 | 102.071 | 0.025821 | 335.181 | 98.2932 | 0.019457 | 420.489 | 420.487 | 944306 | 33.6779 | 904064 | 869153 | 847254 | 0 | 0 | 841315 | 688.054 | 0 | 0 | 0 | 0 | 841315 | 688.054 | 829198 | 812614.125
3513 | 2005-05-27 08:00 | 699 | 785 | 143 | 24.19 | 2.23 | 0 | 45.1158 | 93.659 | 48.6098 | 0 | 699 | 518.843 | 146.608 | 6.5491 | 518.843 | 137.202 | 0.034184 | 505.549 | 132.124 | 0.025758 | 618.567 | 618.561 | 1389130 | 40.9276 | 1361950 | 1268020 | 1236830 | 0 | 0 | 1223840 | 676.792 | 0 | 0 | 0 | 0 | 1223840 | 676.792 | 1205490 | 1181377.875
3514 | 2005-05-27 09:00 | 872 | 892 | 121 | 26.09 | 1.05 | 0 | 57.3085 | 104.641 | 34.8716 | 0 | 872 | 732.121 | 124.343 | 8.17 | 732.121 | 116.365 | 0.042644 | 724.109 | 112.058 | 0.032134 | 811.114 | 811.113 | 1821560 | 49.8436 | 1813630 | 1621170 | 1581710 | 0 | 0 | 1559330 | 656.691 | 0 | 0 | 0 | 548.817 | 1558780 | 660 | 1532920 | 1502261
3515 | 2005-05-27 10:00 | 967 | 883 | 145 | 27.98 | 1.05 | 0 | 68.6525 | 122.991 | 21.8911 | 0 | 967 | 818.915 | 147.045 | 9.06 | 818.915 | 137.61 | 0.04729 | 815.733 | 132.517 | 0.035634 | 919.837 | 919.831 | 2065710 | 54.9174 | 2070280 | 1807040 | 1764980 | 0 | 0 | 1736050 | 642.945 | 0 | 0 | 0 | 16126.3 | 1719920 | 660 | 1688620 | 1654848.875
3516 | 2005-05-27 11:00 | 1027 | 880 | 174 | 29.21 | 1.05 | 0 | 76.3656 | 163.413 | 12.5137 | 0 | 1027 | 856.884 | 183.197 | 9.6222 | 856.884 | 171.443 | 0.050225 | 855.841 | 165.098 | 0.037845 | 990.348 | 990.334 | 2224040 | 58.2121 | 2237090 | 1922110 | 1881000 | 0 | 0 | 1847080 | 631.632 | 0 | 0 | 0 | 42804 | 1804270 | 660 | 1769910 | 1734515.75
3517 | 2005-05-27 12:00 | 986 | 827 | 193 | 30.45 | 1.4 | 0 | 73.7673 | 218.839 | 15.8044 | 0 | 986 | 794.704 | 201.413 | 9.238 | 794.704 | 188.49 | 0.048219 | 793.143 | 181.514 | 0.036334 | 945.453 | 945.443 | 2123230 | 57.4936 | 2130850 | 1836550 | 1796040 | 0 | 0 | 1765370 | 634.827 | 0 | 0 | 0 | 36569 | 1728800 | 660 | 1697180 | 1663239.625
3518 | 2005-05-27 13:00 | 946 | 922 | 119 | 31.68 | 1.4 | 0 | 63.7846 | 246.771 | 27.5365 | 0 | 946 | 817.392 | 122.373 | 8.8633 | 817.392 | 114.521 | 0.046263 | 812.171 | 110.283 | 0.03486 | 894.814 | 894.807 | 2009520 | 57.2752 | 2011140 | 1734210 | 1695170 | 0 | 0 | 1667590 | 632.861 | 0 | 0 | 0 | 36329.8 | 1631270 | 660 | 1603020 | 1570962.625
3519 | 2005-05-27 14:00 | 818 | 901 | 109 | 32.07 | 1.4 | 0 | 51.9187 | 260.824 | 40.9787 | 0 | 818 | 680.012 | 112.48 | 7.664 | 680.012 | 105.263 | 0.040004 | 668.976 | 101.368 | 0.030144 | 747.263 | 747.256 | 1678150 | 53.4446 | 1663350 | 1459440 | 1426790 | 0 | 0 | 1407600 | 640.643 | 0 | 0 | 0 | 15445 | 1392160 | 660 | 1370780 | 1343367.125
3520 | 2005-05-27 15:00 | 635 | 839 | 100 | 32.46 | 3.07 | 0 | 39.6154 | 270.351 | 54.8377 | 0 | 635 | 483.2 | 102.959 | 5.9495 | 483.2 | 96.3528 | 0.031054 | 465.408 | 92.7869 | 0.0234 | 541.472 | 541.469 | 1216010 | 46.3162 | 1182700 | 1071900 | 1046140 | 0 | 0 | 1036220 | 655.699 | 0 | 0 | 0 | 603.96 | 1035620 | 660 | 1021930 | 1001492.0625
3521 | 2005-05-27 16:00 | 425 | 688 | 109 | 32.85 | 3.07 | 0 | 27.3108 | 278.281 | 68.7926 | 0 | 425 | 249.143 | 104.96 | 3.9819 | 249.143 | 98.2252 | 0.020784 | 227.164 | 94.5899 | 0.015661 | 312.117 | 312.114 | 700929 | 40.837 | 658146 | 610271 | 595519 | 0 | 0 | 592260 | 653.901 | 0 | 0 | 0 | 842.295 | 591418 | 660 | 583704 | 572029.75
3522 | 2005-05-27 17:00 | 190 | 304 | 110 | 32.13 | 3.07 | 0 | 15.2415 | 285.819 | 82.6979 | 0 | 190 | 38.6786 | 94.4177 | 1.7801 | 38.6786 | 88.3597 | 0.0092918 | 25.3969 | 85.0896 | 0.0070016 | 107.179 | 107.173 | 240685 | 34.8726 | 208238 | 197858 | 193300 | 0 | 0 | 192923 | 626.469 | 0 | 0 | 0 | 7836.83 | 185086 | 660 | 180109 | 176506.4688
3523 | 2005-05-27 18:00 | 25 | 129 | 14 | 31.4 | 8.93 | 0 | 3.6233 | 293.669 | 90 | 0 | 25 | 0 | 10.3624 | 0.23423 | 0 | 9.6975 | 0.0012226 | 0 | 9.3386 | 0.00092126 | 9.0593 | 9.0589 | 20344 | 31.559 | 11695.3 | 11301.6 | 11089.8 | 0 | 0 | 11087.9 | 504.709 | 0 | 0 | 0 | 11087.9 | 0 | 660 | 0 | 0
3524 | 2005-05-27 19:00 | 0 | 0 | 0 | 30.67 | 8.93 | 0
3525 | 2005-05-27 20:00 | 0 | 0 | 0 | 29.26 | 8.93 | 0
3526 | 2005-05-27 21:00 | 0 | 0 | 0 | 27.85 | 6.47 | 0
3527 | 2005-05-27 22:00 | 0 | 0 | 0 | 26.44 | 6.47 | 0
3528 | 2005-05-27 23:00 | 0 | 0 | 0 | 25.4 | 6.47 | 0
3529 | 2005-05-28 | 0 | 0 | 0 | 24.36 | 6.07 | 0
3530 | 2005-05-28 01:00 | 0 | 0 | 0 | 23.32 | 6.07 | 0
3531 | 2005-05-28 02:00 | 0 | 0 | 0 | 22.03 | 6.07 | 0
3532 | 2005-05-28 03:00 | 0 | 0 | 0 | 20.74 | 3.77 | 0
3533 | 2005-05-28 04:00 | 3 | 65 | 1 | 19.45 | 3.77 | 0 | -2.4931 | 61.5837 | 90 | 0 | 3 | 0 | 0.72669 | 0.028108 | 0 | 0.68007 | 0 | 0 | 0.6549 | 0 | 0.63525 | 0.63523 | 1426.56 | 19.4655 | 98.7003 | 98.0529 | 97.3622 | 0 | 0 | 97.3582 | 98.0321 | 0 | 0 | 0 | 97.3582 | 0 | 660 | 0 | 0
3534 | 2005-05-28 05:00 | 113 | 421 | 48 | 20.04 | 3.77 | 0 | 8.7677 | 69.838 | 90 | 0 | 113 | 0 | 37.213 | 1.0587 | 0 | 34.8253 | 0.0055262 | 0 | 33.5364 | 0.0041641 | 32.5344 | 32.5322 | 73058.8 | 20.8349 | 55314.5 | 56558.3 | 55149.4 | 0 | 0 | 55117.7 | 616.871 | 0 | 0 | 0 | 3439.08 | 51678.6 | 660 | 49875.1 | 48877.5742
3535 | 2005-05-28 06:00 | 324 | 709 | 74 | 20.64 | 3.48 | 0 | 20.618 | 77.4566 | 76.5122 | 0 | 324 | 165.588 | 68.1755 | 3.0356 | 163.684 | 63.8012 | 0.015845 | 136.778 | 61.44 | 0.01194 | 192.283 | 192.283 | 431823 | 25.429 | 391921 | 391053 | 373100 | 0 | 0 | 371894 | 675.808 | 0 | 0 | 0 | 473.131 | 371421 | 681.318 | 364993 | 357692.9375
3536 | 2005-05-28 07:00 | 537 | 827 | 88 | 21.24 | 3.48 | 0 | 32.8212 | 85.0403 | 62.5786 | 0 | 537 | 381.497 | 88.8391 | 5.0313 | 381.497 | 83.1391 | 0.026262 | 359.152 | 80.0621 | 0.019789 | 426.057 | 426.053 | 956808 | 31.8512 | 916797 | 888917 | 866271 | 0 | 0 | 860209 | 696.04 | 0 | 0 | 0 | 0 | 860209 | 696.04 | 847476 | 830526.8125
3537 | 2005-05-28 08:00 | 729 | 885 | 101 | 22.98 | 3.48 | 0 | 45.1656 | 93.4388 | 48.656 | 0 | 729 | 584.989 | 104.048 | 6.8302 | 584.989 | 97.3724 | 0.035651 | 569.96 | 93.7687 | 0.026864 | 643.843 | 643.837 | 1445890 | 39.0153 | 1420960 | 1335140 | 1302420 | 0 | 0 | 1288320 | 683.671 | 0 | 0 | 0 | 0 | 1288320 | 683.671 | 1268260 | 1242890.125
3538 | 2005-05-28 09:00 | 880 | 907 | 116 | 24.73 | 1.19 | 0 | 57.3664 | 104.358 | 34.9401 | 0 | 880 | 743.693 | 119.416 | 8.2449 | 743.693 | 111.754 | 0.043036 | 735.516 | 107.618 | 0.032428 | 817.872 | 817.865 | 1836720 | 48.4568 | 1829550 | 1646550 | 1609170 | 0 | 0 | 1586220 | 660.078 | 0 | 0 | 0 | 56.3629 | 1586160 | 661.591 | 1559370 | 1528179.25
3539 | 2005-05-28 10:00 | 992 | 934 | 122 | 26.47 | 1.19 | 0 | 68.7379 | 122.61 | 21.9962 | 0 | 992 | 865.592 | 124.965 | 9.2943 | 865.592 | 116.947 | 0.048513 | 862.194 | 112.619 | 0.036555 | 945.604 | 945.597 | 2123570 | 53.9024 | 2131210 | 1870160 | 1828240 | 0 | 0 | 1797430 | 645.086 | 0 | 0 | 0 | 10480.4 | 1786950 | 660 | 1753230 | 1718169.25
3540 | 2005-05-28 11:00 | 1045 | 949 | 124 | 27.7 | 1.19 | 0 | 76.5127 | 163.12 | 12.6741 | 0 | 1045 | 924.042 | 126.202 | 9.7908 | 924.042 | 118.105 | 0.051105 | 922.888 | 113.734 | 0.038509 | 1005.56 | 1005.56 | 2258230 | 56.8718 | 2273140 | 1966670 | 1922970 | 0 | 0 | 1888070 | 636.643 | 0 | 0 | 0 | 28495.5 | 1859580 | 660 | 1823140 | 1786672.25
3541 | 2005-05-28 12:00 | 1026 | 940 | 124 | 28.93 | 3.11 | 0 | 73.916 | 219.071 | 15.9018 | 0 | 1026 | 902.822 | 126.472 | 9.6128 | 902.822 | 118.357 | 0.050176 | 901.026 | 113.977 | 0.037808 | 984.589 | 984.584 | 2211120 | 54.0588 | 2223480 | 1950450 | 1906220 | 0 | 0 | 1872700 | 644.717 | 0 | 0 | 0 | 10025.6 | 1862680 | 660 | 1826120 | 1789596.875
3542 | 2005-05-28 13:00 | 959 | 940 | 115 | 30.15 | 3.11 | 0 | 63.9008 | 247.027 | 27.5682 | 0 | 959 | 833.123 | 118.392 | 8.9851 | 833.123 | 110.796 | 0.046899 | 827.788 | 106.695 | 0.035339 | 906.483 | 906.473 | 2035710 | 53.2853 | 2038700 | 1793750 | 1752130 | 0 | 0 | 1723970 | 647.097 | 0 | 0 | 0 | 8257.02 | 1715710 | 660 | 1684560 | 1650867.25
3543 | 2005-05-28 14:00 | 827 | 913 | 107 | 30.23 | 3.11 | 0 | 52.0215 | 261.027 | 40.9788 | 0 | 827 | 689.593 | 110.453 | 7.7484 | 689.593 | 103.367 | 0.040444 | 678.401 | 99.541 | 0.030475 | 754.633 | 754.632 | 1694710 | 49.4899 | 1680680 | 1504020 | 1468930 | 0 | 0 | 1449460 | 654.047 | 0 | 0 | 0 | 1013.78 | 1448440 | 659.999 | 1425720 | 1397201
3544 | 2005-05-28 15:00 | 650 | 866 | 96 | 30.31 | 6.34 | 0 | 39.7152 | 270.516 | 54.8179 | 0 | 650 | 499.556 | 98.3889 | 6.09 | 499.556 | 92.0761 | 0.031788 | 481.183 | 88.6684 | 0.023953 | 552.779 | 552.772 | 1241390 | 41.7396 | 1208910 | 1120480 | 1093560 | 0 | 0 | 1083210 | 671.096 | 0 | 0 | 0 | 0 | 1083210 | 671.096 | 1068030 | 1046671.5
3545 | 2005-05-28 16:00 | 438 | 648 | 139 | 30.38 | 6.34 | 0 | 27.413 | 278.422 | 68.7572 | 0 | 438 | 235.303 | 132.777 | 4.1037 | 235.303 | 124.258 | 0.02142 | 214.597 | 119.659 | 0.01614 | 324.244 | 324.24 | 728160 | 37.0843 | 685454 | 647667 | 632870 | 0 | 0 | 629328 | 666.395 | 0 | 0 | 0 | 0 | 629328 | 666.395 | 620945 | 608526.4375
3546 | 2005-05-28 17:00 | 179 | 242 | 115 | 29.65 | 6.34 | 0 | 15.3495 | 285.943 | 82.6482 | 0 | 179 | 30.9381 | 98.4681 | 1.6771 | 30.9381 | 92.1502 | 0.0087538 | 20.3962 | 88.7398 | 0.0065962 | 105.868 | 105.862 | 237740 | 31.8389 | 205467 | 198383 | 193683 | 0 | 0 | 193316 | 636.468 | 0 | 0 | 0 | 3612.96 | 189703 | 660 | 184654 | 180960.7188
3547 | 2005-05-28 18:00 | 25 | 104 | 16 | 28.92 | 8.22 | 0 | 3.7398 | 293.78 | 90 | 0 | 25 | 0 | 12.2335 | 0.23423 | 0 | 11.4486 | 0.0012226 | 0 | 11.0249 | 0.00092126 | 10.6951 | 10.6945 | 24017.1 | 29.1163 | 14525.9 | 14210.9 | 13929.3 | 0 | 0 | 13926.5 | 520.938 | 0 | 0 | 0 | 13926.5 | 0 | 660 | 0 | 0
3548 | 2005-05-28 19:00 | 0 | 0 | 0 | 28.19 | 8.22 | 0
3549 | 2005-05-28 20:00 | 0 | 0 | 0 | 27.02 | 8.22 | 0
3550 | 2005-05-28 21:00 | 0 | 0 | 0 | 25.84 | 8.88 | 0
3551 | 2005-05-28 22:00 | 0 | 0 | 0 | 24.67 | 8.88 | 0
3552 | 2005-05-28 23:00 | 0 | 0 | 0 | 23.66 | 8.88 | 0
3553 | 2005-05-29 | 0 | 0 | 0 | 22.65 | 8.85 | 0
3554 | 2005-05-29 01:00 | 0 | 0 | 0 | 21.64 | 8.85 | 0
3555 | 2005-05-29 02:00 | 0 | 0 | 0 | 20.3 | 8.85 | 0
3556 | 2005-05-29 03:00 | 0 | 0 | 0 | 18.96 | 10.09 | 0
3557 | 2005-05-29 04:00 | 1 | 0 | 1 | 17.63 | 10.09 | 0 | -2.4192 | 61.4436 | 90 | 0 | 1 | 0 | 1.0003 | 0.0093692 | 0 | 0.93612 | 0 | 0 | 0.90148 | 0 | 0.87443 | 0.87435 | 1963.55 | 17.6443 | 186.777 | 185.158 | 184.294 | 0 | 0 | 184.286 | 129.954 | 0 | 0 | 0 | 184.286 | 0 | 660 | 0 | 0
3558 | 2005-05-29 05:00 | 34 | 0 | 34 | 18.07 | 10.09 | 0 | 8.8287 | 69.6905 | 90 | 0 | 34 | 0 | 31.3173 | 0.31855 | 0 | 29.3079 | 0.0016627 | 0 | 28.2232 | 0.0012529 | 27.3778 | 27.3769 | 61481.4 | 18.5174 | 45361.8 | 46954 | 45806.2 | 0 | 0 | 45784.3 | 616.301 | 0 | 0 | 0 | 2926.67 | 42857.6 | 660 | 41339.3 | 40512.4844
3559 | 2005-05-29 06:00 | 319 | 528 | 132 | 18.5 | 6.92 | 0 | 20.6695 | 77.2972 | 76.5288 | 0 | 319 | 123.416 | 118.7 | 2.9888 | 122.139 | 111.084 | 0.0156 | 102.031 | 106.972 | 0.011755 | 202.745 | 202.736 | 455292 | 22.5394 | 414801 | 419550 | 401909 | 0 | 0 | 400563 | 688.843 | 0 | 0 | 0 | 84.3644 | 400478 | 689.915 | 393870 | 385992.8438
3560 | 2005-05-29 07:00 | 530 | 808 | 91 | 18.94 | 6.92 | 0 | 32.867 | 84.8608 | 62.6098 | 0 | 530 | 372.148 | 91.6585 | 4.9657 | 372.148 | 85.7775 | 0.025919 | 350.309 | 82.6029 | 0.019531 | 419.943 | 419.94 | 943075 | 27.307 | 902808 | 893540 | 870265 | 0 | 0 | 864382 | 710.572 | 0 | 0 | 0 | 0 | 864382 | 710.572 | 850959 | 833939.9375
3561 | 2005-05-29 08:00 | 725 | 875 | 104 | 20.26 | 6.92 | 0 | 45.2105 | 93.2249 | 48.7035 | 0 | 725 | 577.473 | 106.868 | 6.7927 | 577.473 | 100.012 | 0.035456 | 562.596 | 96.3102 | 0.026717 | 639.165 | 639.156 | 1435380 | 32.9948 | 1410020 | 1361640 | 1327130 | 0 | 0 | 1313340 | 704.674 | 0 | 0 | 0 | 0 | 1313340 | 704.674 | 1291780 | 1265945.375
3562 | 2005-05-29 09:00 | 893 | 928 | 111 | 21.58 | 5.76 | 0 | 57.419 | 104.084 | 35.0091 | 0 | 893 | 760.127 | 114.474 | 8.3667 | 760.127 | 107.129 | 0.043671 | 751.731 | 103.164 | 0.032907 | 829.28 | 829.282 | 1862350 | 39.3787 | 1856460 | 1743610 | 1697880 | 0 | 0 | 1674630 | 692.327 | 0 | 0 | 0 | 0 | 1674630 | 692.327 | 1644030 | 1611150.5
3563 | 2005-05-29 10:00 | 993 | 936 | 121 | 22.9 | 5.76 | 0 | 68.817 | 122.236 | 22.1002 | 0 | 993 | 866.479 | 123.9 | 9.3036 | 866.479 | 115.95 | 0.048562 | 863.043 | 111.659 | 0.036592 | 945.496 | 945.488 | 2123320 | 43.1928 | 2130950 | 1968170 | 1923980 | 0 | 0 | 1893370 | 681.925 | 0 | 0 | 0 | 0 | 1893370 | 681.925 | 1855410 | 1818303
3564 | 2005-05-29 11:00 | 1047 | 951 | 124 | 23.75 | 5.76 | 0 | 76.653 | 162.82 | 12.8293 | 0 | 1047 | 924.941 | 126.088 | 9.8096 | 924.941 | 117.998 | 0.051203 | 923.757 | 113.631 | 0.038582 | 1006.3 | 1006.29 | 2259890 | 45.3478 | 2274900 | 2081030 | 2031780 | 0 | 0 | 1997110 | 675.814 | 0 | 0 | 0 | 0 | 1997110 | 675.814 | 1955230 | 1916123.125
3565 | 2005-05-29 12:00 | 1037 | 953 | 122 | 24.6 | 9.36 | 0 | 74.0603 | 219.289 | 15.9944 | 0 | 1037 | 914.75 | 124.436 | 9.7159 | 914.75 | 116.452 | 0.050714 | 912.908 | 112.142 | 0.038214 | 994.336 | 994.329 | 2233010 | 41.5971 | 2246550 | 2090800 | 2037370 | 0 | 0 | 2003770 | 688.414 | 0 | 0 | 0 | 0 | 2003770 | 688.414 | 1961630 | 1922394
3566 | 2005-05-29 13:00 | 960 | 940 | 115 | 25.46 | 9.36 | 0 | 64.0143 | 247.271 | 27.5969 | 0 | 960 | 833.085 | 118.3 | 8.9945 | 833.085 | 110.709 | 0.046948 | 827.737 | 106.612 | 0.035376 | 906.353 | 906.346 | 2035420 | 40.9532 | 2038400 | 1901750 | 1854660 | 0 | 0 | 1826770 | 689.297 | 0 | 0 | 0 | 0 | 1826770 | 689.297 | 1791110 | 1755283.5
3567 | 2005-05-29 14:00 | 828 | 914 | 107 | 25.15 | 9.36 | 0 | 52.1224 | 261.22 | 40.9766 | 0 | 828 | 689.626 | 110.374 | 7.7577 | 689.626 | 103.293 | 0.040493 | 678.435 | 99.4699 | 0.030512 | 754.598 | 754.592 | 1694620 | 38.0491 | 1680590 | 1587400 | 1549640 | 0 | 0 | 1530230 | 692.359 | 0 | 0 | 0 | 0 | 1530230 | 692.359 | 1504120 | 1474036.625
3568 | 2005-05-29 15:00 | 652 | 867 | 97 | 24.84 | 11.96 | 0 | 39.8133 | 270.673 | 54.7964 | 0 | 652 | 499.695 | 99.2842 | 6.1087 | 499.695 | 92.9139 | 0.031885 | 481.34 | 89.4752 | 0.024026 | 553.714 | 553.711 | 1243490 | 32.9226 | 1211080 | 1169470 | 1139960 | 0 | 0 | 1129630 | 700.45 | 0 | 0 | 0 | 0 | 1129630 | 700.45 | 1112080 | 1089839
3569 | 2005-05-29 16:00 | 436 | 700 | 112 | 24.53 | 11.96 | 0 | 27.5135 | 278.555 | 68.7205 | 0 | 436 | 254.537 | 107.606 | 4.085 | 254.537 | 100.702 | 0.021322 | 232.196 | 96.9753 | 0.016067 | 319.311 | 319.306 | 717078 | 29.1909 | 674333 | 661494 | 644591 | 0 | 0 | 641190 | 693.135 | 0 | 0 | 0 | 0 | 641190 | 693.135 | 631792 | 619156.5
3570 | 2005-05-29 17:00 | 201 | 337 | 111 | 23.43 | 11.96 | 0 | 15.4556 | 286.06 | 82.5977 | 0 | 201 | 43.5102 | 95.2386 | 1.8832 | 43.5102 | 89.1279 | 0.0098297 | 28.7996 | 85.8294 | 0.0074069 | 111.197 | 111.191 | 249707 | 25.0531 | 216748 | 216684 | 211257 | 0 | 0 | 210855 | 662.524 | 0 | 0 | 0 | -2.043 | 210857 | 662.623 | 205464 | 201354.6562
3571 | 2005-05-29 18:00 | 28 | 147 | 16 | 22.32 | 10.97 | 0 | 3.8539 | 293.885 | 90 | 0 | 28 | 0 | 11.9866 | 0.26234 | 0 | 11.2175 | 0.0013693 | 0 | 10.8023 | 0.0010318 | 10.4793 | 10.4789 | 23533 | 22.4823 | 14149.7 | 14332.7 | 14036.4 | 0 | 0 | 14033.7 | 543.17 | 0 | 0 | 0 | 10961.5 | 3072.26 | 660 | 2956.08 | 2896.96
3572 | 2005-05-29 19:00 | 0 | 0 | 0 | 21.22 | 10.97 | 0
3573 | 2005-05-29 20:00 | 0 | 0 | 0 | 20.06 | 10.97 | 0
3574 | 2005-05-29 21:00 | 0 | 0 | 0 | 18.89 | 12.42 | 0
3575 | 2005-05-29 22:00 | 0 | 0 | 0 | 17.72 | 12.42 | 0
3576 | 2005-05-29 23:00 | 0 | 0 | 0 | 17.05 | 12.42 | 0
3577 | 2005-05-30 | 0 | 0 | 0 | 16.37 | 10.21 | 0
3578 | 2005-05-30 01:00 | 0 | 0 | 0 | 15.69 | 10.21 | 0
3579 | 2005-05-30 02:00 | 0 | 0 | 0 | 15.3 | 10.21 | 0
3580 | 2005-05-30 03:00 | 0 | 0 | 0 | 14.9 | 11.13 | 0
3581 | 2005-05-30 04:00 | 3 | 66 | 1 | 14.5 | 11.13 | 0 | -2.3505 | 61.3074 | 90 | 0 | 3 | 0 | 0.72572 | 0.028108 | 0 | 0.67916 | 0 | 0 | 0.65402 | 0 | 0.6344 | 0.6344 | 1424.69 | 14.5097 | 98.4505 | 97.2253 | 96.471 | 0 | 0 | 96.4672 | 98.1566 | 0 | 0 | 0 | 96.4672 | 0 | 660 | 0 | 0
3582 | 2005-05-30 05:00 | 114 | 414 | 49 | 15.16 | 11.13 | 0 | 8.8848 | 69.5473 | 90 | 0 | 114 | 0 | 38.0306 | 1.0681 | 0 | 35.5905 | 0.0055751 | 0 | 34.2733 | 0.0042009 | 33.2492 | 33.2478 | 74665.8 | 15.6701 | 56706.7 | 59545.6 | 58065.9 | 0 | 0 | 58032.8 | 636.373 | 0 | 0 | 0 | 880.848 | 57152 | 660 | 55176.2 | 54072.6758
3583 | 2005-05-30 06:00 | 326 | 710 | 74 | 15.81 | 2.97 | 0 | 20.7164 | 77.1426 | 76.5476 | 0 | 326 | 165.726 | 68.0032 | 3.0544 | 164.125 | 63.64 | 0.015943 | 137.056 | 61.2847 | 0.012013 | 192.402 | 192.393 | 432067 | 20.766 | 392145 | 399901 | 383742 | 0 | 0 | 382523 | 691.686 | 0 | 0 | 0 | 135.127 | 382388 | 693.601 | 375666 | 368152.8438
3584 | 2005-05-30 07:00 | 539 | 827 | 89 | 16.47 | 2.97 | 0 | 32.9082 | 84.6869 | 62.6427 | 0 | 539 | 380.626 | 89.6316 | 5.05 | 380.626 | 83.8807 | 0.026359 | 358.243 | 80.7763 | 0.019862 | 425.868 | 425.866 | 956387 | 27.4403 | 916370 | 906403 | 882555 | 0 | 0 | 876503 | 710.122 | 0 | 0 | 0 | 0 | 876503 | 710.122 | 862912 | 845653.875
3585 | 2005-05-30 08:00 | 714 | 851 | 110 | 18.18 | 2.97 | 0 | 45.2508 | 93.0175 | 48.7522 | 0 | 714 | 560.73 | 114.162 | 6.6896 | 560.73 | 106.837 | 0.034918 | 546.243 | 102.883 | 0.026311 | 629.677 | 629.672 | 1414080 | 34.4004 | 1387870 | 1331710 | 1297520 | 0 | 0 | 1284160 | 700.2 | 0 | 0 | 0 | 0 | 1284160 | 700.2 | 1263430 | 1238161.375
3586 | 2005-05-30 09:00 | 875 | 896 | 120 | 19.89 | 2.35 | 0 | 57.4664 | 103.817 | 35.0785 | 0 | 875 | 732.871 | 123.1 | 8.1981 | 732.871 | 115.202 | 0.042791 | 724.738 | 110.938 | 0.032244 | 810.638 | 810.637 | 1820490 | 41.6502 | 1812510 | 1684440 | 1641010 | 0 | 0 | 1618680 | 682.403 | 0 | 0 | 0 | 0 | 1618680 | 682.403 | 1590170 | 1558367.875
3587 | 2005-05-30 10:00 | 986 | 923 | 126 | 21.61 | 2.35 | 0 | 68.89 | 121.869 | 22.2031 | 0 | 986 | 853.51 | 128.619 | 9.238 | 853.51 | 120.366 | 0.048219 | 850.092 | 115.911 | 0.036334 | 937.059 | 937.053 | 2104390 | 46.7636 | 2111010 | 1917300 | 1869950 | 0 | 0 | 1839940 | 669.272 | 0 | 0 | 0 | 0 | 1839940 | 669.272 | 1804110 | 1768030.75
3588 | 2005-05-30 11:00 | 1051 | 955 | 123 | 23 | 2.35 | 0 | 76.7865 | 162.515 | 12.9791 | 0 | 1051 | 928.884 | 125.019 | 9.847 | 928.884 | 116.998 | 0.051398 | 927.666 | 112.668 | 0.03873 | 1009.16 | 1009.15 | 2266300 | 50.089 | 2281660 | 2040910 | 1994190 | 0 | 0 | 1959370 | 661.273 | 0 | 0 | 0 | 43.7249 | 1959330 | 661.515 | 1918970 | 1880594.375
3589 | 2005-05-30 12:00 | 1030 | 944 | 123 | 24.39 | 1 | 0 | 74.2001 | 219.494 | 16.0823 | 0 | 1030 | 905.724 | 125.292 | 9.6503 | 905.724 | 117.253 | 0.050371 | 903.88 | 112.914 | 0.037956 | 986.327 | 986.317 | 2215010 | 53.3719 | 2227570 | 1960620 | 1918540 | 0 | 0 | 1884840 | 646.997 | 0 | 0 | 0 | 7625.1 | 1877220 | 660 | 1840100 | 1803299
3590 | 2005-05-30 13:00 | 960 | 940 | 115 | 25.78 | 1 | 0 | 64.1252 | 247.503 | 27.6225 | 0 | 960 | 832.107 | 118.211 | 8.9945 | 832.107 | 110.626 | 0.046948 | 826.755 | 106.532 | 0.035376 | 905.323 | 905.321 | 2033130 | 52.3819 | 2035980 | 1799240 | 1755510 | 0 | 0 | 1727720 | 652.568 | 0 | 0 | 0 | 4209.43 | 1723510 | 660 | 1692080 | 1658238.75
3591 | 2005-05-30 14:00 | 828 | 914 | 106 | 26.21 | 1 | 0 | 52.2214 | 261.404 | 40.9722 | 0 | 828 | 689.703 | 109.327 | 7.7577 | 689.703 | 102.312 | 0.040493 | 678.514 | 98.5258 | 0.030512 | 753.758 | 753.753 | 1692740 | 48.3582 | 1678620 | 1510420 | 1475120 | 0 | 0 | 1455700 | 658.203 | 0 | 0 | 0 | 60.7446 | 1455640 | 660.251 | 1432730 | 1404074.125
3592 | 2005-05-30 15:00 | 635 | 831 | 102 | 26.64 | 2.58 | 0 | 39.9098 | 270.822 | 54.7731 | 0 | 635 | 479.196 | 104.676 | 5.9495 | 479.196 | 97.9598 | 0.031054 | 461.618 | 94.3344 | 0.0234 | 539.297 | 539.29 | 1211110 | 40.8964 | 1177650 | 1095700 | 1068550 | 0 | 0 | 1058720 | 673.231 | 0 | 0 | 0 | 0 | 1058720 | 673.231 | 1043930 | 1023047.375
3593 | 2005-05-30 16:00 | 428 | 736 | 86 | 27.07 | 2.58 | 0 | 27.6123 | 278.682 | 68.6826 | 0 | 428 | 268.247 | 84.5716 | 4.01 | 268.247 | 79.1453 | 0.020931 | 244.765 | 76.2162 | 0.015772 | 311.367 | 311.362 | 699241 | 35.301 | 656452 | 625521 | 610395 | 0 | 0 | 607148 | 671.983 | 0 | 0 | 0 | 0 | 607148 | 671.983 | 598891 | 586913.0625
3594 | 2005-05-30 17:00 | 222 | 559 | 71 | 26.86 | 2.58 | 0 | 15.5598 | 286.171 | 82.5466 | 0 | 222 | 73.0224 | 61.8558 | 2.08 | 73.0224 | 57.8871 | 0.010857 | 48.5275 | 55.7447 | 0.0081808 | 101.152 | 101.15 | 227158 | 29.534 | 195514 | 191033 | 186341 | 0 | 0 | 186010 | 643.897 | 0 | 0 | 0 | 1740.67 | 184269 | 660 | 179304 | 175718.2188
3595 | 2005-05-30 18:00 | 31 | 247 | 10 | 26.65 | 4.71 | 0 | 3.9657 | 293.984 | 90 | 0 | 31 | 0 | 8.6463 | 0.29045 | 0 | 8.0916 | 0.001516 | 0 | 7.7921 | 0.0011424 | 7.5595 | 7.5592 | 16976.1 | 26.8237 | 9157.67 | 9077.93 | 8902.28 | 0 | 0 | 8901.07 | 509.818 | 0 | 0 | 0 | 8901.07 | 0 | 660 | 0 | 0
3596 | 2005-05-30 19:00 | 0 | 0 | 0 | 26.44 | 4.71 | 0
3597 | 2005-05-30 20:00 | 0 | 0 | 0 | 25.39 | 4.71 | 0
3598 | 2005-05-30 21:00 | 0 | 0 | 0 | 24.33 | 5.76 | 0
3599 | 2005-05-30 22:00 | 0 | 0 | 0 | 23.28 | 5.76 | 0
3600 | 2005-05-30 23:00 | 0 | 0 | 0 | 22.32 | 5.76 | 0
3601 | 2005-05-31 | 0 | 0 | 0 | 21.37 | 3.13 | 0
3602 | 2005-05-31 01:00 | 0 | 0 | 0 | 20.42 | 3.13 | 0
3603 | 2005-05-31 02:00 | 0 | 0 | 0 | 19.76 | 3.13 | 0
3604 | 2005-05-31 03:00 | 0 | 0 | 0 | 19.09 | 2.07 | 0
3605 | 2005-05-31 04:00 | 3 | 62 | 1 | 18.43 | 2.07 | 0 | -2.2869 | 61.1752 | 90 | 0 | 3 | 0 | 0.72529 | 0.028108 | 0 | 0.67875 | 0 | 0 | 0.65363 | 0 | 0.63402 | 0.63398 | 1423.77 | 18.4473 | 98.3064 | 97.5426 | 96.8541 | 0 | 0 | 96.8502 | 97.8747 | 0 | 0 | 0 | 96.8502 | 0 | 660 | 0 | 0
3606 | 2005-05-31 05:00 | 111 | 379 | 51 | 18.73 | 2.07 | 0 | 8.9361 | 69.4085 | 90 | 0 | 111 | 0 | 39.9106 | 1.04 | 0 | 37.3499 | 0.0054284 | 0 | 35.9676 | 0.0040904 | 34.8925 | 34.891 | 78356.1 | 19.6842 | 59912.9 | 61625.8 | 60119.3 | 0 | 0 | 60082.5 | 624.593 | 0 | 0 | 0 | 2364.4 | 57718.1 | 660 | 55724.8 | 54610.2852
3607 | 2005-05-31 06:00 | 327 | 677 | 86 | 19.03 | 1.26 | 0 | 20.7586 | 76.993 | 76.5687 | 0 | 327 | 157.941 | 78.9791 | 3.0637 | 156.529 | 73.9116 | 0.015992 | 130.662 | 71.1762 | 0.01205 | 195.794 | 195.788 | 439691 | 24.6833 | 399571 | 400095 | 384314 | 0 | 0 | 383038 | 676.801 | 0 | 0 | 0 | 417.439 | 382621 | 680.96 | 376267 | 368741.2188
3608 | 2005-05-31 07:00 | 539 | 827 | 89 | 19.33 | 1.26 | 0 | 32.9448 | 84.5186 | 62.6774 | 0 | 539 | 379.806 | 89.5465 | 5.05 | 379.806 | 83.801 | 0.026359 | 357.423 | 80.6996 | 0.019862 | 424.998 | 424.992 | 954423 | 31.6014 | 914368 | 887552 | 864241 | 0 | 0 | 858200 | 695.628 | 0 | 0 | 0 | 0 | 858200 | 695.628 | 845514 | 828604.25
3609 | 2005-05-31 08:00 | 734 | 891 | 101 | 21.43 | 1.26 | 0 | 45.2863 | 92.8167 | 48.802 | 0 | 734 | 586.708 | 103.822 | 6.877 | 586.708 | 97.1602 | 0.035896 | 571.506 | 93.5644 | 0.027048 | 645.144 | 645.142 | 1448830 | 40.0581 | 1424020 | 1331520 | 1296940 | 0 | 0 | 1282900 | 682.475 | 0 | 0 | 0 | 0 | 1282900 | 682.475 | 1263010 | 1237748.375
3610 | 2005-05-31 09:00 | 893 | 926 | 112 | 23.53 | 3 | 0 | 57.5087 | 103.558 | 35.1482 | 0 | 893 | 757.104 | 115.283 | 8.3667 | 757.104 | 107.886 | 0.043671 | 748.663 | 103.894 | 0.032907 | 827.012 | 827.011 | 1857260 | 44.7915 | 1851100 | 1695510 | 1656820 | 0 | 0 | 1633450 | 673.054 | 0 | 0 | 0 | 0 | 1633450 | 673.054 | 1604740 | 1572646.5
3611 | 2005-05-31 10:00 | 986 | 922 | 126 | 25.63 | 3 | 0 | 68.9568 | 121.511 | 22.3045 | 0 | 986 | 852.508 | 128.524 | 9.238 | 852.508 | 120.278 | 0.048219 | 849.061 | 115.827 | 0.036334 | 935.977 | 935.971 | 2101950 | 49.6928 | 2108450 | 1888430 | 1844110 | 0 | 0 | 1814150 | 660.047 | 0 | 0 | 0 | 27.5777 | 1814120 | 660.615 | 1779390 | 1743799.875
3612 | 2005-05-31 11:00 | 1051 | 955 | 123 | 26.85 | 3 | 0 | 76.913 | 162.204 | 13.1234 | 0 | 1051 | 927.863 | 124.915 | 9.847 | 927.863 | 116.9 | 0.051398 | 926.618 | 112.574 | 0.03873 | 1008.05 | 1008.05 | 2263820 | 52.7658 | 2279040 | 2012370 | 1967450 | 0 | 0 | 1932420 | 650.316 | 0 | 0 | 0 | 4406.17 | 1928010 | 660 | 1888910 | 1851130.625
3613 | 2005-05-31 12:00 | 1033 | 948 | 122 | 28.06 | 2.19 | 0 | 74.3353 | 219.684 | 16.1652 | 0 | 1033 | 908.733 | 124.23 | 9.6784 | 908.733 | 116.259 | 0.050518 | 906.863 | 111.956 | 0.038066 | 988.292 | 988.289 | 2219450 | 54.8735 | 2232260 | 1950340 | 1905730 | 0 | 0 | 1872080 | 643.414 | 0 | 0 | 0 | 14320.1 | 1857760 | 660 | 1821390 | 1784961.375
3614 | 2005-05-31 13:00 | 961 | 940 | 115 | 29.28 | 2.19 | 0 | 64.2333 | 247.723 | 27.645 | 0 | 961 | 832.161 | 118.126 | 9.0038 | 832.161 | 110.547 | 0.046997 | 826.798 | 106.455 | 0.035413 | 905.291 | 905.284 | 2033030 | 53.8414 | 2035880 | 1786310 | 1744460 | 0 | 0 | 1716440 | 645.956 | 0 | 0 | 0 | 10640.4 | 1705800 | 660 | 1674990 | 1641492
3615 | 2005-05-31 14:00 | 830 | 914 | 107 | 29.66 | 2.19 | 0 | 52.3184 | 261.578 | 40.9655 | 0 | 830 | 689.824 | 110.227 | 7.7764 | 689.824 | 103.155 | 0.040591 | 678.638 | 99.3369 | 0.030586 | 754.665 | 754.661 | 1694780 | 50.1349 | 1680750 | 1499320 | 1465820 | 0 | 0 | 1446270 | 651.824 | 0 | 0 | 0 | 2630.11 | 1443640 | 659.999 | 1421030 | 1392608.5
3616 | 2005-05-31 15:00 | 654 | 867 | 96 | 30.03 | 3.44 | 0 | 40.0045 | 270.964 | 54.7481 | 0 | 654 | 500.992 | 98.2042 | 6.1275 | 500.992 | 91.9032 | 0.031983 | 482.641 | 88.5019 | 0.0241 | 554.032 | 554.029 | 1244210 | 43.8651 | 1211820 | 1111750 | 1085390 | 0 | 0 | 1074980 | 663.917 | 0 | 0 | 0 | 0 | 1074980 | 663.917 | 1060330 | 1039120.625
3617 | 2005-05-31 16:00 | 445 | 780 | 82 | 30.41 | 3.44 | 0 | 27.7093 | 278.802 | 68.6435 | 0 | 445 | 284.297 | 80.6941 | 4.1693 | 284.297 | 75.5167 | 0.021762 | 259.478 | 72.7218 | 0.016398 | 322.25 | 322.243 | 723678 | 38.457 | 680952 | 639069 | 624092 | 0 | 0 | 620599 | 661.649 | 0 | 0 | 0 | 0 | 620599 | 661.649 | 612480 | 600230.75
3618 | 2005-05-31 17:00 | 228 | 588 | 68 | 30.04 | 3.44 | 0 | 15.6618 | 286.276 | 82.4947 | 0 | 228 | 77.4148 | 59.073 | 2.1362 | 77.4148 | 55.2828 | 0.01115 | 51.6514 | 53.2368 | 0.0084019 | 101.75 | 101.746 | 228496 | 32.5808 | 196770 | 189218 | 184843 | 0 | 0 | 184504 | 632.089 | 0 | 0 | 0 | 4993.83 | 179510 | 660 | 174622 | 171129.9531
3619 | 2005-05-31 18:00 | 33 | 263 | 10 | 29.67 | 5.59 | 0 | 4.0749 | 294.076 | 90 | 0 | 33 | 0 | 8.645 | 0.30918 | 0 | 8.0903 | 0.0016138 | 0 | 7.7909 | 0.0012161 | 7.5583 | 7.5579 | 16973.1 | 29.834 | 9155.31 | 8941.46 | 8776.12 | 0 | 0 | 8774.9 | 499.706 | 0 | 0 | 0 | 8774.9 | 0 | 660 | 0 | 0
3620 | 2005-05-31 19:00 | 0 | 0 | 0 | 29.29 | 5.59 | 0
3621 | 2005-05-31 20:00 | 0 | 0 | 0 | 28.19 | 5.59 | 0
3622 | 2005-05-31 21:00 | 0 | 0 | 0 | 28.48 | 6.44 | 0
3623 | 2005-05-31 22:00 | 0 | 0 | 0 | 28.27 | 6.78 | 0
3624 | 2005-05-31 23:00 | 0 | 0 | 0 | 28.06 | 7.13 | 0
3625 | 2001-06-01 | 0 | 0 | 0 | 27.84 | 7.48 | 0
3626 | 2001-06-01 01:00 | 0 | 0 | 0 | 27.63 | 7.83 | 0
3627 | 2001-06-01 02:00 | 0 | 0 | 0 | 27.42 | 8.17 | 0
3628 | 2001-06-01 03:00 | 0 | 0 | 0 | 26.71 | 8.02 | 0
3629 | 2001-06-01 04:00 | 4 | 68 | 2 | 26.36 | 8.02 | 0 | -2.2296 | 61.0541 | 90 | 0 | 4 | 0 | 1.4292 | 0.037477 | 0 | 1.3375 | 0 | 0 | 1.288 | 0 | 1.2494 | 1.2493 | 2805.62 | 26.3832 | 380.594 | 381.189 | 379.447 | 0 | 0 | 379.431 | 185.322 | 0 | 0 | 0 | 379.431 | 0 | 660 | 0 | 0
3630 | 2001-06-01 05:00 | 114 | 413 | 49 | 27 | 8.02 | 0 | 8.9821 | 69.2815 | 90 | 0 | 114 | 0 | 37.9082 | 1.0681 | 0 | 35.476 | 0.0055751 | 0 | 34.163 | 0.0042009 | 33.1422 | 33.1409 | 74426 | 27.6159 | 56498.9 | 55692.2 | 54379.6 | 0 | 0 | 54346.4 | 593.806 | 0 | 0 | 0 | 10150.2 | 44196.2 | 660 | 42634 | 41781.2891
3631 | 2001-06-01 06:00 | 322 | 695 | 75 | 27.64 | 4.12 | 0 | 20.7962 | 76.8561 | 76.5887 | 0 | 322 | 161.357 | 68.7649 | 3.0169 | 160.023 | 64.3528 | 0.015747 | 133.528 | 61.9712 | 0.011866 | 189.646 | 189.635 | 425874 | 32.1684 | 386093 | 372834 | 358948 | 0 | 0 | 357747 | 651.535 | 0 | 0 | 0 | 2163.09 | 355584 | 661.519 | 349626 | 342633.6875
3632 | 2001-06-01 07:00 | 532 | 810 | 91 | 28.29 | 4.12 | 0 | 32.9773 | 84.3647 | 62.7099 | 0 | 532 | 371.476 | 91.4041 | 4.9844 | 371.476 | 85.5394 | 0.026017 | 349.539 | 82.3737 | 0.019604 | 418.975 | 418.967 | 940893 | 38.2946 | 900587 | 847148 | 826185 | 0 | 0 | 820282 | 672.751 | 0 | 0 | 0 | 0 | 820282 | 672.751 | 809095 | 792913.1875
3633 | 2001-06-01 08:00 | 716 | 853 | 109 | 30.25 | 4.12 | 0 | 45.3177 | 92.6331 | 48.8485 | 0 | 716 | 561.784 | 111.445 | 6.7084 | 561.784 | 104.295 | 0.035015 | 547.188 | 100.435 | 0.026385 | 628.22 | 628.218 | 1410820 | 45.2514 | 1384490 | 1262860 | 1232850 | 0 | 0 | 1219460 | 663.725 | 0 | 0 | 0 | 0 | 1219460 | 663.725 | 1201820 | 1177782.75
3634 | 2001-06-01 09:00 | 870 | 885 | 123 | 32.22 | 3.48 | 0 | 57.5462 | 103.321 | 35.2127 | 0 | 870 | 723.269 | 125.818 | 8.1512 | 723.269 | 117.745 | 0.042547 | 715.169 | 113.388 | 0.03206 | 803.731 | 803.723 | 1804960 | 52.2374 | 1796220 | 1586770 | 1550650 | 0 | 0 | 1528470 | 647.06 | 0 | 0 | 0 | 7379.3 | 1521090 | 660 | 1496430 | 1466501.5
3635 | 2001-06-01 10:00 | 1002 | 947 | 119 | 34.18 | 3.48 | 0 | 69.0165 | 121.181 | 22.3979 | 0 | 1002 | 874.372 | 121.702 | 9.388 | 874.372 | 113.893 | 0.049002 | 870.805 | 109.678 | 0.036924 | 951.104 | 951.1 | 2135930 | 57.868 | 2144230 | 1844820 | 1806600 | 0 | 0 | 1775250 | 631.686 | 0 | 0 | 0 | 41660.7 | 1733590 | 660 | 1701800 | 1667763.75
3636 | 2001-06-01 11:00 | 1047 | 948 | 125 | 34.25 | 3.48 | 0 | 77.0277 | 161.913 | 13.2551 | 0 | 1047 | 920.94 | 126.735 | 9.8096 | 920.94 | 118.603 | 0.051203 | 919.68 | 114.214 | 0.038582 | 1002.91 | 1002.91 | 2252280 | 59.2283 | 2266870 | 1938080 | 1897660 | 0 | 0 | 1862760 | 628.231 | 0 | 0 | 0 | 54248.4 | 1808510 | 660 | 1773990 | 1738510.875
3637 | 2001-06-01 12:00 | 1016 | 879 | 170 | 34.32 | 7.74 | 0 | 74.4588 | 219.857 | 16.241 | 0 | 1016 | 843.064 | 178.337 | 9.5191 | 843.064 | 166.895 | 0.049687 | 841.312 | 160.718 | 0.03744 | 972.005 | 971.996 | 2182870 | 52.7052 | 2193690 | 1937070 | 1892480 | 0 | 0 | 1859920 | 649.498 | 0 | 0 | 0 | 4556.86 | 1855370 | 660 | 1819090 | 1782703.75
3638 | 2001-06-01 13:00 | 962 | 940 | 115 | 34.39 | 7.74 | 0 | 64.3321 | 247.923 | 27.6653 | 0 | 962 | 832.298 | 118.048 | 9.0132 | 832.298 | 110.474 | 0.047046 | 826.926 | 106.386 | 0.03545 | 905.347 | 905.336 | 2033150 | 51.5143 | 2036010 | 1807150 | 1765550 | 0 | 0 | 1737380 | 652.501 | 0 | 0 | 0 | 2567.04 | 1734810 | 660 | 1702980 | 1668922
3639 | 2001-06-01 14:00 | 827 | 907 | 108 | 34.54 | 7.74 | 0 | 52.4072 | 261.737 | 40.959 | 0 | 827 | 685.256 | 111.131 | 7.7484 | 685.256 | 104.001 | 0.040444 | 674.149 | 100.152 | 0.030475 | 751.101 | 751.098 | 1686770 | 48.7469 | 1672370 | 1502050 | 1465700 | 0 | 0 | 1446500 | 657.392 | 0 | 0 | 0 | 181.741 | 1446310 | 660 | 1423640 | 1395166.375
3640 | 2001-06-01 15:00 | 655 | 866 | 97 | 34.69 | 7.9 | 0 | 40.0913 | 271.093 | 54.7249 | 0 | 655 | 500.378 | 99.1097 | 6.1368 | 500.378 | 92.7506 | 0.032032 | 482.074 | 89.318 | 0.024137 | 554.274 | 554.27 | 1244750 | 45.0687 | 1212380 | 1105810 | 1079630 | 0 | 0 | 1069190 | 659.626 | 0 | 0 | 0 | 0.1067 | 1069190 | 660.773 | 1054810 | 1033711.875
3641 | 2001-06-01 16:00 | 443 | 792 | 73 | 34.84 | 7.9 | 0 | 27.7982 | 278.91 | 68.6072 | 0 | 443 | 289.394 | 72.0087 | 4.1506 | 289.394 | 67.3885 | 0.021664 | 264.194 | 64.8944 | 0.016325 | 319.232 | 319.229 | 716906 | 40.8176 | 674158 | 625298 | 610734 | 0 | 0 | 607304 | 653.67 | 0 | 0 | 0 | 738.126 | 606566 | 660 | 598681 | 586707.25
3642 | 2001-06-01 17:00 | 219 | 552 | 68 | 32.99 | 7.9 | 0 | 15.7553 | 286.371 | 82.4468 | 0 | 219 | 73.0987 | 59.0395 | 2.0519 | 73.0987 | 55.2514 | 0.01071 | 48.9482 | 53.2066 | 0.0080702 | 99.098 | 99.0935 | 222539 | 34.8455 | 191180 | 181615 | 177518 | 0 | 0 | 177196 | 622.427 | 0 | 0 | 0 | 9063.72 | 168132 | 660 | 163439 | 160170.4688
3643 | 2001-06-01 18:00 | 32 | 250 | 10 | 31.14 | 10.93 | 0 | 4.1749 | 294.161 | 90 | 0 | 32 | 0 | 8.6435 | 0.29981 | 0 | 8.089 | 0.0015649 | 0 | 7.7896 | 0.0011792 | 7.5571 | 7.5572 | 16971.5 | 31.2574 | 9154.36 | 8876.11 | 8707.94 | 0 | 0 | 8706.71 | 494.328 | 0 | 0 | 0 | 8706.71 | 0 | 660 | 0 | 0
3644 | 2001-06-01 19:00 | 0 | 0 | 0 | 29.29 | 10.93 | 0
3645 | 2001-06-01 20:00 | 0 | 0 | 0 | 28.07 | 10.93 | 0
3646 | 2001-06-01 21:00 | 0 | 0 | 0 | 26.85 | 9.11 | 0
3647 | 2001-06-01 22:00 | 0 | 0 | 0 | 25.63 | 9.11 | 0
3648 | 2001-06-01 23:00 | 0 | 0 | 0 | 24.69 | 9.11 | 0
3649 | 2001-06-02 | 0 | 0 | 0 | 23.74 | 8.77 | 0
3650 | 2001-06-02 01:00 | 0 | 0 | 0 | 22.79 | 8.77 | 0
3651 | 2001-06-02 02:00 | 0 | 0 | 0 | 22.58 | 8.77 | 0
3652 | 2001-06-02 03:00 | 0 | 0 | 0 | 22.36 | 9.31 | 0
3653 | 2001-06-02 04:00 | 4 | 54 | 2 | 22.14 | 9.31 | 0 | -2.1761 | 60.9299 | 90 | 0 | 4 | 0 | 1.4285 | 0.037477 | 0 | 1.3368 | 0 | 0 | 1.2873 | 0 | 1.2487 | 1.2486 | 2804.11 | 22.1614 | 380.166 | 378.93 | 377.235 | 0 | 0 | 377.219 | 184.831 | 0 | 0 | 0 | 377.219 | 0 | 660 | 0 | 0
3654 | 2001-06-02 05:00 | 114 | 319 | 63 | 22.41 | 9.31 | 0 | 9.0239 | 69.1516 | 90 | 0 | 114 | 0 | 47.6749 | 1.0681 | 0 | 44.616 | 0.0055751 | 0 | 42.9648 | 0.0042009 | 41.6799 | 41.6764 | 93594.9 | 23.1246 | 73272.5 | 74006.7 | 72199.4 | 0 | 0 | 72146.1 | 623.119 | 0 | 0 | 0 | 3576.15 | 68570 | 660 | 66246.5 | 64921.5664
3655 | 2001-06-02 06:00 | 245 | 265 | 151 | 22.68 | 7.15 | 0 | 20.8294 | 76.7165 | 76.6139 | 0 | 245 | 61.2007 | 134.355 | 2.2955 | 60.7245 | 125.734 | 0.011982 | 50.646 | 121.081 | 0.0090283 | 166.584 | 166.572 | 374078 | 25.9506 | 335751 | 334192 | 322350 | 0 | 0 | 321451 | 675.743 | 0 | 0 | 0 | 0 | 321451 | 675.743 | 315036 | 308734.8125
3656 | 2001-06-02 07:00 | 509 | 658 | 150 | 22.95 | 7.15 | 0 | 33.0051 | 84.2078 | 62.7477 | 0 | 509 | 301.791 | 146.104 | 4.7689 | 301.791 | 136.729 | 0.024892 | 283.928 | 131.669 | 0.018757 | 403.147 | 403.139 | 905348 | 30.8656 | 864438 | 841846 | 820435 | 0 | 0 | 815001 | 697.141 | 0 | 0 | 0 | 0 | 815001 | 697.141 | 802892 | 786834.3125
3657 | 2001-06-02 08:00 | 696 | 811 | 119 | 23.75 | 7.15 | 0 | 45.3443 | 92.446 | 48.9002 | 0 | 696 | 533.222 | 122.708 | 6.521 | 533.222 | 114.835 | 0.034037 | 519.326 | 110.585 | 0.025648 | 611.039 | 611.033 | 1372230 | 35.7476 | 1344400 | 1282060 | 1251450 | 0 | 0 | 1238800 | 694.37 | 0 | 0 | 0 | 0 | 1238800 | 694.37 | 1219300 | 1194913.125
3658 | 2001-06-02 09:00 | 847 | 839 | 139 | 24.56 | 8.27 | 0 | 57.5787 | 103.079 | 35.2825 | 0 | 847 | 684.67 | 145.421 | 7.9357 | 684.67 | 136.091 | 0.041422 | 676.967 | 131.054 | 0.031212 | 783.811 | 783.807 | 1760230 | 38.8995 | 1749320 | 1646200 | 1605470 | 0 | 0 | 1584530 | 689.755 | 0 | 0 | 0 | 0 | 1584530 | 689.755 | 1556860 | 1525720
3659 | 2001-06-02 10:00 | 963 | 884 | 138 | 25.36 | 8.27 | 0 | 69.0716 | 120.84 | 22.4961 | 0 | 963 | 816.06 | 139.785 | 9.0226 | 816.06 | 130.816 | 0.047095 | 812.699 | 125.975 | 0.035487 | 910.548 | 910.541 | 2044840 | 42.0181 | 2048310 | 1901730 | 1854340 | 0 | 0 | 1826070 | 684.368 | 0 | 0 | 0 | 0 | 1826070 | 684.368 | 1790510 | 1754696.125
3660 | 2001-06-02 11:00 | 1019 | 911 | 133 | 26.16 | 8.27 | 0 | 77.1407 | 161.594 | 13.3884 | 0 | 1019 | 884.094 | 134.254 | 9.5472 | 884.094 | 125.64 | 0.049833 | 882.859 | 120.99 | 0.037551 | 973.77 | 973.762 | 2186810 | 43.9747 | 2197850 | 2023060 | 1974220 | 0 | 0 | 1941880 | 680.792 | 0 | 0 | 0 | 0 | 1941880 | 680.792 | 1902120 | 1864074.625
3661 | 2001-06-02 12:00 | 1008 | 917 | 125 | 26.95 | 8.91 | 0 | 74.585 | 220.017 | 16.3141 | 0 | 1008 | 879.071 | 126.921 | 9.4442 | 879.071 | 118.777 | 0.049295 | 877.227 | 114.381 | 0.037145 | 961.896 | 961.892 | 2160160 | 43.858 | 2169770 | 1998150 | 1948100 | 0 | 0 | 1916690 | 681.273 | 0 | 0 | 0 | 0 | 1916690 | 681.273 | 1877860 | 1840303.375
3662 | 2001-06-02 13:00 | 951 | 939 | 104 | 27.75 | 8.91 | 0 | 64.4349 | 248.119 | 27.6815 | 0 | 951 | 831.46 | 107.251 | 8.9101 | 831.46 | 100.37 | 0.046508 | 826.086 | 96.6549 | 0.035045 | 895.093 | 895.092 | 2010150 | 43.4838 | 2011810 | 1855090 | 1809820 | 0 | 0 | 1782520 | 679.512 | 0 | 0 | 0 | 0 | 1782520 | 679.512 | 1748580 | 1713612.125
3663 | 2001-06-02 14:00 | 829 | 926 | 94 | 27.59 | 8.91 | 0 | 52.5002 | 261.893 | 40.9478 | 0 | 829 | 699.75 | 97.3936 | 7.7671 | 699.75 | 91.1447 | 0.040542 | 688.415 | 87.7715 | 0.030549 | 752.931 | 752.927 | 1690880 | 40.8249 | 1676670 | 1563660 | 1525540 | 0 | 0 | 1506240 | 683.665 | 0 | 0 | 0 | 0 | 1506240 | 683.665 | 1481160 | 1451533.125
3664 | 2001-06-02 15:00 | 653 | 880 | 85 | 27.43 | 10.5 | 0 | 40.1824 | 271.218 | 54.6967 | 0 | 653 | 508.739 | 87.4716 | 6.1181 | 508.739 | 81.8593 | 0.031934 | 490.16 | 78.8297 | 0.024063 | 551.943 | 551.94 | 1239520 | 36.2274 | 1206980 | 1148040 | 1120280 | 0 | 0 | 1109960 | 688.697 | 0 | 0 | 0 | 0 | 1109960 | 688.697 | 1093380 | 1071512.5
3665 | 2001-06-02 16:00 | 449 | 805 | 72 | 27.26 | 10.5 | 0 | 27.8914 | 279.016 | 68.566 | 0 | 449 | 294.502 | 71.0026 | 4.2068 | 294.502 | 66.447 | 0.021958 | 268.932 | 63.9878 | 0.016546 | 322.948 | 322.947 | 725256 | 32.4075 | 682537 | 659550 | 643035 | 0 | 0 | 639553 | 683.224 | 0 | 0 | 0 | 0 | 639553 | 683.224 | 630496 | 617886.1875
3666 | 2001-06-02 17:00 | 223 | 572 | 66 | 26.47 | 10.5 | 0 | 15.8531 | 286.463 | 82.3938 | 0 | 223 | 76.0729 | 57.1902 | 2.0893 | 76.0729 | 53.5208 | 0.010906 | 51.1401 | 51.54 | 0.0082176 | 99.6077 | 99.6051 | 223687 | 28.0576 | 192256 | 189285 | 184675 | 0 | 0 | 184353 | 647.599 | 0 | 0 | 0 | 898.957 | 183454 | 660 | 178502 | 174931.8125
3667 | 2001-06-02 18:00 | 33 | 261 | 10 | 25.68 | 9.36 | 0 | 4.279 | 294.242 | 90 | 0 | 33 | 0 | 8.6419 | 0.30918 | 0 | 8.0874 | 0.0016138 | 0 | 7.7881 | 0.0012161 | 7.5556 | 7.5556 | 16968 | 25.8092 | 9151.67 | 9116.34 | 8940.08 | 0 | 0 | 8938.88 | 513.154 | 0 | 0 | 0 | 8938.88 | 0 | 660 | 0 | 0
3668 | 2001-06-02 19:00 | 0 | 0 | 0 | 24.89 | 9.36 | 0
3669 | 2001-06-02 20:00 | 0 | 0 | 0 | 23.84 | 9.36 | 0
3670 | 2001-06-02 21:00 | 0 | 0 | 0 | 22.79 | 8.84 | 0
3671 | 2001-06-02 22:00 | 0 | 0 | 0 | 21.74 | 8.84 | 0
3672 | 2001-06-02 23:00 | 0 | 0 | 0 | 20.79 | 8.84 | 0
3673 | 2001-06-03 | 0 | 0 | 0 | 19.83 | 10.22 | 0
3674 | 2001-06-03 01:00 | 0 | 0 | 0 | 18.88 | 10.22 | 0
3675 | 2001-06-03 02:00 | 0 | 0 | 0 | 17.99 | 10.22 | 0
3676 | 2001-06-03 03:00 | 0 | 0 | 0 | 17.09 | 10.25 | 0
3677 | 2001-06-03 04:00 | 4 | 75 | 2 | 16.2 | 10.25 | 0 | -2.1278 | 60.8098 | 90 | 0 | 4 | 0 | 1.4278 | 0.037477 | 0 | 1.3362 | 0 | 0 | 1.2867 | 0 | 1.2481 | 1.2481 | 2802.86 | 16.2202 | 379.871 | 376.017 | 374.287 | 0 | 0 | 374.271 | 184.184 | 0 | 0 | 0 | 374.271 | 0 | 660 | 0 | 0
3678 | 2001-06-03 05:00 | 115 | 440 | 45 | 16.68 | 10.25 | 0 | 9.0609 | 69.0263 | 90 | 0 | 115 | 0 | 34.0354 | 1.0775 | 0 | 31.8516 | 0.005624 | 0 | 30.6728 | 0.0042378 | 29.7567 | 29.7541 | 66820.2 | 17.1615 | 49933.7 | 52045.1 | 50766.8 | 0 | 0 | 50740.7 | 625.914 | 0 | 0 | 0 | 1860.13 | 48880.5 | 660 | 47166.5 | 46223.1406
3679 | 2001-06-03 06:00 | 318 | 701 | 68 | 17.16 | 8.29 | 0 | 20.858 | 76.582 | 76.641 | 0 | 318 | 162.23 | 64.0795 | 2.9794 | 161.07 | 59.9681 | 0.015551 | 134.268 | 57.7487 | 0.011718 | 186.267 | 186.253 | 418275 | 20.5632 | 378681 | 386583 | 372034 | 0 | 0 | 370899 | 694.254 | 0 | 0 | 0 | 0 | 370899 | 694.254 | 364090 | 356807.9688
3680 | 2001-06-03 07:00 | 514 | 747 | 106 | 17.63 | 8.29 | 0 | 33.0284 | 84.057 | 62.7869 | 0 | 514 | 342.312 | 104.491 | 4.8158 | 342.312 | 97.7871 | 0.025137 | 322 | 94.1681 | 0.018941 | 403.702 | 403.697 | 906601 | 25.0063 | 865710 | 865610 | 842577 | 0 | 0 | 837160 | 716.413 | 0 | 0 | 0 | 0 | 837160 | 716.413 | 823915 | 807437.125
3681 | 2001-06-03 08:00 | 722 | 843 | 122 | 19.7 | 8.29 | 0 | 45.3665 | 92.266 | 48.9527 | 0 | 722 | 553.683 | 125.54 | 6.7646 | 553.683 | 117.485 | 0.035309 | 539.21 | 113.137 | 0.026606 | 632.802 | 632.795 | 1421100 | 31.2623 | 1395170 | 1357670 | 1321520 | 0 | 0 | 1308080 | 710.988 | 0 | 0 | 0 | 0 | 1308080 | 710.988 | 1286350 | 1260619.75
3682 | 2001-06-03 09:00 | 871 | 904 | 108 | 21.77 | 6.34 | 0 | 57.6064 | 102.845 | 35.3522 | 0 | 871 | 736.996 | 111.185 | 8.1606 | 736.996 | 104.051 | 0.042596 | 728.665 | 100.2 | 0.032097 | 804.03 | 804.024 | 1805630 | 38.3947 | 1796930 | 1695050 | 1652480 | 0 | 0 | 1630480 | 693.027 | 0 | 0 | 0 | 0 | 1630480 | 693.027 | 1601270 | 1569246.125
3683 | 2001-06-03 10:00 | 991 | 946 | 108 | 23.84 | 6.34 | 0 | 69.1208 | 120.51 | 22.5924 | 0 | 991 | 872.536 | 110.877 | 9.2849 | 872.536 | 103.763 | 0.048464 | 868.91 | 99.9228 | 0.036519 | 939.803 | 939.8 | 2110560 | 43.2721 | 2117510 | 1954970 | 1905660 | 0 | 0 | 1875620 | 681.978 | 0 | 0 | 0 | 0 | 1875620 | 681.978 | 1838310 | 1801544.75
3684 | 2001-06-03 11:00 | 1034 | 943 | 116 | 24.83 | 6.34 | 0 | 77.2467 | 161.273 | 13.5161 | 0 | 1034 | 915.153 | 117.917 | 9.6878 | 915.153 | 110.351 | 0.050567 | 913.849 | 106.267 | 0.038103 | 989.55 | 989.546 | 2222270 | 45.2907 | 2235230 | 2045090 | 1994310 | 0 | 0 | 1960820 | 674.904 | 0 | 0 | 0 | 0 | 1960820 | 674.904 | 1920350 | 1881947.75
3685 | 2001-06-03 12:00 | 1026 | 950 | 111 | 25.83 | 8.84 | 0 | 74.7065 | 220.162 | 16.3821 | 0 | 1026 | 910.081 | 113.348 | 9.6128 | 910.081 | 106.075 | 0.050176 | 908.156 | 102.149 | 0.037808 | 980.032 | 980.025 | 2200900 | 43.132 | 2212690 | 2044740 | 1995550 | 0 | 0 | 1962810 | 683.452 | 0 | 0 | 0 | 0 | 1962810 | 683.452 | 1922230 | 1883790.125
3686 | 2001-06-03 13:00 | 952 | 940 | 104 | 26.82 | 8.84 | 0 | 64.5348 | 248.302 | 27.6944 | 0 | 952 | 831.65 | 107.184 | 8.9195 | 831.65 | 100.307 | 0.046557 | 826.27 | 96.5943 | 0.035082 | 895.212 | 895.208 | 2010410 | 42.6246 | 2012070 | 1862720 | 1817380 | 0 | 0 | 1790120 | 683.147 | 0 | 0 | 0 | 0 | 1790120 | 683.147 | 1755850 | 1720736
3687 | 2001-06-03 14:00 | 823 | 914 | 97 | 26.53 | 8.84 | 0 | 52.5912 | 262.038 | 40.9344 | 0 | 823 | 690.482 | 100.285 | 7.7109 | 690.482 | 93.8502 | 0.040248 | 679.307 | 90.3768 | 0.030328 | 746.622 | 746.62 | 1676710 | 39.7113 | 1661850 | 1557730 | 1519330 | 0 | 0 | 1500410 | 687.401 | 0 | 0 | 0 | 0 | 1500410 | 687.401 | 1475350 | 1445845.625
3688 | 2001-06-03 15:00 | 656 | 883 | 85 | 26.23 | 11.07 | 0 | 40.2716 | 271.336 | 54.6669 | 0 | 656 | 510.859 | 87.4269 | 6.1462 | 510.859 | 81.8174 | 0.032081 | 492.235 | 78.7894 | 0.024174 | 553.918 | 553.912 | 1243940 | 34.7589 | 1211550 | 1160200 | 1129960 | 0 | 0 | 1119650 | 694.905 | 0 | 0 | 0 | 0 | 1119650 | 694.905 | 1102570 | 1080522.375
3689 | 2001-06-03 16:00 | 447 | 797 | 72 | 25.94 | 11.07 | 0 | 27.9826 | 279.116 | 68.5237 | 0 | 447 | 292.61 | 70.9629 | 4.188 | 292.61 | 66.4098 | 0.02186 | 267.279 | 63.952 | 0.016472 | 321.31 | 321.309 | 721580 | 30.8874 | 678849 | 660690 | 643233 | 0 | 0 | 639810 | 689.248 | 0 | 0 | 0 | 0 | 639810 | 689.248 | 630557 | 617945.5
3690 | 2001-06-03 17:00 | 231 | 608 | 63 | 25.25 | 11.07 | 0 | 15.9486 | 286.549 | 82.3404 | 0 | 231 | 81.493 | 54.4482 | 2.1643 | 81.493 | 50.9547 | 0.011297 | 54.9972 | 49.0689 | 0.0085124 | 100.952 | 100.95 | 226708 | 26.8044 | 195090 | 193313 | 188570 | 0 | 0 | 188238 | 650.438 | 0 | 0 | 0 | 294.601 | 187943 | 660 | 182921 | 179262.1719
3691 | 2001-06-03 18:00 | 34 | 281 | 9 | 24.55 | 10.64 | 0 | 4.3804 | 294.317 | 90 | 0 | 34 | 0 | 7.7972 | 0.31855 | 0 | 7.2969 | 0.0016627 | 0 | 7.0269 | 0.0012529 | 6.8173 | 6.8168 | 15308.9 | 24.6577 | 7927.26 | 7939.15 | 7785.49 | 0 | 0 | 7784.57 | 510.236 | 0 | 0 | 0 | 7784.57 | 0 | 660 | 0 | 0
3692 | 2001-06-03 19:00 | 0 | 0 | 0 | 23.86 | 10.64 | 0
3693 | 2001-06-03 20:00 | 0 | 0 | 0 | 22.9 | 10.64 | 0
3694 | 2001-06-03 21:00 | 0 | 0 | 0 | 21.94 | 10.95 | 0
3695 | 2001-06-03 22:00 | 0 | 0 | 0 | 20.98 | 10.95 | 0
3696 | 2001-06-03 23:00 | 0 | 0 | 0 | 20.21 | 10.95 | 0
3697 | 2001-06-04 | 0 | 0 | 0 | 19.44 | 9.39 | 0
3698 | 2001-06-04 01:00 | 0 | 0 | 0 | 18.67 | 9.39 | 0
3699 | 2001-06-04 02:00 | 0 | 0 | 0 | 17.31 | 9.39 | 0
3700 | 2001-06-04 03:00 | 0 | 0 | 0 | 15.96 | 9.29 | 0
3701 | 2001-06-04 04:00 | 4 | 81 | 1 | 14.6 | 9.29 | 0 | -2.0845 | 60.6939 | 90 | 0 | 4 | 0 | 0.91841 | 0.037477 | 0 | 0.85949 | 0 | 0 | 0.82768 | 0 | 0.80285 | 0.8028 | 1802.88 | 14.6138 | 157.513 | 155.579 | 154.818 | 0 | 0 | 154.812 | 119.896 | 0 | 0 | 0 | 154.812 | 0 | 660 | 0 | 0
3702 | 2001-06-04 05:00 | 120 | 471 | 44 | 15.41 | 9.29 | 0 | 9.0932 | 68.9057 | 90 | 0 | 120 | 0 | 33.078 | 1.1243 | 0 | 30.9557 | 0.0058685 | 0 | 29.81 | 0.004422 | 28.92 | 28.919 | 64944.9 | 15.9065 | 48324.3 | 50693 | 49415.1 | 0 | 0 | 49390.6 | 628.889 | 0 | 0 | 0 | 1440.82 | 47949.8 | 660 | 46265.7 | 45340.3984
3703 | 2001-06-04 06:00 | 329 | 737 | 66 | 16.22 | 5.43 | 0 | 20.8822 | 76.4528 | 76.6701 | 0 | 329 | 170.113 | 62.131 | 3.0825 | 168.999 | 58.1446 | 0.016089 | 140.799 | 55.9927 | 0.012124 | 190.9 | 190.888 | 428686 | 20.4053 | 388823 | 397202 | 381498 | 0 | 0 | 380314 | 696.794 | 0 | 0 | 0 | 0 | 380314 | 696.794 | 373481 | 366011.1875
3704 | 2001-06-04 07:00 | 533 | 830 | 80 | 17.04 | 5.43 | 0 | 33.0475 | 83.9122 | 62.8275 | 0 | 533 | 379.35 | 80.5036 | 4.9938 | 379.35 | 75.3383 | 0.026066 | 356.783 | 72.5501 | 0.019641 | 416.472 | 416.467 | 935283 | 26.1712 | 894874 | 890165 | 867221 | 0 | 0 | 861436 | 713.922 | 0 | 0 | 0 | 0 | 861436 | 713.922 | 847915 | 830956.375
3705 | 2001-06-04 08:00 | 727 | 893 | 91 | 19.1 | 5.43 | 0 | 45.3842 | 92.0933 | 49.0059 | 0 | 727 | 586.099 | 93.86 | 6.8114 | 586.099 | 87.8378 | 0.035553 | 570.73 | 84.587 | 0.02679 | 635.684 | 635.68 | 1427570 | 33.0375 | 1401900 | 1353500 | 1318910 | 0 | 0 | 1305260 | 704.358 | 0 | 0 | 0 | 0 | 1305260 | 704.358 | 1283890 | 1258216.125
3706 | 2001-06-04 09:00 | 883 | 926 | 101 | 21.17 | 4.49 | 0 | 57.6294 | 102.621 | 35.4217 | 0 | 883 | 754.507 | 104.288 | 8.273 | 754.507 | 97.5967 | 0.043182 | 745.938 | 93.9848 | 0.032539 | 814.757 | 814.754 | 1829730 | 40.1601 | 1822210 | 1705190 | 1663010 | 0 | 0 | 1640440 | 688.193 | 0 | 0 | 0 | 0 | 1640440 | 688.193 | 1611060 | 1578836
3707 | 2001-06-04 10:00 | 998 | 957 | 104 | 23.24 | 4.49 | 0 | 69.1643 | 120.189 | 22.6866 | 0 | 998 | 882.544 | 106.906 | 9.3505 | 882.544 | 100.046 | 0.048806 | 878.844 | 96.3438 | 0.036777 | 945.968 | 945.962 | 2124380 | 45.2883 | 2132070 | 1950090 | 1901270 | 0 | 0 | 1870800 | 675.051 | 0 | 0 | 0 | 0 | 1870800 | 675.051 | 1833750 | 1797071.25
3708 | 2001-06-04 11:00 | 1048 | 964 | 109 | 24.53 | 4.49 | 0 | 77.3456 | 160.949 | 13.638 | 0 | 1048 | 935.242 | 111.077 | 9.8189 | 935.242 | 103.95 | 0.051252 | 933.886 | 100.103 | 0.038619 | 1003.01 | 1003 | 2252500 | 47.9078 | 2267110 | 2049050 | 1997720 | 0 | 0 | 1963550 | 669.033 | 0 | 0 | 0 | 0 | 1963550 | 669.033 | 1923000 | 1884536
3709 | 2001-06-04 12:00 | 1035 | 963 | 107 | 25.82 | 2.04 | 0 | 74.8234 | 220.291 | 16.445 | 0 | 1035 | 922.2 | 109.388 | 9.6971 | 922.2 | 102.369 | 0.050616 | 920.234 | 98.5808 | 0.03814 | 988.287 | 988.286 | 2219440 | 52.9032 | 2232250 | 1969320 | 1926910 | 0 | 0 | 1893080 | 648.492 | 0 | 0 | 0 | 5781.35 | 1887300 | 660 | 1849800 | 1812799.75
3710 | 2001-06-04 13:00 | 945 | 927 | 108 | 27.11 | 2.04 | 0 | 64.632 | 248.471 | 27.7041 | 0 | 945 | 820.128 | 111.027 | 8.8539 | 820.128 | 103.904 | 0.046214 | 814.819 | 100.058 | 0.034824 | 887.464 | 887.46 | 1993010 | 51.4301 | 1993770 | 1769890 | 1728810 | 0 | 0 | 1701970 | 654.259 | 0 | 0 | 0 | 2486.46 | 1699480 | 660 | 1668900 | 1635523
3711 | 2001-06-04 14:00 | 817 | 902 | 100 | 27.49 | 2.04 | 0 | 52.6801 | 262.174 | 40.9186 | 0 | 817 | 681.277 | 103.166 | 7.6547 | 681.277 | 96.5466 | 0.039955 | 670.262 | 92.9735 | 0.030107 | 740.367 | 740.362 | 1662660 | 47.779 | 1647140 | 1486070 | 1452000 | 0 | 0 | 1433230 | 659.264 | 0 | 0 | 0 | -57.8808 | 1433290 | 660.702 | 1410900 | 1382686
3712 | 2001-06-04 15:00 | 638 | 843 | 92 | 27.88 | 4.11 | 0 | 40.359 | 271.446 | 54.6356 | 0 | 638 | 487.992 | 94.1607 | 5.9776 | 487.992 | 88.1192 | 0.031201 | 470.234 | 84.858 | 0.023511 | 538.462 | 538.461 | 1209250 | 40.7465 | 1175720 | 1094700 | 1067930 | 0 | 0 | 1058100 | 672.592 | 0 | 0 | 0 | 0 | 1058100 | 672.592 | 1043340 | 1022477
3713 | 2001-06-04 16:00 | 440 | 774 | 75 | 28.26 | 4.11 | 0 | 28.0718 | 279.208 | 68.4804 | 0 | 440 | 284.52 | 73.8105 | 4.1225 | 284.52 | 69.0747 | 0.021518 | 259.964 | 66.5183 | 0.016214 | 316.704 | 316.7 | 711225 | 35.8275 | 668462 | 635398 | 619490 | 0 | 0 | 616137 | 670.726 | 0 | 0 | 0 | 0 | 616137 | 670.726 | 607797 | 595640.625
3714 | 2001-06-04 17:00 | 221 | 550 | 68 | 27.87 | 4.11 | 0 | 16.0418 | 286.629 | 82.2866 | 0 | 221 | 74.3126 | 58.959 | 2.0706 | 74.3126 | 55.1761 | 0.010808 | 50.3448 | 53.1341 | 0.0081439 | 100.382 | 100.38 | 225428 | 30.2686 | 193890 | 188720 | 184357 | 0 | 0 | 184027 | 638.327 | 0 | 0 | 0 | 2545.26 | 181481 | 660 | 176561 | 173030.0469
3715 | 2001-06-04 18:00 | 34 | 257 | 11 | 27.47 | 7.43 | 0 | 4.479 | 294.385 | 90 | 0 | 34 | 0 | 9.4768 | 0.31855 | 0 | 8.8688 | 0.0016627 | 0 | 8.5405 | 0.0012529 | 8.2855 | 8.2852 | 18606.5 | 27.6298 | 10378.2 | 10243.2 | 10047.3 | 0 | 0 | 10045.7 | 513.571 | 0 | 0 | 0 | 10045.7 | 0 | 660 | 0 | 0
3716 | 2001-06-04 19:00 | 0 | 0 | 0 | 27.08 | 7.43 | 0
3717 | 2001-06-04 20:00 | 0 | 0 | 0 | 25.99 | 7.43 | 0
3718 | 2001-06-04 21:00 | 0 | 0 | 0 | 24.9 | 7.88 | 0
3719 | 2001-06-04 22:00 | 0 | 0 | 0 | 23.81 | 7.88 | 0
3720 | 2001-06-04 23:00 | 0 | 0 | 0 | 22.99 | 7.88 | 0
3721 | 2001-06-05 | 0 | 0 | 0 | 22.16 | 6.69 | 0
3722 | 2001-06-05 01:00 | 0 | 0 | 0 | 21.34 | 6.69 | 0
3723 | 2001-06-05 02:00 | 0 | 0 | 0 | 20.41 | 6.69 | 0
3724 | 2001-06-05 03:00 | 0 | 0 | 0 | 19.48 | 9.46 | 0
3725 | 2001-06-05 04:00 | 4 | 85 | 1 | 18.55 | 9.46 | 0 | -2.0464 | 60.5824 | 90 | 0 | 4 | 0 | 0.91818 | 0.037477 | 0 | 0.85927 | 0 | 0 | 0.82747 | 0 | 0.80264 | 0.80258 | 1802.39 | 18.5636 | 157.42 | 156.224 | 155.479 | 0 | 0 | 155.472 | 119.986 | 0 | 0 | 0 | 155.472 | 0 | 660 | 0 | 0
3726 | 2001-06-05 05:00 | 124 | 492 | 45 | 19.13 | 9.46 | 0 | 9.1207 | 68.79 | 90 | 0 | 124 | 0 | 33.9729 | 1.1618 | 0 | 31.7932 | 0.0060641 | 0 | 30.6165 | 0.0045694 | 29.7025 | 29.7006 | 66699.9 | 19.6346 | 49830.3 | 51276.7 | 50043.3 | 0 | 0 | 50017.2 | 617.079 | 0 | 0 | 0 | 3195.69 | 46821.5 | 660 | 45173.9 | 44270.4062
3727 | 2001-06-05 06:00 | 329 | 737 | 65 | 19.72 | 6.99 | 0 | 20.9019 | 76.329 | 76.701 | 0 | 329 | 170.217 | 61.1293 | 3.0825 | 169.181 | 57.2071 | 0.016089 | 140.867 | 55.0899 | 0.012124 | 190.09 | 190.079 | 426867 | 23.4904 | 387045 | 389769 | 375278 | 0 | 0 | 374092 | 685.187 | 0 | 0 | 0 | 0 | 374092 | 685.187 | 367556 | 360205.3438
3728 | 2001-06-05 07:00 | 540 | 845 | 79 | 20.3 | 6.99 | 0 | 33.0622 | 83.7736 | 62.8693 | 0 | 540 | 385.347 | 80.1832 | 5.0594 | 385.347 | 75.0385 | 0.026408 | 362.363 | 72.2614 | 0.019899 | 421.605 | 421.605 | 946819 | 28.6628 | 906622 | 891884 | 867816 | 0 | 0 | 861909 | 706.529 | 0 | 0 | 0 | 0 | 861909 | 706.529 | 848699 | 831724.8125
3729 | 2001-06-05 08:00 | 731 | 901 | 89 | 22.1 | 6.99 | 0 | 45.3976 | 91.928 | 49.0597 | 0 | 731 | 590.852 | 91.8535 | 6.8489 | 590.852 | 85.96 | 0.035749 | 575.31 | 82.7787 | 0.026938 | 638.372 | 638.368 | 1433620 | 34.7625 | 1408190 | 1349110 | 1313600 | 0 | 0 | 1299920 | 700.311 | 0 | 0 | 0 | 0 | 1299920 | 700.311 | 1278840 | 1253268.125
3730 | 2001-06-05 09:00 | 887 | 935 | 97 | 23.89 | 6.86 | 0 | 57.6477 | 102.406 | 35.4908 | 0 | 887 | 761.417 | 100.306 | 8.3105 | 761.417 | 93.8706 | 0.043378 | 752.73 | 90.3965 | 0.032686 | 817.865 | 817.857 | 1836700 | 40.2477 | 1829520 | 1711440 | 1669710 | 0 | 0 | 1646890 | 687.104 | 0 | 0 | 0 | 0 | 1646890 | 687.104 | 1617330 | 1584988.125
3731 | 2001-06-05 10:00 | 998 | 956 | 105 | 25.68 | 6.86 | 0 | 69.2021 | 119.879 | 22.7787 | 0 | 998 | 880.743 | 107.823 | 9.3505 | 880.743 | 100.905 | 0.048806 | 877.018 | 97.1706 | 0.036777 | 944.999 | 944.994 | 2122220 | 44.5806 | 2129790 | 1954510 | 1907140 | 0 | 0 | 1876730 | 677.965 | 0 | 0 | 0 | 0 | 1876730 | 677.965 | 1839420 | 1802635.125
3732 | 2001-06-05 11:00 | 1048 | 964 | 109 | 26.84 | 6.86 | 0 | 77.4376 | 160.624 | 13.7541 | 0 | 1048 | 934.445 | 111.005 | 9.8189 | 934.445 | 103.883 | 0.051252 | 933.066 | 100.038 | 0.038619 | 1002.15 | 1002.14 | 2250560 | 46.8836 | 2265060 | 2057190 | 2007180 | 0 | 0 | 1972780 | 670.152 | 0 | 0 | 0 | 0 | 1972780 | 670.152 | 1931860 | 1893221.75
3733 | 2001-06-05 12:00 | 1035 | 962 | 107 | 28.01 | 5.49 | 0 | 74.9355 | 220.403 | 16.5027 | 0 | 1035 | 921.438 | 109.318 | 9.6971 | 921.438 | 102.304 | 0.050616 | 919.459 | 98.5177 | 0.03814 | 987.474 | 987.468 | 2217600 | 49.5767 | 2230310 | 1999670 | 1952980 | 0 | 0 | 1919580 | 662.264 | 0 | 0 | 0 | 18.5988 | 1919560 | 663.085 | 1880770 | 1843154.375
3734 | 2001-06-05 13:00 | 961 | 950 | 102 | 29.17 | 5.49 | 0 | 64.7263 | 248.628 | 27.7104 | 0 | 961 | 840.98 | 105.101 | 9.0038 | 840.98 | 98.3576 | 0.046997 | 835.533 | 94.7175 | 0.035413 | 902.377 | 902.374 | 2026510 | 48.8782 | 2029020 | 1823960 | 1779730 | 0 | 0 | 1751950 | 662.28 | 0 | 0 | 0 | -48.6289 | 1752000 | 662.505 | 1719500 | 1685108.875
3735 | 2001-06-05 14:00 | 832 | 926 | 95 | 29.75 | 5.49 | 0 | 52.7668 | 262.3 | 40.9007 | 0 | 832 | 699.664 | 98.2192 | 7.7952 | 699.664 | 91.9173 | 0.040688 | 688.364 | 88.5155 | 0.030659 | 753.603 | 753.6 | 1692400 | 46.209 | 1678260 | 1525930 | 1488610 | 0 | 0 | 1469350 | 666.809 | 0 | 0 | 0 | 0 | 1469350 | 666.809 | 1445840 | 1416927.25
3736 | 2001-06-05 15:00 | 658 | 884 | 84 | 30.33 | 6.75 | 0 | 40.4443 | 271.548 | 54.6027 | 0 | 658 | 512.534 | 86.3731 | 6.165 | 512.534 | 80.8313 | 0.032179 | 493.919 | 77.8397 | 0.024248 | 554.63 | 554.624 | 1245550 | 41.501 | 1213200 | 1125780 | 1099170 | 0 | 0 | 1088770 | 672.923 | 0 | 0 | 0 | 0 | 1088770 | 672.923 | 1073400 | 1051927.5
3737 | 2001-06-05 16:00 | 455 | 811 | 72 | 30.91 | 6.75 | 0 | 28.1589 | 279.293 | 68.4362 | 0 | 455 | 298.286 | 70.8934 | 4.263 | 298.286 | 66.3447 | 0.022251 | 272.621 | 63.8893 | 0.016767 | 326.431 | 326.428 | 733074 | 37.4848 | 690385 | 651080 | 635637 | 0 | 0 | 632064 | 666.523 | 0 | 0 | 0 | 0 | 632064 | 666.523 | 623641 | 611168.375
3738 | 2001-06-05 17:00 | 230 | 582 | 68 | 30.2 | 6.75 | 0 | 16.1326 | 286.702 | 82.2324 | 0 | 230 | 78.7992 | 58.9393 | 2.1549 | 78.7992 | 55.1577 | 0.011248 | 53.5879 | 53.1163 | 0.0084756 | 103.511 | 103.51 | 232456 | 32.2848 | 200490 | 193110 | 188615 | 0 | 0 | 188263 | 632.979 | 0 | 0 | 0 | 4383.99 | 183879 | 660 | 178921 | 175342.3594
3739 | 2001-06-05 18:00 | 35 | 274 | 10 | 29.48 | 7.12 | 0 | 4.5748 | 294.448 | 90 | 0 | 35 | 0 | 8.6364 | 0.32792 | 0 | 8.0823 | 0.0017117 | 0 | 7.7831 | 0.0012898 | 7.5509 | 7.5504 | 16956.2 | 29.6285 | 9142.82 | 8938.6 | 8768.38 | 0 | 0 | 8767.16 | 499.979 | 0 | 0 | 0 | 8767.16 | 0 | 660 | 0 | 0
3740 | 2001-06-05 19:00 | 0 | 0 | 0 | 28.77 | 7.12 | 0
3741 | 2001-06-05 20:00 | 0 | 0 | 0 | 27.59 | 7.12 | 0
3742 | 2001-06-05 21:00 | 0 | 0 | 0 | 26.41 | 9.34 | 0
3743 | 2001-06-05 22:00 | 0 | 0 | 0 | 25.23 | 9.34 | 0
3744 | 2001-06-05 23:00 | 0 | 0 | 0 | 24.33 | 9.34 | 0
3745 | 2001-06-06 | 0 | 0 | 0 | 23.44 | 9.07 | 0
3746 | 2001-06-06 01:00 | 0 | 0 | 0 | 22.54 | 9.07 | 0
3747 | 2001-06-06 02:00 | 0 | 0 | 0 | 21.76 | 9.07 | 0
3748 | 2001-06-06 03:00 | 0 | 0 | 0 | 20.99 | 8.21 | 0
3749 | 2001-06-06 04:00 | 4 | 83 | 1 | 20.21 | 8.21 | 0 | -2.0133 | 60.4753 | 90 | 0 | 4 | 0 | 0.91798 | 0.037477 | 0 | 0.85908 | 0 | 0 | 0.82729 | 0 | 0.80247 | 0.80245 | 1802.1 | 20.2247 | 157.399 | 156.512 | 155.739 | 0 | 0 | 155.732 | 120.029 | 0 | 0 | 0 | 155.732 | 0 | 660 | 0 | 0
3750 | 2001-06-06 05:00 | 121 | 473 | 45 | 20.63 | 8.21 | 0 | 9.1436 | 68.6791 | 90 | 0 | 121 | 0 | 33.9496 | 1.1337 | 0 | 31.7713 | 0.0059174 | 0 | 30.5955 | 0.0044589 | 29.6819 | 29.6816 | 66657.4 | 21.1751 | 49794.1 | 50826.5 | 49640.9 | 0 | 0 | 49614.7 | 611.095 | 0 | 0 | 0 | 4276.47 | 45338.3 | 660 | 43738.8 | 42863.9961
3751 | 2001-06-06 06:00 | 321 | 713 | 66 | 21.05 | 2.97 | 0 | 20.9173 | 76.2106 | 76.7338 | 0 | 321 | 163.902 | 62.0153 | 3.0075 | 162.952 | 58.0363 | 0.015698 | 135.594 | 55.8884 | 0.011829 | 185.75 | 185.742 | 417129 | 25.8347 | 377555 | 376011 | 362422 | 0 | 0 | 361294 | 677.633 | 0 | 0 | 0 | 0 | 361294 | 677.633 | 354908 | 347809.4062
3752 | 2001-06-06 07:00 | 537 | 838 | 79 | 21.48 | 2.97 | 0 | 33.0728 | 83.6413 | 62.9124 | 0 | 537 | 382.17 | 80.1359 | 5.0313 | 382.17 | 74.9942 | 0.026262 | 359.314 | 72.2187 | 0.019789 | 418.606 | 418.602 | 940074 | 32.2632 | 899752 | 870691 | 849146 | 0 | 0 | 843246 | 691.907 | 0 | 0 | 0 | 0 | 843246 | 691.907 | 830938 | 814319.625
3753 | 2001-06-06 08:00 | 712 | 858 | 101 | 23.06 | 2.97 | 0 | 45.4068 | 91.7702 | 49.1141 | 0 | 712 | 561.618 | 103.452 | 6.6709 | 561.618 | 96.8142 | 0.03482 | 546.798 | 93.2312 | 0.026237 | 620.854 | 620.852 | 1394280 | 39.0532 | 1367300 | 1284260 | 1252000 | 0 | 0 | 1239010 | 685.209 | 0 | 0 | 0 | 0 | 1239010 | 685.209 | 1219940 | 1195539
3754 | 2001-06-06 09:00 | 866 | 889 | 115 | 24.63 | 3.45 | 0 | 57.6614 | 102.2 | 35.5593 | 0 | 866 | 723.101 | 117.78 | 8.1137 | 723.101 | 110.223 | 0.042351 | 714.813 | 106.144 | 0.031912 | 796.359 | 796.352 | 1788400 | 44.5032 | 1778850 | 1631140 | 1590540 | 0 | 0 | 1568980 | 673.487 | 0 | 0 | 0 | 0 | 1568980 | 673.487 | 1542340 | 1511492.75
3755 | 2001-06-06 10:00 | 970 | 902 | 127 | 26.21 | 3.45 | 0 | 69.2342 | 119.581 | 22.8684 | 0 | 970 | 830.704 | 129.012 | 9.0881 | 830.704 | 120.735 | 0.047437 | 827.161 | 116.266 | 0.035745 | 915.16 | 915.155 | 2055200 | 49.0479 | 2059220 | 1849760 | 1807800 | 0 | 0 | 1779020 | 660.875 | 0 | 0 | 0 | 45.0168 | 1778980 | 661.85 | 1745510 | 1710602.375
3756 | 2001-06-06 11:00 | 1047 | 964 | 108 | 27.78 | 3.45 | 0 | 77.5225 | 160.299 | 13.8643 | 0 | 1047 | 933.696 | 109.97 | 9.8096 | 933.696 | 102.914 | 0.051203 | 932.295 | 99.1056 | 0.038582 | 1000.5 | 1000.49 | 2246860 | 52.7475 | 2261150 | 1996650 | 1951000 | 0 | 0 | 1916610 | 651.144 | 0 | 0 | 0 | 3811.6 | 1912800 | 660 | 1874300 | 1836812.625
3757 | 2001-06-06 12:00 | 1035 | 961 | 108 | 29.35 | 1.1 | 0 | 75.0429 | 220.498 | 16.5551 | 0 | 1035 | 919.733 | 110.223 | 9.6971 | 919.733 | 103.151 | 0.050616 | 917.744 | 99.3331 | 0.03814 | 986.602 | 986.594 | 2215640 | 58.1455 | 2228240 | 1915090 | 1873640 | 0 | 0 | 1840110 | 632.659 | 0 | 0 | 0 | 41823.6 | 1798290 | 660 | 1764150 | 1728866.5
3758 | 2001-06-06 13:00 | 947 | 928 | 108 | 30.92 | 1.1 | 0 | 64.8177 | 248.771 | 27.7135 | 0 | 947 | 820.76 | 110.906 | 8.8727 | 820.76 | 103.79 | 0.046312 | 815.442 | 99.949 | 0.034897 | 887.963 | 887.957 | 1994120 | 56.8366 | 1994940 | 1723920 | 1686400 | 0 | 0 | 1659190 | 633.703 | 0 | 0 | 0 | 33415.5 | 1625780 | 660 | 1597720 | 1565765.875
3759 | 2001-06-06 14:00 | 805 | 870 | 112 | 31.58 | 1.1 | 0 | 52.8513 | 262.416 | 40.8805 | 0 | 805 | 657.358 | 114.696 | 7.5422 | 657.358 | 107.337 | 0.039368 | 646.754 | 103.365 | 0.029664 | 727.644 | 727.638 | 1634090 | 52.8174 | 1617260 | 1423060 | 1391990 | 0 | 0 | 1373770 | 641.456 | 0 | 0 | 0 | 13520 | 1360250 | 660 | 1339620 | 1312831.875
3760 | 2001-06-06 15:00 | 628 | 810 | 101 | 32.24 | 2.04 | 0 | 40.5275 | 271.641 | 54.5684 | 0 | 628 | 470.163 | 103.272 | 5.8839 | 470.163 | 96.6454 | 0.030712 | 453.121 | 93.0687 | 0.023142 | 529.827 | 529.821 | 1189840 | 46.7593 | 1155710 | 1044940 | 1020980 | 0 | 0 | 1011440 | 652.727 | 0 | 0 | 0 | 1725.41 | 1009720 | 660 | 996533 | 976602.5
3761 | 2001-06-06 16:00 | 422 | 701 | 90 | 32.9 | 2.04 | 0 | 28.2438 | 279.371 | 68.3912 | 0 | 422 | 258.366 | 86.5136 | 3.9538 | 258.366 | 80.9627 | 0.020638 | 236.205 | 77.9663 | 0.015551 | 304.762 | 304.759 | 684411 | 41.2517 | 641607 | 593587 | 579633 | 0 | 0 | 576510 | 650 | 0 | 0 | 0 | 1637.8 | 574872 | 660 | 567326 | 555980
3762 | 2001-06-06 17:00 | 235 | 550 | 81 | 32.56 | 2.04 | 0 | 16.2209 | 286.768 | 82.1779 | 0 | 235 | 75.0303 | 70.8293 | 2.2018 | 75.0303 | 66.2848 | 0.011492 | 51.2169 | 63.8316 | 0.0086598 | 111.605 | 111.603 | 250631 | 35.6184 | 217618 | 205984 | 201237 | 0 | 0 | 200827 | 625.073 | 0 | 0 | 0 | 8547.18 | 192279 | 660 | 187191 | 183447.3281
3763 | 2001-06-06 18:00 | 36 | 262 | 12 | 32.21 | 4 | 0 | 4.6676 | 294.505 | 90 | 0 | 36 | 0 | 9.0023 | 0.33729 | 0 | 8.4247 | 0.0017606 | 0 | 8.1129 | 0.0013266 | 7.8708 | 7.8701 | 17674.3 | 32.3994 | 9678.28 | 9323.7 | 9149.22 | 0 | 0 | 9147.85 | 492.996 | 0 | 0 | 0 | 9147.85 | 0 | 660 | 0 | 0
3764 | 2001-06-06 19:00 | 0 | 0 | 0 | 31.86 | 4 | 0
3765 | 2001-06-06 20:00 | 0 | 0 | 0 | 30.91 | 4 | 0
3766 | 2001-06-06 21:00 | 0 | 0 | 0 | 29.96 | 6.01 | 0
3767 | 2001-06-06 22:00 | 0 | 0 | 0 | 29 | 6.01 | 0
3768 | 2001-06-06 23:00 | 0 | 0 | 0 | 27.99 | 6.01 | 0
3769 | 2001-06-07 | 0 | 0 | 0 | 26.97 | 3.49 | 0
3770 | 2001-06-07 01:00 | 0 | 0 | 0 | 25.96 | 3.49 | 0
3771 | 2001-06-07 02:00 | 0 | 0 | 0 | 25.21 | 3.49 | 0
3772 | 2001-06-07 03:00 | 0 | 0 | 0 | 24.46 | 4.88 | 0
3773 | 2001-06-07 04:00 | 4 | 81 | 1 | 23.71 | 4.88 | 0 | -1.9851 | 60.3726 | 90 | 0 | 4 | 0 | 0.91781 | 0.037477 | 0 | 0.85892 | 0 | 0 | 0.82713 | 0 | 0.80232 | 0.80231 | 1801.77 | 23.7282 | 157.338 | 157.102 | 156.336 | 0 | 0 | 156.329 | 120.137 | 0 | 0 | 0 | 156.329 | 0 | 660 | 0 | 0
3774 | 2001-06-07 05:00 | 120 | 460 | 46 | 23.92 | 4.88 | 0 | 9.1619 | 68.5732 | 90 | 0 | 120 | 0 | 34.8597 | 1.1243 | 0 | 32.6231 | 0.0058685 | 0 | 31.4157 | 0.004422 | 30.4775 | 30.4752 | 68439.6 | 24.6125 | 51326.8 | 51434.1 | 50215.8 | 0 | 0 | 50188.1 | 600.874 | 0 | 0 | 0 | 7164.62 | 43023.4 | 660 | 41499.6 | 40669.6289
3775 | 2001-06-07 06:00 | 330 | 737 | 66 | 24.13 | 1.83 | 0 | 20.9283 | 76.0979 | 76.7682 | 0 | 330 | 169.17 | 61.9606 | 3.0918 | 168.258 | 57.9851 | 0.016138 | 139.916 | 55.8391 | 0.012161 | 189.894 | 189.887 | 426438 | 29.4073 | 386620 | 378463 | 365934 | 0 | 0 | 364748 | 667.374 | 0 | 0 | 0 | 21.5425 | 364726 | 668.424 | 358614 | 351442.1875
3776 | 2001-06-07 07:00 | 540 | 845 | 78 | 24.33 | 1.83 | 0 | 33.0792 | 83.5154 | 62.9565 | 0 | 540 | 384.861 | 79.1353 | 5.0594 | 384.861 | 74.0578 | 0.026408 | 361.781 | 71.317 | 0.019899 | 420.124 | 420.119 | 943483 | 36.0058 | 903223 | 858930 | 838620 | 0 | 0 | 832668 | 680.486 | 0 | 0 | 0 | 0 | 832668 | 680.486 | 820991 | 804571
3777 | 2001-06-07 08:00 | 733 | 904 | 89 | 26.37 | 1.83 | 0 | 45.4118 | 91.6202 | 49.1687 | 0 | 733 | 591.247 | 91.7593 | 6.8676 | 591.247 | 85.8719 | 0.035847 | 575.596 | 82.6938 | 0.027011 | 638.567 | 638.563 | 1434060 | 44.1167 | 1408640 | 1292050 | 1260790 | 0 | 0 | 1246960 | 668.414 | 0 | 0 | 0 | 0 | 1246960 | 668.414 | 1228510 | 1203939.125
3778 | 2001-06-07 09:00 | 887 | 934 | 98 | 28.4 | 2.22 | 0 | 57.6706 | 102.004 | 35.6273 | 0 | 887 | 758.967 | 101.19 | 8.3105 | 758.967 | 94.6977 | 0.043378 | 750.229 | 91.193 | 0.032686 | 816.211 | 816.202 | 1832980 | 50.5003 | 1825620 | 1626790 | 1589090 | 0 | 0 | 1566210 | 652.648 | 0 | 0 | 0 | 1844.44 | 1564370 | 660 | 1538330 | 1507562.875
3779 | 2001-06-07 10:00 | 977 | 917 | 120 | 30.44 | 2.22 | 0 | 69.2609 | 119.294 | 22.9557 | 0 | 977 | 843.808 | 122.243 | 9.1537 | 843.808 | 114.399 | 0.047779 | 840.179 | 110.165 | 0.036003 | 921.869 | 921.866 | 2070270 | 55.4013 | 2075080 | 1806950 | 1764770 | 0 | 0 | 1735630 | 640.354 | 0 | 0 | 0 | 18958.4 | 1716670 | 660 | 1685480 | 1651773.75
3780 | 2001-06-07 11:00 | 1034 | 941 | 117 | 31.6 | 2.22 | 0 | 77.6004 | 159.973 | 13.9686 | 0 | 1034 | 911.136 | 118.584 | 9.6878 | 911.136 | 110.975 | 0.050567 | 909.748 | 106.868 | 0.038103 | 986.154 | 986.15 | 2214630 | 58.3019 | 2227180 | 1912690 | 1870330 | 0 | 0 | 1836790 | 631.995 | 0 | 0 | 0 | 42951.7 | 1793840 | 660 | 1759860 | 1724667.125
3781 | 2001-06-07 12:00 | 1012 | 918 | 126 | 32.75 | 1.13 | 0 | 75.1455 | 220.576 | 16.6023 | 0 | 1012 | 878.421 | 127.469 | 9.4817 | 878.421 | 119.29 | 0.049491 | 876.51 | 114.875 | 0.037292 | 961.68 | 961.675 | 2159670 | 60.7616 | 2169250 | 1839040 | 1799640 | 0 | 0 | 1767710 | 623.506 | 0 | 0 | 0 | 74187 | 1693530 | 660 | 1663150 | 1629887.75
3782 | 2001-06-07 13:00 | 940 | 911 | 115 | 33.91 | 1.13 | 0 | 64.9062 | 248.901 | 27.7133 | 0 | 940 | 806.481 | 117.641 | 8.8071 | 806.481 | 110.093 | 0.04597 | 801.256 | 106.018 | 0.034639 | 880.089 | 880.08 | 1976440 | 59.5449 | 1976340 | 1684190 | 1648360 | 0 | 0 | 1621580 | 624.331 | 0 | 0 | 0 | 62649.7 | 1558930 | 660 | 1533070 | 1502406.875
3783 | 2001-06-07 14:00 | 834 | 880 | 132 | 34.37 | 1.13 | 0 | 52.9335 | 262.521 | 40.8581 | 0 | 834 | 665.397 | 136.998 | 7.8139 | 665.397 | 128.208 | 0.040786 | 654.679 | 123.463 | 0.030733 | 754.828 | 754.83 | 1695150 | 56.3566 | 1681140 | 1453560 | 1420000 | 0 | 0 | 1400460 | 631.793 | 0 | 0 | 0 | 34929.6 | 1365540 | 660 | 1344790 | 1317892.375
3784 | 2001-06-07 15:00 | 649 | 861 | 88 | 34.83 | 2.72 | 0 | 40.6087 | 271.726 | 54.5326 | 0 | 649 | 500.108 | 90.1852 | 6.0806 | 500.108 | 84.3988 | 0.031739 | 482.018 | 81.2753 | 0.023916 | 546.418 | 546.412 | 1227100 | 49.141 | 1194150 | 1067250 | 1045030 | 0 | 0 | 1034740 | 642.959 | 0 | 0 | 0 | 7789.95 | 1026950 | 660 | 1013440 | 993169.5625
3785 | 2001-06-07 16:00 | 454 | 775 | 86 | 35.3 | 2.72 | 0 | 28.3265 | 279.442 | 68.3453 | 0 | 454 | 286.192 | 84.2381 | 4.2536 | 286.192 | 78.8332 | 0.022203 | 261.723 | 75.9156 | 0.01673 | 327.526 | 327.52 | 735528 | 43.878 | 692851 | 632889 | 618620 | 0 | 0 | 614983 | 642.872 | 0 | 0 | 0 | 5155.59 | 609828 | 660 | 601900 | 589861.9375
3786 | 2001-06-07 17:00 | 227 | 560 | 69 | 34.9 | 2.72 | 0 | 16.3066 | 286.828 | 82.1233 | 0 | 227 | 77.1171 | 59.8183 | 2.1268 | 77.1171 | 55.9802 | 0.011101 | 52.8368 | 53.9084 | 0.008365 | 103.551 | 103.548 | 232542 | 37.612 | 200571 | 187730 | 183399 | 0 | 0 | 183047 | 614.994 | 0 | 0 | 0 | 14187.2 | 168860 | 660 | 164154 | 160871.1406
3787 | 2001-06-07 18:00 | 36 | 269 | 11 | 34.51 | 5.3 | 0 | 4.7574 | 294.556 | 90 | 0 | 36 | 0 | 9.4715 | 0.33729 | 0 | 8.8638 | 0.0017606 | 0 | 8.5358 | 0.0013266 | 8.281 | 8.2804 | 18595.8 | 34.6931 | 10370.1 | 9860.48 | 9679.33 | 0 | 0 | 9677.76 | 488.426 | 0 | 0 | 0 | 9677.76 | 0 | 660 | 0 | 0
3788 | 2001-06-07 19:00 | 0 | 0 | 0 | 34.12 | 5.3 | 0
3789 | 2001-06-07 20:00 | 0 | 0 | 0 | 33.02 | 5.3 | 0
3790 | 2001-06-07 21:00 | 0 | 0 | 0 | 31.92 | 7.7 | 0
3791 | 2001-06-07 22:00 | 0 | 0 | 0 | 30.82 | 7.7 | 0
3792 | 2001-06-07 23:00 | 0 | 0 | 0 | 29.82 | 7.7 | 0
3793 | 2001-06-08 | 0 | 0 | 0 | 28.83 | 5.57 | 0
3794 | 2001-06-08 01:00 | 0 | 0 | 0 | 27.83 | 5.57 | 0
3795 | 2001-06-08 02:00 | 0 | 0 | 0 | 27.27 | 5.57 | 0
3796 | 2001-06-08 03:00 | 0 | 0 | 0 | 26.7 | 5.17 | 0
3797 | 2001-06-08 04:00 | 4 | 74 | 2 | 26.14 | 5.17 | 0 | -1.962 | 60.2744 | 90 | 0 | 4 | 0 | 1.4255 | 0.037477 | 0 | 1.334 | 0 | 0 | 1.2847 | 0 | 1.2461 | 1.2461 | 2798.36 | 26.1678 | 378.63 | 379.131 | 377.408 | 0 | 0 | 377.391 | 184.849 | 0 | 0 | 0 | 377.391 | 0 | 660 | 0 | 0
3798 | 2001-06-08 05:00 | 115 | 417 | 48 | 26.31 | 5.17 | 0 | 9.1757 | 68.4723 | 90 | 0 | 115 | 0 | 36.7247 | 1.0775 | 0 | 34.3684 | 0.005624 | 0 | 33.0964 | 0.0042378 | 32.1076 | 32.1068 | 72103.6 | 27.0259 | 54488.3 | 53885.3 | 52638.3 | 0 | 0 | 52607.3 | 594.602 | 0 | 0 | 0 | 9641.7 | 42965.6 | 660 | 41443.7 | 40614.8008
3799 | 2001-06-08 06:00 | 330 | 702 | 78 | 26.49 | 2.93 | 0 | 20.9351 | 75.9907 | 76.8042 | 0 | 330 | 160.999 | 71.0117 | 3.0918 | 160.174 | 66.4555 | 0.016138 | 133.1 | 63.996 | 0.012161 | 191.195 | 191.188 | 429358 | 31.4281 | 389461 | 377487 | 364898 | 0 | 0 | 363695 | 660.598 | 0 | 0 | 0 | 194.538 | 363500 | 662.971 | 357534 | 350383.6562
3800 | 2001-06-08 07:00 | 529 | 820 | 81 | 26.66 | 2.93 | 0 | 33.0815 | 83.3959 | 63.0016 | 0 | 529 | 372.6 | 81.2293 | 4.9563 | 372.6 | 76.0175 | 0.02587 | 350.192 | 73.2042 | 0.019494 | 410.713 | 410.708 | 922341 | 37.2679 | 881708 | 833383 | 813403 | 0 | 0 | 807705 | 674.767 | 0 | 0 | 0 | 0 | 807705 | 674.767 | 796609 | 780676.4375
3801 | 2001-06-08 08:00 | 721 | 881 | 93 | 28.5 | 2.93 | 0 | 45.4127 | 91.4779 | 49.2237 | 0 | 721 | 575.909 | 95.6143 | 6.7552 | 575.909 | 89.4795 | 0.03526 | 560.614 | 86.1679 | 0.026569 | 627.404 | 627.401 | 1408980 | 44.7048 | 1382580 | 1264420 | 1233660 | 0 | 0 | 1220320 | 666.1 | 0 | 0 | 0 | 0 | 1220320 | 666.1 | 1202560 | 1178506.125
3802 | 2001-06-08 09:00 | 890 | 893 | 136 | 30.33 | 2.02 | 0 | 57.6754 | 101.818 | 35.6945 | 0 | 890 | 724.651 | 137.672 | 8.3386 | 724.651 | 128.838 | 0.043525 | 716.27 | 124.07 | 0.032797 | 815.162 | 815.16 | 1830650 | 52.6987 | 1823170 | 1607080 | 1570460 | 0 | 0 | 1547600 | 644.594 | 0 | 0 | 0 | 8693.54 | 1538900 | 660 | 1513680 | 1483406.875
3803 | 2001-06-08 10:00 | 971 | 869 | 159 | 32.17 | 2.02 | 0 | 69.2821 | 119.02 | 23.0405 | 0 | 971 | 798.887 | 158.94 | 9.0975 | 798.887 | 148.742 | 0.047486 | 795.424 | 143.237 | 0.035782 | 910.536 | 910.53 | 2044810 | 57.1557 | 2048280 | 1767700 | 1729170 | 0 | 0 | 1700550 | 633.825 | 0 | 0 | 0 | 35278.4 | 1665270 | 660 | 1635870 | 1603153
3804 | 2001-06-08 11:00 | 1048 | 920 | 151 | 32.87 | 2.02 | 0 | 77.6712 | 159.649 | 14.067 | 0 | 1048 | 890.641 | 150.607 | 9.8189 | 890.641 | 140.944 | 0.051252 | 889.264 | 135.727 | 0.038619 | 994.279 | 994.274 | 2232890 | 60.1537 | 2246430 | 1911260 | 1871410 | 0 | 0 | 1837180 | 625.657 | 0 | 0 | 0 | 65840.7 | 1771340 | 660 | 1738190 | 1703429.875
3805 | 2001-06-08 12:00 | 1022 | 938 | 116 | 33.57 | 4.28 | 0 | 75.2432 | 220.637 | 16.6441 | 0 | 1022 | 897.649 | 117.827 | 9.5753 | 897.649 | 110.267 | 0.04998 | 895.687 | 106.186 | 0.037661 | 971.853 | 971.851 | 2182530 | 56.535 | 2193340 | 1900240 | 1857980 | 0 | 0 | 1825450 | 637.745 | 0 | 0 | 0 | 27100.7 | 1798350 | 660 | 1764210 | 1728928.875
3806 | 2001-06-08 13:00 | 963 | 950 | 102 | 34.27 | 4.28 | 0 | 64.9917 | 249.017 | 27.7097 | 0 | 963 | 841.113 | 104.944 | 9.0226 | 841.113 | 98.2109 | 0.047095 | 835.665 | 94.5762 | 0.035487 | 902.368 | 902.364 | 2026470 | 55.593 | 2028980 | 1764780 | 1725350 | 0 | 0 | 1697340 | 638.922 | 0 | 0 | 0 | 22432.1 | 1674910 | 660 | 1645180 | 1612278.25
3807 | 2001-06-08 14:00 | 835 | 926 | 95 | 34.55 | 4.28 | 0 | 53.0135 | 262.617 | 40.8335 | 0 | 835 | 700.938 | 98.0893 | 7.8233 | 700.938 | 91.7958 | 0.040835 | 689.664 | 88.3985 | 0.03077 | 754.75 | 754.75 | 1694980 | 52.3849 | 1680960 | 1482950 | 1447650 | 0 | 0 | 1428280 | 646.426 | 0 | 0 | 0 | 8963.89 | 1419320 | 660 | 1397300 | 1369351
3808 | 2001-06-08 15:00 | 651 | 864 | 87 | 34.83 | 7.79 | 0 | 40.6876 | 271.803 | 54.4954 | 0 | 651 | 502.433 | 89.1859 | 6.0994 | 502.433 | 83.4636 | 0.031837 | 484.299 | 80.3746 | 0.02399 | 547.757 | 547.752 | 1230120 | 45.158 | 1197260 | 1091440 | 1065060 | 0 | 0 | 1054910 | 659.947 | 0 | 0 | 0 | 34.3339 | 1054880 | 661.049 | 1040760 | 1019947.625
3809 | 2001-06-08 16:00 | 452 | 795 | 73 | 35.11 | 7.79 | 0 | 28.4068 | 279.505 | 68.2987 | 0 | 452 | 294.584 | 71.7746 | 4.2349 | 294.584 | 67.1694 | 0.022105 | 269.48 | 64.6835 | 0.016656 | 324.155 | 324.149 | 727957 | 41.2219 | 685247 | 634369 | 619858 | 0 | 0 | 616317 | 652.636 | 0 | 0 | 0 | 1038.64 | 615278 | 660 | 607280 | 595134.125
3810 | 2001-06-08 17:00 | 233 | 586 | 67 | 34.18 | 7.79 | 0 | 16.3897 | 286.882 | 82.0685 | 0 | 233 | 81.1795 | 57.9946 | 2.183 | 81.1795 | 54.2736 | 0.011395 | 55.8234 | 52.265 | 0.0085861 | 104.854 | 104.851 | 235470 | 36.157 | 203324 | 191839 | 187446 | 0 | 0 | 187086 | 620.661 | 0 | 0 | 0 | 10669.3 | 176417 | 660 | 171580 | 168148.5625
3811 | 2001-06-08 18:00 | 37 | 284 | 11 | 33.25 | 7.65 | 0 | 4.8441 | 294.601 | 90 | 0 | 37 | 0 | 9.4696 | 0.34666 | 0 | 8.862 | 0.0018094 | 0 | 8.5341 | 0.0013635 | 8.2794 | 8.2788 | 18592.1 | 33.4075 | 10367.4 | 9927.53 | 9740.89 | 0 | 0 | 9739.34 | 493.003 | 0 | 0 | 0 | 9739.34 | 0 | 660 | 0 | 0
3812 | 2001-06-08 19:00 | 0 | 0 | 0 | 32.32 | 7.65 | 0
3813 | 2001-06-08 20:00 | 0 | 0 | 0 | 31.14 | 7.65 | 0
3814 | 2001-06-08 21:00 | 0 | 0 | 0 | 29.96 | 8.02 | 0
3815 | 2001-06-08 22:00 | 0 | 0 | 0 | 28.78 | 8.02 | 0
3816 | 2001-06-08 23:00 | 0 | 0 | 0 | 27.81 | 8.02 | 0
3817 | 2001-06-09 | 0 | 0 | 0 | 26.84 | 8.42 | 0
3818 | 2001-06-09 01:00 | 0 | 0 | 0 | 25.87 | 8.42 | 0
3819 | 2001-06-09 02:00 | 0 | 0 | 0 | 25.03 | 8.42 | 0
3820 | 2001-06-09 03:00 | 0 | 0 | 0 | 24.18 | 7.03 | 0
3821 | 2001-06-09 04:00 | 4 | 81 | 1 | 23.33 | 7.03 | 0 | -1.9438 | 60.1809 | 90 | 0 | 4 | 0 | 0.91756 | 0.037477 | 0 | 0.85869 | 0 | 0 | 0.82691 | 0 | 0.8021 | 0.80205 | 1801.2 | 23.3459 | 157.221 | 156.914 | 156.164 | 0 | 0 | 156.157 | 120.029 | 0 | 0 | 0 | 156.157 | 0 | 660 | 0 | 0
3822 | 2001-06-09 05:00 | 119 | 455 | 45 | 23.79 | 7.03 | 0 | 9.1849 | 68.3765 | 90 | 0 | 119 | 0 | 33.9095 | 1.1149 | 0 | 31.7338 | 0.0058196 | 0 | 30.5594 | 0.0043852 | 29.6469 | 29.6458 | 66577.2 | 24.3766 | 49725.1 | 49893.1 | 48701.1 | 0 | 0 | 48674.9 | 599.41 | 0 | 0 | 0 | 7099.66 | 41575.2 | 660 | 40099.1 | 39297.125
3823 | 2001-06-09 06:00 | 322 | 714 | 66 | 24.24 | 3.69 | 0 | 20.9377 | 75.8892 | 76.8417 | 0 | 322 | 163.078 | 61.8577 | 3.0169 | 162.298 | 57.8888 | 0.015747 | 134.765 | 55.7464 | 0.011866 | 184.807 | 184.797 | 415007 | 28.7793 | 375482 | 368676 | 356090 | 0 | 0 | 354975 | 669.663 | 0 | 0 | 0 | 1.2098 | 354973 | 669.754 | 348778 | 341802.0625
3824 | 2001-06-09 07:00 | 533 | 830 | 80 | 24.7 | 3.69 | 0 | 33.0798 | 83.2831 | 63.0476 | 0 | 533 | 376.181 | 80.2034 | 4.9938 | 376.181 | 75.0574 | 0.026066 | 353.492 | 72.2796 | 0.019641 | 413.018 | 413.013 | 927525 | 34.8451 | 886980 | 848058 | 827457 | 0 | 0 | 821729 | 684.103 | 0 | 0 | 0 | 0 | 821729 | 684.103 | 810056 | 793854.75
3825 | 2001-06-09 08:00 | 732 | 904 | 88 | 26.49 | 3.69 | 0 | 45.4096 | 91.3436 | 49.2788 | 0 | 732 | 589.953 | 90.6993 | 6.8583 | 589.953 | 84.8799 | 0.035798 | 574.236 | 81.7386 | 0.026974 | 636.321 | 636.318 | 1429000 | 42.1202 | 1403390 | 1299530 | 1268330 | 0 | 0 | 1254550 | 673.468 | 0 | 0 | 0 | 0 | 1254550 | 673.468 | 1235690 | 1210978.75
3826 | 2001-06-09 09:00 | 890 | 937 | 98 | 28.27 | 4.01 | 0 | 57.6758 | 101.642 | 35.7608 | 0 | 890 | 760.534 | 101.104 | 8.3386 | 760.534 | 94.6173 | 0.043525 | 751.699 | 91.1156 | 0.032797 | 817.562 | 817.559 | 1836030 | 47.9341 | 1828820 | 1650120 | 1611530 | 0 | 0 | 1588630 | 661.587 | 0 | 0 | 0 | -38.8672 | 1588670 | 661.892 | 1561780 | 1530544.75
3827 | 2001-06-09 10:00 | 992 | 947 | 107 | 30.06 | 4.01 | 0 | 69.2981 | 118.758 | 23.1225 | 0 | 992 | 870.085 | 109.568 | 9.2943 | 870.085 | 102.538 | 0.048513 | 866.285 | 98.7432 | 0.036555 | 936.113 | 936.106 | 2102250 | 52.5754 | 2108760 | 1862490 | 1818460 | 0 | 0 | 1788470 | 650.445 | 0 | 0 | 0 | 4649.97 | 1783820 | 660 | 1750220 | 1715212.5
3828 | 2001-06-09 11:00 | 1048 | 920 | 151 | 30.87 | 4.01 | 0 | 77.735 | 159.327 | 14.1593 | 0 | 1048 | 890.064 | 150.534 | 9.8189 | 890.064 | 140.875 | 0.051252 | 888.669 | 135.662 | 0.038619 | 993.639 | 993.635 | 2231460 | 54.7691 | 2244920 | 1962580 | 1916110 | 0 | 0 | 1882230 | 644.455 | 0 | 0 | 0 | 12502.3 | 1869730 | 660 | 1832900 | 1796242.625
3829 | 2001-06-09 12:00 | 989 | 811 | 206 | 31.68 | 6.72 | 0 | 75.336 | 220.68 | 16.6805 | 0 | 989 | 775.306 | 211.922 | 9.2662 | 775.306 | 198.325 | 0.048366 | 773.603 | 190.985 | 0.036445 | 935.685 | 935.684 | 2101310 | 50.5622 | 2107770 | 1880030 | 1838950 | 0 | 0 | 1808650 | 654.639 | 0 | 0 | 0 | 660.615 | 1807990 | 660 | 1773490 | 1738022.5
3830 | 2001-06-09 13:00 | 963 | 902 | 145 | 32.48 | 6.72 | 0 | 65.0743 | 249.12 | 27.7028 | 0 | 963 | 798.621 | 146.066 | 9.0226 | 798.621 | 136.694 | 0.047095 | 793.451 | 131.635 | 0.035487 | 897.367 | 897.362 | 2015250 | 50.5889 | 2017170 | 1798340 | 1756490 | 0 | 0 | 1729030 | 657.019 | 0 | 0 | 0 | 851.849 | 1728170 | 660 | 1696580 | 1662647.5
3831 | 2001-06-09 14:00 | 835 | 926 | 95 | 32.34 | 6.72 | 0 | 53.0911 | 262.702 | 40.8068 | 0 | 835 | 700.506 | 98.0524 | 7.8233 | 700.506 | 91.7612 | 0.040835 | 689.258 | 88.3651 | 0.03077 | 754.324 | 754.319 | 1694010 | 47.5623 | 1679950 | 1517590 | 1482800 | 0 | 0 | 1463310 | 660.514 | 0 | 0 | 0 | -66.2809 | 1463380 | 661.322 | 1440240 | 1411431.125
3832 | 2001-06-09 15:00 | 662 | 884 | 85 | 32.2 | 7.49 | 0 | 40.7644 | 271.872 | 54.4568 | 0 | 662 | 513.699 | 87.2182 | 6.2024 | 513.699 | 81.6221 | 0.032375 | 495.2 | 78.6013 | 0.024395 | 556.611 | 556.607 | 1250000 | 42.8958 | 1217800 | 1122550 | 1095710 | 0 | 0 | 1085250 | 668.755 | 0 | 0 | 0 | 0 | 1085250 | 668.755 | 1070160 | 1048752.25
3833 | 2001-06-09 16:00 | 458 | 777 | 87 | 32.05 | 7.49 | 0 | 28.4847 | 279.562 | 68.2514 | 0 | 458 | 288.239 | 85.1425 | 4.2911 | 288.239 | 79.6796 | 0.022398 | 263.756 | 76.7307 | 0.016877 | 330.289 | 330.284 | 741736 | 38.3968 | 699088 | 656394 | 640363 | 0 | 0 | 636717 | 664.349 | 0 | 0 | 0 | 0 | 636717 | 664.349 | 628301 | 615735.375
3834 | 2001-06-09 17:00 | 228 | 525 | 78 | 31.62 | 7.49 | 0 | 16.47 | 286.929 | 82.0136 | 0 | 228 | 73.5083 | 68.0172 | 2.1362 | 73.5083 | 63.6531 | 0.01115 | 50.73 | 61.2973 | 0.0084019 | 108.675 | 108.671 | 244047 | 33.7082 | 211404 | 202134 | 197425 | 0 | 0 | 197038 | 631.237 | 0 | 0 | 0 | 5693.71 | 191344 | 660 | 186270 | 182544.5938
3835 | 2001-06-09 18:00 | 37 | 256 | 13 | 31.18 | 6.97 | 0 | 4.9276 | 294.64 | 90 | 0 | 37 | 0 | 9.7789 | 0.34666 | 0 | 9.1515 | 0.0018094 | 0 | 8.8128 | 0.0013635 | 8.5497 | 8.5495 | 19200 | 31.3498 | 10826.3 | 10479 | 10279.5 | 0 | 0 | 10277.9 | 502.186 | 0 | 0 | 0 | 10277.9 | 0 | 660 | 0 | 0
3836 | 2001-06-09 19:00 | 0 | 0 | 0 | 30.75 | 6.97 | 0
3837 | 2001-06-09 20:00 | 0 | 0 | 0 | 29.75 | 6.97 | 0
3838 | 2001-06-09 21:00 | 0 | 0 | 0 | 28.75 | 7.69 | 0
3839 | 2001-06-09 22:00 | 0 | 0 | 0 | 27.75 | 7.69 | 0
3840 | 2001-06-09 23:00 | 0 | 0 | 0 | 26.81 | 7.69 | 0
3841 | 2001-06-10 | 0 | 0 | 0 | 25.86 | 7.57 | 0
3842 | 2001-06-10 01:00 | 0 | 0 | 0 | 24.92 | 7.57 | 0
3843 | 2001-06-10 02:00 | 0 | 0 | 0 | 24.01 | 7.57 | 0
3844 | 2001-06-10 03:00 | 0 | 0 | 0 | 23.09 | 5.67 | 0
3845 | 2001-06-10 04:00 | 4 | 82 | 1 | 22.18 | 5.67 | 0 | -1.9305 | 60.092 | 90 | 0 | 4 | 0 | 0.91748 | 0.037477 | 0 | 0.85861 | 0 | 0 | 0.82683 | 0 | 0.80203 | 0.802 | 1801.09 | 22.1973 | 157.22 | 156.7 | 155.932 | 0 | 0 | 155.925 | 120.014 | 0 | 0 | 0 | 155.925 | 0 | 660 | 0 | 0
3846 | 2001-06-10 05:00 | 119 | 456 | 45 | 22.67 | 5.67 | 0 | 9.1896 | 68.2859 | 90 | 0 | 119 | 0 | 33.906 | 1.1149 | 0 | 31.7305 | 0.0058196 | 0 | 30.5562 | 0.0043852 | 29.6438 | 29.6417 | 66568.1 | 23.3099 | 49717 | 50173 | 49023.3 | 0 | 0 | 48997.2 | 604.306 | 0 | 0 | 0 | 6083.46 | 42913.8 | 660 | 41393.6 | 40565.7031
3847 | 2001-06-10 06:00 | 322 | 714 | 66 | 23.17 | 5.82 | 0 | 20.9361 | 75.7936 | 76.8808 | 0 | 322 | 162.614 | 61.8096 | 3.0169 | 161.868 | 57.8438 | 0.015747 | 134.304 | 55.703 | 0.011866 | 184.318 | 184.312 | 413915 | 27.1106 | 374418 | 370622 | 358240 | 0 | 0 | 357129 | 675.214 | 0 | 0 | 0 | 0 | 357129 | 675.214 | 350791 | 343775.0625
3848 | 2001-06-10 07:00 | 539 | 844 | 78 | 23.66 | 5.82 | 0 | 33.0741 | 83.1769 | 63.0945 | 0 | 539 | 382.267 | 79.0149 | 5.05 | 382.267 | 73.9452 | 0.026359 | 359.142 | 71.2085 | 0.019862 | 417.46 | 417.457 | 937502 | 32.5852 | 897134 | 866880 | 845241 | 0 | 0 | 839384 | 691.367 | 0 | 0 | 0 | 0 | 839384 | 691.367 | 827155 | 810612.25
3849 | 2001-06-10 08:00 | 732 | 904 | 88 | 25.45 | 5.82 | 0 | 45.4026 | 91.2174 | 49.334 | 0 | 732 | 589.364 | 90.6625 | 6.8583 | 589.364 | 84.8454 | 0.035798 | 573.611 | 81.7054 | 0.026974 | 635.683 | 635.678 | 1427570 | 39.0407 | 1401900 | 1317020 | 1283430 | 0 | 0 | 1269790 | 684.769 | 0 | 0 | 0 | 0 | 1269790 | 684.769 | 1250080 | 1225075.375
3850 | 2001-06-10 09:00 | 889 | 937 | 97 | 27.24 | 5.87 | 0 | 57.6721 | 101.476 | 35.8262 | 0 | 889 | 759.94 | 100.086 | 8.3292 | 759.94 | 93.6639 | 0.043476 | 751.073 | 90.1975 | 0.03276 | 816.064 | 816.062 | 1832680 | 44.6311 | 1825300 | 1673060 | 1630720 | 0 | 0 | 1608130 | 674.055 | 0 | 0 | 0 | 0 | 1608130 | 674.055 | 1580210 | 1548609.625
3851 | 2001-06-10 10:00 | 986 | 935 | 112 | 29.02 | 5.87 | 0 | 69.3088 | 118.51 | 23.2018 | 0 | 986 | 858.701 | 114.377 | 9.238 | 858.701 | 107.039 | 0.048219 | 854.923 | 103.077 | 0.036334 | 929.296 | 929.295 | 2086960 | 48.8243 | 2092660 | 1882110 | 1840230 | 0 | 0 | 1810630 | 662.927 | 0 | 0 | 0 | 0 | 1810630 | 662.927 | 1775980 | 1740463.25
3852 | 2001-06-10 11:00 | 1048 | 920 | 151 | 29.99 | 5.87 | 0 | 77.7918 | 159.009 | 14.2456 | 0 | 1048 | 889.533 | 150.467 | 9.8189 | 889.533 | 140.813 | 0.051252 | 888.122 | 135.601 | 0.038619 | 993.05 | 993.044 | 2230120 | 51.1528 | 2243510 | 1996400 | 1949910 | 0 | 0 | 1916260 | 657.837 | 0 | 0 | 0 | 704.817 | 1915560 | 660.052 | 1876940 | 1839405.875
3853 | 2001-06-10 12:00 | 1006 | 872 | 163 | 30.95 | 7.28 | 0 | 75.4238 | 220.706 | 16.7115 | 0 | 1006 | 834.247 | 161.865 | 9.4254 | 834.247 | 151.479 | 0.049198 | 832.408 | 145.873 | 0.037071 | 948.968 | 948.96 | 2131120 | 49.4296 | 2139170 | 1918730 | 1875000 | 0 | 0 | 1844020 | 660.08 | 0 | 0 | 0 | -57.1924 | 1844080 | 661.055 | 1808210 | 1772049.5
3854 | 2001-06-10 13:00 | 964 | 950 | 102 | 31.91 | 7.28 | 0 | 65.1538 | 249.208 | 27.6927 | 0 | 964 | 841.115 | 104.857 | 9.0319 | 841.115 | 98.1295 | 0.047144 | 835.675 | 94.4978 | 0.035524 | 902.302 | 902.3 | 2026340 | 49.481 | 2028840 | 1818580 | 1775640 | 0 | 0 | 1747710 | 659.14 | 0 | 0 | 0 | 65.74 | 1747640 | 660.588 | 1715340 | 1681029.625
3855 | 2001-06-10 14:00 | 835 | 926 | 94 | 31.77 | 7.28 | 0 | 53.1663 | 262.777 | 40.778 | 0 | 835 | 701.067 | 97.0381 | 7.8233 | 701.067 | 90.812 | 0.040835 | 689.83 | 87.4511 | 0.03077 | 753.992 | 753.986 | 1693270 | 46.4528 | 1679170 | 1525010 | 1488260 | 0 | 0 | 1468870 | 664.698 | 0 | 0 | 0 | 0 | 1468870 | 664.698 | 1445460 | 1416553.25
3856 | 2001-06-10 15:00 | 663 | 884 | 85 | 31.62 | 9.61 | 0 | 40.8388 | 271.933 | 54.417 | 0 | 663 | 514.315 | 87.1934 | 6.2118 | 514.315 | 81.5989 | 0.032424 | 495.837 | 78.5789 | 0.024432 | 557.207 | 557.202 | 1251340 | 40.999 | 1219180 | 1134100 | 1106840 | 0 | 0 | 1096330 | 674.41 | 0 | 0 | 0 | 0 | 1096330 | 674.41 | 1080730 | 1059119
3857 | 2001-06-10 16:00 | 462 | 813 | 73 | 31.48 | 9.61 | 0 | 28.5602 | 279.612 | 68.2035 | 0 | 462 | 302.124 | 71.7373 | 4.3286 | 302.124 | 67.1345 | 0.022594 | 276.547 | 64.6499 | 0.017025 | 330.978 | 330.975 | 743289 | 37.0511 | 700648 | 662214 | 645860 | 0 | 0 | 642193 | 668.337 | 0 | 0 | 0 | 0 | 642193 | 668.337 | 633577 | 620905.1875
3858 | 2001-06-10 17:00 | 243 | 631 | 62 | 30.69 | 9.61 | 0 | 16.5476 | 286.97 | 81.9588 | 0 | 243 | 88.8978 | 53.4777 | 2.2767 | 88.8978 | 50.0465 | 0.011884 | 61.5674 | 48.1943 | 0.0089546 | 106.478 | 106.476 | 239118 | 32.4822 | 206758 | 198963 | 194170 | 0 | 0 | 193799 | 634.357 | 0 | 0 | 0 | 4183.86 | 189615 | 660 | 184567 | 180876.0312
3859 | 2001-06-10 18:00 | 39 | 311 | 10 | 29.9 | 10.35 | 0 | 5.0078 | 294.673 | 90 | 0 | 39 | 0 | 8.6263 | 0.3654 | 0 | 8.0728 | 0.0019073 | 0 | 7.774 | 0.0014372 | 7.5422 | 7.5417 | 16936.8 | 30.0213 | 9128.3 | 8906.95 | 8743.73 | 0 | 0 | 8742.51 | 498.988 | 0 | 0 | 0 | 8742.51 | 0 | 660 | 0 | 0
3860 | 2001-06-10 19:00 | 0 | 0 | 0 | 29.11 | 10.35 | 0
3861 | 2001-06-10 20:00 | 0 | 0 | 0 | 28.01 | 10.35 | 0
3862 | 2001-06-10 21:00 | 0 | 0 | 0 | 26.9 | 10.54 | 0
3863 | 2001-06-10 22:00 | 0 | 0 | 0 | 25.79 | 10.54 | 0
3864 | 2001-06-10 23:00 | 0 | 0 | 0 | 25.01 | 10.54 | 0
3865 | 2001-06-11 | 0 | 0 | 0 | 24.23 | 8.9 | 0
3866 | 2001-06-11 01:00 | 0 | 0 | 0 | 23.45 | 8.9 | 0
3867 | 2001-06-11 02:00 | 0 | 0 | 0 | 22.43 | 8.9 | 0
3868 | 2001-06-11 03:00 | 0 | 0 | 0 | 21.41 | 10.25 | 0
3869 | 2001-06-11 04:00 | 4 | 84 | 1 | 20.39 | 10.25 | 0 | -1.9221 | 60.0079 | 90 | 0 | 4 | 0 | 0.91742 | 0.037477 | 0 | 0.85856 | 0 | 0 | 0.82678 | 0 | 0.80198 | 0.80195 | 1800.96 | 20.403 | 157.186 | 156.333 | 155.581 | 0 | 0 | 155.574 | 119.918 | 0 | 0 | 0 | 155.574 | 0 | 660 | 0 | 0
3870 | 2001-06-11 05:00 | 120 | 467 | 44 | 21.04 | 10.25 | 0 | 9.19 | 68.2005 | 90 | 0 | 120 | 0 | 32.9872 | 1.1243 | 0 | 30.8707 | 0.0058685 | 0 | 29.7282 | 0.004422 | 28.8406 | 28.8396 | 64766.4 | 21.5067 | 48171.2 | 49084.3 | 47923.1 | 0 | 0 | 47898.5 | 608.802 | 0 | 0 | 0 | 4684.2 | 43214.3 | 660 | 41684.2 | 40850.5234
3871 | 2001-06-11 06:00 | 322 | 713 | 67 | 21.69 | 6.12 | 0 | 20.9305 | 75.7038 | 76.9212 | 0 | 322 | 161.531 | 62.7045 | 3.0169 | 160.797 | 58.6813 | 0.015747 | 133.308 | 56.5095 | 0.011866 | 184.134 | 184.126 | 413498 | 25.5513 | 374012 | 372998 | 360208 | 0 | 0 | 359102 | 680.043 | 0 | 0 | 0 | 0 | 359102 | 680.043 | 352637 | 345584.4062
3872 | 2001-06-11 07:00 | 526 | 811 | 83 | 22.34 | 6.12 | 0 | 33.0646 | 83.0775 | 63.1421 | 0 | 526 | 366.833 | 83.0133 | 4.9282 | 366.833 | 77.687 | 0.025724 | 344.576 | 74.8118 | 0.019383 | 406.825 | 406.823 | 913625 | 30.8715 | 872848 | 850030 | 827238 | 0 | 0 | 821722 | 697.419 | 0 | 0 | 0 | 0 | 821722 | 697.419 | 809502 | 793312.1875
3873 | 2001-06-11 08:00 | 712 | 860 | 100 | 24.01 | 6.12 | 0 | 45.3918 | 91.0993 | 49.3892 | 0 | 712 | 559.555 | 102.264 | 6.6709 | 559.555 | 95.7025 | 0.03482 | 544.551 | 92.1606 | 0.026237 | 617.635 | 617.635 | 1387050 | 36.9624 | 1359790 | 1289610 | 1258850 | 0 | 0 | 1245910 | 690.305 | 0 | 0 | 0 | 0 | 1245910 | 690.305 | 1226450 | 1201925.5
3874 | 2001-06-11 09:00 | 889 | 937 | 97 | 25.67 | 4.49 | 0 | 57.6643 | 101.321 | 35.8905 | 0 | 889 | 759.39 | 100.051 | 8.3292 | 759.39 | 93.6318 | 0.043476 | 750.491 | 90.1666 | 0.03276 | 815.47 | 815.466 | 1831330 | 44.6767 | 1823890 | 1671360 | 1630790 | 0 | 0 | 1608190 | 673.728 | 0 | 0 | 0 | 0 | 1608190 | 673.728 | 1580290 | 1548679.625
3875 | 2001-06-11 10:00 | 998 | 955 | 105 | 27.33 | 4.49 | 0 | 69.3144 | 118.275 | 23.2781 | 0 | 998 | 876.834 | 107.542 | 9.3505 | 876.834 | 100.642 | 0.048806 | 872.949 | 96.9174 | 0.036777 | 940.806 | 940.801 | 2112800 | 49.258 | 2119870 | 1902770 | 1859300 | 0 | 0 | 1828840 | 660.285 | 0 | 0 | 0 | -64.7622 | 1828910 | 661.09 | 1793610 | 1757739.125
3876 | 2001-06-11 11:00 | 1048 | 963 | 108 | 28.28 | 4.49 | 0 | 77.8416 | 158.694 | 14.3257 | 0 | 1048 | 931.669 | 109.706 | 9.8189 | 931.669 | 102.667 | 0.051252 | 930.174 | 98.867 | 0.038619 | 998.207 | 998.205 | 2241720 | 51.546 | 2255730 | 2003530 | 1956420 | 0 | 0 | 1922380 | 656.513 | 0 | 0 | 0 | 1319.04 | 1921060 | 660 | 1882230 | 1844586
3877 | 2001-06-11 12:00 | 1037 | 961 | 108 | 29.23 | 6.88 | 0 | 75.5065 | 220.713 | 16.7371 | 0 | 1037 | 918.887 | 109.951 | 9.7159 | 918.887 | 102.896 | 0.050714 | 916.854 | 99.0879 | 0.038214 | 985.501 | 985.495 | 2213160 | 48.9155 | 2225630 | 2001790 | 1953250 | 0 | 0 | 1920120 | 664.45 | 0 | 0 | 0 | 0 | 1920120 | 664.45 | 1881290 | 1843667.25
3878 | 2001-06-11 13:00 | 964 | 950 | 102 | 30.18 | 6.88 | 0 | 65.2301 | 249.283 | 27.6792 | 0 | 964 | 840.701 | 104.819 | 9.0319 | 840.701 | 98.0938 | 0.047144 | 835.269 | 94.4634 | 0.035524 | 901.875 | 901.871 | 2025370 | 48.1951 | 2027820 | 1828890 | 1787220 | 0 | 0 | 1759310 | 663.805 | 0 | 0 | 0 | -29.0561 | 1759340 | 664.172 | 1726540 | 1692007.625
3879 | 2001-06-11 14:00 | 836 | 926 | 94 | 29.94 | 6.88 | 0 | 53.239 | 262.841 | 40.7471 | 0 | 836 | 701.673 | 97.0078 | 7.8327 | 701.673 | 90.7836 | 0.040884 | 690.448 | 87.4237 | 0.030807 | 754.565 | 754.562 | 1694560 | 45.0126 | 1680520 | 1536780 | 1499970 | 0 | 0 | 1480600 | 670.596 | 0 | 0 | 0 | 0 | 1480600 | 670.596 | 1456680 | 1427544.125
3880 | 2001-06-11 15:00 | 665 | 884 | 86 | 29.7 | 10.08 | 0 | 40.9108 | 271.985 | 54.376 | 0 | 665 | 514.972 | 88.1414 | 6.2305 | 514.972 | 82.4861 | 0.032521 | 496.515 | 79.4333 | 0.024505 | 558.693 | 558.686 | 1254670 | 38.8363 | 1222630 | 1148980 | 1121160 | 0 | 0 | 1110590 | 680.63 | 0 | 0 | 0 | 0 | 1110590 | 680.63 | 1094390 | 1072506
3881 | 2001-06-11 16:00 | 464 | 813 | 74 | 29.46 | 10.08 | 0 | 28.6332 | 279.654 | 68.155 | 0 | 464 | 302.833 | 72.6835 | 4.3473 | 302.833 | 68.02 | 0.022691 | 277.282 | 65.5026 | 0.017098 | 332.518 | 332.514 | 746740 | 34.8977 | 704116 | 672461 | 656193 | 0 | 0 | 652504 | 677.314 | 0 | 0 | 0 | 0 | 652504 | 677.314 | 643457 | 630587.75
3882 | 2001-06-11 17:00 | 239 | 597 | 67 | 28.73 | 10.08 | 0 | 16.6223 | 287.005 | 81.9041 | 0 | 239 | 84.6769 | 57.9874 | 2.2392 | 84.6769 | 54.2668 | 0.011688 | 58.8473 | 52.2584 | 0.0088072 | 107.781 | 107.778 | 242042 | 30.4925 | 209513 | 203727 | 199011 | 0 | 0 | 198630 | 641.657 | 0 | 0 | 0 | 2079.28 | 196551 | 660 | 191400 | 187572.2344
3883 | 2001-06-11 18:00 | 39 | 296 | 11 | 28.01 | 10.79 | 0 | 5.0847 | 294.7 | 90 | 0 | 39 | 0 | 9.4638 | 0.3654 | 0 | 8.8566 | 0.0019073 | 0 | 8.5288 | 0.0014372 | 8.2744 | 8.2738 | 18581 | 28.1396 | 10358.9 | 10197.8 | 10006.2 | 0 | 0 | 10004.7 | 511.423 | 0 | 0 | 0 | 10004.7 | 0 | 660 | 0 | 0
3884 | 2001-06-11 19:00 | 0 | 0 | 0 | 27.29 | 10.79 | 0
3885 | 2001-06-11 20:00 | 0 | 0 | 0 | 26.08 | 10.79 | 0
3886 | 2001-06-11 21:00 | 0 | 0 | 0 | 24.87 | 10.35 | 0
3887 | 2001-06-11 22:00 | 0 | 0 | 0 | 23.66 | 10.35 | 0
3888 | 2001-06-11 23:00 | 0 | 0 | 0 | 22.75 | 10.35 | 0
3889 | 2001-06-12 | 0 | 0 | 0 | 21.84 | 10.6 | 0
3890 | 2001-06-12 01:00 | 0 | 0 | 0 | 20.93 | 10.6 | 0
3891 | 2001-06-12 02:00 | 0 | 0 | 0 | 19.72 | 10.6 | 0
3892 | 2001-06-12 03:00 | 0 | 0 | 0 | 18.5 | 12.47 | 0
3893 | 2001-06-12 04:00 | 4 | 78 | 1 | 17.29 | 12.47 | 0 | -1.9185 | 59.9286 | 90 | 0 | 4 | 0 | 0.9174 | 0.037477 | 0 | 0.85854 | 0 | 0 | 0.82676 | 0 | 0.80196 | 0.80193 | 1800.93 | 17.3014 | 157.183 | 155.753 | 154.988 | 0 | 0 | 154.982 | 119.888 | 0 | 0 | 0 | 154.982 | 0 | 660 | 0 | 0
3894 | 2001-06-12 05:00 | 116 | 435 | 46 | 18.02 | 12.47 | 0 | 9.1859 | 68.1204 | 90 | 0 | 116 | 0 | 34.8411 | 1.0868 | 0 | 32.6056 | 0.0056729 | 0 | 31.3989 | 0.0042746 | 30.4611 | 30.4597 | 68404.7 | 18.4514 | 51296.6 | 53109.8 | 51815.5 | 0 | 0 | 51788 | 622.146 | 0 | 0 | 0 | 2376.42 | 49411.6 | 660 | 47680.5 | 46726.8555
3895 | 2001-06-12 06:00 | 313 | 677 | 71 | 18.75 | 10.45 | 0 | 20.9208 | 75.6199 | 76.9628 | 0 | 313 | 152.883 | 64.3711 | 2.9326 | 152.211 | 60.2409 | 0.015307 | 126.084 | 58.0114 | 0.011534 | 178.584 | 178.572 | 401026 | 21.605 | 361884 | 367693 | 354882 | 0 | 0 | 353843 | 691.524 | 0 | 0 | 0 | 0 | 353843 | 691.524 | 347043 | 340102.375
3896 | 2001-06-12 07:00 | 523 | 800 | 86 | 19.48 | 10.45 | 0 | 33.0513 | 82.9849 | 63.1903 | 0 | 523 | 361.392 | 85.8682 | 4.9001 | 361.392 | 80.3587 | 0.025577 | 339.399 | 77.3847 | 0.019273 | 404.298 | 404.297 | 907949 | 25.9438 | 867079 | 863396 | 840628 | 0 | 0 | 835185 | 713.353 | 0 | 0 | 0 | 0 | 835185 | 713.353 | 822099 | 805657.1875
3897 | 2001-06-12 08:00 | 691 | 796 | 124 | 21.31 | 10.45 | 0 | 45.3773 | 90.9894 | 49.4442 | 0 | 691 | 517.96 | 126.814 | 6.4741 | 517.96 | 118.677 | 0.033793 | 504.026 | 114.285 | 0.025464 | 599.787 | 599.778 | 1346950 | 30.8991 | 1318180 | 1284690 | 1251170 | 0 | 0 | 1239080 | 710.715 | 0 | 0 | 0 | 0 | 1239080 | 710.715 | 1218800 | 1194428.875
3898 | 2001-06-12 09:00 | 842 | 824 | 146 | 23.14 | 7.1 | 0 | 57.6524 | 101.176 | 35.9536 | 0 | 842 | 666.898 | 151.427 | 7.8889 | 666.898 | 141.711 | 0.041177 | 659.05 | 136.466 | 0.031028 | 771.681 | 771.676 | 1732990 | 38.34 | 1720770 | 1623330 | 1584610 | 0 | 0 | 1564290 | 691.653 | 0 | 0 | 0 | 0 | 1564290 | 691.653 | 1537170 | 1506429.5
3899 | 2001-06-12 10:00 | 972 | 872 | 157 | 24.97 | 7.1 | 0 | 69.3151 | 118.054 | 23.3514 | 0 | 972 | 799.802 | 156.86 | 9.1069 | 799.802 | 146.795 | 0.047535 | 796.234 | 141.362 | 0.035819 | 909.503 | 909.493 | 2042490 | 42.8847 | 2045840 | 1891840 | 1847220 | 0 | 0 | 1818950 | 681.722 | 0 | 0 | 0 | 0 | 1818950 | 681.722 | 1783680 | 1748008.375
3900 | 2001-06-12 11:00 | 1045 | 960 | 108 | 25.94 | 7.1 | 0 | 77.8844 | 158.385 | 14.3998 | 0 | 1045 | 928.239 | 109.666 | 9.7908 | 928.239 | 102.63 | 0.051105 | 926.733 | 98.8315 | 0.038509 | 994.835 | 994.83 | 2234140 | 45.5356 | 2247750 | 2054280 | 2004310 | 0 | 0 | 1970440 | 674.755 | 0 | 0 | 0 | 0 | 1970440 | 674.755 | 1929600 | 1891011.125
3901 | 2001-06-12 12:00 | 1033 | 956 | 108 | 26.9 | 8.73 | 0 | 75.5842 | 220.703 | 16.7573 | 0 | 1033 | 914.514 | 109.909 | 9.6784 | 914.514 | 102.857 | 0.050518 | 912.486 | 99.0501 | 0.038066 | 981.227 | 981.217 | 2203560 | 44.3421 | 2215500 | 2035940 | 1986200 | 0 | 0 | 1953390 | 679.361 | 0 | 0 | 0 | 0 | 1953390 | 679.361 | 1913190 | 1874929.5
3902 | 2001-06-12 13:00 | 955 | 935 | 106 | 27.86 | 8.73 | 0 | 65.3033 | 249.344 | 27.6624 | 0 | 955 | 827.662 | 108.686 | 8.9476 | 827.662 | 101.713 | 0.046704 | 822.322 | 97.9486 | 0.035192 | 892.696 | 892.694 | 2004760 | 43.7285 | 2006130 | 1847710 | 1800990 | 0 | 0 | 1773890 | 678.897 | 0 | 0 | 0 | 0 | 1773890 | 678.897 | 1740270 | 1705467.5
3903 | 2001-06-12 14:00 | 837 | 927 | 94 | 28.04 | 8.73 | 0 | 53.3091 | 262.895 | 40.7142 | 0 | 837 | 702.325 | 96.9806 | 7.842 | 702.325 | 90.7581 | 0.040933 | 691.112 | 87.3992 | 0.030844 | 755.186 | 755.182 | 1695940 | 41.4641 | 1681970 | 1563980 | 1525060 | 0 | 0 | 1505720 | 681.889 | 0 | 0 | 0 | 0 | 1505720 | 681.889 | 1480710 | 1451100.25
3904 | 2001-06-12 15:00 | 652 | 857 | 90 | 28.21 | 10.3 | 0 | 40.9804 | 272.029 | 54.3337 | 0 | 652 | 499.666 | 91.9888 | 6.1087 | 499.666 | 86.0866 | 0.031885 | 481.801 | 82.9006 | 0.024026 | 547.784 | 547.781 | 1230170 | 37.0483 | 1197320 | 1134500 | 1106440 | 0 | 0 | 1096270 | 685.385 | 0 | 0 | 0 | 0 | 1096270 | 685.385 | 1080130 | 1058526.875
3905 | 2001-06-12 16:00 | 454 | 790 | 74 | 28.39 | 10.3 | 0 | 28.7035 | 279.689 | 68.1061 | 0 | 454 | 295.034 | 72.6728 | 4.2536 | 295.034 | 68.01 | 0.022203 | 270.225 | 65.493 | 0.01673 | 325.663 | 325.657 | 731343 | 33.6444 | 688647 | 661587 | 645534 | 0 | 0 | 641974 | 678.318 | 0 | 0 | 0 | 0 | 641974 | 678.318 | 633041 | 620379.9375
3906 | 2001-06-12 17:00 | 240 | 607 | 65 | 27.92 | 10.3 | 0 | 16.6941 | 287.033 | 81.8496 | 0 | 240 | 86.368 | 56.1857 | 2.2486 | 86.368 | 52.5807 | 0.011737 | 60.2263 | 50.6347 | 0.0088441 | 107.544 | 107.545 | 241517 | 29.6552 | 209019 | 204130 | 199052 | 0 | 0 | 198677 | 646.223 | 0 | 0 | 0 | 1292.57 | 197384 | 660 | 192221 | 188376.875
3907 | 2001-06-12 18:00 | 40 | 303 | 11 | 27.46 | 10.38 | 0 | 5.1582 | 294.721 | 90 | 0 | 40 | 0 | 9.4619 | 0.37477 | 0 | 8.8548 | 0.0019562 | 0 | 8.5271 | 0.001474 | 8.2727 | 8.2721 | 18577.1 | 27.5928 | 10355.9 | 10223.2 | 10033.6 | 0 | 0 | 10032.1 | 513.75 | 0 | 0 | 0 | 10032.1 | 0 | 660 | 0 | 0
3908 | 2001-06-12 19:00 | 0 | 0 | 0 | 26.99 | 10.38 | 0
3909 | 2001-06-12 20:00 | 0 | 0 | 0 | 25.78 | 10.38 | 0
3910 | 2001-06-12 21:00 | 0 | 0 | 0 | 24.56 | 11.68 | 0
3911 | 2001-06-12 22:00 | 0 | 0 | 0 | 23.35 | 11.68 | 0
3912 | 2001-06-12 23:00 | 0 | 0 | 0 | 22.56 | 11.68 | 0
3913 | 2001-06-13 | 0 | 0 | 0 | 21.78 | 11.06 | 0
3914 | 2001-06-13 01:00 | 0 | 0 | 0 | 20.99 | 11.06 | 0
3915 | 2001-06-13 02:00 | 0 | 0 | 0 | 19.84 | 11.06 | 0
3916 | 2001-06-13 03:00 | 0 | 0 | 0 | 18.69 | 10.52 | 0
3917 | 2001-06-13 04:00 | 4 | 82 | 1 | 17.54 | 10.52 | 0 | -1.9196 | 59.8541 | 90 | 0 | 4 | 0 | 0.91741 | 0.037477 | 0 | 0.85854 | 0 | 0 | 0.82677 | 0 | 0.80197 | 0.8019 | 1800.86 | 17.5528 | 157.163 | 155.781 | 155.022 | 0 | 0 | 155.016 | 119.856 | 0 | 0 | 0 | 155.016 | 0 | 660 | 0 | 0
3918 | 2001-06-13 05:00 | 118 | 456 | 44 | 18.4 | 10.52 | 0 | 9.1776 | 68.0457 | 90 | 0 | 118 | 0 | 33.0031 | 1.1056 | 0 | 30.8856 | 0.0057707 | 0 | 29.7425 | 0.0043483 | 28.8545 | 28.8527 | 64795.7 | 18.8593 | 48196.3 | 49797.4 | 48568.5 | 0 | 0 | 48544.1 | 618.396 | 0 | 0 | 0 | 2858.47 | 45685.6 | 660 | 44074.8 | 43193.3164
3919 | 2001-06-13 06:00 | 313 | 663 | 76 | 19.26 | 6.12 | 0 | 20.9072 | 75.542 | 77.0057 | 0 | 313 | 149.333 | 68.8923 | 2.9326 | 148.676 | 64.472 | 0.015307 | 123.049 | 62.0859 | 0.011534 | 179.592 | 179.581 | 403292 | 23.026 | 364084 | 367470 | 355204 | 0 | 0 | 354148 | 687.014 | 0 | 0 | 0 | 0 | 354148 | 687.014 | 347473 | 340523.2812
3920 | 2001-06-13 07:00 | 538 | 802 | 100 | 20.12 | 6.12 | 0 | 33.0343 | 82.8992 | 63.2391 | 0 | 538 | 361.774 | 99.2682 | 5.0406 | 361.774 | 92.8989 | 0.02631 | 339.69 | 89.4608 | 0.019825 | 416.295 | 416.29 | 934883 | 28.85 | 894468 | 879163 | 857713 | 0 | 0 | 851886 | 703.273 | 0 | 0 | 0 | 0 | 851886 | 703.273 | 838968 | 822188.75
3921 | 2001-06-13 08:00 | 727 | 893 | 91 | 21.71 | 6.12 | 0 | 45.359 | 90.8879 | 49.499 | 0 | 727 | 580.525 | 93.492 | 6.8114 | 580.525 | 87.4934 | 0.035553 | 564.858 | 84.2553 | 0.02679 | 629.666 | 629.664 | 1414060 | 34.9146 | 1387860 | 1328660 | 1295270 | 0 | 0 | 1281880 | 697.923 | 0 | 0 | 0 | 0 | 1281880 | 697.923 | 1261300 | 1236071.125
3922 | 2001-06-13 09:00 | 888 | 936 | 97 | 23.31 | 4.53 | 0 | 57.6366 | 101.042 | 36.0153 | 0 | 888 | 757.465 | 99.9926 | 8.3199 | 757.465 | 93.5768 | 0.043427 | 748.515 | 90.1136 | 0.032723 | 813.501 | 813.496 | 1826900 | 42.2213 | 1819240 | 1686320 | 1644370 | 0 | 0 | 1621880 | 681.677 | 0 | 0 | 0 | 0 | 1621880 | 681.677 | 1593290 | 1561426
3923 | 2001-06-13 10:00 | 997 | 955 | 104 | 24.9 | 4.53 | 0 | 69.3108 | 117.847 | 23.4216 | 0 | 997 | 875.908 | 106.506 | 9.3411 | 875.908 | 99.6721 | 0.048757 | 871.975 | 95.9833 | 0.03674 | 938.955 | 938.948 | 2108630 | 46.7277 | 2115480 | 1921800 | 1876260 | 0 | 0 | 1846130 | 670.577 | 0 | 0 | 0 | 0 | 1846130 | 670.577 | 1810050 | 1773850
3924 | 2001-06-13 11:00 | 1045 | 960 | 108 | 25.86 | 4.53 | 0 | 77.9203 | 158.081 | 14.4676 | 0 | 1045 | 927.831 | 109.631 | 9.7908 | 927.831 | 102.597 | 0.051105 | 926.312 | 98.8 | 0.038509 | 994.396 | 994.392 | 2233150 | 48.9766 | 2246700 | 2020220 | 1971240 | 0 | 0 | 1937470 | 664.664 | 0 | 0 | 0 | 0 | 1937470 | 664.664 | 1897970 | 1860010.125
3925 | 2001-06-13 12:00 | 1037 | 961 | 107 | 26.82 | 4.88 | 0 | 75.6566 | 220.675 | 16.7719 | 0 | 1037 | 919.088 | 108.903 | 9.7159 | 919.088 | 101.916 | 0.050714 | 917.046 | 98.1438 | 0.038214 | 984.771 | 984.77 | 2211550 | 49.1964 | 2223920 | 1997500 | 1950520 | 0 | 0 | 1917300 | 662.467 | 0 | 0 | 0 | -26.5862 | 1917320 | 662.595 | 1878620 | 1841049.625
3926 | 2001-06-13 13:00 | 965 | 950 | 102 | 27.78 | 4.88 | 0 | 65.3733 | 249.39 | 27.6423 | 0 | 965 | 840.993 | 104.754 | 9.0413 | 840.993 | 98.0324 | 0.047192 | 835.575 | 94.4043 | 0.035561 | 902.115 | 902.111 | 2025900 | 48.2781 | 2028380 | 1828630 | 1786080 | 0 | 0 | 1758170 | 663.595 | 0 | 0 | 0 | -23.3411 | 1758190 | 663.793 | 1725440 | 1690927.875
3927 | 2001-06-13 14:00 | 830 | 912 | 98 | 27.9 | 4.88 | 0 | 53.3767 | 262.939 | 40.6793 | 0 | 830 | 691.683 | 100.869 | 7.7764 | 691.683 | 94.3971 | 0.040591 | 680.664 | 90.9035 | 0.030586 | 748.45 | 748.447 | 1680820 | 44.9065 | 1666150 | 1524260 | 1488890 | 0 | 0 | 1469770 | 669.749 | 0 | 0 | 0 | 0 | 1469770 | 669.749 | 1446140 | 1417218.625
3928 | 2001-06-13 15:00 | 667 | 885 | 86 | 28.03 | 4.71 | 0 | 41.0475 | 272.064 | 54.2904 | 0 | 667 | 516.408 | 88.1056 | 6.2493 | 516.408 | 82.4526 | 0.032619 | 497.991 | 79.4011 | 0.024579 | 560.094 | 560.093 | 1257820 | 40.8984 | 1225890 | 1140860 | 1113130 | 0 | 0 | 1102490 | 673.479 | 0 | 0 | 0 | 0 | 1102490 | 673.479 | 1086810 | 1065073
3929 | 2001-06-13 16:00 | 464 | 813 | 72 | 28.15 | 4.71 | 0 | 28.7711 | 279.718 | 68.0567 | 0 | 464 | 304.347 | 70.7449 | 4.3473 | 304.347 | 66.2058 | 0.022691 | 278.842 | 63.7556 | 0.017098 | 332.336 | 332.333 | 746333 | 35.7855 | 703707 | 669191 | 652848 | 0 | 0 | 649136 | 671.637 | 0 | 0 | 0 | 0 | 649136 | 671.637 | 640320 | 627513.4375
3930 | 2001-06-13 17:00 | 245 | 639 | 60 | 27.78 | 4.71 | 0 | 16.7628 | 287.054 | 81.7953 | 0 | 245 | 91.5409 | 51.7006 | 2.2955 | 91.5409 | 48.3834 | 0.011982 | 64.0457 | 46.5928 | 0.0090283 | 107.328 | 107.328 | 241031 | 30.2459 | 208560 | 203058 | 198045 | 0 | 0 | 197671 | 643.63 | 0 | 0 | 0 | 1747.92 | 195923 | 660 | 190781 | 186965.3438
3931 | 2001-06-13 18:00 | 54 | 426 | 13 | 27.41 | 3.74 | 0 | 5.2283 | 294.736 | 90 | 0 | 54 | 0 | 11.1272 | 0.50594 | 0 | 10.4133 | 0.0026408 | 0 | 10.0279 | 0.0019899 | 9.729 | 9.7285 | 21847.8 | 27.6482 | 12847.1 | 12671.5 | 12424.3 | 0 | 0 | 12422.1 | 521.501 | 0 | 0 | 0 | 12422.1 | 0 | 660 | 0 | 0
3932 | 2001-06-13 19:00 | 0 | 1 | 0 | 27.04 | 3.74 | 0
3933 | 2001-06-13 20:00 | 0 | 0 | 0 | 26.02 | 3.74 | 0
3934 | 2001-06-13 21:00 | 0 | 0 | 0 | 25 | 5.18 | 0
3935 | 2001-06-13 22:00 | 0 | 0 | 0 | 23.98 | 5.18 | 0
3936 | 2001-06-13 23:00 | 0 | 0 | 0 | 22.96 | 5.18 | 0
3937 | 2001-06-14 | 0 | 0 | 0 | 21.93 | 6.42 | 0
3938 | 2001-06-14 01:00 | 0 | 0 | 0 | 20.91 | 6.42 | 0
3939 | 2001-06-14 02:00 | 0 | 0 | 0 | 19.98 | 6.42 | 0
3940 | 2001-06-14 03:00 | 0 | 0 | 0 | 19.05 | 5.42 | 0
3941 | 2001-06-14 04:00 | 4 | 85 | 1 | 18.12 | 5.42 | 0 | -1.9255 | 59.7846 | 90 | 0 | 4 | 0 | 0.91744 | 0.037477 | 0 | 0.85857 | 0 | 0 | 0.8268 | 0 | 0.802 | 0.80193 | 1800.92 | 18.1376 | 157.172 | 155.898 | 155.144 | 0 | 0 | 155.137 | 119.867 | 0 | 0 | 0 | 155.137 | 0 | 660 | 0 | 0
3942 | 2001-06-14 05:00 | 121 | 475 | 44 | 18.84 | 5.42 | 0 | 9.165 | 67.9765 | 90 | 0 | 121 | 0 | 33.0178 | 1.1337 | 0 | 30.8993 | 0.0059174 | 0 | 29.7557 | 0.0044589 | 28.8674 | 28.8648 | 64822.8 | 19.4733 | 48219.2 | 49661.5 | 48510 | 0 | 0 | 48485.4 | 616.468 | 0 | 0 | 0 | 3270.97 | 45214.4 | 660 | 43619 | 42746.6094
3943 | 2001-06-14 06:00 | 326 | 730 | 65 | 19.56 | 5.81 | 0 | 20.8898 | 75.4702 | 77.0498 | 0 | 326 | 164.038 | 60.7002 | 3.0544 | 163.333 | 56.8056 | 0.015943 | 135.058 | 54.7032 | 0.012013 | 184.08 | 184.075 | 413385 | 23.498 | 373902 | 376533 | 363402 | 0 | 0 | 362298 | 687.066 | 0 | 0 | 0 | 0 | 362298 | 687.066 | 355650 | 348537.4062
3944 | 2001-06-14 07:00 | 538 | 844 | 78 | 20.28 | 5.81 | 0 | 33.0137 | 82.8205 | 63.2883 | 0 | 538 | 379.508 | 78.8865 | 5.0406 | 379.508 | 73.825 | 0.02631 | 356.269 | 71.0928 | 0.019825 | 414.56 | 414.557 | 930990 | 29.1489 | 890507 | 874084 | 851494 | 0 | 0 | 845761 | 703.707 | 0 | 0 | 0 | 0 | 845761 | 703.707 | 832918 | 816259.875
3945 | 2001-06-14 08:00 | 731 | 903 | 89 | 21.75 | 5.81 | 0 | 45.3372 | 90.7948 | 49.5535 | 0 | 731 | 585.569 | 91.5187 | 6.8489 | 585.569 | 85.6467 | 0.035749 | 569.716 | 82.4769 | 0.026938 | 632.653 | 632.648 | 1420770 | 35.2846 | 1394830 | 1333110 | 1298620 | 0 | 0 | 1285130 | 697.159 | 0 | 0 | 0 | 0 | 1285130 | 697.159 | 1264510 | 1239222.625
3946 | 2001-06-14 09:00 | 888 | 936 | 98 | 23.21 | 4.3 | 0 | 57.617 | 100.919 | 36.0757 | 0 | 888 | 756.091 | 100.948 | 8.3199 | 756.091 | 94.4707 | 0.043427 | 747.122 | 90.9744 | 0.032723 | 812.985 | 812.979 | 1825750 | 42.3957 | 1818030 | 1683830 | 1642600 | 0 | 0 | 1620060 | 680.545 | 0 | 0 | 0 | 0 | 1620060 | 680.545 | 1591570 | 1559733.875
3947 | 2001-06-14 10:00 | 997 | 955 | 104 | 24.68 | 4.3 | 0 | 69.3017 | 117.654 | 23.4886 | 0 | 997 | 875.516 | 106.481 | 9.3411 | 875.516 | 99.6485 | 0.048757 | 871.561 | 95.9606 | 0.03674 | 938.531 | 938.528 | 2107700 | 46.8286 | 2114500 | 1919970 | 1872610 | 0 | 0 | 1842690 | 671.074 | 0 | 0 | 0 | 0 | 1842690 | 671.074 | 1806730 | 1770599
3948 | 2001-06-14 11:00 | 1049 | 963 | 109 | 25.8 | 4.3 | 0 | 77.9492 | 157.785 | 14.5293 | 0 | 1049 | 930.442 | 110.566 | 9.8283 | 930.442 | 103.472 | 0.0513 | 928.905 | 99.6422 | 0.038656 | 997.729 | 997.725 | 2240640 | 49.3456 | 2254600 | 2023800 | 1974720 | 0 | 0 | 1940820 | 664.142 | 0 | 0 | 0 | -8.9878 | 1940830 | 664.214 | 1901200 | 1863171.375
3949 | 2001-06-14 12:00 | 1037 | 961 | 107 | 26.92 | 2.23 | 0 | 75.7239 | 220.628 | 16.7811 | 0 | 1037 | 918.768 | 108.87 | 9.7159 | 918.768 | 101.885 | 0.050714 | 916.725 | 98.1139 | 0.038214 | 984.431 | 984.424 | 2210770 | 53.5574 | 2223110 | 1954930 | 1911350 | 0 | 0 | 1877980 | 647.787 | 0 | 0 | 0 | 7584.77 | 1870400 | 660 | 1833540 | 1796871.875
3950 | 2001-06-14 13:00 | 957 | 937 | 105 | 28.04 | 2.23 | 0 | 65.44 | 249.423 | 27.619 | 0 | 957 | 830.008 | 107.652 | 8.9663 | 830.008 | 100.745 | 0.046801 | 824.671 | 97.0168 | 0.035266 | 894.071 | 894.067 | 2007840 | 52.2325 | 2009380 | 1776890 | 1736370 | 0 | 0 | 1708970 | 650.237 | 0 | 0 | 0 | 4638.42 | 1704330 | 660 | 1673580 | 1640106
3951 | 2001-06-14 14:00 | 839 | 927 | 94 | 28.39 | 2.23 | 0 | 53.4415 | 262.973 | 40.6424 | 0 | 839 | 703.764 | 96.9357 | 7.8608 | 703.764 | 90.7161 | 0.041031 | 692.578 | 87.3588 | 0.030917 | 756.569 | 756.566 | 1699050 | 48.8618 | 1685230 | 1512730 | 1477640 | 0 | 0 | 1458080 | 657.053 | 0 | 0 | 0 | 439.312 | 1457640 | 660 | 1434690 | 1405993.125
3952 | 2001-06-14 15:00 | 667 | 884 | 85 | 28.74 | 1.4 | 0 | 41.1119 | 272.091 | 54.246 | 0 | 667 | 517.186 | 87.1223 | 6.2493 | 517.186 | 81.5324 | 0.032619 | 498.789 | 78.5149 | 0.024579 | 560.009 | 560.004 | 1257620 | 44.7584 | 1225680 | 1119650 | 1092350 | 0 | 0 | 1081740 | 661.707 | 0 | 0 | 0 | 0 | 1081740 | 661.707 | 1067060 | 1045719.875
3953 | 2001-06-14 16:00 | 466 | 813 | 73 | 29.1 | 1.4 | 0 | 28.836 | 279.739 | 68.0071 | 0 | 466 | 305.15 | 71.7011 | 4.3661 | 305.15 | 67.1006 | 0.022789 | 279.666 | 64.6173 | 0.017172 | 333.971 | 333.97 | 750014 | 38.6529 | 707409 | 663392 | 646701 | 0 | 0 | 642989 | 664.97 | 0 | 0 | 0 | 0 | 642989 | 664.97 | 634471 | 621781.3125
3954 | 2001-06-14 17:00 | 243 | 608 | 66 | 29.02 | 1.4 | 0 | 16.8285 | 287.07 | 81.7413 | 0 | 243 | 87.8202 | 57.1055 | 2.2767 | 87.8202 | 53.4415 | 0.011884 | 61.6421 | 51.4636 | 0.0089546 | 109.721 | 109.721 | 246405 | 32.1585 | 213627 | 205939 | 201314 | 0 | 0 | 200917 | 635.786 | 0 | 0 | 0 | 3652.82 | 197264 | 660 | 192103 | 188261.0938
3955 | 2001-06-14 18:00 | 54 | 405 | 15 | 28.95 | 2.45 | 0 | 5.2947 | 294.745 | 90 | 0 | 54 | 0 | 12.7769 | 0.50594 | 0 | 11.9571 | 0.0026408 | 0 | 11.5146 | 0.0019899 | 11.1711 | 11.1706 | 25086.3 | 29.2479 | 15360.2 | 15013.8 | 14712.5 | 0 | 0 | 14709.4 | 523.362 | 0 | 0 | 0 | 14709.4 | 0 | 660 | 0 | 0
3956 | 2001-06-14 19:00 | 0 | 2 | 0 | 28.88 | 2.45 | 0
3957 | 2001-06-14 20:00 | 0 | 0 | 0 | 28.17 | 2.45 | 0
3958 | 2001-06-14 21:00 | 0 | 0 | 0 | 27.45 | 4.43 | 0
3959 | 2001-06-14 22:00 | 0 | 0 | 0 | 26.74 | 4.43 | 0
3960 | 2001-06-14 23:00 | 0 | 0 | 0 | 26.01 | 4.43 | 0
3961 | 2001-06-15 | 0 | 0 | 0 | 25.28 | 5.22 | 0
3962 | 2001-06-15 01:00 | 0 | 0 | 0 | 24.55 | 5.22 | 0
3963 | 2001-06-15 02:00 | 0 | 0 | 0 | 24.01 | 5.22 | 0
3964 | 2001-06-15 03:00 | 0 | 0 | 0 | 23.47 | 5.17 | 0
3965 | 2001-06-15 04:00 | 4 | 79 | 1 | 22.94 | 5.17 | 0 | -1.936 | 59.7201 | 90 | 0 | 4 | 0 | 0.9175 | 0.037477 | 0 | 0.85863 | 0 | 0 | 0.82686 | 0 | 0.80205 | 0.80201 | 1801.1 | 22.9579 | 157.203 | 156.825 | 156.075 | 0 | 0 | 156.068 | 120.035 | 0 | 0 | 0 | 156.068 | 0 | 660 | 0 | 0
3966 | 2001-06-15 05:00 | 117 | 444 | 45 | 23.2 | 5.17 | 0 | 9.1482 | 67.9127 | 90 | 0 | 117 | 0 | 33.9589 | 1.0962 | 0 | 31.78 | 0.0057218 | 0 | 30.6038 | 0.0043115 | 29.6899 | 29.6892 | 66674.6 | 23.862 | 49808.9 | 50116.5 | 48918.7 | 0 | 0 | 48892.5 | 601.823 | 0 | 0 | 0 | 6565.85 | 42326.6 | 660 | 40825.7 | 40009.2109
3967 | 2001-06-15 06:00 | 312 | 659 | 77 | 23.47 | 1.17 | 0 | 20.8685 | 75.4045 | 77.0949 | 0 | 312 | 147.335 | 69.7117 | 2.9232 | 146.701 | 65.2388 | 0.015258 | 121.194 | 62.8244 | 0.011497 | 178.509 | 178.498 | 400859 | 28.6553 | 361720 | 355354 | 343407 | 0 | 0 | 342367 | 669.16 | 0 | 0 | 0 | 1.7108 | 342366 | 669.626 | 336131 | 329408.8438
3968 | 2001-06-15 07:00 | 538 | 801 | 101 | 23.73 | 1.17 | 0 | 32.9895 | 82.7489 | 63.3378 | 0 | 538 | 360.147 | 100.136 | 5.0406 | 360.147 | 93.7112 | 0.02631 | 338.025 | 90.243 | 0.019825 | 415.439 | 415.435 | 932961 | 35.7982 | 892512 | 849526 | 829193 | 0 | 0 | 823372 | 680.098 | 0 | 0 | 0 | 0 | 823372 | 680.098 | 811841 | 795604.25
3969 | 2001-06-15 08:00 | 731 | 902 | 90 | 25.57 | 1.17 | 0 | 45.312 | 90.7102 | 49.6075 | 0 | 731 | 584.265 | 92.4695 | 6.8489 | 584.265 | 86.5365 | 0.035749 | 568.397 | 83.3338 | 0.026938 | 632.205 | 632.202 | 1419770 | 43.9353 | 1393790 | 1279440 | 1248670 | 0 | 0 | 1235180 | 669.982 | 0 | 0 | 0 | 0 | 1235180 | 669.982 | 1216900 | 1192566.625
3970 | 2001-06-15 09:00 | 887 | 936 | 97 | 27.4 | 0.42 | 0 | 57.5937 | 100.807 | 36.1346 | 0 | 887 | 755.72 | 99.947 | 8.3105 | 755.72 | 93.5342 | 0.043378 | 746.72 | 90.0726 | 0.032686 | 811.72 | 811.712 | 1822900 | 52.2035 | 1815050 | 1603740 | 1567570 | 0 | 0 | 1544980 | 647.15 | 0 | 0 | 0 | 6988.74 | 1537990 | 660 | 1512800 | 1482540
3971 | 2001-06-15 10:00 | 997 | 955 | 104 | 29.24 | 0.42 | 0 | 69.2879 | 117.477 | 23.5523 | 0 | 997 | 875.172 | 106.459 | 9.3411 | 875.172 | 99.6286 | 0.048757 | 871.195 | 95.9414 | 0.03674 | 938.158 | 938.152 | 2106850 | 57.9071 | 2113600 | 1817670 | 1778340 | 0 | 0 | 1747950 | 631.685 | 0 | 0 | 0 | 41354.8 | 1706600 | 660 | 1675770 | 1642249.75
3972 | 2001-06-15 11:00 | 1048 | 963 | 108 | 30.26 | 0.42 | 0 | 77.9713 | 157.496 | 14.5848 | 0 | 1048 | 930.132 | 109.575 | 9.8189 | 930.132 | 102.544 | 0.051252 | 928.583 | 98.7494 | 0.038619 | 996.55 | 996.544 | 2237990 | 60.7114 | 2251800 | 1910340 | 1870680 | 0 | 0 | 1836280 | 623.794 | 0 | 0 | 0 | 73062 | 1763220 | 660 | 1730360 | 1695755.125
3973 | 2001-06-15 12:00 | 1037 | 960 | 108 | 31.28 | 4.28 | 0 | 75.7858 | 220.563 | 16.7849 | 0 | 1037 | 917.511 | 109.808 | 9.7159 | 917.511 | 102.763 | 0.050714 | 915.469 | 98.9595 | 0.038214 | 984.033 | 984.027 | 2209880 | 54.5327 | 2222160 | 1944790 | 1901460 | 0 | 0 | 1868090 | 644.034 | 0 | 0 | 0 | 12872.6 | 1855210 | 660 | 1818940 | 1782560.875
3974 | 2001-06-15 13:00 | 966 | 950 | 102 | 32.31 | 4.28 | 0 | 65.5033 | 249.441 | 27.5925 | 0 | 966 | 841.478 | 104.702 | 9.0507 | 841.478 | 97.9845 | 0.047241 | 836.078 | 94.3581 | 0.035597 | 902.558 | 902.554 | 2026910 | 53.6375 | 2029440 | 1782470 | 1741850 | 0 | 0 | 1714040 | 647.528 | 0 | 0 | 0 | 10240.7 | 1703800 | 660 | 1673070 | 1639605.25
3975 | 2001-06-15 14:00 | 840 | 926 | 96 | 32.55 | 4.28 | 0 | 53.5037 | 262.995 | 40.6037 | 0 | 840 | 702.662 | 98.8757 | 7.8701 | 702.662 | 92.5317 | 0.041079 | 691.521 | 89.1071 | 0.030954 | 757.239 | 757.235 | 1700550 | 50.4436 | 1686800 | 1502520 | 1467810 | 0 | 0 | 1448260 | 652.976 | 0 | 0 | 0 | 3044.36 | 1445220 | 660 | 1422570 | 1394119.375
3976 | 2001-06-15 15:00 | 669 | 884 | 87 | 32.8 | 4.29 | 0 | 41.1738 | 272.11 | 54.2006 | 0 | 669 | 517.116 | 89.0495 | 6.268 | 517.116 | 83.3359 | 0.032717 | 498.77 | 80.2517 | 0.024653 | 561.675 | 561.668 | 1261360 | 46.0636 | 1229550 | 1116100 | 1089450 | 0 | 0 | 1078750 | 657.165 | 0 | 0 | 0 | 228.56 | 1078520 | 660.361 | 1063970 | 1042693.0625
3977 | 2001-06-15 16:00 | 463 | 806 | 73 | 33.05 | 4.29 | 0 | 28.8981 | 279.753 | 67.9571 | 0 | 463 | 302.879 | 71.6999 | 4.338 | 302.879 | 67.0995 | 0.022643 | 277.671 | 64.6162 | 0.017062 | 332.035 | 332.034 | 745665 | 40.8909 | 703035 | 652014 | 636654 | 0 | 0 | 632950 | 655.31 | 0 | 0 | 0 | 470.137 | 632480 | 660 | 624258 | 611772.375
3978 | 2001-06-15 17:00 | 244 | 618 | 64 | 32.66 | 4.29 | 0 | 16.891 | 287.079 | 81.6878 | 0 | 244 | 89.5605 | 55.3168 | 2.2861 | 89.5605 | 51.7676 | 0.011933 | 63.063 | 49.8517 | 0.0089915 | 109.536 | 109.532 | 245982 | 35.2466 | 213228 | 202217 | 197576 | 0 | 0 | 197181 | 625.523 | 0 | 0 | 0 | 8189.3 | 188992 | 660 | 183954 | 180274.5312
3979 | 2001-06-15 18:00 | 54 | 412 | 14 | 32.28 | 6.07 | 0 | 5.3576 | 294.749 | 90 | 0 | 54 | 0 | 11.9518 | 0.50594 | 0 | 11.185 | 0.0026408 | 0 | 10.771 | 0.0019899 | 10.4498 | 10.4494 | 23466.8 | 32.4998 | 14098.2 | 13538.2 | 13287.8 | 0 | 0 | 13285.1 | 507.561 | 0 | 0 | 0 | 13285.1 | 0 | 660 | 0 | 0
3980 | 2001-06-15 19:00 | 0 | 4 | 0 | 31.89 | 6.07 | 0
3981 | 2001-06-15 20:00 | 0 | 0 | 0 | 30.79 | 6.07 | 0
3982 | 2001-06-15 21:00 | 0 | 0 | 0 | 29.68 | 6.25 | 0
3983 | 2001-06-15 22:00 | 0 | 0 | 0 | 28.58 | 6.25 | 0
3984 | 2001-06-15 23:00 | 0 | 0 | 0 | 27.69 | 6.25 | 0
3985 | 2001-06-16 | 0 | 0 | 0 | 26.8 | 6.16 | 0
3986 | 2001-06-16 01:00 | 0 | 0 | 0 | 25.91 | 6.16 | 0
3987 | 2001-06-16 02:00 | 0 | 0 | 0 | 25.32 | 6.16 | 0
3988 | 2001-06-16 03:00 | 0 | 0 | 0 | 24.73 | 3.68 | 0
3989 | 2001-06-16 04:00 | 4 | 55 | 2 | 24.14 | 3.68 | 0 | -1.9512 | 59.6607 | 90 | 0 | 4 | 0 | 1.4255 | 0.037477 | 0 | 1.334 | 0 | 0 | 1.2847 | 0 | 1.2461 | 1.2461 | 2798.31 | 24.1706 | 378.632 | 378.272 | 376.533 | 0 | 0 | 376.517 | 184.66 | 0 | 0 | 0 | 376.517 | 0 | 660 | 0 | 0
3990 | 2001-06-16 05:00 | 109 | 311 | 59 | 24.49 | 3.68 | 0 | 9.1273 | 67.8545 | 90 | 0 | 109 | 0 | 44.3953 | 1.0212 | 0 | 41.5468 | 0.0053305 | 0 | 40.0092 | 0.0040167 | 38.8128 | 38.8106 | 87159.2 | 25.444 | 67608.2 | 67444.3 | 65808.6 | 0 | 0 | 65762.6 | 610.578 | 0 | 0 | 0 | 6195.56 | 59567 | 660 | 57516.4 | 56366.1211
3991 | 2001-06-16 06:00 | 325 | 652 | 92 | 24.83 | 2.07 | 0 | 20.8434 | 75.345 | 77.1409 | 0 | 325 | 145.736 | 83.4073 | 3.045 | 145.102 | 78.0557 | 0.015894 | 119.758 | 75.1669 | 0.011976 | 189.089 | 189.076 | 424615 | 30.0011 | 384829 | 375620 | 363507 | 0 | 0 | 362330 | 665.5 | 0 | 0 | 0 | 68.7402 | 362261 | 666.75 | 356182 | 349058.0938
3992 | 2001-06-16 07:00 | 535 | 838 | 79 | 25.17 | 2.07 | 0 | 32.9618 | 82.6843 | 63.3877 | 0 | 535 | 375.434 | 79.788 | 5.0125 | 375.434 | 74.6686 | 0.026164 | 352.3 | 71.9052 | 0.019715 | 411.498 | 411.496 | 924112 | 36.4241 | 883509 | 838440 | 817078 | 0 | 0 | 811378 | 677.383 | 0 | 0 | 0 | 0 | 811378 | 677.383 | 800125 | 784122.6875
3993 | 2001-06-16 08:00 | 716 | 873 | 95 | 27.11 | 2.07 | 0 | 45.2833 | 90.6342 | 49.661 | 0 | 716 | 565.693 | 97.2989 | 6.7084 | 565.693 | 91.056 | 0.035015 | 550.282 | 87.6861 | 0.026385 | 618.855 | 618.851 | 1389780 | 44.0352 | 1362630 | 1250050 | 1219830 | 0 | 0 | 1206880 | 668.379 | 0 | 0 | 0 | 0 | 1206880 | 668.379 | 1189290 | 1165506.375
3994 | 2001-06-16 09:00 | 865 | 893 | 111 | 29.04 | 2.66 | 0 | 57.5667 | 100.706 | 36.1919 | 0 | 865 | 720.971 | 113.542 | 8.1044 | 720.971 | 106.257 | 0.042302 | 712.352 | 102.324 | 0.031876 | 790.267 | 790.263 | 1774720 | 49.8203 | 1764510 | 1577130 | 1540690 | 0 | 0 | 1519270 | 654.323 | 0 | 0 | 0 | 1117.86 | 1518150 | 660 | 1493590 | 1463715.25
3995 | 2001-06-16 10:00 | 979 | 923 | 116 | 30.98 | 2.66 | 0 | 69.2696 | 117.314 | 23.6126 | 0 | 979 | 845.485 | 118.06 | 9.1725 | 845.485 | 110.485 | 0.047877 | 841.622 | 106.396 | 0.036076 | 919.612 | 919.603 | 2065200 | 55.1613 | 2069740 | 1804440 | 1764660 | 0 | 0 | 1735420 | 639.483 | 0 | 0 | 0 | 18991.6 | 1716420 | 660 | 1685250 | 1651540.875
3996 | 2001-06-16 11:00 | 1038 | 949 | 112 | 31.74 | 2.66 | 0 | 77.9866 | 157.216 | 14.634 | 0 | 1038 | 916.022 | 113.406 | 9.7253 | 916.022 | 106.13 | 0.050763 | 914.486 | 102.202 | 0.038251 | 986.224 | 986.226 | 2214810 | 57.6732 | 2227360 | 1918950 | 1874590 | 0 | 0 | 1841160 | 634.641 | 0 | 0 | 0 | 35395.9 | 1805770 | 660 | 1771350 | 1735926.875
3997 | 2001-06-16 12:00 | 1019 | 930 | 119 | 32.51 | 4.54 | 0 | 75.8423 | 220.481 | 16.7831 | 0 | 1019 | 888.656 | 120.36 | 9.5472 | 888.656 | 112.638 | 0.049833 | 886.679 | 108.469 | 0.037551 | 965.33 | 965.322 | 2167870 | 54.9362 | 2177880 | 1901880 | 1862990 | 0 | 0 | 1830610 | 640.944 | 0 | 0 | 0 | 17639 | 1812970 | 660 | 1778290 | 1742721.5
3998 | 2001-06-16 13:00 | 966 | 950 | 101 | 33.27 | 4.54 | 0 | 65.5632 | 249.445 | 27.5628 | 0 | 966 | 842.279 | 103.705 | 9.0507 | 842.279 | 97.0512 | 0.047241 | 836.887 | 93.4594 | 0.035597 | 902.471 | 902.463 | 2026710 | 54.2358 | 2029230 | 1777010 | 1737870 | 0 | 0 | 1709740 | 642.254 | 0 | 0 | 0 | 14047.7 | 1695690 | 660 | 1665240 | 1631936
3999 | 2001-06-16 14:00 | 840 | 880 | 132 | 33.64 | 4.54 | 0 | 53.563 | 263.008 | 40.5631 | 0 | 840 | 668.557 | 133.353 | 7.8701 | 668.557 | 124.797 | 0.041079 | 657.983 | 120.178 | 0.030954 | 754.846 | 754.839 | 1695170 | 51.1763 | 1681170 | 1492060 | 1456730 | 0 | 0 | 1437320 | 649.825 | 0 | 0 | 0 | 4582.58 | 1432740 | 660 | 1410390 | 1382183.125
4000 | 2001-06-16 15:00 | 638 | 745 | 147 | 34 | 4.86 | 0 | 41.2328 | 272.121 | 54.1543 | 0 | 638 | 436.236 | 146.917 | 5.9776 | 436.236 | 137.491 | 0.031201 | 420.801 | 132.402 | 0.023511 | 536.63 | 536.622 | 1205120 | 46.2092 | 1171460 | 1062210 | 1037530 | 0 | 0 | 1027740 | 654.943 | 0 | 0 | 0 | 796.334 | 1026950 | 660 | 1013430 | 993161.9375
4001 | 2001-06-16 16:00 | 468 | 783 | 88 | 34.36 | 4.86 | 0 | 28.9573 | 279.76 | 67.907 | 0 | 468 | 295.198 | 86.0367 | 4.3848 | 295.198 | 80.5165 | 0.022887 | 270.714 | 77.5366 | 0.017246 | 337.82 | 337.816 | 758650 | 42.046 | 716093 | 660385 | 645865 | 0 | 0 | 642004 | 651.119 | 0 | 0 | 0 | 1585.87 | 640418 | 660 | 632092 | 619450.6875
4002 | 2001-06-16 17:00 | 242 | 601 | 66 | 33.95 | 4.86 | 0 | 16.9503 | 287.082 | 81.6348 | 0 | 242 | 87.8259 | 57.1347 | 2.2673 | 87.8259 | 53.4688 | 0.011835 | 62.0329 | 51.49 | 0.0089178 | 110.126 | 110.124 | 247311 | 36.4556 | 214482 | 202094 | 197545 | 0 | 0 | 197146 | 621.61 | 0 | 0 | 0 | 10537.8 | 186608 | 660 | 181607 | 177974.4375
4003 | 2001-06-16 18:00 | 54 | 401 | 15 | 33.53 | 6.87 | 0 | 5.4167 | 294.747 | 90 | 0 | 54 | 0 | 12.7744 | 0.50594 | 0 | 11.9548 | 0.0026408 | 0 | 11.5123 | 0.0019899 | 11.1689 | 11.1682 | 25080.9 | 33.7532 | 15355.9 | 14634.4 | 14352.6 | 0 | 0 | 14349.5 | 507.444 | 0 | 0 | 0 | 14349.5 | 0 | 660 | 0 | 0
4004 | 2001-06-16 19:00 | 0 | 5 | 0 | 33.12 | 6.87 | 0
4005 | 2001-06-16 20:00 | 0 | 0 | 0 | 32 | 6.87 | 0
4006 | 2001-06-16 21:00 | 0 | 0 | 0 | 30.88 | 6.22 | 0
4007 | 2001-06-16 22:00 | 0 | 0 | 0 | 29.76 | 6.22 | 0
4008 | 2001-06-16 23:00 | 0 | 0 | 0 | 28.75 | 6.22 | 0
4009 | 2001-06-17 | 0 | 0 | 0 | 27.75 | 5.86 | 0
4010 | 2001-06-17 01:00 | 0 | 0 | 0 | 26.74 | 5.86 | 0
4011 | 2001-06-17 02:00 | 0 | 0 | 0 | 26.32 | 5.86 | 0
4012 | 2001-06-17 03:00 | 0 | 0 | 0 | 25.9 | 4.99 | 0
4013 | 2001-06-17 04:00 | 4 | 81 | 1 | 25.48 | 4.99 | 0 | -1.9709 | 59.6064 | 90 | 0 | 4 | 0 | 0.91771 | 0.037477 | 0 | 0.85883 | 0 | 0 | 0.82704 | 0 | 0.80223 | 0.80219 | 1801.52 | 25.4981 | 157.277 | 157.369 | 156.625 | 0 | 0 | 156.619 | 120.098 | 0 | 0 | 0 | 156.619 | 0 | 660 | 0 | 0
4014 | 2001-06-17 05:00 | 119 | 458 | 45 | 25.72 | 4.99 | 0 | 9.1024 | 67.8019 | 90 | 0 | 119 | 0 | 34.0121 | 1.1149 | 0 | 31.8298 | 0.0058196 | 0 | 30.6518 | 0.0043852 | 29.7365 | 29.7354 | 66778.3 | 26.3908 | 49897.7 | 49517.2 | 48374.4 | 0 | 0 | 48347.9 | 591.761 | 0 | 0 | 0 | 9429.33 | 38918.5 | 660 | 37530.5 | 36779.9375
4015 | 2001-06-17 06:00 | 327 | 700 | 78 | 25.96 | 3.17 | 0 | 20.8148 | 75.2917 | 77.1878 | 0 | 327 | 155.389 | 70.542 | 3.0637 | 154.706 | 66.0159 | 0.015992 | 127.559 | 63.5727 | 0.01205 | 185.409 | 185.4 | 416360 | 30.6731 | 376793 | 366546 | 354963 | 0 | 0 | 353831 | 662.411 | 0 | 0 | 0 | 157.691 | 353673 | 664.268 | 347623 | 340670.5
4016 | 2001-06-17 07:00 | 527 | 820 | 81 | 26.2 | 3.17 | 0 | 32.9307 | 82.6269 | 63.4378 | 0 | 527 | 366.867 | 80.8494 | 4.9376 | 366.867 | 75.662 | 0.025773 | 344.19 | 72.8618 | 0.01942 | 404.559 | 404.554 | 908524 | 36.4842 | 867662 | 823108 | 803156 | 0 | 0 | 797650 | 677.443 | 0 | 0 | 0 | 0 | 797650 | 677.443 | 786584 | 770852.6875
4017 | 2001-06-17 08:00 | 720 | 882 | 93 | 28.14 | 3.17 | 0 | 45.2513 | 90.5668 | 49.714 | 0 | 720 | 570.853 | 95.3446 | 6.7458 | 570.853 | 89.2271 | 0.035211 | 555.254 | 85.9249 | 0.026532 | 621.969 | 621.964 | 1396780 | 43.951 | 1369890 | 1257290 | 1228170 | 0 | 0 | 1215040 | 668.335 | 0 | 0 | 0 | 0 | 1215040 | 668.335 | 1197280 | 1173331.5
4018 | 2001-06-17 09:00 | 876 | 916 | 103 | 30.07 | 5.06 | 0 | 57.5362 | 100.616 | 36.2475 | 0 | 876 | 738.863 | 105.773 | 8.2074 | 738.863 | 98.9863 | 0.04284 | 729.998 | 95.3228 | 0.032281 | 800.593 | 800.587 | 1797920 | 48.0495 | 1788830 | 1612900 | 1575440 | 0 | 0 | 1553530 | 661.044 | 0 | 0 | 0 | -34.4413 | 1553570 | 661.446 | 1527830 | 1497269.875
4019 | 2001-06-17 10:00 | 957 | 871 | 143 | 32.01 | 5.06 | 0 | 69.2467 | 117.167 | 23.6695 | 0 | 957 | 797.253 | 143.679 | 8.9663 | 797.253 | 134.461 | 0.046801 | 793.592 | 129.484 | 0.035266 | 895.418 | 895.413 | 2010870 | 52.1191 | 2012570 | 1780810 | 1739920 | 0 | 0 | 1712400 | 650.293 | 0 | 0 | 0 | 4259.79 | 1708140 | 660 | 1677250 | 1643709.75
4020 | 2001-06-17 11:00 | 1017 | 905 | 133 | 32.76 | 5.06 | 0 | 77.995 | 156.946 | 14.677 | 0 | 1017 | 874.276 | 133.369 | 9.5285 | 874.276 | 124.812 | 0.049736 | 872.801 | 120.192 | 0.037477 | 963.24 | 963.235 | 2163180 | 54.3923 | 2172940 | 1902640 | 1859720 | 0 | 0 | 1827640 | 643.164 | 0 | 0 | 0 | 12465.3 | 1815170 | 660 | 1780410 | 1744799.875
4021 | 2001-06-17 12:00 | 995 | 846 | 176 | 33.51 | 6.98 | 0 | 75.8934 | 220.38 | 16.7758 | 0 | 995 | 808.526 | 182.812 | 9.3224 | 808.526 | 171.083 | 0.04866 | 806.729 | 164.751 | 0.036666 | 942.372 | 942.357 | 2116290 | 52.2143 | 2123550 | 1879070 | 1834980 | 0 | 0 | 1804680 | 652.738 | 0 | 0 | 0 | 3462.35 | 1801220 | 660 | 1766970 | 1731633.875
4022 | 2001-06-17 13:00 | 960 | 940 | 104 | 34.26 | 6.98 | 0 | 65.6196 | 249.435 | 27.5299 | 0 | 960 | 833.393 | 106.616 | 8.9945 | 833.393 | 99.7756 | 0.046948 | 828.072 | 96.083 | 0.035376 | 896.464 | 896.463 | 2013230 | 52.0533 | 2015040 | 1783650 | 1742630 | 0 | 0 | 1715130 | 651.165 | 0 | 0 | 0 | 4123.16 | 1711000 | 660 | 1680020 | 1646415.625
4023 | 2001-06-17 14:00 | 835 | 917 | 97 | 34.62 | 6.98 | 0 | 53.6194 | 263.01 | 40.5208 | 0 | 835 | 696.82 | 99.8265 | 7.8233 | 696.82 | 93.4214 | 0.040835 | 685.828 | 89.9639 | 0.03077 | 752.548 | 752.541 | 1690020 | 49.5567 | 1675770 | 1499180 | 1464400 | 0 | 0 | 1445080 | 655.518 | 0 | 0 | 0 | 1287.1 | 1443790 | 660.003 | 1421180 | 1392757
4024 | 2001-06-17 15:00 | 669 | 885 | 85 | 34.98 | 9.64 | 0 | 41.2891 | 272.123 | 54.1071 | 0 | 669 | 518.873 | 87.0985 | 6.268 | 518.873 | 81.5101 | 0.032717 | 500.565 | 78.4935 | 0.024653 | 561.71 | 561.707 | 1261450 | 44.4174 | 1229640 | 1125260 | 1100080 | 0 | 0 | 1089340 | 662.669 | 0 | 0 | 0 | -22.8073 | 1089360 | 662.94 | 1074470 | 1052977
4025 | 2001-06-17 16:00 | 469 | 816 | 73 | 35.33 | 9.64 | 0 | 29.0134 | 279.76 | 67.8568 | 0 | 469 | 307.746 | 71.7069 | 4.3942 | 307.746 | 67.106 | 0.022936 | 282.31 | 64.6225 | 0.017283 | 336.542 | 336.537 | 755778 | 40.9842 | 713204 | 661224 | 646362 | 0 | 0 | 642534 | 654.742 | 0 | 0 | 0 | 571.232 | 641963 | 660 | 633617 | 620944.75
4026 | 2001-06-17 17:00 | 246 | 625 | 62 | 34.43 | 9.64 | 0 | 17.0062 | 287.078 | 81.5823 | 0 | 246 | 92.0947 | 53.5554 | 2.3048 | 92.0947 | 50.1192 | 0.01203 | 65.2438 | 48.2643 | 0.0090652 | 110.112 | 110.109 | 247278 | 36.28 | 214450 | 202256 | 197639 | 0 | 0 | 197240 | 622.238 | 0 | 0 | 0 | 10126.1 | 187114 | 660 | 182104 | 178462.0781
4027 | 2001-06-17 18:00 | 55 | 417 | 14 | 33.53 | 7.86 | 0 | 5.472 | 294.739 | 90 | 0 | 55 | 0 | 11.949 | 0.51531 | 0 | 11.1823 | 0.0026897 | 0 | 10.7685 | 0.0020268 | 10.4474 | 10.4464 | 23459.8 | 33.7261 | 14092.7 | 13439.1 | 13180.1 | 0 | 0 | 13177.4 | 503.16 | 0 | 0 | 0 | 13177.4 | 0 | 660 | 0 | 0
4028 | 2001-06-17 19:00 | 0 | 6 | 0 | 32.62 | 7.86 | 0
4029 | 2001-06-17 20:00 | 0 | 0 | 0 | 31.67 | 7.86 | 0
4030 | 2001-06-17 21:00 | 0 | 0 | 0 | 30.72 | 9.32 | 0
4031 | 2001-06-17 22:00 | 0 | 0 | 0 | 29.78 | 9.32 | 0
4032 | 2001-06-17 23:00 | 0 | 0 | 0 | 28.75 | 9.32 | 0
4033 | 2001-06-18 | 0 | 0 | 0 | 27.72 | 6.98 | 0
4034 | 2001-06-18 01:00 | 0 | 0 | 0 | 26.7 | 6.98 | 0
4035 | 2001-06-18 02:00 | 0 | 0 | 0 | 26.48 | 6.98 | 0
4036 | 2001-06-18 03:00 | 0 | 0 | 0 | 26.27 | 6.73 | 0
4037 | 2001-06-18 04:00 | 4 | 82 | 1 | 26.05 | 6.73 | 0 | -1.9951 | 59.5572 | 90 | 0 | 4 | 0 | 0.91785 | 0.037477 | 0 | 0.85896 | 0 | 0 | 0.82717 | 0 | 0.80236 | 0.80233 | 1801.83 | 26.0662 | 157.342 | 157.539 | 156.783 | 0 | 0 | 156.776 | 120.172 | 0 | 0 | 0 | 156.776 | 0 | 660 | 0 | 0
4038 | 2001-06-18 05:00 | 120 | 464 | 46 | 26.56 | 6.73 | 0 | 9.0734 | 67.755 | 90 | 0 | 120 | 0 | 34.9784 | 1.1243 | 0 | 32.7341 | 0.0058685 | 0 | 31.5227 | 0.004422 | 30.5813 | 30.58 | 68674.6 | 27.1767 | 51529.3 | 50915.2 | 49721 | 0 | 0 | 49693 | 592.043 | 0 | 0 | 0 | 10222.1 | 39470.9 | 660 | 38064.6 | 37303.2578
4039 | 2001-06-18 06:00 | 314 | 669 | 76 | 27.06 | 4.32 | 0 | 20.7825 | 75.2447 | 77.2356 | 0 | 314 | 148.2 | 68.677 | 2.9419 | 147.541 | 64.2706 | 0.015356 | 121.529 | 61.892 | 0.011571 | 177.93 | 177.923 | 399567 | 31.2533 | 360465 | 349619 | 338392 | 0 | 0 | 337350 | 658.59 | 0 | 0 | 0 | 285.797 | 337065 | 661.363 | 331038 | 324417.5
4040 | 2001-06-18 07:00 | 527 | 821 | 81 | 27.57 | 4.32 | 0 | 32.8963 | 82.5767 | 63.4879 | 0 | 527 | 366.565 | 80.8231 | 4.9376 | 366.565 | 75.6374 | 0.025773 | 343.834 | 72.8381 | 0.01942 | 404.191 | 404.184 | 907696 | 37.096 | 866821 | 819927 | 800193 | 0 | 0 | 794694 | 675.686 | 0 | 0 | 0 | 0 | 794694 | 675.686 | 783740 | 768065.25
4041 | 2001-06-18 08:00 | 729 | 902 | 89 | 29.22 | 4.32 | 0 | 45.216 | 90.5082 | 49.7662 | 0 | 729 | 582.418 | 91.4443 | 6.8302 | 582.418 | 85.5771 | 0.035651 | 566.454 | 82.4099 | 0.026864 | 629.424 | 629.425 | 1413520 | 44.0545 | 1387300 | 1272750 | 1240970 | 0 | 0 | 1227530 | 667.492 | 0 | 0 | 0 | 0 | 1227530 | 667.492 | 1209540 | 1185345.75
4042 | 2001-06-18 09:00 | 887 | 935 | 99 | 30.87 | 7.74 | 0 | 57.5022 | 100.537 | 36.3014 | 0 | 887 | 752.966 | 101.86 | 8.3105 | 752.966 | 95.3247 | 0.043378 | 743.899 | 91.7968 | 0.032686 | 810.657 | 810.65 | 1820510 | 46.2034 | 1812530 | 1649010 | 1613270 | 0 | 0 | 1590580 | 665.583 | 0 | 0 | 0 | 0 | 1590580 | 665.583 | 1563510 | 1532241.625
4043 | 2001-06-18 10:00 | 996 | 954 | 105 | 32.52 | 7.74 | 0 | 69.2195 | 117.035 | 23.7228 | 0 | 996 | 872.47 | 107.392 | 9.3317 | 872.47 | 100.501 | 0.048709 | 868.444 | 96.7817 | 0.036703 | 936.304 | 936.297 | 2102690 | 50.2299 | 2109220 | 1884400 | 1841600 | 0 | 0 | 1811380 | 656.597 | 0 | 0 | 0 | 247.223 | 1811130 | 660.084 | 1776510 | 1740983.125
4044 | 2001-06-18 11:00 | 1048 | 962 | 109 | 32.89 | 7.74 | 0 | 77.9967 | 156.687 | 14.7137 | 0 | 1048 | 928.509 | 110.489 | 9.8189 | 928.509 | 103.4 | 0.051252 | 926.935 | 99.5731 | 0.038619 | 995.75 | 995.744 | 2236180 | 51.7244 | 2249900 | 1996660 | 1949120 | 0 | 0 | 1915150 | 654.175 | 0 | 0 | 0 | 1168.62 | 1913980 | 660 | 1875430 | 1837921.625
4045 | 2001-06-18 12:00 | 1038 | 960 | 108 | 33.26 | 7.79 | 0 | 75.939 | 220.262 | 16.7631 | 0 | 1038 | 917.985 | 109.746 | 9.7253 | 917.985 | 102.705 | 0.050763 | 915.948 | 98.9036 | 0.038251 | 984.443 | 984.437 | 2210800 | 51.8219 | 2223130 | 1971780 | 1926600 | 0 | 0 | 1893320 | 654.289 | 0 | 0 | 0 | 2118.02 | 1891200 | 660 | 1853540 | 1816468.25
4046 | 2001-06-18 13:00 | 967 | 950 | 102 | 33.63 | 7.79 | 0 | 65.6724 | 249.41 | 27.494 | 0 | 967 | 842.079 | 104.653 | 9.06 | 842.079 | 97.9379 | 0.04729 | 836.718 | 94.3132 | 0.035634 | 903.135 | 903.13 | 2028200 | 50.6588 | 2030800 | 1810020 | 1770530 | 0 | 0 | 1742300 | 653.328 | 0 | 0 | 0 | 1108.33 | 1741190 | 660 | 1709130 | 1674950.625
4047 | 2001-06-18 14:00 | 841 | 926 | 95 | 33.87 | 7.79 | 0 | 53.6728 | 263.001 | 40.4767 | 0 | 841 | 704.352 | 97.8631 | 7.8795 | 704.352 | 91.584 | 0.041128 | 693.272 | 88.1945 | 0.030991 | 758.052 | 758.05 | 1702390 | 48.1633 | 1688720 | 1521170 | 1486000 | 0 | 0 | 1466380 | 659.79 | 0 | 0 | 0 | 72.4397 | 1466310 | 661.218 | 1443100 | 1414235.125
4048 | 2001-06-18 15:00 | 670 | 885 | 85 | 34.1 | 10.91 | 0 | 41.3425 | 272.117 | 54.0592 | 0 | 670 | 519.811 | 87.0962 | 6.2774 | 519.811 | 81.5079 | 0.032766 | 501.52 | 78.4914 | 0.02469 | 562.635 | 562.631 | 1263520 | 42.8474 | 1231780 | 1135820 | 1108480 | 0 | 0 | 1097710 | 666.778 | 0 | 0 | 0 | 0 | 1097710 | 666.778 | 1082460 | 1060810.25
4049 | 2001-06-18 16:00 | 470 | 816 | 73 | 34.34 | 10.91 | 0 | 29.0665 | 279.752 | 67.8065 | 0 | 470 | 308.673 | 71.7149 | 4.4035 | 308.673 | 67.1136 | 0.022985 | 283.248 | 64.6297 | 0.01732 | 337.458 | 337.454 | 757832 | 39.5865 | 715271 | 667771 | 652260 | 0 | 0 | 648418 | 659.854 | 0 | 0 | 0 | -7.5879 | 648425 | 660.96 | 639965 | 627165.5
4050 | 2001-06-18 17:00 | 247 | 628 | 62 | 33.78 | 10.91 | 0 | 17.0588 | 287.068 | 81.5305 | 0 | 247 | 92.8823 | 53.5773 | 2.3142 | 92.8823 | 50.1397 | 0.012079 | 65.9944 | 48.284 | 0.009102 | 110.859 | 110.857 | 248957 | 35.5035 | 216035 | 204613 | 199843 | 0 | 0 | 199440 | 626.177 | 0 | 0 | 0 | 8401.51 | 191039 | 660 | 185969 | 182249.7969
4051 | 2001-06-18 18:00 | 56 | 419 | 14 | 33.22 | 7.76 | 0 | 5.5235 | 294.725 | 90 | 0 | 56 | 0 | 11.9477 | 0.52468 | 0 | 11.1811 | 0.0027386 | 0 | 10.7673 | 0.0020636 | 10.4463 | 10.4461 | 23459.4 | 33.4173 | 14092.6 | 13462.8 | 13205.5 | 0 | 0 | 13202.8 | 504.312 | 0 | 0 | 0 | 13202.8 | 0 | 660 | 0 | 0
4052 | 2001-06-18 19:00 | 0 | 7 | 0 | 32.66 | 7.76 | 0
4053 | 2001-06-18 20:00 | 0 | 0 | 0 | 31.62 | 7.76 | 0
4054 | 2001-06-18 21:00 | 0 | 0 | 0 | 30.57 | 11.22 | 0
4055 | 2001-06-18 22:00 | 0 | 0 | 0 | 29.53 | 11.22 | 0
4056 | 2001-06-18 23:00 | 0 | 0 | 0 | 28.62 | 11.22 | 0
4057 | 2001-06-19 | 0 | 0 | 0 | 27.71 | 7.72 | 0
4058 | 2001-06-19 01:00 | 0 | 0 | 0 | 26.8 | 7.72 | 0
4059 | 2001-06-19 02:00 | 0 | 0 | 0 | 26.16 | 7.72 | 0
4060 | 2001-06-19 03:00 | 0 | 0 | 0 | 25.52 | 8.22 | 0
4061 | 2001-06-19 04:00 | 4 | 62 | 2 | 24.87 | 8.22 | 0 | -2.0237 | 59.5133 | 90 | 0 | 4 | 0 | 1.4266 | 0.037477 | 0 | 1.3351 | 0 | 0 | 1.2857 | 0 | 1.2471 | 1.247 | 2800.51 | 24.8929 | 379.228 | 379.179 | 377.439 | 0 | 0 | 377.422 | 184.875 | 0 | 0 | 0 | 377.422 | 0 | 660 | 0 | 0
4062 | 2001-06-19 05:00 | 106 | 355 | 49 | 25.47 | 8.22 | 0 | 9.0406 | 67.7138 | 90 | 0 | 106 | 0 | 37.8671 | 0.99314 | 0 | 35.4375 | 0.0051838 | 0 | 34.126 | 0.0039061 | 33.106 | 33.1048 | 74345 | 26.0775 | 56428.8 | 56096.7 | 54799.9 | 0 | 0 | 54766.8 | 600.34 | 0 | 0 | 0 | 8210.58 | 46556.2 | 660 | 44917.2 | 44018.8359
4063 | 2001-06-19 06:00 | 313 | 668 | 76 | 26.06 | 5.06 | 0 | 20.7467 | 75.204 | 77.284 | 0 | 313 | 147.269 | 68.6429 | 2.9326 | 146.6 | 64.2387 | 0.015307 | 120.63 | 61.8613 | 0.011534 | 177.028 | 177.022 | 397545 | 30.0355 | 358503 | 349816 | 338400 | 0 | 0 | 337373 | 663.359 | 0 | 0 | 0 | 116.777 | 337257 | 665.207 | 331129 | 324506.4688
4064 | 2001-06-19 07:00 | 519 | 798 | 86 | 26.65 | 5.06 | 0 | 32.8586 | 82.5338 | 63.5381 | 0 | 519 | 355.617 | 85.6293 | 4.8626 | 355.617 | 80.1352 | 0.025381 | 333.495 | 77.1695 | 0.019125 | 398.363 | 398.359 | 894610 | 35.5963 | 853530 | 813074 | 792914 | 0 | 0 | 787590 | 680.568 | 0 | 0 | 0 | 0 | 787590 | 680.568 | 776541 | 761010.0625
4065 | 2001-06-19 08:00 | 699 | 831 | 109 | 28.29 | 5.06 | 0 | 45.1776 | 90.4583 | 49.8176 | 0 | 699 | 536.704 | 111.942 | 6.5491 | 536.704 | 104.76 | 0.034184 | 521.948 | 100.883 | 0.025758 | 604.171 | 604.17 | 1356820 | 41.8584 | 1328410 | 1231240 | 1200120 | 0 | 0 | 1187780 | 673.49 | 0 | 0 | 0 | 0 | 1187780 | 673.49 | 1170350 | 1146942.75
4066 | 2001-06-19 09:00 | 859 | 880 | 117 | 29.93 | 7 | 0 | 57.4648 | 100.47 | 36.3533 | 0 | 859 | 708.833 | 119.272 | 8.0482 | 708.833 | 111.619 | 0.042009 | 700.268 | 107.488 | 0.031654 | 783.554 | 783.549 | 1759660 | 45.4624 | 1748710 | 1596140 | 1556860 | 0 | 0 | 1535920 | 668.787 | 0 | 0 | 0 | 0 | 1535920 | 668.787 | 1510480 | 1480268.25
4067 | 2001-06-19 10:00 | 979 | 926 | 114 | 31.57 | 7 | 0 | 69.188 | 116.919 | 23.7725 | 0 | 979 | 846.865 | 116.101 | 9.1725 | 846.865 | 108.651 | 0.047877 | 842.939 | 104.63 | 0.036076 | 919.177 | 919.168 | 2064220 | 49.7908 | 2068710 | 1851820 | 1809640 | 0 | 0 | 1780700 | 659.254 | 0 | 0 | 0 | 90.8135 | 1780610 | 660.629 | 1747110 | 1712165.125
4068 | 2001-06-19 11:00 | 1047 | 962 | 108 | 32.1 | 7 | 0 | 77.9918 | 156.439 | 14.744 | 0 | 1047 | 928.396 | 109.517 | 9.8096 | 928.396 | 102.49 | 0.051203 | 926.816 | 98.6973 | 0.038582 | 994.785 | 994.777 | 2234010 | 51.8196 | 2247600 | 1993680 | 1950470 | 0 | 0 | 1916250 | 652.915 | 0 | 0 | 0 | 2331.38 | 1913920 | 660 | 1875370 | 1837867.125
4069 | 2001-06-19 12:00 | 1038 | 960 | 108 | 32.63 | 6.8 | 0 | 75.9789 | 220.126 | 16.7449 | 0 | 1038 | 917.913 | 109.734 | 9.7253 | 917.913 | 102.693 | 0.050763 | 915.881 | 98.8927 | 0.038251 | 984.367 | 984.366 | 2210640 | 52.3935 | 2222970 | 1966110 | 1918590 | 0 | 0 | 1885460 | 652.68 | 0 | 0 | 0 | 2805.66 | 1882660 | 660 | 1845330 | 1808422
4070 | 2001-06-19 13:00 | 967 | 950 | 101 | 33.16 | 6.8 | 0 | 65.7215 | 249.371 | 27.455 | 0 | 967 | 843.024 | 103.667 | 9.06 | 843.024 | 97.0151 | 0.04729 | 837.674 | 93.4247 | 0.035634 | 903.201 | 903.197 | 2028340 | 51.2938 | 2030950 | 1804530 | 1763260 | 0 | 0 | 1735210 | 653.097 | 0 | 0 | 0 | 2029.02 | 1733180 | 660 | 1701410 | 1667383.625
4071 | 2001-06-19 14:00 | 841 | 926 | 94 | 33.76 | 6.8 | 0 | 53.7232 | 262.982 | 40.431 | 0 | 841 | 705.32 | 96.8789 | 7.8795 | 705.32 | 90.663 | 0.041128 | 694.256 | 87.3076 | 0.030991 | 758.147 | 758.146 | 1702610 | 48.9816 | 1688950 | 1515320 | 1480020 | 0 | 0 | 1460410 | 657 | 0 | 0 | 0 | 444.198 | 1459970 | 660 | 1436960 | 1408219.25
4072 | 2001-06-19 15:00 | 671 | 885 | 86 | 34.35 | 5.69 | 0 | 41.3929 | 272.103 | 54.0106 | 0 | 671 | 519.899 | 88.0663 | 6.2867 | 519.899 | 82.4158 | 0.032815 | 501.658 | 79.3656 | 0.024727 | 563.617 | 563.613 | 1265730 | 46.5015 | 1234060 | 1117850 | 1092170 | 0 | 0 | 1081330 | 655.201 | 0 | 0 | 0 | 639.29 | 1080690 | 660 | 1066110 | 1044791.75
4073 | 2001-06-19 16:00 | 469 | 811 | 74 | 34.95 | 5.69 | 0 | 29.1165 | 279.738 | 67.7563 | 0 | 469 | 307.295 | 72.6861 | 4.3942 | 307.295 | 68.0225 | 0.022936 | 282.071 | 65.505 | 0.017283 | 337.165 | 337.163 | 757184 | 42.2192 | 714619 | 658448 | 643678 | 0 | 0 | 639824 | 649.65 | 0 | 0 | 0 | 1685.8 | 638138 | 660 | 629842 | 617245.5
4074 | 2001-06-19 17:00 | 252 | 650 | 60 | 34.38 | 5.69 | 0 | 17.1078 | 287.052 | 81.4795 | 0 | 252 | 96.7037 | 51.8092 | 2.361 | 96.7037 | 48.485 | 0.012324 | 68.9048 | 46.6906 | 0.0092863 | 112.137 | 112.136 | 251828 | 36.7976 | 218747 | 205751 | 201051 | 0 | 0 | 200637 | 621.273 | 0 | 0 | 0 | 10905.2 | 189732 | 660 | 184682 | 180988.3906
4075 | 2001-06-19 18:00 | 57 | 433 | 13 | 33.82 | 6.67 | 0 | 5.5711 | 294.705 | 90 | 0 | 57 | 0 | 11.1181 | 0.53405 | 0 | 10.4048 | 0.0027875 | 0 | 10.0197 | 0.0021005 | 9.7211 | 9.7206 | 21830 | 34.0168 | 12833.4 | 12225.7 | 11995.2 | 0 | 0 | 11992.9 | 498.049 | 0 | 0 | 0 | 11992.9 | 0 | 660 | 0 | 0
4076 | 2001-06-19 19:00 | 0 | 8 | 0 | 33.26 | 6.67 | 0
4077 | 2001-06-19 20:00 | 0 | 0 | 0 | 32.32 | 6.67 | 0
4078 | 2001-06-19 21:00 | 0 | 0 | 0 | 31.38 | 7.35 | 0
4079 | 2001-06-19 22:00 | 0 | 0 | 0 | 30.44 | 7.35 | 0
4080 | 2001-06-19 23:00 | 0 | 0 | 0 | 29.54 | 7.35 | 0
4081 | 2001-06-20 | 0 | 0 | 0 | 28.64 | 6.54 | 0
4082 | 2001-06-20 01:00 | 0 | 0 | 0 | 27.74 | 6.54 | 0
4083 | 2001-06-20 02:00 | 0 | 0 | 0 | 27.12 | 6.54 | 0
4084 | 2001-06-20 03:00 | 0 | 0 | 0 | 26.5 | 6.87 | 0
4085 | 2001-06-20 04:00 | 4 | 81 | 1 | 25.89 | 6.87 | 0 | -2.0567 | 59.4748 | 90 | 0 | 4 | 0 | 0.91822 | 0.037477 | 0 | 0.85931 | 0 | 0 | 0.8275 | 0 | 0.80268 | 0.80267 | 1802.6 | 25.906 | 157.488 | 157.655 | 156.885 | 0 | 0 | 156.879 | 120.177 | 0 | 0 | 0 | 156.879 | 0 | 660 | 0 | 0
4086 | 2001-06-20 05:00 | 119 | 468 | 45 | 26.28 | 6.87 | 0 | 9.0039 | 67.6783 | 90 | 0 | 119 | 0 | 34.1255 | 1.1149 | 0 | 31.9359 | 0.0058196 | 0 | 30.754 | 0.0043852 | 29.8357 | 29.8341 | 67000.1 | 26.8763 | 50088.3 | 49573.1 | 48419.1 | 0 | 0 | 48392.5 | 591.584 | 0 | 0 | 0 | 10019.3 | 38373.2 | 660 | 37003.4 | 36263.3633
4087 | 2001-06-20 06:00 | 325 | 733 | 65 | 26.67 | 4.05 | 0 | 20.7074 | 75.1698 | 77.3331 | 0 | 325 | 161.24 | 60.5194 | 3.045 | 160.48 | 56.6364 | 0.015894 | 131.912 | 54.5403 | 0.011976 | 180.87 | 180.861 | 406166 | 31.0087 | 366883 | 356292 | 344687 | 0 | 0 | 343613 | 660.634 | 0 | 0 | 0 | 213.126 | 343400 | 662.913 | 337349 | 330602.4688
4088 | 2001-06-20 07:00 | 535 | 842 | 78 | 27.07 | 4.05 | 0 | 32.8178 | 82.4981 | 63.5882 | 0 | 535 | 375.082 | 78.7646 | 5.0125 | 375.082 | 73.7109 | 0.026164 | 351.675 | 70.9829 | 0.019715 | 409.998 | 409.992 | 920734 | 36.9053 | 880072 | 833271 | 814106 | 0 | 0 | 808420 | 675.801 | 0 | 0 | 0 | 0 | 808420 | 675.801 | 797272 | 781326.375
4089 | 2001-06-20 08:00 | 728 | 901 | 89 | 28.61 | 4.05 | 0 | 45.1362 | 90.4172 | 49.8682 | 0 | 728 | 581.088 | 91.4246 | 6.8208 | 581.088 | 85.5586 | 0.035602 | 565.065 | 82.3921 | 0.026827 | 628.059 | 628.058 | 1410460 | 43.6766 | 1384120 | 1272110 | 1239940 | 0 | 0 | 1226620 | 669.698 | 0 | 0 | 0 | 0 | 1226620 | 669.698 | 1208540 | 1184373.5
4090 | 2001-06-20 09:00 | 874 | 916 | 102 | 30.16 | 2.05 | 0 | 57.4242 | 100.414 | 36.4034 | 0 | 874 | 737.351 | 104.774 | 8.1887 | 737.351 | 98.0515 | 0.042742 | 728.412 | 94.4227 | 0.032207 | 798.181 | 798.178 | 1792500 | 52.0188 | 1783150 | 1576780 | 1541060 | 0 | 0 | 1519150 | 646.711 | 0 | 0 | 0 | 6758.23 | 1512390 | 660 | 1488000 | 1458241.25
4091 | 2001-06-20 10:00 | 995 | 954 | 104 | 31.71 | 2.05 | 0 | 69.1522 | 116.819 | 23.8186 | 0 | 995 | 872.217 | 106.41 | 9.3224 | 872.217 | 99.583 | 0.04866 | 868.157 | 95.8975 | 0.036666 | 935.168 | 935.164 | 2100140 | 57.3203 | 2106540 | 1817000 | 1776970 | 0 | 0 | 1746960 | 635.132 | 0 | 0 | 0 | 35425.1 | 1711530 | 660 | 1680530 | 1646918.625
4092 | 2001-06-20 11:00 | 1025 | 921 | 126 | 32.47 | 2.05 | 0 | 77.9802 | 156.203 | 14.7681 | 0 | 1025 | 888.788 | 126.727 | 9.6035 | 888.788 | 118.596 | 0.050127 | 887.27 | 114.207 | 0.037772 | 971.469 | 971.461 | 2181660 | 59.0743 | 2192420 | 1875120 | 1833410 | 0 | 0 | 1800890 | 629.182 | 0 | 0 | 0 | 51791.1 | 1749100 | 660 | 1716750 | 1682418.75
4093 | 2001-06-20 12:00 | 1029 | 947 | 111 | 33.24 | 3.44 | 0 | 76.0132 | 219.973 | 16.7212 | 0 | 1029 | 906.046 | 112.621 | 9.6409 | 906.046 | 105.395 | 0.050322 | 904.046 | 101.494 | 0.037919 | 975.411 | 975.405 | 2190510 | 57.5975 | 2201750 | 1897440 | 1855950 | 0 | 0 | 1823060 | 633.675 | 0 | 0 | 0 | 36517.2 | 1786540 | 660 | 1752840 | 1717783.5
4094 | 2001-06-20 13:00 | 967 | 950 | 101 | 34 | 3.44 | 0 | 65.7669 | 249.318 | 27.4129 | 0 | 967 | 843.044 | 103.661 | 9.06 | 843.044 | 97.0098 | 0.04729 | 837.712 | 93.4196 | 0.035634 | 903.232 | 903.23 | 2028430 | 56.5552 | 2031040 | 1758030 | 1717870 | 0 | 0 | 1689820 | 635.914 | 0 | 0 | 0 | 29204 | 1660610 | 660 | 1631380 | 1598749.375
4095 | 2001-06-20 14:00 | 842 | 926 | 95 | 34.62 | 3.44 | 0 | 53.7705 | 262.953 | 40.3838 | 0 | 842 | 705.389 | 97.8561 | 7.8889 | 705.389 | 91.5775 | 0.041177 | 694.356 | 88.1883 | 0.031028 | 759.098 | 759.095 | 1704740 | 53.5759 | 1691180 | 1483170 | 1448820 | 0 | 0 | 1429100 | 641.423 | 0 | 0 | 0 | 15143.9 | 1413950 | 660 | 1392060 | 1364220
4096 | 2001-06-20 15:00 | 672 | 795 | 146 | 35.23 | 4.99 | 0 | 41.4403 | 272.08 | 53.9613 | 0 | 672 | 467.579 | 145.999 | 6.2961 | 467.579 | 136.631 | 0.032864 | 451.221 | 131.575 | 0.024763 | 565.335 | 565.327 | 1269580 | 47.984 | 1238050 | 1113290 | 1088270 | 0 | 0 | 1077340 | 649.137 | 0 | 0 | 0 | 2863.56 | 1074470 | 659.999 | 1060020 | 1038823.0625
4097 | 2001-06-20 16:00 | 427 | 638 | 116 | 35.84 | 4.99 | 0 | 29.1632 | 279.717 | 67.7063 | 0 | 427 | 242.108 | 110.788 | 4.0007 | 242.108 | 103.68 | 0.020882 | 222.303 | 99.8425 | 0.015735 | 312.497 | 312.492 | 701777 | 42.8899 | 658994 | 604766 | 590948 | 0 | 0 | 587654 | 645.39 | 0 | 0 | 0 | 3912.51 | 583742 | 660 | 576105 | 564583.375
4098 | 2001-06-20 17:00 | 211 | 421 | 86 | 35.08 | 4.99 | 0 | 17.1534 | 287.03 | 81.4293 | 0 | 211 | 63.1634 | 73.9654 | 1.9769 | 63.1634 | 69.2197 | 0.010319 | 45.1302 | 66.6579 | 0.0077754 | 108.442 | 108.44 | 243528 | 37.5264 | 210915 | 197561 | 193080 | 0 | 0 | 192692 | 617.284 | 0 | 0 | 0 | 13196.8 | 179496 | 660 | 174608 | 171115.9688
4099 | 2001-06-20 18:00 | 48 | 281 | 19 | 34.33 | 6.43 | 0 | 5.6147 | 294.68 | 90 | 0 | 48 | 0 | 14.8395 | 0.44972 | 0 | 13.8874 | 0.0023474 | 0 | 13.3734 | 0.0017688 | 12.9739 | 12.973 | 29134.1 | 34.5967 | 18553.7 | 17579.8 | 17229.5 | 0 | 0 | 17225.1 | 516.349 | 0 | 0 | 0 | 17225.1 | 0 | 660 | 0 | 0
4100 | 2001-06-20 19:00 | 0 | 6 | 0 | 33.57 | 6.43 | 0
4101 | 2001-06-20 20:00 | 0 | 0 | 0 | 32.38 | 6.43 | 0
4102 | 2001-06-20 21:00 | 0 | 0 | 0 | 31.18 | 5.33 | 0
4103 | 2001-06-20 22:00 | 0 | 0 | 0 | 29.99 | 5.33 | 0
4104 | 2001-06-20 23:00 | 0 | 0 | 0 | 29.03 | 5.33 | 0
4105 | 2001-06-21 | 0 | 0 | 0 | 28.06 | 4.23 | 0
4106 | 2001-06-21 01:00 | 0 | 0 | 0 | 27.1 | 4.23 | 0
4107 | 2001-06-21 02:00 | 0 | 0 | 0 | 26.67 | 4.23 | 0
4108 | 2001-06-21 03:00 | 0 | 0 | 0 | 26.25 | 3.4 | 0
4109 | 2001-06-21 04:00 | 4 | 77 | 2 | 25.82 | 3.4 | 0 | -2.0941 | 59.4415 | 90 | 0 | 4 | 0 | 1.4277 | 0.037477 | 0 | 1.336 | 0 | 0 | 1.2866 | 0 | 1.248 | 1.248 | 2802.63 | 25.8512 | 379.848 | 380.213 | 378.419 | 0 | 0 | 378.403 | 185.132 | 0 | 0 | 0 | 378.403 | 0 | 660 | 0 | 0
4110 | 2001-06-21 05:00 | 115 | 447 | 44 | 26.03 | 3.4 | 0 | 8.9634 | 67.6487 | 90 | 0 | 115 | 0 | 33.2421 | 1.0775 | 0 | 31.1092 | 0.005624 | 0 | 29.9579 | 0.0042378 | 29.0633 | 29.063 | 65268.2 | 26.7577 | 48601.6 | 48133 | 47055.1 | 0 | 0 | 47029.9 | 590.206 | 0 | 0 | 0 | 10111.5 | 36918.4 | 660 | 35597.3 | 34885.3477
4111 | 2001-06-21 06:00 | 311 | 685 | 69 | 26.24 | 2.07 | 0 | 20.6648 | 75.1419 | 77.3827 | 0 | 311 | 149.793 | 62.1998 | 2.9138 | 149.044 | 58.2089 | 0.015209 | 122.38 | 56.0547 | 0.01146 | 173.093 | 173.086 | 388706 | 30.9738 | 349931 | 339843 | 328500 | 0 | 0 | 327516 | 657.585 | 0 | 0 | 0 | 326.723 | 327189 | 660.506 | 321168 | 314744.625
4112 | 2001-06-21 07:00 | 521 | 808 | 83 | 26.45 | 2.07 | 0 | 32.7739 | 82.4698 | 63.6381 | 0 | 521 | 359.284 | 82.6973 | 4.8814 | 359.284 | 77.3912 | 0.025479 | 336.792 | 74.527 | 0.019199 | 398.998 | 398.994 | 896041 | 37.3622 | 854982 | 807628 | 787934 | 0 | 0 | 782573 | 673.487 | 0 | 0 | 0 | 0 | 782573 | 673.487 | 771872 | 756434.4375
4113 | 2001-06-21 08:00 | 703 | 812 | 128 | 28.28 | 2.07 | 0 | 45.0917 | 90.3849 | 49.9178 | 0 | 703 | 522.754 | 130.366 | 6.5866 | 522.754 | 122.002 | 0.03438 | 508.298 | 117.487 | 0.025906 | 607.036 | 607.029 | 1363240 | 44.8818 | 1335070 | 1219610 | 1190090 | 0 | 0 | 1177600 | 663.756 | 0 | 0 | 0 | 0 | 1177600 | 663.756 | 1160850 | 1137633.875
4114 | 2001-06-21 09:00 | 827 | 766 | 182 | 30.11 | 2.47 | 0 | 57.3804 | 100.37 | 36.4514 | 0 | 827 | 615.971 | 185.57 | 7.7484 | 615.971 | 173.663 | 0.040444 | 608.48 | 167.236 | 0.030475 | 752.474 | 752.464 | 1689840 | 50.1479 | 1675590 | 1494590 | 1460220 | 0 | 0 | 1440820 | 652.486 | 0 | 0 | 0 | 2329.71 | 1438490 | 660 | 1416010 | 1387686.5
4115 | 2001-06-21 10:00 | 979 | 887 | 151 | 31.94 | 2.47 | 0 | 69.1124 | 116.734 | 23.8609 | 0 | 979 | 810.495 | 151.115 | 9.1725 | 810.495 | 141.419 | 0.047877 | 806.708 | 136.185 | 0.036076 | 914.641 | 914.637 | 2054050 | 56.2965 | 2058000 | 1783900 | 1742940 | 0 | 0 | 1714300 | 638.118 | 0 | 0 | 0 | 26562.7 | 1687740 | 660 | 1657570 | 1624415.125
4116 | 2001-06-21 11:00 | 1026 | 923 | 125 | 32.77 | 2.47 | 0 | 77.962 | 155.98 | 14.7859 | 0 | 1026 | 890.753 | 125.78 | 9.6128 | 890.753 | 117.71 | 0.050176 | 889.227 | 113.353 | 0.037808 | 972.54 | 972.536 | 2184070 | 58.6684 | 2194960 | 1881230 | 1838940 | 0 | 0 | 1806430 | 630.868 | 0 | 0 | 0 | 46932.1 | 1759500 | 660 | 1726780 | 1692242
4117 | 2001-06-21 12:00 | 1029 | 949 | 109 | 33.59 | 3.79 | 0 | 76.0417 | 219.804 | 16.6921 | 0 | 1029 | 908.047 | 110.689 | 9.6409 | 908.047 | 103.587 | 0.050322 | 906.049 | 99.753 | 0.037919 | 975.665 | 975.658 | 2191090 | 57.3984 | 2202360 | 1899890 | 1858900 | 0 | 0 | 1826040 | 634.456 | 0 | 0 | 0 | 34912 | 1791120 | 660 | 1757250 | 1722105.25
4118 | 2001-06-21 13:00 | 963 | 871 | 169 | 34.41 | 3.79 | 0 | 65.8085 | 249.251 | 27.368 | 0 | 963 | 773.015 | 174.986 | 9.0226 | 773.015 | 163.758 | 0.047095 | 768.144 | 157.698 | 0.035487 | 898.1 | 898.094 | 2016890 | 56.3257 | 2018890 | 1749440 | 1711050 | 0 | 0 | 1683220 | 635.669 | 0 | 0 | 0 | 28463.7 | 1654750 | 660 | 1625720 | 1593201.625
4119 | 2001-06-21 14:00 | 752 | 609 | 260 | 34.63 | 3.79 | 0 | 53.8145 | 262.913 | 40.3351 | 0 | 752 | 464.668 | 260.063 | 7.0457 | 464.668 | 243.376 | 0.036776 | 457.422 | 234.369 | 0.027711 | 671.064 | 671.057 | 1507020 | 51.0054 | 1484620 | 1317190 | 1287190 | 0 | 0 | 1271740 | 644.814 | 0 | 0 | 0 | 7692.78 | 1264040 | 660 | 1245610 | 1220696.875
4120 | 2001-06-21 15:00 | 477 | 281 | 291 | 34.85 | 2.74 | 0 | 41.4845 | 272.049 | 53.9115 | 0 | 477 | 165.395 | 276.046 | 4.4691 | 165.395 | 258.334 | 0.023327 | 159.625 | 248.773 | 0.017578 | 396.163 | 396.147 | 889642 | 45.2116 | 848503 | 771116 | 752294 | 0 | 0 | 747015 | 647.602 | 0 | 0 | 0 | 3696.67 | 743318 | 660 | 733655 | 718982.125
4121 | 2001-06-21 16:00 | 417 | 521 | 162 | 35.07 | 2.74 | 0 | 29.2067 | 279.689 | 67.6564 | 0 | 417 | 198.664 | 151.025 | 3.907 | 198.664 | 141.335 | 0.020393 | 182.469 | 136.104 | 0.015367 | 309.031 | 309.027 | 693999 | 43.1529 | 651209 | 596750 | 582157 | 0 | 0 | 578966 | 645.952 | 0 | 0 | 0 | 4222.14 | 574744 | 660 | 567200 | 555855.625
4122 | 2001-06-21 17:00 | 187 | 260 | 110 | 34.68 | 2.74 | 0 | 17.1953 | 287.002 | 81.3799 | 0 | 187 | 39.0384 | 95.09 | 1.752 | 39.0384 | 88.9889 | 0.0091451 | 27.9672 | 85.6955 | 0.006891 | 110.26 | 110.259 | 247613 | 37.5639 | 214773 | 201152 | 196640 | 0 | 0 | 196239 | 617.523 | 0 | 0 | 0 | 13051.1 | 183188 | 660 | 178241 | 174675.8125
4123 | 2001-06-21 18:00 | 43 | 173 | 25 | 34.28 | 5.15 | 0 | 5.6542 | 294.65 | 90 | 0 | 43 | 0 | 18.9132 | 0.40288 | 0 | 17.6997 | 0.0021029 | 0 | 17.0446 | 0.0015846 | 16.5348 | 16.5341 | 37131.4 | 34.6492 | 24998.4 | 23660.1 | 23175.2 | 0 | 0 | 23167.7 | 530.409 | 0 | 0 | 0 | 23167.7 | 0 | 660 | 0 | 0
4124 | 2001-06-21 19:00 | 0 | 4 | 0 | 33.89 | 5.15 | 0
4125 | 2001-06-21 20:00 | 0 | 0 | 0 | 32.95 | 5.15 | 0
4126 | 2001-06-21 21:00 | 0 | 0 | 0 | 32.01 | 6.91 | 0
4127 | 2001-06-21 22:00 | 0 | 0 | 0 | 31.08 | 6.91 | 0
4128 | 2001-06-21 23:00 | 0 | 0 | 0 | 30.17 | 6.91 | 0
4129 | 2001-06-22 | 0 | 0 | 0 | 29.26 | 5.56 | 0
4130 | 2001-06-22 01:00 | 0 | 0 | 0 | 28.35 | 5.56 | 0
4131 | 2001-06-22 02:00 | 0 | 0 | 0 | 27.81 | 5.56 | 0
4132 | 2001-06-22 03:00 | 0 | 0 | 0 | 27.27 | 5.56 | 0
4133 | 2001-06-22 04:00 | 4 | 82 | 1 | 26.73 | 5.56 | 0 | -2.1356 | 59.4137 | 90 | 0 | 4 | 0 | 0.91869 | 0.037477 | 0 | 0.85975 | 0 | 0 | 0.82793 | 0 | 0.80309 | 0.80305 | 1803.44 | 26.7475 | 157.611 | 157.935 | 157.185 | 0 | 0 | 157.178 | 120.319 | 0 | 0 | 0 | 157.178 | 0 | 660 | 0 | 0
4134 | 2001-06-22 05:00 | 120 | 483 | 44 | 27.12 | 5.56 | 0 | 8.9191 | 67.625 | 90 | 0 | 120 | 0 | 33.2913 | 1.1243 | 0 | 31.1553 | 0.0058685 | 0 | 30.0023 | 0.004422 | 29.1065 | 29.1058 | 65364.4 | 27.7528 | 48684.1 | 47949.2 | 46835.6 | 0 | 0 | 46810.4 | 587.802 | 0 | 0 | 0 | 11432.1 | 35378.3 | 660 | 34109 | 33426.8555
4135 | 2001-06-22 06:00 | 324 | 651 | 94 | 27.51 | 3.32 | 0 | 20.6189 | 75.1205 | 77.4327 | 0 | 324 | 142.112 | 85.0382 | 3.0356 | 141.356 | 79.582 | 0.015845 | 115.941 | 76.6367 | 0.01194 | 186.812 | 186.801 | 419505 | 32.2118 | 379855 | 366724 | 354163 | 0 | 0 | 353025 | 659.089 | 0 | 0 | 0 | 330.964 | 352694 | 661.955 | 346704 | 339769.875
4136 | 2001-06-22 07:00 | 480 | 611 | 149 | 27.9 | 3.32 | 0 | 32.7269 | 82.4489 | 63.6878 | 0 | 480 | 271.384 | 143.718 | 4.4972 | 271.384 | 134.497 | 0.023474 | 254.341 | 129.519 | 0.017688 | 372.361 | 372.356 | 836217 | 37.2723 | 794353 | 750412 | 732618 | 0 | 0 | 727964 | 672.511 | 0 | 0 | 0 | 0 | 727964 | 672.511 | 718046 | 703684.6875
4137 | 2001-06-22 08:00 | 692 | 788 | 134 | 29.33 | 3.32 | 0 | 45.0444 | 90.3615 | 49.9664 | 0 | 692 | 507.205 | 136.118 | 6.4835 | 507.205 | 127.384 | 0.033842 | 493.14 | 122.67 | 0.0255 | 597.36 | 597.356 | 1341510 | 44.3656 | 1312540 | 1201900 | 1173330 | 0 | 0 | 1161200 | 664.717 | 0 | 0 | 0 | 0 | 1161200 | 664.717 | 1144750 | 1121859.75
4138 | 2001-06-22 09:00 | 839 | 829 | 141 | 30.75 | 3.7 | 0 | 57.3335 | 100.337 | 36.4974 | 0 | 839 | 666.54 | 146.245 | 7.8608 | 666.54 | 136.861 | 0.041031 | 658.41 | 131.796 | 0.030917 | 766.53 | 766.519 | 1721410 | 49.566 | 1708640 | 1528700 | 1493710 | 0 | 0 | 1473680 | 655.669 | 0 | 0 | 0 | 1050.96 | 1472630 | 659.999 | 1449310 | 1420321.125
4139 | 2001-06-22 10:00 | 957 | 877 | 138 | 32.18 | 3.7 | 0 | 69.0686 | 116.666 | 23.8995 | 0 | 957 | 801.681 | 138.968 | 8.9663 | 801.681 | 130.051 | 0.046801 | 797.921 | 125.238 | 0.035266 | 895.499 | 895.491 | 2011040 | 54.162 | 2012750 | 1763050 | 1723910 | 0 | 0 | 1696240 | 642.454 | 0 | 0 | 0 | 13439.7 | 1682800 | 660 | 1652790 | 1619738.75
4140 | 2001-06-22 11:00 | 996 | 822 | 194 | 32.84 | 3.7 | 0 | 77.9373 | 155.77 | 14.7973 | 0 | 996 | 792.91 | 200.096 | 9.3317 | 792.91 | 187.258 | 0.048709 | 791.55 | 180.327 | 0.036703 | 942.756 | 942.745 | 2117170 | 55.9819 | 2124470 | 1845080 | 1805410 | 0 | 0 | 1774650 | 637.577 | 0 | 0 | 0 | 24471.2 | 1750180 | 660 | 1717800 | 1683443.75
4141 | 2001-06-22 12:00 | 1015 | 883 | 159 | 33.5 | 4.17 | 0 | 76.0643 | 219.618 | 16.6575 | 0 | 1015 | 844.948 | 157.794 | 9.5098 | 844.948 | 147.67 | 0.049638 | 843.097 | 142.205 | 0.037403 | 955.779 | 955.77 | 2146420 | 56.2484 | 2155280 | 1869640 | 1828570 | 0 | 0 | 1797120 | 637.895 | 0 | 0 | 0 | 25566.8 | 1771550 | 660 | 1738390 | 1703626
4142 | 2001-06-22 13:00 | 897 | 761 | 203 | 34.17 | 4.17 | 0 | 65.8462 | 249.169 | 27.3201 | 0 | 897 | 675.75 | 211.487 | 8.4042 | 675.75 | 197.917 | 0.043867 | 671.508 | 190.593 | 0.033055 | 836.27 | 836.263 | 1878030 | 54.074 | 1872920 | 1640150 | 1602890 | 0 | 0 | 1578970 | 643.318 | 0 | 0 | 0 | 14970.1 | 1564000 | 660 | 1537970 | 1507211
4143 | 2001-06-22 14:00 | 778 | 764 | 161 | 34.66 | 4.17 | 0 | 53.8553 | 262.863 | 40.2849 | 0 | 778 | 582.853 | 164.688 | 7.2893 | 582.853 | 154.121 | 0.038047 | 573.793 | 148.417 | 0.02867 | 700.572 | 700.565 | 1573290 | 51.3342 | 1553740 | 1376870 | 1345430 | 0 | 0 | 1328620 | 646.229 | 0 | 0 | 0 | 7603.08 | 1321010 | 660 | 1301300 | 1275271.125
4144 | 2001-06-22 15:00 | 631 | 763 | 125 | 35.15 | 5.5 | 0 | 41.5255 | 272.01 | 53.8613 | 0 | 631 | 450.121 | 126.273 | 5.912 | 450.121 | 118.172 | 0.030859 | 434.464 | 113.798 | 0.023252 | 531.837 | 531.827 | 1194350 | 46.7578 | 1160360 | 1049210 | 1024360 | 0 | 0 | 1014780 | 653.266 | 0 | 0 | 0 | 1536.64 | 1013250 | 660 | 999993 | 979992.9375
4145 | 2001-06-22 16:00 | 463 | 770 | 86 | 35.64 | 5.5 | 0 | 29.2468 | 279.654 | 67.6069 | 0 | 463 | 293.962 | 84.2168 | 4.338 | 293.962 | 78.8133 | 0.022643 | 270.078 | 75.8965 | 0.017062 | 335.612 | 335.61 | 753696 | 42.9651 | 711111 | 652730 | 637559 | 0 | 0 | 633760 | 647.679 | 0 | 0 | 0 | 2775.2 | 630985 | 660 | 622782 | 610326.5625
4146 | 2001-06-22 17:00 | 242 | 589 | 67 | 34.79 | 5.5 | 0 | 17.2335 | 286.967 | 81.3316 | 0 | 242 | 89.0253 | 58.1905 | 2.2673 | 89.0253 | 54.4568 | 0.011835 | 63.9424 | 52.4414 | 0.0089178 | 112.901 | 112.897 | 253538 | 37.2541 | 220363 | 206769 | 202086 | 0 | 0 | 201665 | 620.059 | 0 | 0 | 0 | 11837.2 | 189828 | 660 | 184777 | 181081.2812
4147 | 2001-06-22 18:00 | 56 | 393 | 16 | 33.94 | 8.61 | 0 | 5.6896 | 294.614 | 90 | 0 | 56 | 0 | 13.5886 | 0.52468 | 0 | 12.7167 | 0.0027386 | 0 | 12.2461 | 0.0020636 | 11.8807 | 11.8803 | 26680.1 | 34.1528 | 16611.2 | 15787.9 | 15493 | 0 | 0 | 15489.4 | 510.542 | 0 | 0 | 0 | 15489.4 | 0 | 660 | 0 | 0
4148 | 2001-06-22 19:00 | 0 | 10 | 0 | 33.09 | 8.61 | 0
4149 | 2001-06-22 20:00 | 0 | 0 | 0 | 31.98 | 8.61 | 0
4150 | 2001-06-22 21:00 | 0 | 0 | 0 | 30.87 | 5.3 | 0
4151 | 2001-06-22 22:00 | 0 | 0 | 0 | 29.75 | 5.3 | 0
4152 | 2001-06-22 23:00 | 0 | 0 | 0 | 28.8 | 5.3 | 0
4153 | 2001-06-23 | 0 | 0 | 0 | 27.85 | 6.43 | 0
4154 | 2001-06-23 01:00 | 0 | 0 | 0 | 26.9 | 6.43 | 0
4155 | 2001-06-23 02:00 | 0 | 0 | 0 | 26.24 | 6.43 | 0
4156 | 2001-06-23 03:00 | 0 | 0 | 0 | 25.59 | 4.14 | 0
4157 | 2001-06-23 04:00 | 4 | 68 | 2 | 24.93 | 4.14 | 0 | -2.1814 | 59.3913 | 90 | 0 | 4 | 0 | 1.4289 | 0.037477 | 0 | 1.3373 | 0 | 0 | 1.2878 | 0 | 1.2491 | 1.249 | 2805.04 | 24.9598 | 380.449 | 380.43 | 378.68 | 0 | 0 | 378.663 | 185.174 | 0 | 0 | 0 | 378.663 | 0 | 660 | 0 | 0
4158 | 2001-06-23 05:00 | 111 | 406 | 47 | 25.46 | 4.14 | 0 | 8.8713 | 67.6071 | 90 | 0 | 111 | 0 | 36.1707 | 1.04 | 0 | 33.8499 | 0.0054284 | 0 | 32.5972 | 0.0040904 | 31.6232 | 31.6215 | 71014.1 | 26.2141 | 53546.8 | 53191.1 | 51938.7 | 0 | 0 | 51908.6 | 596.43 | 0 | 0 | 0 | 8717.21 | 43191.4 | 660 | 41662.1 | 40828.8867
4159 | 2001-06-23 06:00 | 289 | 545 | 97 | 25.99 | 3.27 | 0 | 20.5698 | 75.1056 | 77.4832 | 0 | 289 | 118.434 | 87.7724 | 2.7077 | 117.764 | 82.1408 | 0.014133 | 96.4833 | 79.1008 | 0.01065 | 170.327 | 170.315 | 382482 | 30.2911 | 343892 | 335103 | 323917 | 0 | 0 | 322968 | 660.917 | 0 | 0 | 0 | 277.701 | 322690 | 664.26 | 316568 | 310236.9375
4160 | 2001-06-23 07:00 | 515 | 767 | 101 | 26.51 | 3.27 | 0 | 32.6771 | 82.4354 | 63.7372 | 0 | 515 | 339.302 | 99.9371 | 4.8251 | 339.302 | 93.525 | 0.025186 | 317.927 | 90.0637 | 0.018978 | 395.77 | 395.767 | 888789 | 36.5046 | 847622 | 803933 | 783544 | 0 | 0 | 778279 | 676.028 | 0 | 0 | 0 | 0 | 778279 | 676.028 | 767537 | 752186.5
4161 | 2001-06-23 08:00 | 702 | 847 | 103 | 28.09 | 3.27 | 0 | 44.9943 | 90.347 | 50.0138 | 0 | 702 | 544.412 | 104.924 | 6.5772 | 544.412 | 98.1915 | 0.034331 | 529.273 | 94.5575 | 0.025869 | 605.14 | 605.136 | 1358980 | 43.3719 | 1330650 | 1224440 | 1194730 | 0 | 0 | 1182360 | 669.96 | 0 | 0 | 0 | 0 | 1182360 | 669.96 | 1165220 | 1141911.625
4162 | 2001-06-23 09:00 | 864 | 895 | 111 | 29.66 | 4.06 | 0 | 57.2836 | 100.315 | 36.5412 | 0 | 864 | 719.056 | 113.503 | 8.095 | 719.056 | 106.221 | 0.042253 | 710.26 | 102.289 | 0.031839 | 788.204 | 788.2 | 1770090 | 48.5558 | 1759650 | 1582490 | 1545600 | 0 | 0 | 1524260 | 657.776 | 0 | 0 | 0 | 16.5644 | 1524250 | 660.146 | 1499480 | 1469492.875
4163 | 2001-06-23 10:00 | 972 | 913 | 120 | 31.24 | 4.06 | 0 | 69.0208 | 116.613 | 23.9343 | 0 | 972 | 834.025 | 121.883 | 9.1069 | 834.025 | 114.063 | 0.047535 | 830.101 | 109.842 | 0.035819 | 911.779 | 911.77 | 2047600 | 53.0982 | 2051220 | 1806590 | 1766050 | 0 | 0 | 1737440 | 646.99 | 0 | 0 | 0 | 7777.97 | 1729660 | 660 | 1698020 | 1664054.75
4164 | 2001-06-23 11:00 | 1027 | 926 | 123 | 31.85 | 4.06 | 0 | 77.9062 | 155.575 | 14.8024 | 0 | 1027 | 893.836 | 123.899 | 9.6222 | 893.836 | 115.949 | 0.050225 | 892.302 | 111.658 | 0.037845 | 973.878 | 973.88 | 2187080 | 55.1972 | 2198140 | 1917200 | 1871990 | 0 | 0 | 1839530 | 643.583 | 0 | 0 | 0 | 15853.6 | 1823680 | 660 | 1788600 | 1752825.125
4165 | 2001-06-23 12:00 | 1015 | 921 | 122 | 32.46 | 5.57 | 0 | 76.081 | 219.415 | 16.6176 | 0 | 1015 | 881.59 | 123.165 | 9.5098 | 881.59 | 115.262 | 0.049638 | 879.669 | 110.997 | 0.037403 | 960.982 | 960.974 | 2158100 | 53.3398 | 2167590 | 1907830 | 1868360 | 0 | 0 | 1836280 | 645.95 | 0 | 0 | 0 | 8913.35 | 1827370 | 660 | 1792150 | 1756304.125
4166 | 2001-06-23 13:00 | 968 | 950 | 101 | 33.06 | 5.57 | 0 | 65.8799 | 249.074 | 27.2694 | 0 | 968 | 844.364 | 103.666 | 9.0694 | 844.364 | 97.0143 | 0.047339 | 839.085 | 93.4239 | 0.035671 | 904.569 | 904.561 | 2031420 | 52.7141 | 2034190 | 1794880 | 1754830 | 0 | 0 | 1726640 | 648.136 | 0 | 0 | 0 | 6553.42 | 1720080 | 660 | 1688780 | 1655000.75
4167 | 2001-06-23 14:00 | 834 | 910 | 99 | 33.44 | 5.57 | 0 | 53.8927 | 262.803 | 40.2334 | 0 | 834 | 694.521 | 101.776 | 7.8139 | 694.521 | 95.246 | 0.040786 | 683.759 | 91.721 | 0.030733 | 752.246 | 752.24 | 1689340 | 49.7845 | 1675060 | 1496840 | 1461020 | 0 | 0 | 1441790 | 654.845 | 0 | 0 | 0 | 1311.49 | 1440480 | 660 | 1417950 | 1389588.375
4168 | 2001-06-23 15:00 | 653 | 842 | 94 | 33.81 | 8.09 | 0 | 41.5633 | 271.963 | 53.8107 | 0 | 653 | 497.499 | 95.811 | 6.1181 | 497.499 | 89.6636 | 0.031934 | 480.246 | 86.3452 | 0.024063 | 549.616 | 549.611 | 1234290 | 43.9792 | 1201570 | 1101710 | 1075790 | 0 | 0 | 1065550 | 663.952 | 0 | 0 | 0 | 0 | 1065550 | 663.952 | 1051080 | 1030056.0625
4169 | 2001-06-23 16:00 | 448 | 748 | 82 | 34.18 | 8.09 | 0 | 29.2835 | 279.612 | 67.5577 | 0 | 448 | 285.652 | 80.4249 | 4.1974 | 285.652 | 75.2647 | 0.021909 | 262.522 | 72.4792 | 0.016509 | 324.967 | 324.963 | 729785 | 40.1926 | 687081 | 639356 | 625173 | 0 | 0 | 621600 | 655.405 | 0 | 0 | 0 | 302.763 | 621298 | 660 | 613221 | 600956.5
4170 | 2001-06-23 17:00 | 247 | 606 | 66 | 33.28 | 8.09 | 0 | 17.268 | 286.927 | 81.2843 | 0 | 247 | 92.3965 | 57.323 | 2.3142 | 92.3965 | 53.645 | 0.012079 | 66.5287 | 51.6597 | 0.009102 | 114.652 | 114.65 | 257475 | 35.4013 | 224086 | 212388 | 207560 | 0 | 0 | 207126 | 626.893 | 0 | 0 | 0 | 7776.93 | 199350 | 660 | 194159 | 190275.6094
4171 | 2001-06-23 18:00 | 57 | 404 | 15 | 32.38 | 7.76 | 0 | 5.7208 | 294.572 | 90 | 0 | 57 | 0 | 12.7668 | 0.53405 | 0 | 11.9477 | 0.0027875 | 0 | 11.5055 | 0.0021005 | 11.1624 | 11.1617 | 25066.3 | 32.5909 | 15344.5 | 14721.1 | 14435.5 | 0 | 0 | 14432.3 | 511.513 | 0 | 0 | 0 | 14432.3 | 0 | 660 | 0 | 0
4172 | 2001-06-23 19:00 | 0 | 11 | 0 | 31.48 | 7.76 | 0
4173 | 2001-06-23 20:00 | 0 | 0 | 0 | 30.54 | 7.76 | 0
4174 | 2001-06-23 21:00 | 0 | 0 | 0 | 29.59 | 8.4 | 0
4175 | 2001-06-23 22:00 | 0 | 0 | 0 | 28.65 | 8.4 | 0
4176 | 2001-06-23 23:00 | 0 | 0 | 0 | 27.48 | 8.4 | 0
4177 | 2001-06-24 | 0 | 0 | 0 | 26.31 | 7.69 | 0
4178 | 2001-06-24 01:00 | 0 | 0 | 0 | 25.14 | 7.69 | 0
4179 | 2001-06-24 02:00 | 0 | 0 | 0 | 24.53 | 7.69 | 0
4180 | 2001-06-24 03:00 | 0 | 0 | 0 | 23.93 | 7.95 | 0
4181 | 2001-06-24 04:00 | 4 | 79 | 2 | 23.32 | 7.95 | 0 | -2.2313 | 59.3744 | 90 | 0 | 4 | 0 | 1.4297 | 0.037477 | 0 | 1.3379 | 0 | 0 | 1.2884 | 0 | 1.2498 | 1.2497 | 2806.45 | 23.3433 | 380.821 | 380.099 | 378.366 | 0 | 0 | 378.35 | 185.116 | 0 | 0 | 0 | 378.35 | 0 | 660 | 0 | 0
4182 | 2001-06-24 05:00 | 119 | 480 | 44 | 23.59 | 7.95 | 0 | 8.8199 | 67.5952 | 90 | 0 | 119 | 0 | 33.4026 | 1.1149 | 0 | 31.2594 | 0.0058196 | 0 | 30.1025 | 0.0043852 | 29.2037 | 29.2027 | 65581.9 | 24.1351 | 48870.6 | 49100 | 47928.6 | 0 | 0 | 47903.2 | 599.645 | 0 | 0 | 0 | 6960.18 | 40943 | 660 | 39487.8 | 38698.0508
4183 | 2001-06-24 06:00 | 322 | 731 | 65 | 23.86 | 4.78 | 0 | 20.5175 | 75.0973 | 77.5339 | 0 | 322 | 158.281 | 60.45 | 3.0169 | 157.332 | 56.5714 | 0.015747 | 128.756 | 54.4777 | 0.011866 | 177.748 | 177.743 | 399166 | 27.9251 | 360091 | 355017 | 342299 | 0 | 0 | 341271 | 670.838 | 0 | 0 | 0 | 4.6543 | 341267 | 671.144 | 334991 | 328291.1562
4184 | 2001-06-24 07:00 | 531 | 840 | 78 | 24.14 | 4.78 | 0 | 32.6244 | 82.4293 | 63.7861 | 0 | 531 | 371.155 | 78.7321 | 4.9751 | 371.155 | 73.6805 | 0.025968 | 347.7 | 70.9537 | 0.019568 | 406.113 | 406.11 | 912017 | 33.4281 | 871211 | 838474 | 817765 | 0 | 0 | 812225 | 688.302 | 0 | 0 | 0 | 0 | 812225 | 688.302 | 800517 | 784506.75
4185 | 2001-06-24 08:00 | 725 | 901 | 88 | 25.84 | 4.78 | 0 | 44.9414 | 90.3415 | 50.0601 | 0 | 725 | 578.926 | 90.4465 | 6.7927 | 578.926 | 84.6433 | 0.035456 | 562.783 | 81.5107 | 0.026717 | 624.991 | 624.988 | 1403570 | 40.134 | 1376950 | 1286890 | 1256310 | 0 | 0 | 1243040 | 680.361 | 0 | 0 | 0 | 0 | 1243040 | 680.361 | 1224110 | 1199627.5
4186 | 2001-06-24 09:00 | 883 | 934 | 98 | 27.55 | 4.37 | 0 | 57.2307 | 100.305 | 36.5828 | 0 | 883 | 749.655 | 100.885 | 8.273 | 749.655 | 94.412 | 0.043182 | 740.459 | 90.9179 | 0.032539 | 806.467 | 806.465 | 1811110 | 46.495 | 1802680 | 1637610 | 1598440 | 0 | 0 | 1576310 | 667.437 | 0 | 0 | 0 | 0 | 1576310 | 667.437 | 1549630 | 1518641
4187 | 2001-06-24 10:00 | 990 | 906 | 145 | 29.26 | 4.37 | 0 | 68.9692 | 116.577 | 23.9653 | 0 | 990 | 827.26 | 145.561 | 9.2755 | 827.26 | 136.221 | 0.048415 | 823.358 | 131.18 | 0.036482 | 925.937 | 925.93 | 2079400 | 51.0114 | 2084690 | 1855180 | 1812190 | 0 | 0 | 1782850 | 655.825 | 0 | 0 | 0 | 1120.08 | 1781730 | 660 | 1748200 | 1713234.125
4188 | 2001-06-24 11:00 | 970 | 728 | 260 | 29.88 | 4.37 | 0 | 77.8688 | 155.394 | 14.8012 | 0 | 970 | 702.12 | 269.992 | 9.0881 | 702.12 | 252.669 | 0.047437 | 700.915 | 243.318 | 0.035745 | 915.941 | 915.928 | 2056940 | 51.3964 | 2061050 | 1830520 | 1788130 | 0 | 0 | 1759490 | 654.863 | 0 | 0 | 0 | 1890.77 | 1757600 | 660 | 1724950 | 1690447.75
4189 | 2001-06-24 12:00 | 1006 | 866 | 167 | 30.5 | 6.08 | 0 | 76.0917 | 219.198 | 16.5723 | 0 | 1006 | 828.437 | 174.087 | 9.4254 | 828.437 | 162.917 | 0.049198 | 826.642 | 156.888 | 0.037071 | 954.059 | 954.049 | 2142560 | 50.5588 | 2151220 | 1919120 | 1873580 | 0 | 0 | 1842480 | 658.04 | 0 | 0 | 0 | 410.387 | 1842060 | 660.312 | 1806290 | 1770159.5
4190 | 2001-06-24 13:00 | 964 | 944 | 103 | 31.12 | 6.08 | 0 | 65.9094 | 248.965 | 27.216 | 0 | 964 | 838.73 | 105.627 | 9.0319 | 838.73 | 98.8499 | 0.047144 | 833.509 | 95.1915 | 0.035524 | 900.874 | 900.868 | 2023120 | 50.0607 | 2025450 | 1810420 | 1768540 | 0 | 0 | 1740660 | 657.468 | 0 | 0 | 0 | 348.59 | 1740310 | 660.457 | 1708270 | 1674108.375
4191 | 2001-06-24 14:00 | 834 | 909 | 99 | 31.43 | 6.08 | 0 | 53.9266 | 262.733 | 40.1807 | 0 | 834 | 694.762 | 101.788 | 7.8139 | 694.762 | 95.2567 | 0.040786 | 684.032 | 91.7313 | 0.030733 | 752.52 | 752.517 | 1689970 | 47.2516 | 1675720 | 1516000 | 1479030 | 0 | 0 | 1459840 | 663.866 | 0 | 0 | 0 | 0 | 1459840 | 663.866 | 1436680 | 1407949.875
4192 | 2001-06-24 15:00 | 646 | 823 | 99 | 31.73 | 10.39 | 0 | 41.5977 | 271.908 | 53.7598 | 0 | 646 | 487.081 | 101.152 | 6.0525 | 487.081 | 94.6621 | 0.031592 | 470.238 | 91.1587 | 0.023805 | 544.578 | 544.575 | 1222980 | 40.4684 | 1189900 | 1109490 | 1081750 | 0 | 0 | 1071710 | 674.1 | 0 | 0 | 0 | 0 | 1071710 | 674.1 | 1056610 | 1035481.5
4193 | 2001-06-24 16:00 | 453 | 750 | 85 | 32.03 | 10.39 | 0 | 29.3166 | 279.564 | 67.509 | 0 | 453 | 287.508 | 83.3171 | 4.2443 | 287.508 | 77.9713 | 0.022154 | 264.304 | 75.0856 | 0.016693 | 329.224 | 329.219 | 739345 | 37.3128 | 696684 | 657613 | 642205 | 0 | 0 | 638555 | 666.082 | 0 | 0 | 0 | 0 | 638555 | 666.082 | 630059 | 617458.125
4194 | 2001-06-24 17:00 | 232 | 512 | 79 | 30.86 | 10.39 | 0 | 17.2987 | 286.88 | 81.2382 | 0 | 232 | 78.3783 | 69.1685 | 2.1737 | 78.3783 | 64.7305 | 0.011346 | 56.5701 | 62.3349 | 0.0085493 | 115.346 | 115.344 | 259032 | 32.7108 | 225560 | 216856 | 211792 | 0 | 0 | 211356 | 637.152 | 0 | 0 | 0 | 3590.92 | 207765 | 660 | 202460 | 198410.5
4195 | 2001-06-24 18:00 | 54 | 341 | 19 | 29.68 | 8.01 | 0 | 5.7477 | 294.525 | 90 | 0 | 54 | 0 | 14.7697 | 0.50594 | 0 | 13.822 | 0.0026408 | 0 | 13.3105 | 0.0019899 | 12.9131 | 12.9127 | 28998.5 | 29.9201 | 18445.9 | 17954.7 | 17595 | 0 | 0 | 17590.7 | 532.032 | 0 | 0 | 0 | 17590.7 | 0 | 660 | 0 | 0
4196 | 2001-06-24 19:00 | 0 | 10 | 0 | 28.5 | 8.01 | 0
4197 | 2001-06-24 20:00 | 0 | 0 | 0 | 27.65 | 8.01 | 0
4198 | 2001-06-24 21:00 | 0 | 0 | 0 | 26.81 | 8.69 | 0
4199 | 2001-06-24 22:00 | 0 | 0 | 0 | 25.96 | 8.69 | 0
4200 | 2001-06-24 23:00 | 0 | 0 | 0 | 24.91 | 8.69 | 0
4201 | 2001-06-25 | 0 | 0 | 0 | 23.86 | 7.75 | 0
4202 | 2001-06-25 01:00 | 0 | 0 | 0 | 22.81 | 7.75 | 0
4203 | 2001-06-25 02:00 | 0 | 0 | 0 | 22.04 | 7.75 | 0
4204 | 2001-06-25 03:00 | 0 | 0 | 0 | 21.27 | 7.59 | 0
4205 | 2001-06-25 04:00 | 4 | 74 | 2 | 20.5 | 7.59 | 0 | -2.2852 | 59.363 | 90 | 0 | 4 | 0 | 1.4305 | 0.037477 | 0 | 1.3387 | 0 | 0 | 1.2891 | 0 | 1.2505 | 1.2504 | 2808.01 | 20.5239 | 381.268 | 379.309 | 377.559 | 0 | 0 | 377.543 | 184.924 | 0 | 0 | 0 | 377.543 | 0 | 660 | 0 | 0
4206 | 2001-06-25 05:00 | 114 | 458 | 43 | 21.07 | 7.59 | 0 | 8.765 | 67.5893 | 90 | 0 | 114 | 0 | 32.5337 | 1.0681 | 0 | 30.4463 | 0.0055751 | 0 | 29.3195 | 0.0042009 | 28.444 | 28.4432 | 63876.4 | 21.6131 | 47409.1 | 48280.6 | 47082.4 | 0 | 0 | 47058.6 | 607.755 | 0 | 0 | 0 | 4803.78 | 42254.8 | 660 | 40756.3 | 39941.1562
4207 | 2001-06-25 06:00 | 321 | 730 | 65 | 21.65 | 4.92 | 0 | 20.4622 | 75.0955 | 77.5849 | 0 | 321 | 157.437 | 60.4393 | 3.0075 | 156.432 | 56.5614 | 0.015698 | 127.873 | 54.4681 | 0.011829 | 176.883 | 176.878 | 397223 | 25.6586 | 358207 | 357040 | 344288 | 0 | 0 | 343263 | 675.992 | 0 | 0 | 0 | 2.0139 | 343261 | 676.621 | 336843 | 330106.5938
4208 | 2001-06-25 07:00 | 531 | 839 | 79 | 22.23 | 4.92 | 0 | 32.569 | 82.4307 | 63.8346 | 0 | 531 | 370.259 | 78.7969 | 4.9751 | 370.259 | 73.7411 | 0.025968 | 346.789 | 71.012 | 0.019568 | 405.286 | 405.282 | 910162 | 31.415 | 869328 | 844477 | 822926 | 0 | 0 | 817435 | 695.057 | 0 | 0 | 0 | 0 | 817435 | 695.057 | 805375 | 789267.9375
4209 | 2001-06-25 08:00 | 723 | 900 | 88 | 23.61 | 4.92 | 0 | 44.8859 | 90.3448 | 50.1052 | 0 | 723 | 577.127 | 90.4528 | 6.774 | 577.127 | 84.6492 | 0.035358 | 560.992 | 81.5164 | 0.026643 | 623.259 | 623.255 | 1399670 | 37.735 | 1372900 | 1297460 | 1265820 | 0 | 0 | 1252640 | 687.275 | 0 | 0 | 0 | 0 | 1252640 | 687.275 | 1233180 | 1208513.5
4210 | 2001-06-25 09:00 | 882 | 934 | 97 | 25 | 6.09 | 0 | 57.175 | 100.307 | 36.6221 | 0 | 882 | 749.743 | 99.9183 | 8.2637 | 749.743 | 93.5074 | 0.043133 | 740.522 | 90.0467 | 0.032502 | 805.683 | 805.679 | 1809350 | 41.9284 | 1800830 | 1671460 | 1630350 | 0 | 0 | 1608250 | 681.497 | 0 | 0 | 0 | 0 | 1608250 | 681.497 | 1580100 | 1548500.375
4211 | 2001-06-25 10:00 | 991 | 907 | 145 | 26.38 | 6.09 | 0 | 68.9138 | 116.557 | 23.9923 | 0 | 991 | 828.373 | 145.583 | 9.2849 | 828.373 | 136.242 | 0.048464 | 824.456 | 131.2 | 0.036519 | 927.022 | 927.013 | 2081840 | 45.8578 | 2087270 | 1903810 | 1857120 | 0 | 0 | 1827780 | 672.053 | 0 | 0 | 0 | 0 | 1827780 | 672.053 | 1792360 | 1756509
4212 | 2001-06-25 11:00 | 995 | 820 | 195 | 27.22 | 6.09 | 0 | 77.825 | 155.229 | 14.7937 | 0 | 995 | 791.279 | 201.116 | 9.3224 | 791.279 | 188.212 | 0.04866 | 789.922 | 181.246 | 0.036666 | 942.069 | 942.058 | 2115620 | 47.014 | 2122840 | 1925980 | 1880230 | 0 | 0 | 1849870 | 669.403 | 0 | 0 | 0 | 0 | 1849870 | 669.403 | 1813660 | 1777389.25
4213 | 2001-06-25 12:00 | 989 | 858 | 157 | 28.06 | 6.64 | 0 | 76.0964 | 218.965 | 16.5216 | 0 | 989 | 821.724 | 155.995 | 9.2662 | 821.724 | 145.986 | 0.048366 | 819.955 | 140.584 | 0.036445 | 931.758 | 931.753 | 2092490 | 46.9593 | 2098480 | 1904220 | 1857410 | 0 | 0 | 1827780 | 668.902 | 0 | 0 | 0 | 0 | 1827780 | 668.902 | 1792400 | 1756550.5
4214 | 2001-06-25 13:00 | 933 | 878 | 132 | 28.89 | 6.64 | 0 | 65.9348 | 248.842 | 27.1599 | 0 | 933 | 780.52 | 133.518 | 8.7415 | 780.52 | 124.951 | 0.045628 | 775.683 | 120.326 | 0.034381 | 869.163 | 869.159 | 1951910 | 46.5196 | 1950560 | 1772790 | 1729200 | 0 | 0 | 1703540 | 669.689 | 0 | 0 | 0 | 0 | 1703540 | 669.689 | 1672570 | 1639121.375
4215 | 2001-06-25 14:00 | 820 | 720 | 238 | 29.08 | 6.64 | 0 | 53.957 | 262.652 | 40.1267 | 0 | 820 | 550.362 | 239.888 | 7.6828 | 550.362 | 224.496 | 0.040101 | 541.891 | 216.188 | 0.030217 | 735.366 | 735.352 | 1651420 | 43.9955 | 1635380 | 1502440 | 1466970 | 0 | 0 | 1448610 | 673.453 | 0 | 0 | 0 | 0 | 1448610 | 673.453 | 1425340 | 1396833.375
4216 | 2001-06-25 15:00 | 396 | 155 | 293 | 29.27 | 7.48 | 0 | 41.6286 | 271.845 | 53.7087 | 0 | 396 | 91.7729 | 275.164 | 3.7102 | 91.7729 | 257.509 | 0.019366 | 88.609 | 247.979 | 0.014593 | 326.504 | 326.494 | 733221 | 35.5479 | 690553 | 657374 | 640818 | 0 | 0 | 637263 | 673.214 | 0 | 0 | 0 | 0 | 637263 | 673.214 | 628557 | 615986.25
4217 | 2001-06-25 16:00 | 455 | 580 | 170 | 29.46 | 7.48 | 0 | 29.3461 | 279.508 | 67.4609 | 0 | 455 | 222.909 | 158.415 | 4.263 | 222.909 | 148.251 | 0.022251 | 204.978 | 142.764 | 0.016767 | 337.326 | 337.321 | 757537 | 35.9461 | 714980 | 679436 | 662874 | 0 | 0 | 659041 | 671.004 | 0 | 0 | 0 | 0 | 659041 | 671.004 | 650111 | 637108.5625
4218 | 2001-06-25 17:00 | 245 | 595 | 67 | 28.79 | 7.48 | 0 | 17.3254 | 286.828 | 81.1933 | 0 | 245 | 91.5113 | 58.3022 | 2.2955 | 91.5113 | 54.5614 | 0.011982 | 66.2009 | 52.5421 | 0.0090283 | 115.19 | 115.186 | 258678 | 31.0048 | 225224 | 218462 | 213113 | 0 | 0 | 212680 | 643.955 | 0 | 0 | 0 | 1803.68 | 210877 | 660 | 205532 | 201420.8594
4219 | 2001-06-25 18:00 | 57 | 397 | 16 | 28.13 | 8.22 | 0 | 5.7703 | 294.473 | 90 | 0 | 57 | 0 | 13.5865 | 0.53405 | 0 | 12.7148 | 0.0027875 | 0 | 12.2442 | 0.0021005 | 11.8789 | 11.8786 | 26676.5 | 28.348 | 16608.5 | 16311.3 | 15974.1 | 0 | 0 | 15970.5 | 530.407 | 0 | 0 | 0 | 15967.1 | 3.3976 | 660.388 | 3.2685 | 3.2031
4220 | 2001-06-25 19:00 | 0 | 12 | 0 | 27.47 | 8.22 | 0
4221 | 2001-06-25 20:00 | 0 | 0 | 0 | 26.33 | 8.22 | 0
4222 | 2001-06-25 21:00 | 0 | 0 | 0 | 25.19 | 5.53 | 0
4223 | 2001-06-25 22:00 | 0 | 0 | 0 | 24.06 | 5.53 | 0
4224 | 2001-06-25 23:00 | 0 | 0 | 0 | 23.22 | 5.53 | 0
4225 | 2001-06-26 | 0 | 0 | 0 | 22.38 | 5.17 | 0
4226 | 2001-06-26 01:00 | 0 | 0 | 0 | 21.54 | 5.17 | 0
4227 | 2001-06-26 02:00 | 0 | 0 | 0 | 21.04 | 5.17 | 0
4228 | 2001-06-26 03:00 | 0 | 0 | 0 | 20.54 | 6.12 | 0
4229 | 2001-06-26 04:00 | 1 | 0 | 1 | 20.04 | 6.12 | 0 | -2.3431 | 59.3573 | 90 | 0 | 1 | 0 | 1.0002 | 0.0093692 | 0 | 0.93598 | 0 | 0 | 0.90134 | 0 | 0.8743 | 0.87429 | 1963.44 | 20.0583 | 186.777 | 185.691 | 184.806 | 0 | 0 | 184.798 | 130.087 | 0 | 0 | 0 | 184.798 | 0 | 660 | 0 | 0
4230 | 2001-06-26 05:00 | 43 | 0 | 43 | 20.6 | 6.12 | 0 | 8.7066 | 67.5894 | 90 | 0 | 43 | 0 | 38.5611 | 0.40288 | 0 | 36.0869 | 0.0021029 | 0 | 34.7514 | 0.0015846 | 33.7103 | 33.7089 | 75701.6 | 21.3069 | 57605.5 | 58753.3 | 57305.4 | 0 | 0 | 57271.3 | 617.807 | 0 | 0 | 0 | 3568.23 | 53703 | 660 | 51835.4 | 50798.6875
4231 | 2001-06-26 06:00 | 202 | 159 | 146 | 21.16 | 5.33 | 0 | 20.4039 | 75.1002 | 77.636 | 0 | 202 | 34.3936 | 128.747 | 1.8926 | 34.1576 | 120.487 | 0.0098786 | 27.8892 | 116.027 | 0.0074438 | 139.606 | 139.598 | 313502 | 24.2406 | 277435 | 278442 | 269484 | 0 | 0 | 268853 | 674.774 | 0 | 0 | 0 | 0 | 268853 | 674.774 | 262645 | 257392.1875
4232 | 2001-06-26 07:00 | 416 | 375 | 214 | 21.72 | 5.33 | 0 | 32.5108 | 82.4396 | 63.8826 | 0 | 416 | 165.451 | 199.02 | 3.8976 | 165.451 | 186.251 | 0.020344 | 154.931 | 179.358 | 0.01533 | 324.275 | 324.271 | 728232 | 28.876 | 685534 | 673456 | 655730 | 0 | 0 | 652240 | 695.962 | 0 | 0 | 0 | 0 | 652240 | 695.962 | 642588 | 629736.0625
4233 | 2001-06-26 08:00 | 482 | 239 | 313 | 23.27 | 5.33 | 0 | 44.8277 | 90.3572 | 50.1489 | 0 | 482 | 153.614 | 299.049 | 4.516 | 153.614 | 279.861 | 0.023572 | 149.308 | 269.504 | 0.017762 | 406.265 | 406.248 | 912328 | 32.235 | 871548 | 843425 | 820825 | 0 | 0 | 815317 | 692.322 | 0 | 0 | 0 | 0 | 815317 | 692.322 | 803400 | 787331.8125
4234 | 2001-06-26 09:00 | 575 | 217 | 393 | 24.81 | 5.16 | 0 | 57.1166 | 100.32 | 36.659 | 0 | 575 | 173.857 | 377.798 | 5.3873 | 173.857 | 353.558 | 0.02812 | 171.713 | 340.473 | 0.021189 | 496.841 | 496.827 | 1115750 | 35.8955 | 1079480 | 1027800 | 1002100 | 0 | 0 | 993776 | 686.314 | 0 | 0 | 0 | 0 | 993776 | 686.314 | 979544 | 959953.4375
4235 | 2001-06-26 10:00 | 917 | 683 | 280 | 26.36 | 5.16 | 0 | 68.8548 | 116.553 | 24.0154 | 0 | 917 | 623.864 | 286.447 | 8.5916 | 623.864 | 268.068 | 0.044845 | 620.908 | 258.147 | 0.033792 | 852.716 | 852.707 | 1914970 | 45.3861 | 1911730 | 1746550 | 1704100 | 0 | 0 | 1679450 | 674.07 | 0 | 0 | 0 | 0 | 1679450 | 674.07 | 1649190 | 1616201.875
4236 | 2001-06-26 11:00 | 652 | 232 | 426 | 26.57 | 5.16 | 0 | 77.775 | 155.079 | 14.7798 | 0 | 652 | 223.593 | 424.851 | 6.1087 | 223.593 | 397.592 | 0.031885 | 223.21 | 382.877 | 0.024026 | 587.928 | 587.897 | 1320270 | 39.6875 | 1290540 | 1208210 | 1178090 | 0 | 0 | 1166410 | 679.621 | 0 | 0 | 0 | 0 | 1166410 | 679.621 | 1149120 | 1126142.5
4237 | 2001-06-26 12:00 | 935 | 634 | 320 | 26.79 | 7.39 | 0 | 76.0948 | 218.718 | 16.4657 | 0 | 935 | 607.584 | 326.12 | 8.7602 | 607.584 | 305.195 | 0.045725 | 606.285 | 293.9 | 0.034455 | 873.213 | 873.195 | 1960970 | 43.676 | 1960080 | 1805440 | 1761920 | 0 | 0 | 1735880 | 677.746 | 0 | 0 | 0 | 0 | 1735880 | 677.746 | 1703610 | 1669533.375
4238 | 2001-06-26 13:00 | 898 | 762 | 202 | 27 | 7.39 | 0 | 65.9559 | 248.705 | 27.1012 | 0 | 898 | 678.449 | 206.49 | 8.4136 | 678.449 | 193.241 | 0.043916 | 674.265 | 186.089 | 0.033092 | 834.576 | 834.564 | 1874220 | 43.139 | 1868920 | 1725320 | 1684540 | 0 | 0 | 1660770 | 678.94 | 0 | 0 | 0 | 0 | 1660770 | 678.94 | 1630990 | 1598374.5
4239 | 2001-06-26 14:00 | 820 | 845 | 137 | 26.99 | 7.39 | 0 | 53.9837 | 262.561 | 40.0718 | 0 | 820 | 646.175 | 141.676 | 7.6828 | 646.175 | 132.586 | 0.040101 | 636.263 | 127.679 | 0.030217 | 741.053 | 741.045 | 1664200 | 41.3205 | 1648750 | 1533920 | 1496570 | 0 | 0 | 1478000 | 682.727 | 0 | 0 | 0 | 0 | 1478000 | 682.727 | 1453670 | 1424594.25
4240 | 2001-06-26 15:00 | 675 | 745 | 180 | 26.99 | 8.62 | 0 | 41.656 | 271.774 | 53.6575 | 0 | 675 | 441.344 | 178.385 | 6.3242 | 441.344 | 166.939 | 0.03301 | 426.174 | 160.761 | 0.024874 | 569.35 | 569.344 | 1278600 | 37.1804 | 1247380 | 1181410 | 1151740 | 0 | 0 | 1140770 | 686.271 | 0 | 0 | 0 | 0 | 1140770 | 686.271 | 1123680 | 1101210.25
4241 | 2001-06-26 16:00 | 402 | 483 | 165 | 26.98 | 8.62 | 0 | 29.372 | 279.446 | 67.4134 | 0 | 402 | 185.588 | 153.978 | 3.7664 | 185.588 | 144.098 | 0.019659 | 170.707 | 138.765 | 0.014814 | 300.202 | 300.197 | 674164 | 32.353 | 631364 | 610105 | 594814 | 0 | 0 | 591796 | 678.898 | 0 | 0 | 0 | 0 | 591796 | 678.898 | 583508 | 571838.25
4242 | 2001-06-26 17:00 | 245 | 465 | 106 | 26.71 | 8.62 | 0 | 17.3482 | 286.77 | 81.1498 | 0 | 245 | 71.7203 | 91.3583 | 2.2955 | 71.7203 | 85.4965 | 0.011982 | 51.9981 | 82.3324 | 0.0090283 | 130.309 | 130.302 | 292625 | 29.0422 | 257477 | 252336 | 245935 | 0 | 0 | 245379 | 655.57 | 0 | 0 | 0 | 77.1123 | 245302 | 660 | 239591 | 234799.2656
4243 | 2001-06-26 18:00 | 57 | 310 | 25 | 26.44 | 7.44 | 0 | 5.7886 | 294.415 | 90 | 0 | 57 | 0 | 18.783 | 0.53405 | 0 | 17.5779 | 0.0027875 | 0 | 16.9273 | 0.0021005 | 16.4215 | 16.4213 | 36878 | 26.7566 | 24791.9 | 24553.3 | 24027.2 | 0 | 0 | 24019.9 | 557.83 | 0 | 0 | 0 | 14070.4 | 9949.47 | 660 | 9577.34 | 9385.7979
4244 | 2001-06-26 19:00 | 0 | 9 | 0 | 26.17 | 7.44 | 0
4245 | 2001-06-26 20:00 | 0 | 0 | 0 | 25.32 | 7.44 | 0
4246 | 2001-06-26 21:00 | 0 | 0 | 0 | 24.46 | 8.48 | 0
4247 | 2001-06-26 22:00 | 0 | 0 | 0 | 23.61 | 8.48 | 0
4248 | 2001-06-26 23:00 | 0 | 0 | 0 | 22.88 | 8.48 | 0
4249 | 2001-06-27 | 0 | 0 | 0 | 22.15 | 7.58 | 0
4250 | 2001-06-27 01:00 | 0 | 0 | 0 | 21.42 | 7.58 | 0
4251 | 2001-06-27 02:00 | 0 | 0 | 0 | 20.84 | 7.58 | 0
4252 | 2001-06-27 03:00 | 0 | 0 | 0 | 20.25 | 8.14 | 0
4253 | 2001-06-27 04:00 | 3 | 68 | 1 | 19.67 | 8.14 | 0 | -2.4049 | 59.3571 | 90 | 0 | 3 | 0 | 0.72625 | 0.028108 | 0 | 0.67966 | 0 | 0 | 0.6545 | 0 | 0.63487 | 0.63482 | 1425.65 | 19.6817 | 98.5738 | 97.9522 | 97.2621 | 0 | 0 | 97.2582 | 97.9555 | 0 | 0 | 0 | 97.2582 | 0 | 660 | 0 | 0
4254 | 2001-06-27 05:00 | 109 | 433 | 43 | 20.11 | 8.14 | 0 | 8.6449 | 67.5955 | 90 | 0 | 109 | 0 | 32.6654 | 1.0212 | 0 | 30.5696 | 0.0053305 | 0 | 29.4382 | 0.0040167 | 28.559 | 28.5579 | 64133.8 | 20.6367 | 47629.2 | 48756.5 | 47634.2 | 0 | 0 | 47610.2 | 612.295 | 0 | 0 | 0 | 4109.34 | 43500.9 | 660 | 41961.4 | 41122.1953
4255 | 2001-06-27 06:00 | 298 | 638 | 76 | 20.55 | 6.24 | 0 | 20.3427 | 75.1116 | 77.6871 | 0 | 298 | 136.182 | 68.4847 | 2.792 | 135.162 | 64.0906 | 0.014573 | 110.229 | 61.7187 | 0.010981 | 166.8 | 166.793 | 374575 | 24.0209 | 336256 | 337800 | 325216 | 0 | 0 | 324302 | 676.73 | 0 | 0 | 0 | 141.037 | 324161 | 679.27 | 317655 | 311301.9062
4256 | 2001-06-27 07:00 | 529 | 798 | 100 | 20.99 | 6.24 | 0 | 32.4501 | 82.4559 | 63.9299 | 0 | 529 | 351.371 | 98.9767 | 4.9563 | 351.371 | 92.6262 | 0.02587 | 328.963 | 89.1981 | 0.019494 | 405.635 | 405.63 | 910946 | 29.4311 | 870125 | 852955 | 830925 | 0 | 0 | 825430 | 701.781 | 0 | 0 | 0 | 0 | 825430 | 701.781 | 812976 | 796716
4257 | 2001-06-27 08:00 | 722 | 900 | 88 | 23.01 | 6.24 | 0 | 44.7671 | 90.3784 | 50.1912 | 0 | 722 | 576.383 | 90.4742 | 6.7646 | 576.383 | 84.6692 | 0.035309 | 560.189 | 81.5357 | 0.026606 | 622.498 | 622.49 | 1397950 | 35.964 | 1371120 | 1306340 | 1273170 | 0 | 0 | 1260050 | 693.543 | 0 | 0 | 0 | 0 | 1260050 | 693.543 | 1240140 | 1215338.125
4258 | 2001-06-27 09:00 | 881 | 934 | 97 | 25.02 | 4.54 | 0 | 57.0554 | 100.345 | 36.6936 | 0 | 881 | 749.103 | 99.9522 | 8.2543 | 749.103 | 93.5391 | 0.043085 | 739.846 | 90.0773 | 0.032465 | 805.058 | 805.055 | 1807940 | 43.7229 | 1799350 | 1656140 | 1614300 | 0 | 0 | 1592240 | 675.438 | 0 | 0 | 0 | 0 | 1592240 | 675.438 | 1564800 | 1533501.875
4259 | 2001-06-27 10:00 | 992 | 953 | 104 | 27.04 | 4.54 | 0 | 68.7922 | 116.565 | 24.0346 | 0 | 992 | 869.926 | 106.502 | 9.2943 | 869.926 | 99.669 | 0.048513 | 865.797 | 95.9804 | 0.036555 | 932.96 | 932.956 | 2095170 | 48.7142 | 2101300 | 1890890 | 1845970 | 0 | 0 | 1816170 | 663.024 | 0 | 0 | 0 | -12.3567 | 1816180 | 663.109 | 1781330 | 1745701.125
4260 | 2001-06-27 11:00 | 1046 | 962 | 108 | 27.88 | 4.54 | 0 | 77.7188 | 154.945 | 14.7596 | 0 | 1046 | 928.292 | 109.619 | 9.8002 | 928.292 | 102.586 | 0.051154 | 926.709 | 98.7889 | 0.038545 | 994.77 | 994.766 | 2233990 | 50.9902 | 2247580 | 2001590 | 1955350 | 0 | 0 | 1921340 | 656.665 | 0 | 0 | 0 | 624.34 | 1920720 | 660 | 1881910 | 1844268.625
4261 | 2001-06-27 12:00 | 1038 | 960 | 108 | 28.72 | 6.5 | 0 | 76.0871 | 218.458 | 16.4045 | 0 | 1038 | 919.106 | 109.795 | 9.7253 | 919.106 | 102.75 | 0.050763 | 917.156 | 98.9474 | 0.038251 | 985.657 | 985.649 | 2213520 | 48.8923 | 2226000 | 2002340 | 1955910 | 0 | 0 | 1922630 | 664.161 | 0 | 0 | 0 | 0 | 1922630 | 664.161 | 1883720 | 1846041
4262 | 2001-06-27 13:00 | 965 | 944 | 103 | 29.56 | 6.5 | 0 | 65.9727 | 248.556 | 27.04 | 0 | 965 | 840.612 | 105.676 | 9.0413 | 840.612 | 98.896 | 0.047192 | 835.454 | 95.236 | 0.035561 | 902.803 | 902.805 | 2027460 | 48.0368 | 2030030 | 1832250 | 1786920 | 0 | 0 | 1759090 | 664.636 | 0 | 0 | 0 | 0 | 1759090 | 664.636 | 1726290 | 1691765.125
4263 | 2001-06-27 14:00 | 845 | 926 | 96 | 29.69 | 6.5 | 0 | 54.0067 | 262.461 | 40.0158 | 0 | 845 | 708.991 | 98.9115 | 7.917 | 708.991 | 92.5651 | 0.041324 | 698.154 | 89.1393 | 0.031138 | 763.705 | 763.698 | 1715070 | 45.3198 | 1702000 | 1554270 | 1520420 | 0 | 0 | 1500300 | 666.558 | 0 | 0 | 0 | 0 | 1500300 | 666.558 | 1476030 | 1446506.5
4264 | 2001-06-27 15:00 | 676 | 887 | 86 | 29.82 | 8.02 | 0 | 41.6798 | 271.695 | 53.6063 | 0 | 676 | 526.439 | 88.17 | 6.3336 | 526.439 | 82.5128 | 0.033059 | 508.398 | 79.4591 | 0.024911 | 570.245 | 570.243 | 1280620 | 40.4175 | 1249460 | 1165620 | 1138730 | 0 | 0 | 1127690 | 676.598 | 0 | 0 | 0 | 0 | 1127690 | 676.598 | 1111350 | 1089123.625
4265 | 2001-06-27 16:00 | 466 | 796 | 75 | 29.95 | 8.02 | 0 | 29.3941 | 279.378 | 67.3666 | 0 | 466 | 306.571 | 73.8434 | 4.3661 | 306.571 | 69.1055 | 0.022789 | 282.068 | 66.548 | 0.017172 | 338.174 | 338.169 | 759444 | 36.2346 | 716893 | 680325 | 664494 | 0 | 0 | 660649 | 671.715 | 0 | 0 | 0 | 0 | 660649 | 671.715 | 651674 | 638640.0625
4266 | 2001-06-27 17:00 | 256 | 646 | 62 | 29.51 | 8.02 | 0 | 17.367 | 286.706 | 81.1076 | 0 | 256 | 100.467 | 53.8833 | 2.3985 | 100.467 | 50.4261 | 0.012519 | 72.9931 | 48.5598 | 0.0094337 | 117.915 | 117.913 | 264803 | 31.7013 | 231025 | 223297 | 217993 | 0 | 0 | 217537 | 642.121 | 0 | 0 | 0 | 2259.57 | 215277 | 660 | 209878 | 205680.125
4267 | 2001-06-27 18:00 | 60 | 431 | 15 | 29.07 | 7 | 0 | 5.8024 | 294.352 | 90 | 0 | 60 | 0 | 12.7645 | 0.56215 | 0 | 11.9455 | 0.0029342 | 0 | 11.5034 | 0.002211 | 11.1605 | 11.1594 | 25061 | 29.2912 | 15340.3 | 14990.8 | 14689.7 | 0 | 0 | 14686.6 | 523.078 | 0 | 0 | 0 | 14686.6 | 0 | 660 | 0 | 0
4268 | 2001-06-27 19:00 | 0 | 13 | 0 | 28.63 | 7 | 0
4269 | 2001-06-27 20:00 | 0 | 0 | 0 | 27.54 | 7 | 0
4270 | 2001-06-27 21:00 | 0 | 0 | 0 | 26.46 | 6.4 | 0
4271 | 2001-06-27 22:00 | 0 | 0 | 0 | 25.37 | 6.4 | 0
4272 | 2001-06-27 23:00 | 0 | 0 | 0 | 24.36 | 6.4 | 0
4273 | 2001-06-28 | 0 | 0 | 0 | 23.34 | 5.25 | 0
4274 | 2001-06-28 01:00 | 0 | 0 | 0 | 22.33 | 5.25 | 0
4275 | 2001-06-28 02:00 | 0 | 0 | 0 | 21.4 | 5.25 | 0
4276 | 2001-06-28 03:00 | 0 | 0 | 0 | 20.46 | 4.47 | 0
4277 | 2001-06-28 04:00 | 3 | 72 | 1 | 19.53 | 4.47 | 0 | -2.4706 | 59.3627 | 90 | 0 | 3 | 0 | 0.72671 | 0.028108 | 0 | 0.68009 | 0 | 0 | 0.65492 | 0 | 0.63527 | 0.63525 | 1426.6 | 19.5448 | 98.7083 | 98.0701 | 97.3897 | 0 | 0 | 97.3858 | 97.9158 | 0 | 0 | 0 | 97.3858 | 0 | 660 | 0 | 0
4278 | 2001-06-28 05:00 | 113 | 464 | 43 | 20.07 | 4.47 | 0 | 8.58 | 67.6077 | 90 | 0 | 113 | 0 | 32.7376 | 1.0587 | 0 | 30.6371 | 0.0055262 | 0 | 29.5032 | 0.0041641 | 28.6222 | 28.621 | 64275.2 | 20.738 | 47750.5 | 48854 | 47665.9 | 0 | 0 | 47641.8 | 611.184 | 0 | 0 | 0 | 4128.41 | 43513.4 | 660 | 41973.5 | 41134.0469
4279 | 2001-06-28 06:00 | 318 | 728 | 65 | 20.6 | 2.86 | 0 | 20.2787 | 75.1296 | 77.7382 | 0 | 318 | 155.031 | 60.4239 | 2.9794 | 153.799 | 56.547 | 0.015551 | 125.28 | 54.4542 | 0.011718 | 174.354 | 174.346 | 391538 | 25.124 | 352703 | 352443 | 338782 | 0 | 0 | 337779 | 673.149 | 0 | 0 | 0 | 419.024 | 337360 | 677.231 | 330918 | 324299.9062
4280 | 2001-06-28 07:00 | 528 | 838 | 79 | 21.14 | 2.86 | 0 | 32.3868 | 82.4798 | 63.9765 | 0 | 528 | 367.779 | 78.8091 | 4.947 | 367.779 | 73.7526 | 0.025821 | 344.255 | 71.023 | 0.019457 | 402.839 | 402.833 | 904660 | 31.5929 | 863737 | 838340 | 817478 | 0 | 0 | 812032 | 693.56 | 0 | 0 | 0 | 0 | 812032 | 693.56 | 800113 | 784111
4281 | 2001-06-28 08:00 | 719 | 896 | 89 | 22.97 | 2.86 | 0 | 44.7041 | 90.4087 | 50.232 | 0 | 719 | 572.893 | 91.4634 | 6.7365 | 572.893 | 85.5949 | 0.035162 | 556.758 | 82.4271 | 0.026495 | 620.035 | 620.036 | 1392440 | 39.0591 | 1365390 | 1282410 | 1249190 | 0 | 0 | 1236210 | 684.014 | 0 | 0 | 0 | 0 | 1236210 | 684.014 | 1217250 | 1192905.75
4282 | 2001-06-28 09:00 | 864 | 903 | 107 | 24.81 | 1.63 | 0 | 56.9916 | 100.381 | 36.7257 | 0 | 864 | 723.525 | 109.719 | 8.095 | 723.525 | 102.679 | 0.042253 | 714.566 | 98.879 | 0.031839 | 789.072 | 789.065 | 1772040 | 47.035 | 1761690 | 1595940 | 1561470 | 0 | 0 | 1540000 | 662.326 | 0 | 0 | 0 | -20.965 | 1540020 | 662.544 | 1514670 | 1484378
4283 | 2001-06-28 10:00 | 991 | 953 | 103 | 26.65 | 1.63 | 0 | 68.726 | 116.594 | 24.0499 | 0 | 991 | 870.214 | 105.556 | 9.2849 | 870.214 | 98.783 | 0.048464 | 866.078 | 95.1271 | 0.036519 | 932.404 | 932.396 | 2093930 | 52.9121 | 2100000 | 1851540 | 1810150 | 0 | 0 | 1780190 | 648.215 | 0 | 0 | 0 | 6545.65 | 1773640 | 660 | 1740410 | 1705603.5
4284 | 2001-06-28 11:00 | 1045 | 960 | 109 | 28.11 | 1.63 | 0 | 77.6566 | 154.827 | 14.7332 | 0 | 1045 | 926.646 | 110.617 | 9.7908 | 926.646 | 103.52 | 0.051105 | 925.07 | 99.6883 | 0.038509 | 994.053 | 994.047 | 2232370 | 56.1086 | 2245880 | 1950300 | 1905160 | 0 | 0 | 1871310 | 640.629 | 0 | 0 | 0 | 21759.4 | 1849550 | 660 | 1813490 | 1777219.875
4285 | 2001-06-28 12:00 | 1030 | 949 | 110 | 29.58 | 2.11 | 0 | 76.073 | 218.184 | 16.3381 | 0 | 1030 | 909.588 | 111.754 | 9.6503 | 909.588 | 104.584 | 0.050371 | 907.674 | 100.713 | 0.037956 | 978.173 | 978.166 | 2196710 | 56.2609 | 2208290 | 1915890 | 1873400 | 0 | 0 | 1840310 | 637.655 | 0 | 0 | 0 | 24604.4 | 1815700 | 660 | 1780920 | 1745299.25
4286 | 2001-06-28 13:00 | 957 | 930 | 108 | 31.05 | 2.11 | 0 | 65.985 | 248.393 | 26.9764 | 0 | 957 | 828.324 | 110.568 | 8.9663 | 828.324 | 103.474 | 0.046801 | 823.267 | 99.6443 | 0.035266 | 895.259 | 895.253 | 2010510 | 55.4693 | 2012190 | 1751050 | 1714160 | 0 | 0 | 1686400 | 637.724 | 0 | 0 | 0 | 23027.2 | 1663370 | 660 | 1634040 | 1601360.875
4287 | 2001-06-28 14:00 | 845 | 926 | 96 | 31.59 | 2.11 | 0 | 54.0259 | 262.35 | 39.9589 | 0 | 845 | 709.409 | 98.9353 | 7.917 | 709.409 | 92.5875 | 0.041324 | 698.604 | 89.1609 | 0.031138 | 764.162 | 764.16 | 1716110 | 52.4335 | 1703090 | 1502240 | 1468460 | 0 | 0 | 1448440 | 644.971 | 0 | 0 | 0 | 9723.76 | 1438720 | 659.999 | 1416230 | 1387903.5
4288 | 2001-06-28 15:00 | 668 | 872 | 88 | 32.14 | 3.7 | 0 | 41.7 | 271.608 | 53.5551 | 0 | 668 | 517.939 | 90.134 | 6.2586 | 517.939 | 84.3508 | 0.032668 | 500.242 | 81.229 | 0.024616 | 564.05 | 564.046 | 1266700 | 45.9859 | 1235070 | 1121580 | 1095100 | 0 | 0 | 1084290 | 657.433 | 0 | 0 | 0 | 206.438 | 1084080 | 660 | 1069440 | 1048051.625
4289 | 2001-06-28 16:00 | 471 | 807 | 74 | 32.68 | 3.7 | 0 | 29.4125 | 279.302 | 67.3207 | 0 | 471 | 311.697 | 72.9196 | 4.4129 | 311.697 | 68.241 | 0.023034 | 286.862 | 65.7154 | 0.017357 | 342.017 | 342.012 | 768070 | 41.0755 | 725575 | 672445 | 656962 | 0 | 0 | 653010 | 655.112 | 0 | 0 | 0 | 403.595 | 652607 | 660 | 644123 | 631240.4375
4290 | 2001-06-28 17:00 | 254 | 644 | 61 | 32.3 | 3.7 | 0 | 17.3816 | 286.636 | 81.0669 | 0 | 254 | 100.32 | 53.03 | 2.3798 | 100.32 | 49.6275 | 0.012422 | 73.0333 | 47.7908 | 0.00936 | 117.208 | 117.207 | 263217 | 35.1771 | 229522 | 217822 | 212713 | 0 | 0 | 212260 | 628.877 | 0 | 0 | 0 | 6909.98 | 205350 | 660 | 200077 | 196075.75
4291 | 2001-06-28 18:00 | 59 | 429 | 14 | 31.92 | 4.27 | 0 | 5.8117 | 294.284 | 90 | 0 | 59 | 0 | 11.9393 | 0.55278 | 0 | 11.1733 | 0.0028854 | 0 | 10.7598 | 0.0021742 | 10.4391 | 10.439 | 23443.3 | 32.1668 | 14080.1 | 13546.2 | 13285.1 | 0 | 0 | 13282.4 | 508.681 | 0 | 0 | 0 | 13282.4 | 0 | 660 | 0 | 0
4292 | 2001-06-28 19:00 | 0 | 13 | 0 | 31.54 | 4.27 | 0
4293 | 2001-06-28 20:00 | 0 | 0 | 0 | 30.42 | 4.27 | 0
4294 | 2001-06-28 21:00 | 0 | 0 | 0 | 29.29 | 5.18 | 0
4295 | 2001-06-28 22:00 | 0 | 0 | 0 | 28.17 | 5.18 | 0
4296 | 2001-06-28 23:00 | 0 | 0 | 0 | 27.19 | 5.18 | 0
4297 | 2001-06-29 | 0 | 0 | 0 | 26.22 | 4.93 | 0
4298 | 2001-06-29 01:00 | 0 | 0 | 0 | 25.24 | 4.93 | 0
4299 | 2001-06-29 02:00 | 0 | 0 | 0 | 24.29 | 4.93 | 0
4300 | 2001-06-29 03:00 | 0 | 0 | 0 | 23.35 | 5.15 | 0
4301 | 2001-06-29 04:00 | 3 | 70 | 1 | 22.4 | 5.15 | 0 | -2.54 | 59.3739 | 90 | 0 | 3 | 0 | 0.72719 | 0.028108 | 0 | 0.68054 | 0 | 0 | 0.65535 | 0 | 0.63569 | 0.63566 | 1427.53 | 22.4142 | 98.83 | 98.5269 | 97.8655 | 0 | 0 | 97.8615 | 97.9723 | 0 | 0 | 0 | 97.8615 | 0 | 660 | 0 | 0
4302 | 2001-06-29 05:00 | 113 | 467 | 43 | 22.8 | 5.15 | 0 | 8.5119 | 67.626 | 90 | 0 | 113 | 0 | 32.8139 | 1.0587 | 0 | 30.7085 | 0.0055262 | 0 | 29.572 | 0.0041641 | 28.6889 | 28.6878 | 64425.7 | 23.4405 | 47879.3 | 48284.9 | 47165.8 | 0 | 0 | 47141.4 | 601.501 | 0 | 0 | 0 | 6417.83 | 40723.6 | 660 | 39275.6 | 38490.1328
4303 | 2001-06-29 06:00 | 317 | 727 | 65 | 23.2 | 2.95 | 0 | 20.2119 | 75.1543 | 77.7892 | 0 | 317 | 154.273 | 60.4244 | 2.97 | 152.949 | 56.5475 | 0.015503 | 124.44 | 54.4547 | 0.011681 | 173.539 | 173.532 | 389709 | 27.6761 | 350936 | 346382 | 333044 | 0 | 0 | 332043 | 662.099 | 0 | 0 | 0 | 988.662 | 331055 | 669.76 | 324803 | 318307.0625
4304 | 2001-06-29 07:00 | 527 | 838 | 79 | 23.61 | 2.95 | 0 | 32.321 | 82.5111 | 64.0223 | 0 | 527 | 367.023 | 78.8201 | 4.9376 | 367.023 | 73.7628 | 0.025773 | 343.479 | 71.0329 | 0.01942 | 402.095 | 402.091 | 902992 | 33.9816 | 862042 | 827463 | 806759 | 0 | 0 | 801338 | 686.103 | 0 | 0 | 0 | 0 | 801338 | 686.103 | 789875 | 774077.125
4305 | 2001-06-29 08:00 | 709 | 838 | 120 | 25.72 | 2.95 | 0 | 44.6387 | 90.4478 | 50.2713 | 0 | 709 | 535.786 | 122.684 | 6.6428 | 535.786 | 114.812 | 0.034673 | 520.661 | 110.563 | 0.026127 | 612.313 | 612.312 | 1375100 | 41.5141 | 1347390 | 1250940 | 1219240 | 0 | 0 | 1206580 | 675.5 | 0 | 0 | 0 | 0 | 1206580 | 675.5 | 1188650 | 1164879.75
4306 | 2001-06-29 09:00 | 833 | 797 | 165 | 27.83 | 3.07 | 0 | 56.9252 | 100.429 | 36.7554 | 0 | 833 | 638.695 | 169.562 | 7.8046 | 638.695 | 158.683 | 0.040737 | 630.771 | 152.81 | 0.030696 | 760.103 | 760.095 | 1706990 | 47.2808 | 1693530 | 1531950 | 1494740 | 0 | 0 | 1475050 | 662.528 | 0 | 0 | 0 | -23.2023 | 1475080 | 662.765 | 1451590 | 1422557.625
4307 | 2001-06-29 10:00 | 974 | 885 | 150 | 29.95 | 3.07 | 0 | 68.6564 | 116.638 | 24.0611 | 0 | 974 | 807.808 | 150.388 | 9.1256 | 807.808 | 140.739 | 0.047633 | 803.964 | 135.53 | 0.035892 | 911.344 | 911.333 | 2046620 | 53.271 | 2050190 | 1804090 | 1764110 | 0 | 0 | 1735420 | 645.324 | 0 | 0 | 0 | 8665.82 | 1726750 | 660 | 1695210 | 1661301.5
4308 | 2001-06-29 11:00 | 1038 | 950 | 112 | 31.44 | 3.07 | 0 | 77.5883 | 154.726 | 14.7004 | 0 | 1038 | 917.123 | 113.545 | 9.7253 | 917.123 | 106.26 | 0.050763 | 915.571 | 102.328 | 0.038251 | 987.399 | 987.39 | 2217420 | 56.7073 | 2230110 | 1930750 | 1890460 | 0 | 0 | 1856650 | 636.304 | 0 | 0 | 0 | 29364.4 | 1827290 | 660 | 1792070 | 1756230.25
4309 | 2001-06-29 12:00 | 1022 | 934 | 117 | 32.93 | 3.13 | 0 | 76.0525 | 217.898 | 16.2666 | 0 | 1022 | 895.164 | 118.521 | 9.5753 | 895.164 | 110.917 | 0.04998 | 893.297 | 106.812 | 0.037661 | 970.142 | 970.141 | 2178700 | 57.6575 | 2189300 | 1885970 | 1842170 | 0 | 0 | 1809940 | 635.091 | 0 | 0 | 0 | 35801.9 | 1774140 | 660 | 1740890 | 1706070.625
4310 | 2001-06-29 13:00 | 970 | 949 | 103 | 34.43 | 3.13 | 0 | 65.9927 | 248.217 | 26.9105 | 0 | 970 | 846.33 | 105.728 | 9.0881 | 846.33 | 98.9441 | 0.047437 | 841.191 | 95.2823 | 0.035745 | 908.414 | 908.41 | 2040050 | 57.584 | 2043270 | 1759520 | 1721210 | 0 | 0 | 1692710 | 631.856 | 0 | 0 | 0 | 39633.6 | 1653080 | 660 | 1624100 | 1591618
4311 | 2001-06-29 14:00 | 842 | 877 | 132 | 34.58 | 3.13 | 0 | 54.0412 | 262.23 | 39.9012 | 0 | 842 | 672.907 | 133.5 | 7.8889 | 672.907 | 124.934 | 0.041177 | 662.695 | 120.311 | 0.031028 | 759.545 | 759.539 | 1705730 | 53.9395 | 1692220 | 1481370 | 1448200 | 0 | 0 | 1428360 | 638.682 | 0 | 0 | 0 | 17640.6 | 1410720 | 660 | 1388900 | 1361121.25
4312 | 2001-06-29 15:00 | 628 | 706 | 158 | 34.73 | 4.62 | 0 | 41.7163 | 271.513 | 53.5042 | 0 | 628 | 420.08 | 157.849 | 5.8839 | 420.08 | 147.721 | 0.030712 | 405.769 | 142.254 | 0.023142 | 531.605 | 531.595 | 1193830 | 47.0156 | 1159830 | 1047380 | 1022600 | 0 | 0 | 1013020 | 652.201 | 0 | 0 | 0 | 2006.73 | 1011020 | 659.999 | 997806 | 977849.4375
4313 | 2001-06-29 16:00 | 476 | 733 | 115 | 34.88 | 4.62 | 0 | 29.4269 | 279.221 | 67.2756 | 0 | 476 | 283.839 | 110.254 | 4.4597 | 283.839 | 103.18 | 0.023278 | 261.293 | 99.361 | 0.017541 | 349.851 | 349.845 | 785663 | 42.9652 | 743301 | 682510 | 666781 | 0 | 0 | 662638 | 649.451 | 0 | 0 | 0 | 2084.95 | 660553 | 660 | 651966 | 638926.625
4314 | 2001-06-29 17:00 | 249 | 609 | 66 | 34.61 | 4.62 | 0 | 17.3921 | 286.56 | 81.0278 | 0 | 249 | 95.4796 | 57.5809 | 2.3329 | 95.4796 | 53.8864 | 0.012177 | 69.6423 | 51.8921 | 0.0091757 | 117.897 | 117.896 | 264764 | 37.3347 | 230988 | 216699 | 211660 | 0 | 0 | 211201 | 621.504 | 0 | 0 | 0 | 11099.3 | 200102 | 660 | 194900 | 191002.2656
4315 | 2001-06-29 18:00 | 58 | 406 | 15 | 34.33 | 5.99 | 0 | 5.8165 | 294.211 | 90 | 0 | 58 | 0 | 12.7641 | 0.54341 | 0 | 11.9451 | 0.0028364 | 0 | 11.503 | 0.0021373 | 11.16 | 11.1596 | 25061.8 | 34.566 | 15341 | 14551.8 | 14268.8 | 0 | 0 | 14265.6 | 504.49 | 0 | 0 | 0 | 14265.6 | 0 | 660 | 0 | 0
4316 | 2001-06-29 19:00 | 0 | 13 | 0 | 34.05 | 5.99 | 0
4317 | 2001-06-29 20:00 | 0 | 0 | 0 | 33.05 | 5.99 | 0
4318 | 2001-06-29 21:00 | 0 | 0 | 0 | 32.05 | 5.98 | 0
4319 | 2001-06-29 22:00 | 0 | 0 | 0 | 31.05 | 5.98 | 0
4320 | 2001-06-29 23:00 | 0 | 0 | 0 | 30.16 | 5.98 | 0
4321 | 2001-06-30 | 0 | 0 | 0 | 29.27 | 6.99 | 0
4322 | 2001-06-30 01:00 | 0 | 0 | 0 | 28.38 | 6.99 | 0
4323 | 2001-06-30 02:00 | 0 | 0 | 0 | 27.68 | 6.99 | 0
4324 | 2001-06-30 03:00 | 0 | 0 | 0 | 26.98 | 6.85 | 0
4325 | 2001-06-30 04:00 | 3 | 67 | 1 | 26.27 | 6.85 | 0 | -2.6131 | 59.3909 | 90 | 0 | 3 | 0 | 0.7277 | 0.028108 | 0 | 0.68101 | 0 | 0 | 0.65581 | 0 | 0.63613 | 0.63609 | 1428.51 | 26.2827 | 98.9605 | 99.1104 | 98.4705 | 0 | 0 | 98.4664 | 98.0563 | 0 | 0 | 0 | 98.4664 | 0 | 660 | 0 | 0
4326 | 2001-06-30 05:00 | 110 | 451 | 43 | 26.46 | 6.85 | 0 | 8.4406 | 67.6504 | 90 | 0 | 110 | 0 | 32.8945 | 1.0306 | 0 | 30.784 | 0.0053795 | 0 | 29.6447 | 0.0040535 | 28.7593 | 28.758 | 64583.1 | 27.0355 | 48014.1 | 47478.2 | 46400.4 | 0 | 0 | 46375.7 | 588.62 | 0 | 0 | 0 | 10549.5 | 35826.2 | 660 | 34541.9 | 33851.0391
4327 | 2001-06-30 06:00 | 315 | 726 | 64 | 26.65 | 3.81 | 0 | 20.1424 | 75.1856 | 77.8401 | 0 | 315 | 153.536 | 59.4883 | 2.9513 | 152.115 | 55.6715 | 0.015405 | 123.613 | 53.6111 | 0.011608 | 171.919 | 171.914 | 386075 | 30.8396 | 347418 | 337607 | 324837 | 0 | 0 | 323854 | 652.043 | 0 | 0 | 0 | 2305.74 | 321549 | 661.631 | 315502 | 309192.3125
4328 | 2001-06-30 07:00 | 526 | 838 | 78 | 26.84 | 3.81 | 0 | 32.2529 | 82.5499 | 64.0673 | 0 | 526 | 367.122 | 78.7592 | 4.9282 | 367.122 | 73.7059 | 0.025724 | 343.504 | 70.9781 | 0.019383 | 402.066 | 402.061 | 902923 | 36.6384 | 861971 | 817095 | 797443 | 0 | 0 | 791984 | 675.992 | 0 | 0 | 0 | 0 | 791984 | 675.992 | 781055 | 765434.25
4329 | 2001-06-30 08:00 | 719 | 898 | 89 | 29.01 | 3.81 | 0 | 44.571 | 90.4959 | 50.309 | 0 | 719 | 573.313 | 91.5026 | 6.7365 | 573.313 | 85.6316 | 0.035162 | 557.094 | 82.4625 | 0.026495 | 620.395 | 620.392 | 1393240 | 44.1292 | 1366220 | 1252840 | 1222270 | 0 | 0 | 1209230 | 667.359 | 0 | 0 | 0 | 0 | 1209230 | 667.359 | 1191640 | 1167805.625
4330 | 2001-06-30 09:00 | 879 | 933 | 98 | 31.18 | 4.68 | 0 | 56.8564 | 100.488 | 36.7825 | 0 | 879 | 747.058 | 101.007 | 8.2355 | 747.058 | 94.5266 | 0.042987 | 737.773 | 91.0282 | 0.032391 | 803.969 | 803.968 | 1805510 | 49.6877 | 1796800 | 1607320 | 1569900 | 0 | 0 | 1547840 | 656.498 | 0 | 0 | 0 | 676.508 | 1547160 | 660 | 1521680 | 1491245.375
4331 | 2001-06-30 10:00 | 990 | 953 | 103 | 33.36 | 4.68 | 0 | 68.5833 | 116.698 | 24.0683 | 0 | 990 | 869.955 | 105.623 | 9.2755 | 869.955 | 98.8456 | 0.048415 | 865.813 | 95.1874 | 0.036482 | 932.206 | 932.201 | 2093480 | 54.8197 | 2099520 | 1833860 | 1793200 | 0 | 0 | 1763220 | 642.139 | 0 | 0 | 0 | 16255.6 | 1746960 | 660 | 1714700 | 1680402.875
4332 | 2001-06-30 11:00 | 1045 | 960 | 109 | 34.14 | 4.68 | 0 | 77.5141 | 154.641 | 14.6614 | 0 | 1045 | 927.458 | 110.696 | 9.7908 | 927.458 | 103.594 | 0.051105 | 925.897 | 99.7599 | 0.038509 | 994.924 | 994.921 | 2234340 | 57.0435 | 2247960 | 1943130 | 1901640 | 0 | 0 | 1867380 | 635.681 | 0 | 0 | 0 | 31546.7 | 1835830 | 660 | 1800290 | 1764286.75
4333 | 2001-06-30 12:00 | 1038 | 960 | 108 | 34.92 | 5.43 | 0 | 76.0256 | 217.601 | 16.1899 | 0 | 1038 | 920.358 | 109.89 | 9.7253 | 920.358 | 102.839 | 0.050763 | 918.457 | 99.033 | 0.038251 | 987.003 | 987.001 | 2216550 | 56.5604 | 2229200 | 1931430 | 1888490 | 0 | 0 | 1854940 | 638.052 | 0 | 0 | 0 | 26790.7 | 1828150 | 660 | 1792900 | 1757040.375
4334 | 2001-06-30 13:00 | 969 | 949 | 102 | 35.7 | 5.43 | 0 | 65.9957 | 248.028 | 26.8424 | 0 | 969 | 846.82 | 104.782 | 9.0788 | 846.82 | 98.059 | 0.047388 | 841.707 | 94.4299 | 0.035708 | 908.087 | 908.082 | 2039320 | 55.6101 | 2042500 | 1776540 | 1736950 | 0 | 0 | 1708500 | 638.232 | 0 | 0 | 0 | 22357.3 | 1686140 | 660 | 1656030 | 1622905.5
4335 | 2001-06-30 14:00 | 836 | 909 | 100 | 35.89 | 5.43 | 0 | 54.0525 | 262.1 | 39.8429 | 0 | 836 | 698.042 | 102.901 | 7.8327 | 698.042 | 96.2984 | 0.040884 | 687.487 | 92.7344 | 0.030807 | 756.845 | 756.844 | 1699680 | 52.4841 | 1685890 | 1486630 | 1451340 | 0 | 0 | 1431790 | 644.953 | 0 | 0 | 0 | 9329.73 | 1422460 | 660 | 1400370 | 1372358.875
4336 | 2001-06-30 15:00 | 671 | 838 | 113 | 36.07 | 7.63 | 0 | 41.7288 | 271.411 | 53.4534 | 0 | 671 | 499.208 | 115.034 | 6.2867 | 499.208 | 107.653 | 0.032815 | 482.251 | 103.669 | 0.024727 | 568.366 | 568.361 | 1276400 | 46.8954 | 1245100 | 1125750 | 1098840 | 0 | 0 | 1087870 | 654.794 | 0 | 0 | 0 | 778.18 | 1087090 | 660 | 1072390 | 1050943.25
4337 | 2001-06-30 16:00 | 450 | 737 | 87 | 36.26 | 7.63 | 0 | 29.4374 | 279.133 | 67.2316 | 0 | 450 | 285.843 | 85.4613 | 4.2161 | 285.843 | 79.978 | 0.022007 | 263.205 | 77.018 | 0.016583 | 330.033 | 330.029 | 741161 | 42.546 | 698510 | 642444 | 627548 | 0 | 0 | 623886 | 649.564 | 0 | 0 | 0 | 2316.17 | 621569 | 660 | 613489 | 601219.25
4338 | 2001-06-30 17:00 | 247 | 608 | 64 | 35.73 | 7.63 | 0 | 17.3984 | 286.479 | 80.9903 | 0 | 247 | 95.8417 | 55.8266 | 2.3142 | 95.8417 | 52.2447 | 0.012079 | 70.0333 | 50.3112 | 0.009102 | 116.743 | 116.74 | 262168 | 37.9535 | 228529 | 213662 | 208742 | 0 | 0 | 208293 | 619.145 | 0 | 0 | 0 | 12781.3 | 195511 | 660 | 190375 | 186567.8594
4339 | 2001-06-30 18:00 | 58 | 405 | 15 | 35.2 | 7.01 | 0 | 5.8166 | 294.132 | 90 | 0 | 58 | 0 | 12.7641 | 0.54341 | 0 | 11.9451 | 0.0028364 | 0 | 11.503 | 0.0021373 | 11.16 | 11.1593 | 25061 | 35.4211 | 15340.3 | 14478.7 | 14205.6 | 0 | 0 | 14202.4 | 501.409 | 0 | 0 | 0 | 14202.4 | 0 | 660 | 0 | 0
4340 | 2001-06-30 19:00 | 0 | 13 | 0 | 34.67 | 7.01 | 0
4341 | 2001-06-30 20:00 | 0 | 0 | 0 | 33.73 | 7.01 | 0
4342 | 2001-06-30 21:00 | 0 | 0 | 0 | 32.99 | 7.31 | 0
4343 | 2001-06-30 22:00 | 0 | 0 | 0 | 31.76 | 7.1 | 0
4344 | 2001-06-30 23:00 | 0 | 0 | 0 | 30.52 | 6.9 | 0
4345 | 2002-07-01 | 0 | 0 | 0 | 29.29 | 6.69 | 0
4346 | 2002-07-01 01:00 | 0 | 0 | 0 | 28.05 | 6.49 | 0
4347 | 2002-07-01 02:00 | 0 | 0 | 0 | 26.82 | 6.28 | 0
4348 | 2002-07-01 03:00 | 0 | 0 | 0 | 25.08 | 5.58 | 0
4349 | 2002-07-01 04:00 | 2 | 33 | 1 | 24.3 | 5.58 | 0 | -2.6709 | 59.4066 | 90 | 0 | 2 | 0 | 0.69369 | 0.018738 | 0 | 0.64918 | 0 | 0 | 0.62515 | 0 | 0.6064 | 0.60638 | 1361.77 | 24.3132 | 89.9539 | 89.8805 | 89.2127 | 0 | 0 | 89.2092 | 94.1534 | 0 | 0 | 0 | 89.2092 | 0 | 660 | 0 | 0
4350 | 2002-07-01 05:00 | 94 | 228 | 60 | 24.55 | 5.58 | 0 | 8.3844 | 67.672 | 90 | 0 | 94 | 0 | 45.7086 | 0.88071 | 0 | 42.7759 | 0.004597 | 0 | 41.1928 | 0.0034639 | 39.9604 | 39.959 | 89738 | 25.4177 | 69874.4 | 69715.6 | 67992.1 | 0 | 0 | 67943.3 | 612.685 | 0 | 0 | 0 | 5911.31 | 62032 | 660 | 59905.7 | 58707.6094
4351 | 2002-07-01 06:00 | 207 | 185 | 143 | 24.81 | 2.57 | 0 | 20.0878 | 75.2128 | 77.879 | 0 | 207 | 39.1269 | 126.117 | 1.9394 | 38.7468 | 118.026 | 0.010123 | 31.4577 | 113.658 | 0.007628 | 140.769 | 140.761 | 316115 | 28.5336 | 279939 | 275079 | 266026 | 0 | 0 | 265384 | 660.151 | 0 | 0 | 0 | 65.0126 | 265319 | 661.664 | 259427 | 254238.0938
4352 | 2002-07-01 07:00 | 443 | 501 | 176 | 25.06 | 2.57 | 0 | 32.1994 | 82.5833 | 64.1014 | 0 | 443 | 218.854 | 166.447 | 4.1506 | 218.854 | 155.767 | 0.021664 | 204.743 | 150.003 | 0.016325 | 344.119 | 344.113 | 772788 | 34.1629 | 730333 | 700015 | 682728 | 0 | 0 | 678774 | 680.03 | 0 | 0 | 0 | 0 | 678774 | 680.03 | 669270 | 655884.5
4353 | 2002-07-01 08:00 | 657 | 667 | 189 | 27.39 | 2.57 | 0 | 44.518 | 90.537 | 50.3373 | 0 | 657 | 426.037 | 188.844 | 6.1556 | 426.037 | 176.727 | 0.03213 | 413.965 | 170.187 | 0.024211 | 566.65 | 566.645 | 1272540 | 42.3795 | 1241110 | 1146950 | 1119500 | 0 | 0 | 1108590 | 668.738 | 0 | 0 | 0 | 0 | 1108590 | 668.738 | 1093020 | 1071162.125
4354 | 2002-07-01 09:00 | 878 | 864 | 155 | 29.73 | 2.09 | 0 | 56.8023 | 100.539 | 36.8022 | 0 | 878 | 691.828 | 160.035 | 8.2262 | 691.828 | 149.767 | 0.042938 | 683.218 | 144.224 | 0.032355 | 802.65 | 802.641 | 1802520 | 51.6524 | 1793670 | 1589030 | 1551410 | 0 | 0 | 1529390 | 649.266 | 0 | 0 | 0 | 4912.85 | 1524480 | 660 | 1499720 | 1469720.625
4355 | 2002-07-01 10:00 | 969 | 878 | 152 | 32.06 | 2.09 | 0 | 68.5256 | 116.751 | 24.0721 | 0 | 969 | 801.593 | 152.337 | 9.0788 | 801.593 | 142.563 | 0.047388 | 797.776 | 137.287 | 0.035708 | 907.045 | 907.041 | 2036990 | 56.8339 | 2040050 | 1763370 | 1722440 | 0 | 0 | 1694160 | 634.674 | 0 | 0 | 0 | 30878 | 1663280 | 660 | 1633950 | 1601270.875
4356 | 2002-07-01 11:00 | 1045 | 917 | 152 | 33.05 | 2.09 | 0 | 77.4542 | 154.584 | 14.6285 | 0 | 1045 | 885.188 | 151.404 | 9.7908 | 885.188 | 141.69 | 0.051105 | 883.705 | 136.446 | 0.038509 | 989.584 | 989.583 | 2222350 | 60.0783 | 2235320 | 1902450 | 1863730 | 0 | 0 | 1829760 | 625.392 | 0 | 0 | 0 | 65791.7 | 1763960 | 660 | 1731080 | 1696462.25
4357 | 2002-07-01 12:00 | 1015 | 840 | 201 | 34.03 | 5.24 | 0 | 76.0018 | 217.367 | 16.1287 | 0 | 1015 | 805.893 | 207.088 | 9.5098 | 805.893 | 193.801 | 0.049638 | 804.242 | 186.628 | 0.037403 | 961.181 | 961.173 | 2158550 | 55.3652 | 2168070 | 1889180 | 1846780 | 0 | 0 | 1814910 | 640.297 | 0 | 0 | 0 | 18511.4 | 1796400 | 659.999 | 1762330 | 1727087.375
4358 | 2002-07-01 13:00 | 704 | 314 | 417 | 35.02 | 5.24 | 0 | 65.9958 | 247.877 | 26.789 | 0 | 704 | 280.452 | 411.499 | 6.5959 | 280.452 | 385.096 | 0.034429 | 278.766 | 370.844 | 0.025943 | 630.146 | 630.127 | 1415110 | 49.0069 | 1388960 | 1243870 | 1214380 | 0 | 0 | 1200880 | 650.936 | 0 | 0 | 0 | 2885.79 | 1197990 | 660 | 1180990 | 1157372.25
4359 | 2002-07-01 14:00 | 580 | 251 | 377 | 35.54 | 5.24 | 0 | 54.0593 | 261.996 | 39.7978 | 0 | 580 | 192.641 | 366.078 | 5.4341 | 192.641 | 342.59 | 0.028364 | 189.736 | 329.911 | 0.021373 | 504.078 | 504.057 | 1131990 | 46.7286 | 1096170 | 990807 | 966641 | 0 | 0 | 958035 | 650.674 | 0 | 0 | 0 | 2270.67 | 955764 | 660 | 943339 | 924472.6875
4360 | 2002-07-01 15:00 | 676 | 749 | 177 | 36.06 | 6.65 | 0 | 41.7366 | 271.329 | 53.4146 | 0 | 676 | 446.764 | 175.93 | 6.3336 | 446.764 | 164.642 | 0.033059 | 431.623 | 158.548 | 0.024911 | 572.491 | 572.481 | 1285650 | 47.6645 | 1254670 | 1130170 | 1104160 | 0 | 0 | 1092970 | 651.847 | 0 | 0 | 0 | 2000.43 | 1090970 | 660 | 1076200 | 1054672.125
4361 | 2002-07-01 16:00 | 452 | 581 | 166 | 36.57 | 6.65 | 0 | 29.4435 | 279.062 | 67.1982 | 0 | 452 | 225.479 | 155.221 | 4.2349 | 225.479 | 145.262 | 0.022105 | 207.662 | 139.886 | 0.016656 | 337.138 | 337.133 | 757118 | 43.4039 | 714559 | 654468 | 638830 | 0 | 0 | 635017 | 647.929 | 0 | 0 | 0 | 3298.92 | 631718 | 660 | 623506 | 611035.8125
4362 | 2002-07-01 17:00 | 122 | 62 | 103 | 35.57 | 6.65 | 0 | 17.4012 | 286.414 | 80.9623 | 0 | 122 | 9.9799 | 103.254 | 1.143 | 9.9799 | 96.6293 | 0.0059663 | 7.3023 | 93.0531 | 0.0044957 | 97.3491 | 97.3461 | 218615 | 37.5433 | 187512 | 175510 | 171229 | 0 | 0 | 170921 | 613.569 | 0 | 0 | 0 | 15022.3 | 155899 | 660 | 151433 | 148404.4688
4363 | 2002-07-01 18:00 | 28 | 41 | 24 | 34.57 | 8.67 | 0 | 5.8146 | 294.07 | 90 | 0 | 28 | 0 | 20.9792 | 0.26234 | 0 | 19.6331 | 0.0013693 | 0 | 18.9065 | 0.0010318 | 18.3403 | 18.3391 | 41185.1 | 34.8972 | 28320.3 | 26760.7 | 26229.7 | 0 | 0 | 26220.2 | 535.392 | 0 | 0 | 0 | 26216.4 | 3.7647 | 660.349 | 3.6216 | 3.5492
4364 | 2002-07-01 19:00 | 0 | 1 | 0 | 33.57 | 8.67 | 0
4365 | 2002-07-01 20:00 | 0 | 0 | 0 | 32.28 | 8.67 | 0
4366 | 2002-07-01 21:00 | 0 | 0 | 0 | 31 | 7.37 | 0
4367 | 2002-07-01 22:00 | 0 | 0 | 0 | 29.72 | 7.37 | 0
4368 | 2002-07-01 23:00 | 0 | 0 | 0 | 28.65 | 7.37 | 0
4369 | 2002-07-02 | 0 | 0 | 0 | 27.58 | 7.87 | 0
4370 | 2002-07-02 01:00 | 0 | 0 | 0 | 26.51 | 7.87 | 0
4371 | 2002-07-02 02:00 | 0 | 0 | 0 | 26.36 | 7.87 | 0
4372 | 2002-07-02 03:00 | 0 | 0 | 0 | 26.21 | 9.04 | 0
4373 | 2002-07-02 04:00 | 2 | 40 | 1 | 26.07 | 9.04 | 0 | -2.7503 | 59.4338 | 90 | 0 | 2 | 0 | 0.69427 | 0.018738 | 0 | 0.64972 | 0 | 0 | 0.62567 | 0 | 0.6069 | 0.60688 | 1362.89 | 26.0806 | 90.0966 | 90.2116 | 89.5501 | 0 | 0 | 89.5465 | 94.2974 | 0 | 0 | 0 | 89.5465 | 0 | 660 | 0 | 0
4374 | 2002-07-02 05:00 | 95 | 280 | 54 | 26.26 | 9.04 | 0 | 8.3079 | 67.7072 | 90 | 0 | 95 | 0 | 40.8974 | 0.89008 | 0 | 38.2734 | 0.0046459 | 0 | 36.8569 | 0.0035008 | 35.7546 | 35.7534 | 80292.9 | 26.8834 | 61600.4 | 60969.3 | 59543.2 | 0 | 0 | 59504.3 | 601.368 | 0 | 0 | 0 | 8556.37 | 50947.9 | 660 | 49167.7 | 48184.3164
4375 | 2002-07-02 06:00 | 307 | 651 | 84 | 26.46 | 4.72 | 0 | 20.0138 | 75.2558 | 77.9294 | 0 | 307 | 136.256 | 75.8133 | 2.8763 | 134.834 | 70.949 | 0.015014 | 109.337 | 68.3232 | 0.011313 | 172.341 | 172.332 | 387015 | 30.4168 | 348319 | 339204 | 325561 | 0 | 0 | 324582 | 654.252 | 0 | 0 | 0 | 2473.89 | 322108 | 663.755 | 316010 | 309689.6875
4376 | 2002-07-02 07:00 | 494 | 742 | 99 | 26.65 | 4.72 | 0 | 32.1273 | 82.6353 | 64.1448 | 0 | 494 | 323.916 | 98.0952 | 4.6284 | 323.916 | 91.8012 | 0.024159 | 302.974 | 88.4037 | 0.018204 | 379.654 | 379.651 | 852604 | 35.367 | 810938 | 773173 | 753143 | 0 | 0 | 748341 | 680.609 | 0 | 0 | 0 | 0 | 748341 | 680.609 | 737841 | 723084.375
4377 | 2002-07-02 08:00 | 691 | 823 | 115 | 28.4 | 4.72 | 0 | 44.4465 | 90.6008 | 50.3721 | 0 | 691 | 524.635 | 117.908 | 6.4741 | 524.635 | 110.343 | 0.033793 | 509.739 | 106.259 | 0.025464 | 597.543 | 597.542 | 1341930 | 42.1199 | 1312970 | 1215320 | 1187550 | 0 | 0 | 1175410 | 672.127 | 0 | 0 | 0 | 0 | 1175410 | 672.127 | 1158310 | 1135139.625
4378 | 2002-07-02 09:00 | 863 | 929 | 86 | 30.14 | 7.57 | 0 | 56.7293 | 100.618 | 36.8248 | 0 | 863 | 743.901 | 89.2341 | 8.0856 | 743.901 | 83.5087 | 0.042204 | 734.63 | 80.4181 | 0.031802 | 790.628 | 790.624 | 1775540 | 45.256 | 1765370 | 1613030 | 1574090 | 0 | 0 | 1552900 | 671.727 | 0 | 0 | 0 | 0 | 1552900 | 671.727 | 1526820 | 1496283.375
4379 | 2002-07-02 10:00 | 975 | 948 | 94 | 31.88 | 7.57 | 0 | 68.4468 | 116.839 | 24.0723 | 0 | 975 | 864.854 | 96.8643 | 9.135 | 864.854 | 90.6493 | 0.047682 | 860.735 | 87.2945 | 0.035929 | 919.624 | 919.619 | 2065230 | 49.4623 | 2069770 | 1855730 | 1813500 | 0 | 0 | 1784410 | 659.246 | 0 | 0 | 0 | -44.2945 | 1784460 | 660.847 | 1750810 | 1715797
4380 | 2002-07-02 11:00 | 1030 | 955 | 100 | 32.5 | 7.57 | 0 | 77.3697 | 154.529 | 14.5785 | 0 | 1030 | 922.378 | 102.048 | 9.6503 | 922.378 | 95.5001 | 0.050371 | 920.844 | 91.9657 | 0.037956 | 982.462 | 982.46 | 2206360 | 51.2838 | 2218450 | 1972750 | 1926400 | 0 | 0 | 1893420 | 657.02 | 0 | 0 | 0 | 1069.38 | 1892350 | 660 | 1854650 | 1817556.625
4381 | 2002-07-02 12:00 | 1022 | 955 | 97 | 33.12 | 7.27 | 0 | 75.9634 | 217.051 | 16.0433 | 0 | 1022 | 916.335 | 99.2574 | 9.5753 | 916.335 | 92.8888 | 0.04998 | 914.478 | 89.4511 | 0.037661 | 973.848 | 973.843 | 2187000 | 52.0962 | 2198050 | 1946730 | 1900630 | 0 | 0 | 1868220 | 653.97 | 0 | 0 | 0 | 2516.6 | 1865700 | 660 | 1829030 | 1792448.5
4382 | 2002-07-02 13:00 | 955 | 944 | 93 | 33.74 | 7.27 | 0 | 65.9904 | 247.666 | 26.7172 | 0 | 955 | 842.9 | 96.0025 | 8.9476 | 842.9 | 89.8428 | 0.046704 | 837.862 | 86.5178 | 0.035192 | 896.683 | 896.679 | 2013710 | 51.2126 | 2015550 | 1791470 | 1751530 | 0 | 0 | 1723880 | 653.27 | 0 | 0 | 0 | 2332.54 | 1721550 | 660 | 1690190 | 1656388.625
4383 | 2002-07-02 14:00 | 833 | 922 | 86 | 33.76 | 7.27 | 0 | 54.0634 | 261.85 | 39.7384 | 0 | 833 | 709.454 | 89.2013 | 7.8046 | 709.454 | 83.4779 | 0.040737 | 698.796 | 80.3885 | 0.030696 | 755.839 | 755.836 | 1697420 | 48.4881 | 1683520 | 1514060 | 1478830 | 0 | 0 | 1459350 | 659.017 | 0 | 0 | 0 | 106.176 | 1459250 | 660.309 | 1436240 | 1407519.375
4384 | 2002-07-02 15:00 | 666 | 881 | 79 | 33.79 | 7.74 | 0 | 41.7422 | 271.214 | 53.3646 | 0 | 666 | 526.113 | 81.4788 | 6.2399 | 526.113 | 76.2509 | 0.03257 | 508.335 | 73.4289 | 0.024542 | 564.335 | 564.328 | 1267340 | 44.4642 | 1235730 | 1130590 | 1104310 | 0 | 0 | 1093500 | 662.481 | 0 | 0 | 0 | 0 | 1093500 | 662.481 | 1078550 | 1056975.375
4385 | 2002-07-02 16:00 | 469 | 787 | 82 | 33.81 | 7.74 | 0 | 29.4469 | 278.963 | 67.1561 | 0 | 469 | 305.608 | 80.7696 | 4.3942 | 305.608 | 75.5873 | 0.022936 | 281.529 | 72.7898 | 0.017283 | 343.706 | 343.701 | 771865 | 40.3111 | 729396 | 678593 | 662828 | 0 | 0 | 658851 | 658.438 | 0 | 0 | 0 | 38.2048 | 658813 | 660 | 650248 | 637243.5625
4386 | 2002-07-02 17:00 | 245 | 606 | 63 | 33.11 | 7.74 | 0 | 17.4 | 286.323 | 80.9279 | 0 | 245 | 95.9649 | 55.0179 | 2.2955 | 95.9649 | 51.4878 | 0.011982 | 70.3324 | 49.5823 | 0.0090283 | 116.326 | 116.323 | 261232 | 35.3102 | 227642 | 215876 | 211057 | 0 | 0 | 210610 | 627.945 | 0 | 0 | 0 | 7430.42 | 203180 | 660 | 197936 | 193977.3281
4387 | 2002-07-02 18:00 | 57 | 404 | 15 | 32.41 | 8.82 | 0 | 5.8065 | 293.983 | 90 | 0 | 57 | 0 | 12.7644 | 0.53405 | 0 | 11.9454 | 0.0027875 | 0 | 11.5033 | 0.0021005 | 11.1602 | 11.1595 | 25061.5 | 32.6073 | 15340.6 | 14715.9 | 14436.8 | 0 | 0 | 14433.7 | 511.34 | 0 | 0 | 0 | 14433.7 | 0 | 660 | 0 | 0
4388 | 2002-07-02 19:00 | 0 | 12 | 0 | 31.71 | 8.82 | 0
4389 | 2002-07-02 20:00 | 0 | 0 | 0 | 30.59 | 8.82 | 0
4390 | 2002-07-02 21:00 | 0 | 0 | 0 | 29.46 | 5.97 | 0
4391 | 2002-07-02 22:00 | 0 | 0 | 0 | 28.34 | 5.97 | 0
4392 | 2002-07-02 23:00 | 0 | 0 | 0 | 27.32 | 5.97 | 0
4393 | 2002-07-03 | 0 | 0 | 0 | 26.3 | 6.97 | 0
4394 | 2002-07-03 01:00 | 0 | 0 | 0 | 25.28 | 6.97 | 0
4395 | 2002-07-03 02:00 | 0 | 0 | 0 | 24.48 | 6.97 | 0
4396 | 2002-07-03 03:00 | 0 | 0 | 0 | 23.67 | 7.37 | 0
4397 | 2002-07-03 04:00 | 2 | 55 | 1 | 22.87 | 7.37 | 0 | -2.8331 | 59.4667 | 90 | 0 | 2 | 0 | 0.69487 | 0.018738 | 0 | 0.65028 | 0 | 0 | 0.62622 | 0 | 0.60743 | 0.6074 | 1364.08 | 22.8818 | 90.2552 | 90.0287 | 89.3536 | 0 | 0 | 89.35 | 94.3094 | 0 | 0 | 0 | 89.35 | 0 | 660 | 0 | 0
4398 | 2002-07-03 05:00 | 98 | 403 | 39 | 23.29 | 7.37 | 0 | 8.2285 | 67.7486 | 90 | 0 | 98 | 0 | 29.4017 | 0.91818 | 0 | 27.5152 | 0.0047926 | 0 | 26.4969 | 0.0036113 | 25.7055 | 25.7043 | 57725.3 | 23.7877 | 42164.8 | 42442.6 | 41465.9 | 0 | 0 | 41446.7 | 594.808 | 0 | 0 | 0 | 7489.87 | 33956.8 | 660 | 32735.6 | 32080.918
4399 | 2002-07-03 06:00 | 295 | 676 | 64 | 23.71 | 4.52 | 0 | 19.9373 | 75.3055 | 77.9793 | 0 | 295 | 141.086 | 59.5114 | 2.7639 | 139.477 | 55.6931 | 0.014427 | 112.965 | 53.6319 | 0.010871 | 161.61 | 161.598 | 362908 | 27.4691 | 325009 | 321085 | 307003 | 0 | 0 | 306152 | 662.057 | 0 | 0 | 0 | 1558.85 | 304593 | 669.939 | 298354 | 292386.4688
4400 | 2002-07-03 07:00 | 497 | 779 | 83 | 24.14 | 4.52 | 0 | 32.053 | 82.6948 | 64.1871 | 0 | 497 | 339.681 | 82.7618 | 4.6565 | 339.681 | 77.4516 | 0.024305 | 317.66 | 74.5852 | 0.018315 | 380.496 | 380.495 | 854495 | 32.9911 | 812851 | 783721 | 764060 | 0 | 0 | 759215 | 687.077 | 0 | 0 | 0 | 0 | 759215 | 687.077 | 748318 | 733351.4375
4401 | 2002-07-03 08:00 | 667 | 780 | 121 | 25.64 | 4.52 | 0 | 44.3729 | 90.6733 | 50.4052 | 0 | 667 | 497.616 | 123.781 | 6.2493 | 497.616 | 115.839 | 0.032619 | 483.459 | 111.552 | 0.024579 | 577.184 | 577.176 | 1296190 | 39.0664 | 1265580 | 1188210 | 1158870 | 0 | 0 | 1147650 | 682.848 | 0 | 0 | 0 | 0 | 1147650 | 682.848 | 1130600 | 1107986.125
4402 | 2002-07-03 09:00 | 819 | 806 | 146 | 27.14 | 1.49 | 0 | 56.6539 | 100.708 | 36.8448 | 0 | 819 | 644.721 | 151.422 | 7.6734 | 644.721 | 141.706 | 0.040052 | 636.675 | 136.462 | 0.03018 | 749.972 | 749.967 | 1684240 | 48.463 | 1669720 | 1501600 | 1468370 | 0 | 0 | 1449040 | 656.676 | 0 | 0 | 0 | 182.441 | 1448860 | 660 | 1426120 | 1397599.875
4403 | 2002-07-03 10:00 | 941 | 838 | 163 | 28.65 | 1.49 | 0 | 68.3647 | 116.942 | 24.0685 | 0 | 941 | 764.198 | 170.048 | 8.8164 | 764.198 | 159.137 | 0.046019 | 760.559 | 153.247 | 0.034676 | 886.426 | 886.416 | 1990670 | 53.8525 | 1991310 | 1746710 | 1708770 | 0 | 0 | 1681610 | 643.258 | 0 | 0 | 0 | 12880.6 | 1668730 | 660 | 1639220 | 1606433.125
4404 | 2002-07-03 11:00 | 1016 | 930 | 110 | 29.69 | 1.49 | 0 | 77.2794 | 154.491 | 14.5223 | 0 | 1016 | 899.122 | 111.8 | 9.5191 | 899.122 | 104.627 | 0.049687 | 897.638 | 100.755 | 0.03744 | 968.478 | 968.472 | 2174950 | 57.2255 | 2185350 | 1886590 | 1844470 | 0 | 0 | 1812150 | 635.097 | 0 | 0 | 0 | 33002.5 | 1779150 | 660 | 1745710 | 1710799.25
4405 | 2002-07-03 12:00 | 1022 | 955 | 97 | 30.74 | 1.28 | 0 | 75.9184 | 216.726 | 15.953 | 0 | 1022 | 916.93 | 99.3008 | 9.5753 | 916.93 | 92.9295 | 0.04998 | 915.093 | 89.4902 | 0.037661 | 974.483 | 974.474 | 2188410 | 58.8396 | 2199540 | 1883500 | 1842330 | 0 | 0 | 1809530 | 629.459 | 0 | 0 | 0 | 49670.4 | 1759860 | 660 | 1727130 | 1692584.75
4406 | 2002-07-03 13:00 | 951 | 939 | 94 | 31.79 | 1.28 | 0 | 65.9801 | 247.444 | 26.6435 | 0 | 951 | 838.619 | 97.0269 | 8.9101 | 838.619 | 90.8014 | 0.046508 | 833.638 | 87.4409 | 0.035045 | 893.481 | 893.478 | 2006520 | 57.554 | 2007980 | 1729010 | 1689410 | 0 | 0 | 1662020 | 632.731 | 0 | 0 | 0 | 38208.9 | 1623810 | 660 | 1595820 | 1563900.25
4407 | 2002-07-03 14:00 | 833 | 922 | 86 | 32.39 | 1.28 | 0 | 54.0633 | 261.694 | 39.6787 | 0 | 833 | 710.069 | 89.2364 | 7.8046 | 710.069 | 83.5108 | 0.040737 | 699.443 | 80.4201 | 0.030696 | 756.497 | 756.493 | 1698880 | 54.204 | 1685050 | 1473020 | 1439700 | 0 | 0 | 1420040 | 638.128 | 0 | 0 | 0 | 19457.2 | 1400580 | 660 | 1379010 | 1351430
4408 | 2002-07-03 15:00 | 663 | 874 | 81 | 32.99 | 4.57 | 0 | 41.7437 | 271.091 | 53.315 | 0 | 663 | 522.222 | 83.4739 | 6.2118 | 522.222 | 78.1181 | 0.032424 | 504.627 | 75.227 | 0.024432 | 562.482 | 562.479 | 1263180 | 46.0318 | 1231430 | 1118010 | 1091950 | 0 | 0 | 1081170 | 656.355 | 0 | 0 | 0 | 224.596 | 1080950 | 660 | 1066370 | 1045040.5
4409 | 2002-07-03 16:00 | 448 | 741 | 83 | 33.59 | 4.57 | 0 | 29.4461 | 278.857 | 67.1152 | 0 | 448 | 288.731 | 81.7811 | 4.1974 | 288.731 | 76.5339 | 0.021909 | 266.044 | 73.7014 | 0.016509 | 329.569 | 329.563 | 740114 | 41.2313 | 697458 | 645713 | 630882 | 0 | 0 | 627217 | 653.177 | 0 | 0 | 0 | 862.885 | 626354 | 660 | 618211 | 605847.1875
4410 | 2002-07-03 17:00 | 252 | 634 | 62 | 32.99 | 4.57 | 0 | 17.3943 | 286.227 | 80.8953 | 0 | 252 | 100.572 | 54.1715 | 2.361 | 100.572 | 50.6958 | 0.012324 | 73.8218 | 48.8196 | 0.0092863 | 118.971 | 118.972 | 267180 | 35.7485 | 233279 | 220730 | 215466 | 0 | 0 | 215002 | 629.35 | 0 | 0 | 0 | 7628.05 | 207374 | 660 | 202074 | 198032.625
4411 | 2002-07-03 18:00 | 59 | 423 | 15 | 32.38 | 7.69 | 0 | 5.7938 | 293.891 | 90 | 0 | 59 | 0 | 12.7647 | 0.55278 | 0 | 11.9457 | 0.0028854 | 0 | 11.5036 | 0.0021742 | 11.1606 | 11.1598 | 25062 | 32.5918 | 15341 | 14717.7 | 14445.9 | 0 | 0 | 14442.8 | 511.382 | 0 | 0 | 0 | 14442.8 | 0 | 660 | 0 | 0
4412 | 2002-07-03 19:00 | 0 | 13 | 0 | 31.78 | 7.69 | 0
4413 | 2002-07-03 20:00 | 0 | 0 | 0 | 30.46 | 7.69 | 0
4414 | 2002-07-03 21:00 | 0 | 0 | 0 | 29.14 | 8.7 | 0
4415 | 2002-07-03 22:00 | 0 | 0 | 0 | 27.81 | 8.7 | 0
4416 | 2002-07-03 23:00 | 0 | 0 | 0 | 26.79 | 8.7 | 0
4417 | 2002-07-04 | 0 | 0 | 0 | 25.77 | 8.81 | 0
4418 | 2002-07-04 01:00 | 0 | 0 | 0 | 24.75 | 8.81 | 0
4419 | 2002-07-04 02:00 | 0 | 0 | 0 | 23.92 | 8.81 | 0
4420 | 2002-07-04 03:00 | 0 | 0 | 0 | 23.08 | 7.76 | 0
4421 | 2002-07-04 04:00 | 2 | 56 | 1 | 22.24 | 7.76 | 0 | -2.9194 | 59.5055 | 90 | 0 | 2 | 0 | 0.69549 | 0.018738 | 0 | 0.65087 | 0 | 0 | 0.62678 | 0 | 0.60798 | 0.60793 | 1365.25 | 22.2515 | 90.4051 | 90.1107 | 89.4348 | 0 | 0 | 89.4312 | 94.3817 | 0 | 0 | 0 | 89.4312 | 0 | 660 | 0 | 0
4422 | 2002-07-04 05:00 | 100 | 421 | 39 | 22.68 | 7.76 | 0 | 8.1462 | 67.7961 | 90 | 0 | 100 | 0 | 29.4837 | 0.93692 | 0 | 27.5919 | 0.0048904 | 0 | 26.5708 | 0.003685 | 25.7772 | 25.7757 | 57885.5 | 23.1669 | 42300.8 | 42722.9 | 41713.2 | 0 | 0 | 41693.9 | 597.258 | 0 | 0 | 0 | 6830.4 | 34863.5 | 660 | 33611.6 | 32939.3633
4423 | 2002-07-04 06:00 | 294 | 675 | 64 | 23.12 | 2.88 | 0 | 19.8585 | 75.3618 | 78.0288 | 0 | 294 | 140.438 | 59.5255 | 2.7546 | 138.714 | 55.7062 | 0.014378 | 112.212 | 53.6446 | 0.010834 | 160.891 | 160.878 | 361294 | 27.289 | 323455 | 319830 | 305383 | 0 | 0 | 304537 | 661.233 | 0 | 0 | 0 | 1305.53 | 303231 | 669.728 | 297002 | 291061.5625
4424 | 2002-07-04 07:00 | 504 | 807 | 76 | 23.56 | 2.88 | 0 | 31.9765 | 82.7617 | 64.2283 | 0 | 504 | 351.395 | 76.0083 | 4.7221 | 351.395 | 71.1315 | 0.024648 | 328.554 | 68.499 | 0.018573 | 385.16 | 385.156 | 864964 | 33.541 | 823455 | 791931 | 773236 | 0 | 0 | 768233 | 684.517 | 0 | 0 | 0 | 0 | 768233 | 684.517 | 757305 | 742158.5
4425 | 2002-07-04 08:00 | 694 | 869 | 87 | 25.92 | 2.88 | 0 | 44.2973 | 90.7547 | 50.4365 | 0 | 694 | 553.592 | 89.6565 | 6.5022 | 553.592 | 83.904 | 0.033939 | 537.814 | 80.7987 | 0.025574 | 600.079 | 600.077 | 1347620 | 41.4705 | 1318870 | 1224560 | 1195110 | 0 | 0 | 1182860 | 673.496 | 0 | 0 | 0 | 0 | 1182860 | 673.496 | 1165530 | 1142223.375
4426 | 2002-07-04 09:00 | 824 | 805 | 152 | 28.29 | 1.18 | 0 | 56.5762 | 100.81 | 36.8621 | 0 | 824 | 644.192 | 157.309 | 7.7202 | 644.192 | 147.216 | 0.040297 | 636.143 | 141.767 | 0.030365 | 754.603 | 754.594 | 1694620 | 50.196 | 1680590 | 1498690 | 1463670 | 0 | 0 | 1444170 | 651.864 | 0 | 0 | 0 | 2300.02 | 1441870 | 659.999 | 1419300 | 1390916.875
4427 | 2002-07-04 10:00 | 947 | 858 | 150 | 30.65 | 1.18 | 0 | 68.2794 | 117.061 | 24.0607 | 0 | 947 | 783.371 | 150.666 | 8.8727 | 783.371 | 140.999 | 0.046312 | 779.644 | 135.78 | 0.034897 | 887.996 | 887.986 | 1994180 | 56.4284 | 1995010 | 1727550 | 1689790 | 0 | 0 | 1662550 | 634.895 | 0 | 0 | 0 | 29705.3 | 1632840 | 660 | 1604550 | 1572454.625
4428 | 2002-07-04 11:00 | 962 | 734 | 248 | 31.86 | 1.18 | 0 | 77.1834 | 154.469 | 14.4599 | 0 | 962 | 709.048 | 259.234 | 9.0132 | 709.048 | 242.601 | 0.047046 | 707.889 | 233.622 | 0.03545 | 913.3 | 913.292 | 2051020 | 58.373 | 2054820 | 1762400 | 1722810 | 0 | 0 | 1694140 | 630.261 | 0 | 0 | 0 | 46281.9 | 1647860 | 660 | 1619060 | 1586675.5
4429 | 2002-07-04 12:00 | 1017 | 887 | 158 | 33.07 | 2.9 | 0 | 75.8667 | 216.393 | 15.8578 | 0 | 1017 | 852.102 | 157.357 | 9.5285 | 852.102 | 147.261 | 0.049736 | 850.416 | 141.811 | 0.037477 | 962.496 | 962.495 | 2161520 | 57.9792 | 2171200 | 1867180 | 1826190 | 0 | 0 | 1794240 | 632.104 | 0 | 0 | 0 | 40818.6 | 1753420 | 660 | 1720920 | 1686502.75
4430 | 2002-07-04 13:00 | 886 | 713 | 235 | 34.27 | 2.9 | 0 | 65.9648 | 247.21 | 26.568 | 0 | 886 | 637.534 | 243.45 | 8.3011 | 637.534 | 227.829 | 0.043329 | 633.771 | 219.398 | 0.032649 | 827.605 | 827.596 | 1858560 | 55.688 | 1852480 | 1608920 | 1573460 | 0 | 0 | 1549920 | 637.142 | 0 | 0 | 0 | 26739.8 | 1523180 | 660 | 1498460 | 1468486.375
4431 | 2002-07-04 14:00 | 820 | 861 | 123 | 34.57 | 2.9 | 0 | 54.0588 | 261.529 | 39.6187 | 0 | 820 | 663.154 | 125.214 | 7.6828 | 663.154 | 117.18 | 0.040101 | 653.267 | 112.843 | 0.030217 | 743.156 | 743.152 | 1668930 | 53.8026 | 1653700 | 1448300 | 1416930 | 0 | 0 | 1397930 | 639.228 | 0 | 0 | 0 | 18431.5 | 1379500 | 660 | 1358420 | 1331254.5
4432 | 2002-07-04 15:00 | 666 | 843 | 105 | 34.86 | 6.17 | 0 | 41.7411 | 270.961 | 53.2661 | 0 | 666 | 503.982 | 107.476 | 6.2399 | 503.982 | 100.58 | 0.03257 | 487.049 | 96.8574 | 0.024542 | 566.413 | 566.411 | 1272010 | 46.7001 | 1240560 | 1122680 | 1096420 | 0 | 0 | 1085520 | 655.406 | 0 | 0 | 0 | 723.97 | 1084790 | 660.071 | 1070130 | 1048732.125
4433 | 2002-07-04 16:00 | 453 | 756 | 81 | 35.15 | 6.17 | 0 | 29.4411 | 278.746 | 67.0756 | 0 | 453 | 294.795 | 79.9202 | 4.2443 | 294.795 | 74.7924 | 0.022154 | 271.694 | 72.0244 | 0.016693 | 333.423 | 333.419 | 748772 | 42.1197 | 706159 | 650924 | 635741 | 0 | 0 | 631994 | 650.772 | 0 | 0 | 0 | 1584.61 | 630409 | 660 | 622214 | 609769.5
4434 | 2002-07-04 17:00 | 252 | 634 | 62 | 34.53 | 6.17 | 0 | 17.3842 | 286.125 | 80.8646 | 0 | 252 | 100.964 | 54.2281 | 2.361 | 100.964 | 50.7487 | 0.012324 | 74.2161 | 48.8705 | 0.0092863 | 119.403 | 119.403 | 268149 | 37.026 | 234197 | 220093 | 214904 | 0 | 0 | 214435 | 624.208 | 0 | 0 | 0 | 10129.2 | 204306 | 660 | 199047 | 195066.1406
4435 | 2002-07-04 18:00 | 58 | 423 | 14 | 33.91 | 7.34 | 0 | 5.7762 | 293.794 | 90 | 0 | 58 | 0 | 11.9404 | 0.54341 | 0 | 11.1743 | 0.0028364 | 0 | 10.7607 | 0.0021373 | 10.44 | 10.4394 | 23444.4 | 34.1125 | 14080.8 | 13398.2 | 13145 | 0 | 0 | 13142.3 | 501.789 | 0 | 0 | 0 | 13142.3 | 0 | 660 | 0 | 0
4436 | 2002-07-04 19:00 | 0 | 12 | 0 | 33.29 | 7.34 | 0
4437 | 2002-07-04 20:00 | 0 | 0 | 0 | 31.98 | 7.34 | 0
4438 | 2002-07-04 21:00 | 0 | 0 | 0 | 30.66 | 7.49 | 0
4439 | 2002-07-04 22:00 | 0 | 0 | 0 | 29.34 | 7.49 | 0
4440 | 2002-07-04 23:00 | 0 | 0 | 0 | 28.34 | 7.49 | 0
4441 | 2002-07-05 | 0 | 0 | 0 | 27.33 | 6.52 | 0
4442 | 2002-07-05 01:00 | 0 | 0 | 0 | 26.33 | 6.52 | 0
4443 | 2002-07-05 02:00 | 0 | 0 | 0 | 26.02 | 6.52 | 0
4444 | 2002-07-05 03:00 | 0 | 0 | 0 | 25.71 | 6.76 | 0
4445 | 2002-07-05 04:00 | 2 | 54 | 1 | 25.4 | 6.76 | 0 | -3.0089 | 59.5502 | 90 | 0 | 2 | 0 | 0.69614 | 0.018738 | 0 | 0.65148 | 0 | 0 | 0.62737 | 0 | 0.60855 | 0.60849 | 1366.52 | 25.4122 | 90.5725 | 90.6166 | 89.9641 | 0 | 0 | 89.9604 | 94.4024 | 0 | 0 | 0 | 89.9604 | 0 | 660 | 0 | 0
4446 | 2002-07-05 05:00 | 98 | 417 | 38 | 25.49 | 6.76 | 0 | 8.0612 | 67.8499 | 90 | 0 | 98 | 0 | 28.6487 | 0.91818 | 0 | 26.8105 | 0.0047926 | 0 | 25.8183 | 0.0036113 | 25.0472 | 25.045 | 56244.5 | 25.9941 | 40909 | 40684.6 | 39797.4 | 0 | 0 | 39779 | 584.089 | 0 | 0 | 0 | 10244.7 | 29534.3 | 660 | 28464.3 | 27895.0488
4447 | 2002-07-05 06:00 | 293 | 661 | 69 | 25.57 | 2.87 | 0 | 19.7773 | 75.4248 | 78.0778 | 0 | 293 | 136.76 | 62.1454 | 2.7452 | 134.909 | 58.158 | 0.014329 | 109.002 | 56.0056 | 0.010797 | 160.068 | 160.066 | 359470 | 29.7207 | 321699 | 314298 | 299184 | 0 | 0 | 298344 | 649.825 | 0 | 0 | 0 | 2427.39 | 295916 | 661.724 | 289905 | 284106.4688
4448 | 2002-07-05 07:00 | 476 | 653 | 131 | 25.65 | 2.87 | 0 | 31.898 | 82.8361 | 64.2683 | 0 | 476 | 283.462 | 127.114 | 4.4597 | 283.462 | 118.958 | 0.023278 | 264.99 | 114.556 | 0.017541 | 368.177 | 368.171 | 826818 | 35.1972 | 784849 | 748792 | 730235 | 0 | 0 | 725696 | 678.5 | 0 | 0 | 0 | 0 | 725696 | 678.5 | 715591 | 701279.375
4449 | 2002-07-05 08:00 | 600 | 516 | 240 | 27.56 | 2.87 | 0 | 44.2197 | 90.8449 | 50.466 | 0 | 600 | 328.576 | 234.908 | 5.6215 | 328.576 | 219.836 | 0.029343 | 319.195 | 211.7 | 0.02211 | 514.99 | 514.976 | 1156510 | 40.914 | 1121380 | 1042950 | 1016960 | 0 | 0 | 1007990 | 670.369 | 0 | 0 | 0 | 0 | 1007990 | 670.369 | 994317 | 974430.5
4450 | 2002-07-05 09:00 | 318 | 57 | 270 | 29.48 | 1.99 | 0 | 56.4964 | 100.923 | 36.8768 | 0 | 318 | 46.0472 | 271.826 | 2.9794 | 46.0472 | 254.385 | 0.015551 | 45.4714 | 244.97 | 0.011718 | 281.74 | 281.725 | 632682 | 37.2263 | 589985 | 556609 | 542549 | 0 | 0 | 539900 | 661.408 | 0 | 0 | 0 | -1.9559 | 539902 | 661.55 | 532674 | 522020.125
4451 | 2002-07-05 10:00 | 923 | 733 | 243 | 31.39 | 1.99 | 0 | 68.191 | 117.195 | 24.049 | 0 | 923 | 668.845 | 252.066 | 8.6478 | 668.845 | 235.893 | 0.045138 | 665.666 | 227.163 | 0.034013 | 866.077 | 866.07 | 1944980 | 55.2034 | 1943270 | 1692700 | 1653660 | 0 | 0 | 1627970 | 639.774 | 0 | 0 | 0 | 20485 | 1607480 | 660 | 1580030 | 1548431.875
4452 | 2002-07-05 11:00 | 1023 | 911 | 137 | 32.42 | 1.99 | 0 | 77.0817 | 154.464 | 14.3913 | 0 | 1023 | 880.483 | 137.686 | 9.5847 | 880.483 | 128.852 | 0.050029 | 879.057 | 124.083 | 0.037698 | 973.082 | 973.078 | 2185290 | 59.1756 | 2196250 | 1877460 | 1835400 | 0 | 0 | 1802850 | 629.266 | 0 | 0 | 0 | 52652.4 | 1750200 | 660 | 1717810 | 1683458
4453 | 2002-07-05 12:00 | 1022 | 955 | 98 | 33.44 | 3.48 | 0 | 75.8083 | 216.051 | 15.758 | 0 | 1022 | 917.268 | 100.379 | 9.5753 | 917.268 | 93.9383 | 0.04998 | 915.477 | 90.4617 | 0.037661 | 975.797 | 975.79 | 2191390 | 57.7429 | 2202670 | 1896850 | 1856020 | 0 | 0 | 1823140 | 633.36 | 0 | 0 | 0 | 38237.4 | 1784900 | 660 | 1751260 | 1716233
4454 | 2002-07-05 13:00 | 933 | 867 | 142 | 34.47 | 3.48 | 0 | 65.9443 | 246.964 | 26.4909 | 0 | 933 | 775.283 | 143.37 | 8.7415 | 775.283 | 134.171 | 0.045628 | 770.735 | 129.205 | 0.034381 | 872.976 | 872.97 | 1960470 | 56.2121 | 1959550 | 1698450 | 1661170 | 0 | 0 | 1634880 | 635.293 | 0 | 0 | 0 | 28648.7 | 1606230 | 660 | 1578830 | 1547250.75
4455 | 2002-07-05 14:00 | 779 | 755 | 168 | 34.56 | 3.48 | 0 | 54.05 | 261.356 | 39.5585 | 0 | 779 | 581.9 | 172.088 | 7.2986 | 581.9 | 161.047 | 0.038096 | 573.257 | 155.086 | 0.028706 | 706.521 | 706.516 | 1586650 | 52.1564 | 1567690 | 1383650 | 1352460 | 0 | 0 | 1335310 | 642.497 | 0 | 0 | 0 | 11020 | 1324290 | 660 | 1304500 | 1278411.5
4456 | 2002-07-05 15:00 | 642 | 796 | 112 | 34.66 | 6.23 | 0 | 41.7342 | 270.824 | 53.218 | 0 | 642 | 476.732 | 114.366 | 6.015 | 476.732 | 107.028 | 0.031397 | 460.76 | 103.067 | 0.023658 | 546.935 | 546.928 | 1228260 | 46.0488 | 1195350 | 1084920 | 1058670 | 0 | 0 | 1048580 | 657.441 | 0 | 0 | 0 | 318.793 | 1048260 | 660 | 1034330 | 1013642.3125
4457 | 2002-07-05 16:00 | 469 | 739 | 105 | 34.75 | 6.23 | 0 | 29.4318 | 278.628 | 67.0374 | 0 | 469 | 288.993 | 101.295 | 4.3942 | 288.993 | 94.7954 | 0.022936 | 266.404 | 91.2871 | 0.017283 | 346.977 | 346.975 | 779221 | 41.9752 | 736810 | 679876 | 663162 | 0 | 0 | 659117 | 653.321 | 0 | 0 | 0 | 741.826 | 658375 | 660 | 649816 | 636819.9375
4458 | 2002-07-05 17:00 | 239 | 544 | 76 | 34.15 | 6.23 | 0 | 17.3696 | 286.019 | 80.836 | 0 | 239 | 86.9567 | 67.0014 | 2.2392 | 86.9567 | 62.7025 | 0.011688 | 64.0045 | 60.3819 | 0.0088072 | 120.663 | 120.663 | 270978 | 36.6626 | 236882 | 223065 | 218180 | 0 | 0 | 217698 | 624.673 | 0 | 0 | 0 | 9501.62 | 208196 | 660 | 202885 | 198827.7656
4459 | 2002-07-05 18:00 | 55 | 363 | 17 | 33.54 | 7.51 | 0 | 5.7538 | 293.693 | 90 | 0 | 55 | 0 | 12.9649 | 0.51531 | 0 | 12.133 | 0.0026897 | 0 | 11.684 | 0.0020268 | 11.3355 | 11.335 | 25455.4 | 33.7575 | 15649.2 | 14911.9 | 14620.9 | 0 | 0 | 14617.6 | 508.37 | 0 | 0 | 0 | 14617.6 | 0 | 660 | 0 | 0
4460 | 2002-07-05 19:00 | 0 | 10 | 0 | 32.94 | 7.51 | 0
4461 | 2002-07-05 20:00 | 0 | 0 | 0 | 31.61 | 7.51 | 0
4462 | 2002-07-05 21:00 | 0 | 0 | 0 | 30.29 | 5.76 | 0
4463 | 2002-07-05 22:00 | 0 | 0 | 0 | 28.96 | 5.76 | 0
4464 | 2002-07-05 23:00 | 0 | 0 | 0 | 27.82 | 5.76 | 0
4465 | 2002-07-06 | 0 | 0 | 0 | 26.68 | 5.07 | 0
4466 | 2002-07-06 01:00 | 0 | 0 | 0 | 25.53 | 5.07 | 0
4467 | 2002-07-06 02:00 | 0 | 0 | 0 | 25.14 | 5.07 | 0
4468 | 2002-07-06 03:00 | 0 | 0 | 0 | 24.75 | 2.24 | 0
4469 | 2002-07-06 04:00 | 2 | 41 | 1 | 24.36 | 2.24 | 0 | -3.1017 | 59.6007 | 90 | 0 | 2 | 0 | 0.69681 | 0.018738 | 0 | 0.65211 | 0 | 0 | 0.62797 | 0 | 0.60913 | 0.6091 | 1367.88 | 24.3765 | 90.7532 | 90.6865 | 90.0221 | 0 | 0 | 90.0185 | 94.5495 | 0 | 0 | 0 | 90.0185 | 0 | 660 | 0 | 0
4470 | 2002-07-06 05:00 | 89 | 324 | 43 | 24.43 | 2.24 | 0 | 7.9736 | 67.9098 | 90 | 0 | 89 | 0 | 33.4442 | 0.83386 | 0 | 31.2983 | 0.0043525 | 0 | 30.14 | 0.0032797 | 29.239 | 29.2383 | 65661.9 | 25.2206 | 48939.3 | 48879.2 | 47724 | 0 | 0 | 47698.6 | 596.172 | 0 | 0 | 0 | 8128.09 | 39570.5 | 660 | 38160.8 | 37397.5664
4471 | 2002-07-06 06:00 | 288 | 645 | 70 | 24.5 | 1.17 | 0 | 19.6939 | 75.4944 | 78.1261 | 0 | 288 | 133.104 | 63.0789 | 2.6983 | 131.138 | 59.0316 | 0.014084 | 105.828 | 56.8469 | 0.010613 | 157.805 | 157.797 | 354375 | 29.084 | 316787 | 310460 | 294880 | 0 | 0 | 294064 | 650.217 | 0 | 0 | 0 | 2682.82 | 291381 | 663.275 | 285349 | 279641.8438
4472 | 2002-07-06 07:00 | 493 | 778 | 82 | 24.57 | 1.17 | 0 | 31.8176 | 82.918 | 64.3072 | 0 | 493 | 337.977 | 81.8905 | 4.619 | 337.977 | 76.6363 | 0.02411 | 315.898 | 73.8 | 0.018167 | 378.025 | 378.021 | 848940 | 35.5514 | 807225 | 768925 | 750603 | 0 | 0 | 745772 | 676.258 | 0 | 0 | 0 | 0 | 745772 | 676.258 | 735471 | 720761.4375
4473 | 2002-07-06 08:00 | 692 | 834 | 111 | 26.74 | 1.17 | 0 | 44.1402 | 90.9439 | 50.4937 | 0 | 692 | 530.733 | 114.187 | 6.4835 | 530.733 | 106.86 | 0.033842 | 515.556 | 102.905 | 0.0255 | 599.932 | 599.928 | 1347290 | 44.1677 | 1318530 | 1208550 | 1179710 | 0 | 0 | 1167510 | 666.28 | 0 | 0 | 0 | 0 | 1167510 | 666.28 | 1150850 | 1127833.75
4474 | 2002-07-06 09:00 | 795 | 688 | 222 | 28.92 | 2.17 | 0 | 56.4144 | 101.046 | 36.8887 | 0 | 795 | 550.125 | 227.14 | 7.4485 | 550.125 | 212.567 | 0.038879 | 543.24 | 204.7 | 0.029296 | 725.529 | 725.513 | 1629320 | 48.6303 | 1612280 | 1448350 | 1415060 | 0 | 0 | 1397100 | 656.526 | 0 | 0 | 0 | 481.058 | 1396620 | 660 | 1375140 | 1347636.25
4475 | 2002-07-06 10:00 | 947 | 834 | 174 | 31.09 | 2.17 | 0 | 68.0994 | 117.344 | 24.0333 | 0 | 947 | 760.9 | 180.976 | 8.8727 | 760.9 | 169.364 | 0.046312 | 757.289 | 163.096 | 0.034897 | 892.807 | 892.797 | 2004990 | 55.345 | 2006380 | 1747020 | 1708490 | 0 | 0 | 1681040 | 639.408 | 0 | 0 | 0 | 21174.1 | 1659870 | 660 | 1630660 | 1598044.875
4476 | 2002-07-06 11:00 | 953 | 706 | 266 | 32.17 | 2.17 | 0 | 76.9745 | 154.476 | 14.3167 | 0 | 953 | 683.244 | 276.871 | 8.9289 | 683.244 | 259.106 | 0.046606 | 682.149 | 249.517 | 0.035118 | 903.751 | 903.735 | 2029570 | 56.7222 | 2032240 | 1757530 | 1719860 | 0 | 0 | 1691610 | 634.158 | 0 | 0 | 0 | 32095.2 | 1659510 | 660 | 1630310 | 1597706
4477 | 2002-07-06 12:00 | 1021 | 920 | 131 | 33.25 | 3.36 | 0 | 75.7432 | 215.703 | 15.6535 | 0 | 1021 | 884.224 | 132.248 | 9.566 | 884.224 | 123.762 | 0.049931 | 882.521 | 119.182 | 0.037624 | 971.688 | 971.681 | 2182150 | 57.643 | 2192940 | 1889320 | 1848300 | 0 | 0 | 1815680 | 633.061 | 0 | 0 | 0 | 37246.1 | 1778430 | 660 | 1745020 | 1710123.5
4478 | 2002-07-06 13:00 | 955 | 944 | 94 | 34.33 | 3.36 | 0 | 65.9187 | 246.707 | 26.4122 | 0 | 955 | 844.638 | 97.161 | 8.9476 | 844.638 | 90.927 | 0.046704 | 839.716 | 87.5618 | 0.035192 | 899.493 | 899.49 | 2020030 | 56.9107 | 2022200 | 1747150 | 1708580 | 0 | 0 | 1680670 | 633.772 | 0 | 0 | 0 | 33253.5 | 1647420 | 660 | 1618630 | 1586258.625
4479 | 2002-07-06 14:00 | 833 | 922 | 87 | 34.56 | 3.36 | 0 | 54.0367 | 261.173 | 39.4983 | 0 | 833 | 711.207 | 90.3506 | 7.8046 | 711.207 | 84.5536 | 0.040737 | 700.684 | 81.4243 | 0.030696 | 758.675 | 758.671 | 1703780 | 53.6056 | 1690180 | 1482050 | 1448720 | 0 | 0 | 1428880 | 639.375 | 0 | 0 | 0 | 15829.7 | 1413050 | 660 | 1391170 | 1363351.125
4480 | 2002-07-06 15:00 | 666 | 695 | 203 | 34.78 | 4.23 | 0 | 41.7231 | 270.68 | 53.1706 | 0 | 666 | 417.017 | 200.664 | 6.2399 | 417.017 | 187.789 | 0.03257 | 403.084 | 180.839 | 0.024542 | 566.429 | 566.412 | 1272020 | 48.2083 | 1240570 | 1114310 | 1087940 | 0 | 0 | 1077070 | 650.76 | 0 | 0 | 0 | 3175.58 | 1073900 | 660 | 1059460 | 1038272.6875
4481 | 2002-07-06 16:00 | 279 | 137 | 212 | 35.01 | 4.23 | 0 | 29.4182 | 278.504 | 67.0007 | 0 | 279 | 53.2966 | 194.156 | 2.614 | 53.2966 | 181.698 | 0.013644 | 49.1411 | 174.974 | 0.010281 | 217.402 | 217.399 | 488222 | 40.164 | 447047 | 414845 | 404758 | 0 | 0 | 403185 | 640.095 | 0 | 0 | 0 | 5403.04 | 397782 | 660 | 392145 | 384302.4688
4482 | 2002-07-06 17:00 | 221 | 301 | 131 | 34.7 | 4.23 | 0 | 17.3505 | 285.906 | 80.8094 | 0 | 221 | 48.2025 | 113.181 | 2.0706 | 48.2025 | 105.919 | 0.010808 | 35.5229 | 101.999 | 0.0081439 | 133.404 | 133.397 | 299575 | 37.8625 | 264113 | 247257 | 241418 | 0 | 0 | 240830 | 626.021 | 0 | 0 | 0 | 9984.8 | 230845 | 660 | 225270 | 220764.9062
4483 | 2002-07-06 18:00 | 51 | 201 | 30 | 34.4 | 7.99 | 0 | 5.7266 | 293.587 | 90 | 0 | 51 | 0 | 22.8592 | 0.47783 | 0 | 21.3925 | 0.0024941 | 0 | 20.6008 | 0.0018794 | 19.9846 | 19.9839 | 44878.6 | 34.7721 | 31374.4 | 29667.7 | 29076.8 | 0 | 0 | 29065.3 | 540.558 | 0 | 0 | 0 | 28116.1 | 949.153 | 659.998 | 913.147 | 894.8845
4484 | 2002-07-06 19:00 | 0 | 5 | 0 | 34.1 | 7.99 | 0
4485 | 2002-07-06 20:00 | 0 | 0 | 0 | 32.85 | 7.99 | 0
4486 | 2002-07-06 21:00 | 0 | 0 | 0 | 31.61 | 5.55 | 0
4487 | 2002-07-06 22:00 | 0 | 0 | 0 | 30.37 | 5.55 | 0
4488 | 2002-07-06 23:00 | 0 | 0 | 0 | 29.32 | 5.55 | 0
4489 | 2002-07-07 | 0 | 0 | 0 | 28.27 | 4.22 | 0
4490 | 2002-07-07 01:00 | 0 | 0 | 0 | 27.22 | 4.22 | 0
4491 | 2002-07-07 02:00 | 0 | 0 | 0 | 26.62 | 4.22 | 0
4492 | 2002-07-07 03:00 | 0 | 0 | 0 | 26.02 | 2.37 | 0
4493 | 2002-07-07 04:00 | 2 | 40 | 1 | 25.42 | 2.37 | 0 | -3.1976 | 59.6572 | 90 | 0 | 2 | 0 | 0.69751 | 0.018738 | 0 | 0.65276 | 0 | 0 | 0.6286 | 0 | 0.60974 | 0.6097 | 1369.23 | 25.4363 | 90.9331 | 90.9799 | 90.2683 | 0 | 0 | 90.2647 | 95.0914 | 0 | 0 | 0 | 90.2647 | 0 | 660 | 0 | 0
4494 | 2002-07-07 05:00 | 88 | 334 | 41 | 25.63 | 2.37 | 0 | 7.8834 | 67.9759 | 90 | 0 | 88 | 0 | 31.6363 | 0.82449 | 0 | 29.6065 | 0.0043036 | 0 | 28.5107 | 0.0032428 | 27.6586 | 27.657 | 62110.9 | 26.3714 | 45899.2 | 45553.3 | 44499.1 | 0 | 0 | 44476.5 | 589.607 | 0 | 0 | 0 | 9958.01 | 34518.5 | 660 | 33278.3 | 32612.7734
4495 | 2002-07-07 06:00 | 272 | 571 | 80 | 25.85 | 0.74 | 0 | 19.6084 | 75.5707 | 78.1738 | 0 | 272 | 117.254 | 72.2537 | 2.5484 | 115.359 | 67.6177 | 0.013302 | 92.9827 | 65.1153 | 0.010023 | 153.365 | 153.352 | 344391 | 30.4357 | 307156 | 298982 | 283932 | 0 | 0 | 283165 | 645.82 | 0 | 0 | 0 | 3344.43 | 279821 | 660.387 | 273902 | 268424.375
4496 | 2002-07-07 07:00 | 458 | 636 | 123 | 26.07 | 0.74 | 0 | 31.7352 | 83.0072 | 64.3448 | 0 | 458 | 275.744 | 119.711 | 4.2911 | 275.744 | 112.03 | 0.022398 | 257.686 | 107.884 | 0.016877 | 354.62 | 354.617 | 796376 | 36.6743 | 754106 | 714252 | 696254 | 0 | 0 | 692032 | 671.142 | 0 | 0 | 0 | 0 | 692032 | 671.142 | 682650 | 668997.25
4497 | 2002-07-07 08:00 | 645 | 709 | 152 | 28.11 | 0.74 | 0 | 44.0588 | 91.0515 | 50.5194 | 0 | 645 | 450.761 | 154.013 | 6.0431 | 450.761 | 144.132 | 0.031543 | 437.852 | 138.797 | 0.023768 | 559.373 | 559.367 | 1256190 | 44.837 | 1224210 | 1117850 | 1091130 | 0 | 0 | 1080530 | 661.288 | 0 | 0 | 0 | -21.867 | 1080550 | 661.742 | 1065890 | 1044575.4375
4498 | 2002-07-07 09:00 | 802 | 741 | 185 | 30.15 | 0.78 | 0 | 56.3303 | 101.181 | 36.898 | 0 | 802 | 592.875 | 191.595 | 7.5141 | 592.875 | 179.302 | 0.039221 | 585.45 | 172.666 | 0.029554 | 735.401 | 735.394 | 1651500 | 52.0816 | 1635470 | 1444530 | 1411750 | 0 | 0 | 1393210 | 644.849 | 0 | 0 | 0 | 9212.91 | 1384000 | 659.999 | 1362820 | 1335560.75
4499 | 2002-07-07 10:00 | 946 | 860 | 149 | 32.2 | 0.78 | 0 | 68.0049 | 117.508 | 24.0136 | 0 | 946 | 785.167 | 149.966 | 8.8633 | 785.167 | 140.344 | 0.046263 | 781.447 | 135.15 | 0.03486 | 889.133 | 889.121 | 1996740 | 58.7162 | 1997700 | 1709860 | 1673150 | 0 | 0 | 1645900 | 628.038 | 0 | 0 | 0 | 52441.5 | 1593460 | 660 | 1566480 | 1535145.75
4500 | 2002-07-07 11:00 | 989 | 839 | 173 | 33.32 | 0.78 | 0 | 76.8618 | 154.504 | 14.2359 | 0 | 989 | 812.202 | 180.897 | 9.2662 | 812.202 | 169.291 | 0.048366 | 810.915 | 163.025 | 0.036445 | 944.757 | 944.76 | 2121680 | 61.4955 | 2129230 | 1797810 | 1757590 | 0 | 0 | 1726850 | 620.641 | 0 | 0 | 0 | 84034.3 | 1642810 | 660 | 1614180 | 1581896.5
4501 | 2002-07-07 12:00 | 952 | 752 | 225 | 34.44 | 3.15 | 0 | 75.6712 | 215.35 | 15.5444 | 0 | 952 | 722.897 | 236.967 | 8.9195 | 722.897 | 221.763 | 0.046557 | 721.524 | 213.555 | 0.035082 | 907.061 | 907.046 | 2036990 | 57.5287 | 2040050 | 1757230 | 1721970 | 0 | 0 | 1693390 | 631.131 | 0 | 0 | 0 | 41002.7 | 1652390 | 660 | 1623430 | 1590966.25
4502 | 2002-07-07 13:00 | 901 | 811 | 161 | 35.56 | 3.15 | 0 | 65.8877 | 246.44 | 26.332 | 0 | 901 | 726.616 | 168.171 | 8.4417 | 726.616 | 157.381 | 0.044063 | 722.41 | 151.557 | 0.033202 | 847.78 | 847.768 | 1903880 | 57.1398 | 1900070 | 1638600 | 1603360 | 0 | 0 | 1578540 | 631.27 | 0 | 0 | 0 | 38532.2 | 1540000 | 660 | 1514750 | 1484453
4503 | 2002-07-07 14:00 | 778 | 757 | 165 | 35.73 | 3.15 | 0 | 54.0188 | 260.982 | 39.4381 | 0 | 778 | 585.049 | 169.433 | 7.2893 | 585.049 | 158.562 | 0.038047 | 576.425 | 152.693 | 0.02867 | 707.272 | 707.263 | 1588330 | 53.7333 | 1569450 | 1374250 | 1342520 | 0 | 0 | 1325400 | 637.946 | 0 | 0 | 0 | 18640.3 | 1306760 | 659.999 | 1287360 | 1261616.625
4504 | 2002-07-07 15:00 | 663 | 795 | 134 | 35.89 | 4.66 | 0 | 41.7076 | 270.529 | 53.1242 | 0 | 663 | 477.122 | 135.695 | 6.2118 | 477.122 | 126.988 | 0.032424 | 461.224 | 122.288 | 0.024432 | 566.031 | 566.023 | 1271140 | 48.9371 | 1239660 | 1109460 | 1084220 | 0 | 0 | 1073260 | 646.505 | 0 | 0 | 0 | 5338.45 | 1067920 | 660 | 1053600 | 1032529.25
4505 | 2002-07-07 16:00 | 431 | 645 | 114 | 36.06 | 4.66 | 0 | 29.4002 | 278.375 | 66.9656 | 0 | 431 | 252.669 | 109.914 | 4.0381 | 252.669 | 102.862 | 0.021078 | 233.016 | 99.0548 | 0.015883 | 322.124 | 322.118 | 723397 | 43.485 | 680671 | 622925 | 609400 | 0 | 0 | 605867 | 642.436 | 0 | 0 | 0 | 4880.28 | 600986 | 660 | 593172 | 581308.1875
4506 | 2002-07-07 17:00 | 251 | 589 | 75 | 35.9 | 4.66 | 0 | 17.3267 | 285.789 | 80.785 | 0 | 251 | 94.6366 | 66.2235 | 2.3517 | 94.6366 | 61.9745 | 0.012275 | 69.8204 | 59.6809 | 0.0092494 | 125.625 | 125.624 | 282119 | 38.7957 | 247468 | 230424 | 225275 | 0 | 0 | 224752 | 619.383 | 0 | 0 | 0 | 13572 | 211180 | 660 | 205832 | 201714.9375
4507 | 2002-07-07 18:00 | 58 | 393 | 18 | 35.73 | 6.65 | 0 | 5.6945 | 293.476 | 90 | 0 | 58 | 0 | 13.8867 | 0.54341 | 0 | 12.9957 | 0.0028364 | 0 | 12.5148 | 0.0021373 | 12.1414 | 12.1407 | 27264.8 | 35.9761 | 17072.3 | 16050.8 | 15742.2 | 0 | 0 | 15738.4 | 507.373 | 0 | 0 | 0 | 15738.4 | 0 | 660 | 0 | 0
4508 | 2002-07-07 19:00 | 0 | 10 | 0 | 35.57 | 6.65 | 0
4509 | 2002-07-07 20:00 | 0 | 0 | 0 | 34.34 | 6.65 | 0
4510 | 2002-07-07 21:00 | 0 | 0 | 0 | 33.11 | 5.71 | 0
4511 | 2002-07-07 22:00 | 0 | 0 | 0 | 31.87 | 5.71 | 0
4512 | 2002-07-07 23:00 | 0 | 0 | 0 | 30.92 | 5.71 | 0
4513 | 2002-07-08 | 0 | 0 | 0 | 29.97 | 4.67 | 0
4514 | 2002-07-08 01:00 | 0 | 0 | 0 | 29.02 | 4.67 | 0
4515 | 2002-07-08 02:00 | 0 | 0 | 0 | 28.33 | 4.67 | 0
4516 | 2002-07-08 03:00 | 0 | 0 | 0 | 27.63 | 4.37 | 0
4517 | 2002-07-08 04:00 | 2 | 51 | 1 | 26.94 | 4.37 | 0 | -3.2965 | 59.7196 | 90 | 0 | 2 | 0 | 0.69823 | 0.018738 | 0 | 0.65343 | 0 | 0 | 0.62925 | 0 | 0.61037 | 0.61033 | 1370.63 | 26.9543 | 91.1159 | 91.3263 | 90.6821 | 0 | 0 | 90.6785 | 94.6613 | 0 | 0 | 0 | 90.6785 | 0 | 660 | 0 | 0
4518 | 2002-07-08 05:00 | 98 | 435 | 38 | 26.97 | 4.37 | 0 | 7.7906 | 68.0482 | 90 | 0 | 98 | 0 | 28.917 | 0.91818 | 0 | 27.0617 | 0.0047926 | 0 | 26.0601 | 0.0036113 | 25.2818 | 25.2805 | 56773.5 | 27.5639 | 41357.3 | 40773.1 | 39861.6 | 0 | 0 | 39842.8 | 579.097 | 0 | 0 | 0 | 12297 | 27545.8 | 660 | 26544.6 | 26013.7207
4519 | 2002-07-08 06:00 | 299 | 715 | 59 | 27.01 | 1.08 | 0 | 19.5207 | 75.6536 | 78.2207 | 0 | 299 | 146.624 | 54.9072 | 2.8014 | 144.066 | 51.3842 | 0.014622 | 115.983 | 49.4825 | 0.011018 | 160.513 | 160.505 | 360459 | 31.7009 | 322696 | 312140 | 295979 | 0 | 0 | 295138 | 642.947 | 0 | 0 | 0 | 6319.31 | 288818 | 660 | 282891 | 277233.625
4520 | 2002-07-08 07:00 | 507 | 829 | 72 | 27.05 | 1.08 | 0 | 31.651 | 83.1038 | 64.3811 | 0 | 507 | 358.435 | 73.1959 | 4.7502 | 358.435 | 68.4995 | 0.024794 | 334.908 | 65.9644 | 0.018683 | 388.864 | 388.86 | 873279 | 38.4149 | 831887 | 781728 | 762259 | 0 | 0 | 757183 | 669.893 | 0 | 0 | 0 | 0 | 757183 | 669.893 | 746965 | 732025.75
4521 | 2002-07-08 08:00 | 699 | 893 | 79 | 29.26 | 1.08 | 0 | 43.9757 | 91.1677 | 50.5432 | 0 | 699 | 567.445 | 81.9451 | 6.5491 | 567.445 | 76.6873 | 0.034184 | 551.172 | 73.8492 | 0.025758 | 606.295 | 606.292 | 1361580 | 46.9796 | 1333350 | 1205630 | 1178410 | 0 | 0 | 1165850 | 655.74 | 0 | 0 | 0 | 595.286 | 1165260 | 660 | 1148950 | 1125973.875
4522 | 2002-07-08 09:00 | 859 | 928 | 88 | 31.47 | 0.61 | 0 | 56.2441 | 101.327 | 36.9046 | 0 | 859 | 741.533 | 91.4672 | 8.0482 | 741.533 | 85.5985 | 0.042009 | 732.243 | 82.4306 | 0.031654 | 790.264 | 790.261 | 1774730 | 55.3099 | 1764520 | 1534620 | 1500570 | 0 | 0 | 1479140 | 636.593 | 0 | 0 | 0 | 25373.1 | 1453770 | 660 | 1430910 | 1402294
4523 | 2002-07-08 10:00 | 971 | 948 | 93 | 33.67 | 0.61 | 0 | 67.9073 | 117.686 | 23.99 | 0 | 971 | 865.719 | 96.1752 | 9.0975 | 865.719 | 90.0044 | 0.047486 | 861.627 | 86.6734 | 0.035782 | 919.886 | 919.878 | 2065820 | 61.42 | 2070390 | 1748230 | 1711540 | 0 | 0 | 1682300 | 619.608 | 0 | 0 | 0 | 85789.7 | 1596510 | 660 | 1569420 | 1538035.75
4524 | 2002-07-08 11:00 | 1027 | 955 | 99 | 35.17 | 0.61 | 0 | 76.7436 | 154.548 | 14.1491 | 0 | 1027 | 924.481 | 101.426 | 9.6222 | 924.481 | 94.9185 | 0.050225 | 923.035 | 91.4056 | 0.037845 | 984.044 | 984.038 | 2209900 | 64.8555 | 2222180 | 1844540 | 1806760 | 0 | 0 | 1773270 | 610.428 | 0 | 0 | 0 | 142274 | 1630990 | 660 | 1602760 | 1570703.75
4525 | 2002-07-08 12:00 | 1021 | 955 | 98 | 36.66 | 2.97 | 0 | 75.5924 | 214.991 | 15.4309 | 0 | 1021 | 918.618 | 100.557 | 9.566 | 918.618 | 94.1055 | 0.049931 | 916.9 | 90.6227 | 0.037624 | 977.334 | 977.328 | 2194840 | 61.836 | 2206310 | 1860540 | 1822350 | 0 | 0 | 1789250 | 619.698 | 0 | 0 | 0 | 90327.6 | 1698930 | 660 | 1668360 | 1634994.375
4526 | 2002-07-08 13:00 | 954 | 944 | 93 | 38.15 | 2.97 | 0 | 65.8514 | 246.163 | 26.2506 | 0 | 954 | 846.262 | 96.278 | 8.9382 | 846.262 | 90.1006 | 0.046655 | 841.396 | 86.7661 | 0.035155 | 900.352 | 900.346 | 2021950 | 61.3429 | 2024220 | 1709540 | 1673580 | 0 | 0 | 1645580 | 619.299 | 0 | 0 | 0 | 85460 | 1560120 | 660 | 1534220 | 1503535.75
4527 | 2002-07-08 14:00 | 833 | 922 | 87 | 38.62 | 2.97 | 0 | 53.9962 | 260.783 | 39.3781 | 0 | 833 | 712.801 | 90.4474 | 7.8046 | 712.801 | 84.6441 | 0.040737 | 702.334 | 81.5115 | 0.030696 | 760.36 | 760.357 | 1707570 | 58.2068 | 1694140 | 1451100 | 1419620 | 0 | 0 | 1399710 | 624.938 | 0 | 0 | 0 | 53794.3 | 1345920 | 660 | 1325620 | 1299112.25
4528 | 2002-07-08 15:00 | 642 | 822 | 95 | 39.08 | 1.67 | 0 | 41.6877 | 270.371 | 53.0788 | 0 | 642 | 494.071 | 97.3016 | 6.015 | 494.071 | 91.0585 | 0.031397 | 477.651 | 87.6885 | 0.023658 | 548.402 | 548.398 | 1231560 | 54.485 | 1198760 | 1042500 | 1019670 | 0 | 0 | 1009370 | 627.077 | 0 | 0 | 0 | 35894.8 | 973478 | 660 | 960822 | 941606
4529 | 2002-07-08 16:00 | 448 | 752 | 79 | 39.54 | 1.67 | 0 | 29.3777 | 278.24 | 66.9321 | 0 | 448 | 294.726 | 78.2464 | 4.1974 | 294.726 | 73.226 | 0.021909 | 271.852 | 70.5159 | 0.016509 | 332.113 | 332.107 | 745827 | 48.8692 | 703199 | 626021 | 611877 | 0 | 0 | 608144 | 627.104 | 0 | 0 | 0 | 22338.5 | 585806 | 659.999 | 578149 | 566586
4530 | 2002-07-08 17:00 | 241 | 588 | 65 | 39.33 | 1.67 | 0 | 17.2984 | 285.667 | 80.7627 | 0 | 241 | 95.0136 | 57.1882 | 2.258 | 95.0136 | 53.5189 | 0.011786 | 70.1694 | 51.5382 | 0.0088809 | 118.065 | 118.064 | 265142 | 42.6465 | 231346 | 210778 | 206163 | 0 | 0 | 205702 | 603.728 | 0 | 0 | 0 | 27348.6 | 178353 | 659.999 | 173485 | 170014.8125
4531 | 2002-07-08 18:00 | 55 | 392 | 15 | 39.12 | 4.94 | 0 | 5.6574 | 293.361 | 90 | 0 | 55 | 0 | 12.7685 | 0.51531 | 0 | 11.9492 | 0.0026897 | 0 | 11.507 | 0.0020268 | 11.1638 | 11.1629 | 25069.1 | 39.3727 | 15346.7 | 14145.9 | 13881.6 | 0 | 0 | 13878.4 | 488.214 | 0 | 0 | 0 | 13878.4 | 0 | 660 | 0 | 0
4532 | 2002-07-08 19:00 | 0 | 9 | 0 | 38.91 | 4.94 | 0
4533 | 2002-07-08 20:00 | 0 | 0 | 0 | 37.67 | 4.94 | 0
4534 | 2002-07-08 21:00 | 0 | 0 | 0 | 36.43 | 3.4 | 0
4535 | 2002-07-08 22:00 | 0 | 0 | 0 | 35.19 | 3.4 | 0
4536 | 2002-07-08 23:00 | 0 | 0 | 0 | 34.25 | 3.4 | 0
4537 | 2002-07-09 | 0 | 0 | 0 | 33.32 | 2.17 | 0
4538 | 2002-07-09 01:00 | 0 | 0 | 0 | 32.38 | 2.17 | 0
4539 | 2002-07-09 02:00 | 0 | 0 | 0 | 31.84 | 2.17 | 0
4540 | 2002-07-09 03:00 | 0 | 0 | 0 | 31.31 | 1.18 | 0
4541 | 2002-07-09 04:00 | 2 | 48 | 1 | 30.77 | 1.18 | 0 | -3.3985 | 59.7879 | 90 | 0 | 2 | 0 | 0.69897 | 0.018738 | 0 | 0.65412 | 0 | 0 | 0.62991 | 0 | 0.61101 | 0.611 | 1372.14 | 30.7877 | 91.3274 | 91.9508 | 91.3146 | 0 | 0 | 91.3109 | 94.7227 | 0 | 0 | 0 | 91.3109 | 0 | 660 | 0 | 0
4542 | 2002-07-09 05:00 | 95 | 424 | 37 | 30.85 | 1.18 | 0 | 7.6955 | 68.1267 | 90 | 0 | 95 | 0 | 28.0856 | 0.89008 | 0 | 26.2835 | 0.0046459 | 0 | 25.3108 | 0.0035008 | 24.5549 | 24.5546 | 55143.5 | 31.5628 | 39977.8 | 38526.1 | 37685.4 | 0 | 0 | 37667.6 | 562.951 | 0 | 0 | 0 | 19513.8 | 18153.9 | 660 | 17483.8 | 17134.1543
4543 | 2002-07-09 06:00 | 294 | 705 | 59 | 30.94 | 1.61 | 0 | 19.431 | 75.7432 | 78.2669 | 0 | 294 | 143.649 | 54.9341 | 2.7546 | 140.928 | 51.4095 | 0.014378 | 113.323 | 49.5068 | 0.010834 | 157.956 | 157.938 | 354692 | 35.3945 | 317137 | 301016 | 285304 | 0 | 0 | 284483 | 628.027 | 0 | 0 | 0 | 9198.15 | 275285 | 660 | 269418 | 264029.25
4544 | 2002-07-09 07:00 | 505 | 829 | 71 | 31.02 | 1.61 | 0 | 31.5651 | 83.2077 | 64.416 | 0 | 505 | 358.028 | 72.2665 | 4.7315 | 358.028 | 67.6297 | 0.024697 | 334.475 | 65.1268 | 0.018609 | 387.632 | 387.63 | 870519 | 41.9527 | 829088 | 765725 | 748283 | 0 | 0 | 743218 | 658.529 | 0 | 0 | 0 | 113.581 | 743104 | 660.134 | 733439 | 718769.9375
4545 | 2002-07-09 08:00 | 698 | 892 | 79 | 33.24 | 1.61 | 0 | 43.8909 | 91.2926 | 50.565 | 0 | 698 | 567.139 | 81.9878 | 6.5397 | 567.139 | 76.7273 | 0.034135 | 550.853 | 73.8877 | 0.025722 | 606.024 | 606.022 | 1360970 | 50.3323 | 1332720 | 1185180 | 1158100 | 0 | 0 | 1145560 | 644.316 | 0 | 0 | 0 | 7944.54 | 1137610 | 660 | 1121880 | 1099445.5
4546 | 2002-07-09 09:00 | 858 | 928 | 87 | 35.46 | 1.25 | 0 | 56.1559 | 101.483 | 36.9084 | 0 | 858 | 742.26 | 90.5255 | 8.0388 | 742.26 | 84.7172 | 0.04196 | 732.959 | 81.5819 | 0.031618 | 790.135 | 790.131 | 1774430 | 58.2899 | 1764200 | 1511140 | 1478260 | 0 | 0 | 1456780 | 626.596 | 0 | 0 | 0 | 52797.4 | 1403980 | 660 | 1382330 | 1354682.5
4547 | 2002-07-09 10:00 | 967 | 945 | 93 | 37.68 | 1.25 | 0 | 67.8066 | 117.879 | 23.9626 | 0 | 967 | 862.575 | 96.2358 | 9.06 | 862.575 | 90.0611 | 0.04729 | 858.507 | 86.728 | 0.035634 | 916.913 | 916.912 | 2059160 | 64.1731 | 2063380 | 1717220 | 1679730 | 0 | 0 | 1650780 | 611.164 | 0 | 0 | 0 | 129787 | 1520990 | 660 | 1496340 | 1466411.625
4548 | 2002-07-09 11:00 | 1026 | 955 | 99 | 38.59 | 1.25 | 0 | 76.62 | 154.608 | 14.0563 | 0 | 1026 | 924.333 | 101.498 | 9.6128 | 924.333 | 94.986 | 0.050176 | 922.906 | 91.4707 | 0.037808 | 983.982 | 983.977 | 2209770 | 67.0209 | 2222050 | 1823250 | 1784760 | 0 | 0 | 1751360 | 603.661 | 0 | 0 | 0 | 186816 | 1564540 | 660 | 1538500 | 1507726.125
4549 | 2002-07-09 12:00 | 1021 | 955 | 98 | 39.5 | 2.39 | 0 | 75.5068 | 214.628 | 15.3131 | 0 | 1021 | 919.492 | 100.625 | 9.566 | 919.492 | 94.1685 | 0.049931 | 917.799 | 90.6834 | 0.037624 | 978.265 | 978.257 | 2196920 | 65.6898 | 2208500 | 1824990 | 1788250 | 0 | 0 | 1755110 | 607.198 | 0 | 0 | 0 | 159843 | 1595260 | 660 | 1568220 | 1536853.625
4550 | 2002-07-09 13:00 | 955 | 944 | 94 | 40.41 | 2.39 | 0 | 65.8095 | 245.876 | 26.1681 | 0 | 955 | 847.14 | 97.3253 | 8.9476 | 847.14 | 91.0807 | 0.046704 | 842.302 | 87.7099 | 0.035192 | 902.146 | 902.142 | 2025980 | 64.5621 | 2028470 | 1684320 | 1649530 | 0 | 0 | 1621430 | 609.185 | 0 | 0 | 0 | 139381 | 1482050 | 660 | 1458490 | 1429323.25
4551 | 2002-07-09 14:00 | 822 | 899 | 95 | 41.27 | 2.39 | 0 | 53.9689 | 260.575 | 39.3183 | 0 | 822 | 695.482 | 98.4079 | 7.7015 | 695.482 | 92.0939 | 0.040199 | 685.307 | 88.6856 | 0.030291 | 750.802 | 750.796 | 1686100 | 61.3703 | 1671670 | 1408050 | 1377720 | 0 | 0 | 1358300 | 614.001 | 0 | 0 | 0 | 94066.4 | 1264230 | 660 | 1245790 | 1220873.5
4552 | 2002-07-09 15:00 | 665 | 881 | 79 | 42.14 | 0.95 | 0 | 41.6633 | 270.206 | 53.0345 | 0 | 665 | 530.095 | 81.7747 | 6.2305 | 530.095 | 76.5279 | 0.032521 | 512.523 | 73.6957 | 0.024505 | 568.656 | 568.651 | 1277050 | 58.9056 | 1245770 | 1058920 | 1036720 | 0 | 0 | 1025600 | 613.382 | 0 | 0 | 0 | 77398.7 | 948202 | 660 | 935875 | 917157.8125
4553 | 2002-07-09 16:00 | 463 | 803 | 69 | 43 | 0.95 | 0 | 29.3508 | 278.099 | 66.9004 | 0 | 463 | 315.367 | 69.8165 | 4.338 | 315.367 | 65.3369 | 0.022643 | 290.944 | 62.9188 | 0.017062 | 343.263 | 343.261 | 770879 | 53.1204 | 728405 | 634174 | 620209 | 0 | 0 | 616221 | 615.053 | 0 | 0 | 0 | 47666.5 | 568555 | 659.999 | 561074 | 549852.875
4554 | 2002-07-09 17:00 | 247 | 620 | 62 | 42.38 | 0.95 | 0 | 17.2653 | 285.54 | 80.7428 | 0 | 247 | 100.272 | 54.5377 | 2.3142 | 100.272 | 51.0384 | 0.012079 | 74.1193 | 49.1495 | 0.009102 | 119.58 | 119.578 | 268542 | 45.9055 | 234570 | 209825 | 205249 | 0 | 0 | 204776 | 593.319 | 0 | 0 | 0 | 41638.4 | 163138 | 660 | 158535 | 155364.7344
4555 | 2002-07-09 18:00 | 56 | 413 | 14 | 41.75 | 3.06 | 0 | 5.6154 | 293.242 | 90 | 0 | 56 | 0 | 11.9451 | 0.52468 | 0 | 11.1787 | 0.0027386 | 0 | 10.7649 | 0.0020636 | 10.444 | 10.4433 | 23453 | 42.0174 | 14087.5 | 12784.6 | 12562.2 | 0 | 0 | 12559.4 | 473.957 | 0 | 0 | 0 | 12559.4 | 0 | 660 | 0 | 0
4556 | 2002-07-09 19:00 | 0 | 9 | 0 | 41.12 | 3.06 | 0
4557 | 2002-07-09 20:00 | 0 | 0 | 0 | 39.99 | 3.06 | 0
4558 | 2002-07-09 21:00 | 0 | 0 | 0 | 38.85 | 4.94 | 0
4559 | 2002-07-09 22:00 | 0 | 0 | 0 | 37.71 | 4.94 | 0
4560 | 2002-07-09 23:00 | 0 | 0 | 0 | 36.34 | 4.94 | 0
4561 | 2002-07-10 | 0 | 0 | 0 | 34.98 | 5.85 | 0
4562 | 2002-07-10 01:00 | 0 | 0 | 0 | 33.61 | 5.85 | 0
4563 | 2002-07-10 02:00 | 0 | 0 | 0 | 33.05 | 5.85 | 0
4564 | 2002-07-10 03:00 | 0 | 0 | 0 | 32.49 | 3.85 | 0
4565 | 2002-07-10 04:00 | 1 | 20 | 1 | 31.93 | 3.85 | 0 | -3.5034 | 59.8621 | 90 | 0 | 1 | 0 | 1.0012 | 0.0093692 | 0 | 0.93693 | 0 | 0 | 0.90225 | 0 | 0.87519 | 0.87515 | 1965.36 | 31.9513 | 187.128 | 188.638 | 187.764 | 0 | 0 | 187.756 | 130.819 | 0 | 0 | 0 | 187.756 | 0 | 660 | 0 | 0
4566 | 2002-07-10 05:00 | 72 | 188 | 47 | 32.09 | 3.85 | 0 | 7.5979 | 68.2114 | 90 | 0 | 72 | 0 | 35.6693 | 0.67458 | 0 | 33.3807 | 0.0035211 | 0 | 32.1453 | 0.0026532 | 31.1835 | 31.1824 | 70027.7 | 32.8479 | 52695.4 | 50420.1 | 49307.1 | 0 | 0 | 49277.6 | 572.18 | 0 | 0 | 0 | 20018.4 | 29259.2 | 660 | 28198.8 | 27634.8027
4567 | 2002-07-10 06:00 | 274 | 515 | 103 | 32.25 | 3.92 | 0 | 19.3394 | 75.8393 | 78.3122 | 0 | 274 | 104.604 | 91.5911 | 2.5672 | 102.466 | 85.7145 | 0.0134 | 82.2988 | 82.5422 | 0.010097 | 159.906 | 159.898 | 359092 | 36.1187 | 321326 | 303891 | 286330 | 0 | 0 | 285541 | 642.35 | 0 | 0 | 0 | 3118.59 | 282423 | 660 | 276500 | 270969.5
4568 | 2002-07-10 07:00 | 504 | 793 | 90 | 32.41 | 3.92 | 0 | 31.4774 | 83.3189 | 64.4495 | 0 | 504 | 341.964 | 89.7913 | 4.7221 | 341.964 | 84.0301 | 0.024648 | 319.42 | 80.9202 | 0.018573 | 388.348 | 388.345 | 872129 | 41.8059 | 830722 | 767815 | 748725 | 0 | 0 | 743666 | 659.017 | 0 | 0 | 0 | -13.5953 | 743680 | 660.812 | 733982 | 719302.1875
4569 | 2002-07-10 08:00 | 697 | 892 | 79 | 33.92 | 3.92 | 0 | 43.8043 | 91.426 | 50.5849 | 0 | 697 | 566.875 | 82.0332 | 6.5304 | 566.875 | 76.7698 | 0.034086 | 550.578 | 73.9286 | 0.025685 | 605.796 | 605.796 | 1360460 | 48.5771 | 1332190 | 1195170 | 1169180 | 0 | 0 | 1156550 | 648.56 | 0 | 0 | 0 | 3282.96 | 1153270 | 660 | 1137220 | 1114474.375
4570 | 2002-07-10 09:00 | 846 | 905 | 95 | 35.44 | 4.65 | 0 | 56.0658 | 101.65 | 36.9095 | 0 | 846 | 723.76 | 98.504 | 7.9264 | 723.76 | 92.1838 | 0.041373 | 714.689 | 88.7721 | 0.031175 | 779.388 | 779.383 | 1750300 | 53.4169 | 1738910 | 1526700 | 1492380 | 0 | 0 | 1471470 | 641.115 | 0 | 0 | 0 | 13678.4 | 1457800 | 660 | 1434840 | 1406143
4571 | 2002-07-10 10:00 | 967 | 946 | 92 | 36.96 | 4.65 | 0 | 67.7031 | 118.086 | 23.9312 | 0 | 967 | 864.411 | 95.3087 | 9.06 | 864.411 | 89.1935 | 0.04729 | 860.346 | 85.8925 | 0.035634 | 917.886 | 917.88 | 2061330 | 58.1314 | 2065670 | 1774130 | 1734460 | 0 | 0 | 1705510 | 631.556 | 0 | 0 | 0 | 43893.2 | 1661620 | 660 | 1632340 | 1599697.625
4572 | 2002-07-10 11:00 | 1014 | 936 | 106 | 37.31 | 4.65 | 0 | 76.4911 | 154.684 | 13.9576 | 0 | 1014 | 906.264 | 108.412 | 9.5004 | 906.264 | 101.456 | 0.049589 | 904.885 | 97.7014 | 0.037366 | 972.545 | 972.539 | 2184080 | 59.7422 | 2194970 | 1871050 | 1830870 | 0 | 0 | 1798160 | 626.712 | 0 | 0 | 0 | 60524.3 | 1737640 | 660 | 1705710 | 1671591.625
4573 | 2002-07-10 12:00 | 1020 | 920 | 131 | 37.67 | 5.35 | 0 | 75.4143 | 214.262 | 15.191 | 0 | 1020 | 886.506 | 132.591 | 9.5566 | 886.506 | 124.083 | 0.049882 | 884.902 | 119.491 | 0.037587 | 974.297 | 974.294 | 2188020 | 59.1427 | 2199130 | 1880400 | 1838260 | 0 | 0 | 1805590 | 629.211 | 0 | 0 | 0 | 52199 | 1753390 | 660 | 1720890 | 1686474.625
4574 | 2002-07-10 13:00 | 907 | 776 | 200 | 38.02 | 5.35 | 0 | 65.7622 | 245.579 | 26.0846 | 0 | 907 | 696.375 | 205.935 | 8.4979 | 696.375 | 192.722 | 0.044356 | 692.427 | 185.589 | 0.033423 | 851.708 | 851.702 | 1912710 | 56.7909 | 1909350 | 1649680 | 1612240 | 0 | 0 | 1587340 | 633.449 | 0 | 0 | 0 | 33900.2 | 1553440 | 660 | 1527760 | 1497201.25
4575 | 2002-07-10 14:00 | 832 | 881 | 120 | 38.61 | 5.35 | 0 | 53.9368 | 260.36 | 39.259 | 0 | 832 | 681.987 | 122.745 | 7.7952 | 681.987 | 114.87 | 0.040688 | 672.047 | 110.618 | 0.030659 | 759.215 | 759.208 | 1704990 | 55.3424 | 1691450 | 1470270 | 1438480 | 0 | 0 | 1418630 | 634.303 | 0 | 0 | 0 | 27849.6 | 1390780 | 660 | 1369440 | 1342048.125
4576 | 2002-07-10 15:00 | 665 | 881 | 79 | 39.21 | 3.8 | 0 | 41.6344 | 270.035 | 52.9914 | 0 | 665 | 530.926 | 81.8265 | 6.2305 | 530.926 | 76.5764 | 0.032521 | 513.37 | 73.7423 | 0.024505 | 569.523 | 569.52 | 1278990 | 53.0985 | 1247780 | 1093480 | 1069510 | 0 | 0 | 1058380 | 632.325 | 0 | 0 | 0 | 24507.3 | 1033870 | 660 | 1020220 | 999817.3125
4577 | 2002-07-10 16:00 | 467 | 815 | 67 | 39.8 | 3.8 | 0 | 29.3192 | 277.953 | 66.8704 | 0 | 467 | 320.875 | 67.9493 | 4.3754 | 320.875 | 63.5895 | 0.022838 | 296.076 | 61.2361 | 0.017209 | 346.609 | 346.607 | 778390 | 48.2525 | 735969 | 657642 | 643119 | 0 | 0 | 639047 | 631.27 | 0 | 0 | 0 | 18181 | 620866 | 659.999 | 612795 | 600539.25
4578 | 2002-07-10 17:00 | 249 | 634 | 60 | 39.07 | 3.8 | 0 | 17.2276 | 285.408 | 80.7252 | 0 | 249 | 102.851 | 52.7953 | 2.3329 | 102.851 | 49.4079 | 0.012177 | 76.086 | 47.5793 | 0.0091757 | 119.964 | 119.961 | 269401 | 41.9954 | 235385 | 215272 | 210429 | 0 | 0 | 209954 | 606.898 | 0 | 0 | 0 | 24417.8 | 185536 | 659.999 | 180551 | 176939.8594
4579 | 2002-07-10 18:00 | 56 | 423 | 13 | 38.35 | 6.77 | 0 | 5.5684 | 293.118 | 90 | 0 | 56 | 0 | 11.1181 | 0.52468 | 0 | 10.4048 | 0.0027386 | 0 | 10.0197 | 0.0020636 | 9.7211 | 9.7208 | 21830.6 | 38.5455 | 12834 | 11908.7 | 11687.5 | 0 | 0 | 11685.2 | 481.492 | 0 | 0 | 0 | 11685.2 | 0 | 660 | 0 | 0
4580 | 2002-07-10 19:00 | 0 | 8 | 0 | 37.62 | 6.77 | 0
4581 | 2002-07-10 20:00 | 0 | 0 | 0 | 36.5 | 6.77 | 0
4582 | 2002-07-10 21:00 | 0 | 0 | 0 | 35.38 | 5.51 | 0
4583 | 2002-07-10 22:00 | 0 | 0 | 0 | 34.25 | 5.51 | 0
4584 | 2002-07-10 23:00 | 0 | 0 | 0 | 33.19 | 5.51 | 0
4585 | 2002-07-11 | 0 | 0 | 0 | 32.13 | 6.41 | 0
4586 | 2002-07-11 01:00 | 0 | 0 | 0 | 31.07 | 6.41 | 0
4587 | 2002-07-11 02:00 | 0 | 0 | 0 | 30.78 | 6.41 | 0
4588 | 2002-07-11 03:00 | 0 | 0 | 0 | 30.49 | 3.69 | 0
4589 | 2002-07-11 04:00 | 0 | 0 | 0 | 30.2 | 3.69 | 0
4590 | 2002-07-11 05:00 | 18 | 0 | 18 | 30.55 | 3.69 | 0 | 7.4982 | 68.3023 | 90 | 0 | 18 | 0 | 17.1849 | 0.16865 | 0 | 16.0823 | 0.00088028 | 0 | 15.4871 | 0.00066331 | 15.0231 | 15.023 | 33737.8 | 30.919 | 22244.4 | 21522 | 21090.3 | 0 | 0 | 21084.2 | 538.031 | 0 | 0 | 0 | 20805.1 | 279.053 | 660 | 268.455 | 263.0855
4591 | 2002-07-11 06:00 | 117 | 10 | 114 | 30.89 | 2.28 | 0 | 19.2459 | 75.9419 | 78.3565 | 0 | 117 | 1.8368 | 102.725 | 1.0962 | 1.796 | 96.1337 | 0.0057218 | 1.4408 | 92.5758 | 0.0043115 | 91.2003 | 91.1965 | 204804 | 33.3495 | 174607 | 167149 | 162985 | 0 | 0 | 162715 | 623.319 | 0 | 0 | 0 | 7440.96 | 155274 | 660 | 150820 | 147804.0156
4592 | 2002-07-11 07:00 | 137 | 0 | 137 | 31.23 | 2.28 | 0 | 31.3881 | 83.4374 | 64.4816 | 0 | 137 | 0 | 125.853 | 1.2836 | 0 | 117.778 | 0.0066999 | 0 | 113.419 | 0.0050485 | 110.021 | 110.015 | 247066 | 34.197 | 214262 | 204336 | 199295 | 0 | 0 | 198900 | 630.055 | 0 | 0 | 0 | 6173.46 | 192726 | 660 | 187632 | 183879.0312
4593 | 2002-07-11 08:00 | 178 | 2 | 177 | 32.55 | 2.28 | 0 | 43.7162 | 91.5678 | 50.6027 | 0 | 178 | 0.9184 | 163.59 | 1.6677 | 0.9184 | 153.094 | 0.0087049 | 0.89197 | 147.428 | 0.0065594 | 143.876 | 143.873 | 323103 | 36.4301 | 286640 | 270508 | 263624 | 0 | 0 | 262944 | 635.628 | 0 | 0 | 0 | 5598.62 | 257346 | 660 | 251541 | 246509.8125
4594 | 2002-07-11 09:00 | 338 | 37 | 307 | 33.88 | 2.14 | 0 | 55.9736 | 101.827 | 36.9079 | 0 | 338 | 29.9086 | 312.283 | 3.1668 | 29.9086 | 292.247 | 0.01653 | 29.5338 | 281.431 | 0.012455 | 301.648 | 301.63 | 677383 | 42.0909 | 634606 | 584541 | 569628 | 0 | 0 | 566590 | 647.62 | 0 | 0 | 0 | 2762.55 | 563828 | 660 | 556396 | 545268.125
4595 | 2002-07-11 10:00 | 764 | 426 | 370 | 35.2 | 2.14 | 0 | 67.5966 | 118.307 | 23.8961 | 0 | 764 | 389.635 | 374.336 | 7.1581 | 389.635 | 350.318 | 0.037363 | 387.809 | 337.353 | 0.028154 | 703.434 | 703.412 | 1579680 | 54.3482 | 1560420 | 1361950 | 1330040 | 0 | 0 | 1313180 | 636.711 | 0 | 0 | 0 | 22729.4 | 1290450 | 660 | 1271430 | 1246000.125
4596 | 2002-07-11 11:00 | 1022 | 752 | 293 | 35.49 | 2.14 | 0 | 76.3569 | 154.775 | 13.8529 | 0 | 1022 | 728.347 | 303.495 | 9.5753 | 728.347 | 284.022 | 0.04998 | 727.256 | 273.511 | 0.037661 | 970.781 | 970.773 | 2180120 | 61.9162 | 2190800 | 1846460 | 1805120 | 0 | 0 | 1772700 | 620.202 | 0 | 0 | 0 | 89196 | 1683510 | 660 | 1653480 | 1620409.5
4597 | 2002-07-11 12:00 | 420 | 60 | 362 | 35.79 | 3.55 | 0 | 75.315 | 213.894 | 15.0648 | 0 | 420 | 57.898 | 372.282 | 3.9351 | 57.898 | 348.396 | 0.02054 | 57.7949 | 335.502 | 0.015477 | 381.513 | 381.51 | 856774 | 45.2481 | 815194 | 740443 | 723087 | 0 | 0 | 718157 | 644.217 | 0 | 0 | 0 | 4949.94 | 713207 | 659.999 | 703935 | 689856.75
4598 | 2002-07-11 13:00 | 438 | 37 | 404 | 36.08 | 3.55 | 0 | 65.7092 | 245.273 | 26.0002 | 0 | 438 | 33.5271 | 419.829 | 4.1037 | 33.5271 | 392.892 | 0.02142 | 33.3384 | 378.351 | 0.01614 | 399.355 | 399.339 | 896814 | 45.9801 | 855809 | 774769 | 755657 | 0 | 0 | 750302 | 645.581 | 0 | 0 | 0 | 5315.22 | 744987 | 659.999 | 735302 | 720595.9375
4599 | 2002-07-11 14:00 | 551 | 211 | 381 | 36.1 | 3.55 | 0 | 53.8999 | 260.136 | 39.2002 | 0 | 551 | 163.047 | 366.525 | 5.1624 | 163.047 | 343.008 | 0.026946 | 160.679 | 330.314 | 0.020304 | 476.283 | 476.266 | 1069570 | 47.9072 | 1032090 | 926870 | 905237 | 0 | 0 | 897563 | 645.357 | 0 | 0 | 0 | 6505.72 | 891057 | 659.999 | 879474 | 861884.1875
4600 | 2002-07-11 15:00 | 533 | 416 | 257 | 36.12 | 4.06 | 0 | 41.6008 | 269.858 | 52.9496 | 0 | 533 | 250.467 | 249.63 | 4.9938 | 250.467 | 233.613 | 0.026066 | 242.206 | 224.967 | 0.019641 | 453.177 | 453.172 | 1017710 | 46.9841 | 978976 | 882893 | 862119 | 0 | 0 | 855167 | 646.567 | 0 | 0 | 0 | 5099.39 | 850068 | 659.999 | 839017 | 822236.5
4601 | 2002-07-11 16:00 | 466 | 681 | 132 | 36.15 | 4.06 | 0 | 29.2831 | 277.802 | 66.8424 | 0 | 466 | 268.539 | 127.122 | 4.3661 | 268.539 | 118.966 | 0.022789 | 247.824 | 114.563 | 0.017172 | 351.531 | 351.524 | 789432 | 44.5772 | 747103 | 680450 | 664333 | 0 | 0 | 660170 | 645.076 | 0 | 0 | 0 | 4853.77 | 655316 | 660 | 646797 | 633861.375
4602 | 2002-07-11 17:00 | 234 | 536 | 75 | 35.87 | 4.06 | 0 | 17.1851 | 285.271 | 80.71 | 0 | 234 | 86.8739 | 66.5202 | 2.1924 | 86.8739 | 62.2521 | 0.011444 | 64.3103 | 59.9482 | 0.008623 | 120.539 | 120.537 | 270694 | 38.7597 | 236612 | 220295 | 215472 | 0 | 0 | 214990 | 617.589 | 0 | 0 | 0 | 14364.9 | 200626 | 660 | 195417 | 191508.5938
4603 | 2002-07-11 18:00 | 53 | 357 | 17 | 35.59 | 5.48 | 0 | 5.5164 | 292.99 | 90 | 0 | 53 | 0 | 13.069 | 0.49657 | 0 | 12.2305 | 0.0025919 | 0 | 11.7779 | 0.0019531 | 11.4264 | 11.426 | 25659.9 | 35.8397 | 15809.4 | 14881.8 | 14601 | 0 | 0 | 14597.6 | 501.45 | 0 | 0 | 0 | 14597.6 | 0 | 660 | 0 | 0
4604 | 2002-07-11 19:00 | 0 | 6 | 0 | 35.3 | 5.48 | 0
4605 | 2002-07-11 20:00 | 0 | 0 | 0 | 34.42 | 5.48 | 0
4606 | 2002-07-11 21:00 | 0 | 0 | 0 | 33.54 | 5.1 | 0
4607 | 2002-07-11 22:00 | 0 | 0 | 0 | 32.66 | 5.1 | 0
4608 | 2002-07-11 23:00 | 0 | 0 | 0 | 31.77 | 5.1 | 0
4609 | 2002-07-12 | 0 | 0 | 0 | 30.88 | 6.32 | 0
4610 | 2002-07-12 01:00 | 0 | 0 | 0 | 29.99 | 6.32 | 0
4611 | 2002-07-12 02:00 | 0 | 0 | 0 | 29.44 | 6.32 | 0
4612 | 2002-07-12 03:00 | 0 | 0 | 0 | 28.88 | 4.68 | 0
4613 | 2002-07-12 04:00 | 1 | 24 | 1 | 28.32 | 4.68 | 0 | -3.7215 | 60.0285 | 90 | 0 | 1 | 0 | 1.0014 | 0.0093692 | 0 | 0.93711 | 0 | 0 | 0.90243 | 0 | 0.87535 | 0.87528 | 1965.67 | 28.3401 | 187.17 | 187.9 | 187.045 | 0 | 0 | 187.036 | 130.577 | 0 | 0 | 0 | 187.036 | 0 | 660 | 0 | 0
4614 | 2002-07-12 05:00 | 77 | 246 | 45 | 28.81 | 4.68 | 0 | 7.3962 | 68.3993 | 90 | 0 | 77 | 0 | 34.1668 | 0.72143 | 0 | 31.9746 | 0.0037656 | 0 | 30.7912 | 0.0028375 | 29.8702 | 29.8684 | 67076.7 | 29.4976 | 50154.1 | 48915.3 | 47816.4 | 0 | 0 | 47789.6 | 582.577 | 0 | 0 | 0 | 13955.8 | 33833.8 | 660 | 32616.8 | 31964.4961
4615 | 2002-07-12 06:00 | 292 | 641 | 81 | 29.31 | 2.82 | 0 | 19.1506 | 76.0512 | 78.3999 | 0 | 292 | 129.333 | 73.3736 | 2.7358 | 126.248 | 68.6658 | 0.01428 | 101.168 | 66.1245 | 0.01076 | 162.284 | 162.281 | 364446 | 33.5321 | 326548 | 312967 | 292755 | 0 | 0 | 291942 | 648.595 | 0 | 0 | 0 | 842.994 | 291099 | 660 | 285161 | 279457.8438
4616 | 2002-07-12 07:00 | 501 | 828 | 70 | 29.8 | 2.82 | 0 | 31.2971 | 83.5631 | 64.5121 | 0 | 501 | 357.029 | 71.4135 | 4.694 | 357.029 | 66.8314 | 0.024501 | 333.396 | 64.358 | 0.018462 | 385.84 | 385.836 | 866489 | 39.8385 | 825002 | 769893 | 751732 | 0 | 0 | 746732 | 665.157 | 0 | 0 | 0 | 0 | 746732 | 665.157 | 736832 | 722095.625
4617 | 2002-07-12 08:00 | 694 | 890 | 80 | 31.56 | 2.82 | 0 | 43.6264 | 91.718 | 50.6185 | 0 | 694 | 564.635 | 83.1215 | 6.5022 | 564.635 | 77.7883 | 0.033939 | 548.371 | 74.9094 | 0.025574 | 604.607 | 604.604 | 1357790 | 47.2903 | 1329420 | 1200250 | 1172130 | 0 | 0 | 1159720 | 656.01 | 0 | 0 | 0 | 642.893 | 1159070 | 660 | 1142900 | 1120039.875
4618 | 2002-07-12 09:00 | 855 | 862 | 142 | 33.33 | 2.42 | 0 | 55.8796 | 102.015 | 36.9036 | 0 | 855 | 688.701 | 148.27 | 8.0107 | 688.701 | 138.757 | 0.041813 | 680.073 | 133.622 | 0.031507 | 789.314 | 789.309 | 1772580 | 54.4191 | 1762270 | 1539580 | 1505070 | 0 | 0 | 1483630 | 638.715 | 0 | 0 | 0 | 19337.2 | 1464300 | 660 | 1441180 | 1412358.375
4619 | 2002-07-12 10:00 | 822 | 505 | 356 | 35.1 | 2.42 | 0 | 67.4871 | 118.541 | 23.8572 | 0 | 822 | 461.34 | 361.238 | 7.7015 | 461.34 | 338.06 | 0.040199 | 459.185 | 325.549 | 0.030291 | 761.221 | 761.192 | 1709440 | 55.4379 | 1696120 | 1473540 | 1439660 | 0 | 0 | 1419800 | 634.795 | 0 | 0 | 0 | 27395 | 1392410 | 660 | 1371030 | 1343607
4620 | 2002-07-12 11:00 | 298 | 31 | 268 | 35.78 | 2.42 | 0 | 76.2175 | 154.88 | 13.7425 | 0 | 298 | 30.0051 | 269.589 | 2.792 | 30.0051 | 252.291 | 0.014573 | 29.9609 | 242.954 | 0.010981 | 264.738 | 264.734 | 594527 | 42.8533 | 552042 | 505969 | 493563 | 0 | 0 | 491218 | 638.721 | 0 | 0 | 0 | 7179.1 | 484039 | 660 | 477466 | 467916.3125
4621 | 2002-07-12 12:00 | 980 | 773 | 234 | 36.47 | 3.91 | 0 | 75.2087 | 213.525 | 14.9347 | 0 | 980 | 745.505 | 246.706 | 9.1818 | 745.505 | 230.877 | 0.047926 | 744.202 | 222.332 | 0.036113 | 937.573 | 937.556 | 2105510 | 59.1689 | 2112200 | 1804930 | 1765770 | 0 | 0 | 1735400 | 627.52 | 0 | 0 | 0 | 55135.9 | 1680270 | 660 | 1650350 | 1617345.125
4622 | 2002-07-12 13:00 | 951 | 944 | 91 | 37.15 | 3.91 | 0 | 65.6504 | 244.959 | 25.9152 | 0 | 951 | 849.045 | 94.5412 | 8.9101 | 849.045 | 88.4752 | 0.046508 | 844.299 | 85.2008 | 0.035045 | 901.649 | 901.646 | 2024870 | 58.9795 | 2027290 | 1733270 | 1697740 | 0 | 0 | 1669570 | 626.721 | 0 | 0 | 0 | 55920.3 | 1613650 | 660 | 1585990 | 1554273.5
4623 | 2002-07-12 14:00 | 831 | 751 | 225 | 37.49 | 3.91 | 0 | 53.8579 | 259.906 | 39.1421 | 0 | 831 | 582.006 | 229.739 | 7.7858 | 582.006 | 214.998 | 0.040639 | 573.586 | 207.041 | 0.030623 | 757.238 | 757.224 | 1700540 | 55.8229 | 1686780 | 1462550 | 1431460 | 0 | 0 | 1411680 | 632.554 | 0 | 0 | 0 | 32376.6 | 1379300 | 660 | 1358230 | 1331064.25
4624 | 2002-07-12 15:00 | 221 | 10 | 214 | 37.83 | 4.06 | 0 | 41.5626 | 269.674 | 52.9093 | 0 | 221 | 6.3631 | 197.67 | 2.0706 | 6.3631 | 184.987 | 0.010808 | 6.1537 | 178.141 | 0.0081439 | 178.774 | 178.764 | 401461 | 42.1156 | 362296 | 332243 | 324109 | 0 | 0 | 323048 | 625.119 | 0 | 0 | 0 | 14621.6 | 308427 | 659.999 | 302415 | 296366.8438
4625 | 2002-07-12 16:00 | 151 | 0 | 151 | 38.17 | 4.06 | 0 | 29.2423 | 277.645 | 66.8164 | 0 | 151 | 0 | 138.275 | 1.4147 | 0 | 129.403 | 0.0073845 | 0 | 124.614 | 0.0055644 | 120.881 | 120.869 | 271439 | 41.0676 | 237332 | 218184 | 212890 | 0 | 0 | 212408 | 609.375 | 0 | 0 | 0 | 20789.5 | 191619 | 659.999 | 186541 | 182809.8281
4626 | 2002-07-12 17:00 | 108 | 4 | 107 | 37.7 | 4.06 | 0 | 17.1377 | 285.13 | 80.6973 | 0 | 108 | 0.54858 | 95.7453 | 1.0119 | 0.54858 | 89.6021 | 0.0052816 | 0.40633 | 86.286 | 0.0039798 | 84.0954 | 84.0929 | 188851 | 39.716 | 159769 | 147593 | 144075 | 0 | 0 | 143846 | 598.566 | 0 | 0 | 0 | 24138.6 | 119707 | 659.999 | 116019 | 113698.2031
4627 | 2002-07-12 18:00 | 24 | 3 | 24 | 37.24 | 8.38 | 0 | 5.4593 | 292.858 | 90 | 0 | 24 | 0 | 21.9992 | 0.22486 | 0 | 20.5877 | 0.0011737 | 0 | 19.8257 | 0.00088441 | 19.2318 | 19.231 | 43187.8 | 37.5894 | 29973.4 | 27863.8 | 27292.1 | 0 | 0 | 27281.5 | 528.571 | 0 | 0 | 0 | 27281.5 | 0 | 660 | 0 | 0
4628 | 2002-07-12 19:00 | 0 | 0 | 0 | 36.77 | 8.38 | 0
4629 | 2002-07-12 20:00 | 0 | 0 | 0 | 35.6 | 8.38 | 0
4630 | 2002-07-12 21:00 | 0 | 0 | 0 | 34.43 | 6.39 | 0
4631 | 2002-07-12 22:00 | 0 | 0 | 0 | 33.27 | 6.39 | 0
4632 | 2002-07-12 23:00 | 0 | 0 | 0 | 32.36 | 6.39 | 0
4633 | 2002-07-13 | 0 | 0 | 0 | 31.45 | 7.4 | 0
4634 | 2002-07-13 01:00 | 0 | 0 | 0 | 30.55 | 7.4 | 0
4635 | 2002-07-13 02:00 | 0 | 0 | 0 | 30.13 | 7.4 | 0
4636 | 2002-07-13 03:00 | 0 | 0 | 0 | 29.71 | 5.69 | 0
4637 | 2002-07-13 04:00 | 1 | 27 | 1 | 29.29 | 5.69 | 0 | -3.8346 | 60.1207 | 90 | 0 | 1 | 0 | 1.0015 | 0.0093692 | 0 | 0.9372 | 0 | 0 | 0.90252 | 0 | 0.87544 | 0.87541 | 1965.93 | 29.3089 | 187.238 | 188.179 | 187.306 | 0 | 0 | 187.298 | 130.696 | 0 | 0 | 0 | 187.298 | 0 | 660 | 0 | 0
4638 | 2002-07-13 05:00 | 91 | 293 | 53 | 29.62 | 5.69 | 0 | 7.2921 | 68.5025 | 90 | 0 | 91 | 0 | 40.7302 | 0.8526 | 0 | 38.1169 | 0.0044503 | 0 | 36.7062 | 0.0033534 | 35.6082 | 35.6052 | 79960.2 | 30.3876 | 61310.1 | 59509 | 58158.4 | 0 | 0 | 58119.5 | 587.611 | 0 | 0 | 0 | 13843 | 44276.5 | 660 | 42711.7 | 41857.4375
4639 | 2002-07-13 06:00 | 237 | 360 | 119 | 29.96 | 3.4 | 0 | 19.0535 | 76.1669 | 78.4422 | 0 | 237 | 72.4211 | 105.677 | 2.2205 | 70.5608 | 98.8966 | 0.01159 | 56.48 | 95.2365 | 0.0087335 | 147.173 | 147.181 | 330531 | 33.6451 | 293807 | 281339 | 268317 | 0 | 0 | 267638 | 648.344 | 0 | 0 | 0 | 1336.1 | 266302 | 660 | 260449 | 255239.6719
4640 | 2002-07-13 07:00 | 500 | 702 | 136 | 30.29 | 3.4 | 0 | 31.2047 | 83.6959 | 64.5411 | 0 | 500 | 302.01 | 132.331 | 4.6846 | 302.01 | 123.84 | 0.024452 | 281.982 | 119.257 | 0.018425 | 389.219 | 389.211 | 874068 | 40.035 | 832686 | 776365 | 759360 | 0 | 0 | 754196 | 661.491 | 0 | 0 | 0 | -7.0247 | 754202 | 661.588 | 744338 | 729451.25
4641 | 2002-07-13 08:00 | 666 | 786 | 124 | 32.18 | 3.4 | 0 | 43.5351 | 91.8765 | 50.6322 | 0 | 666 | 499.113 | 127.363 | 6.2399 | 499.113 | 119.191 | 0.03257 | 484.725 | 114.78 | 0.024542 | 581.544 | 581.534 | 1305980 | 46.7403 | 1275720 | 1154500 | 1128000 | 0 | 0 | 1116530 | 656.858 | 0 | 0 | 0 | 578.635 | 1115950 | 660 | 1100660 | 1078651.25
4642 | 2002-07-13 09:00 | 841 | 762 | 211 | 34.07 | 1.65 | 0 | 55.7837 | 102.214 | 36.8966 | 0 | 841 | 609.277 | 217.546 | 7.8795 | 609.277 | 203.588 | 0.041128 | 601.648 | 196.054 | 0.030991 | 773.8 | 773.789 | 1737730 | 55.8356 | 1725740 | 1496530 | 1462260 | 0 | 0 | 1441790 | 634.838 | 0 | 0 | 0 | 29724.5 | 1412070 | 660 | 1390220 | 1362412.625
4643 | 2002-07-13 10:00 | 473 | 126 | 357 | 35.96 | 1.65 | 0 | 67.3748 | 118.789 | 23.8146 | 0 | 473 | 114.971 | 349.424 | 4.4316 | 114.971 | 327.005 | 0.023132 | 114.436 | 314.902 | 0.01743 | 416.475 | 416.456 | 935255 | 47.6743 | 894874 | 803510 | 784470 | 0 | 0 | 778605 | 640.903 | 0 | 0 | 0 | 9431.35 | 769174 | 660 | 759175 | 743991.3125
4644 | 2002-07-13 11:00 | 178 | 13 | 165 | 36.62 | 1.65 | 0 | 76.0729 | 155 | 13.6262 | 0 | 178 | 13.0168 | 161.873 | 1.6677 | 13.0168 | 151.487 | 0.0087049 | 12.9979 | 145.88 | 0.0065594 | 154.118 | 154.111 | 346094 | 40.9549 | 308734 | 284545 | 278064 | 0 | 0 | 277270 | 620.25 | 0 | 0 | 0 | 15049.5 | 262221 | 659.999 | 256382 | 251254.7031
4645 | 2002-07-13 12:00 | 917 | 595 | 343 | 37.29 | 5.23 | 0 | 75.0955 | 213.155 | 14.8007 | 0 | 917 | 574.276 | 352.709 | 8.5916 | 574.276 | 330.079 | 0.044845 | 573.29 | 317.863 | 0.033792 | 864.451 | 864.443 | 1941320 | 56.4905 | 1939420 | 1678470 | 1641630 | 0 | 0 | 1615880 | 634.424 | 0 | 0 | 0 | 31540.9 | 1584340 | 660 | 1557650 | 1526500.25
4646 | 2002-07-13 13:00 | 952 | 878 | 153 | 37.95 | 5.23 | 0 | 65.5859 | 244.637 | 25.8297 | 0 | 952 | 789.797 | 154.4 | 8.9195 | 789.797 | 144.494 | 0.046557 | 785.413 | 139.146 | 0.035082 | 896.857 | 896.848 | 2014090 | 57.8703 | 2015950 | 1733280 | 1694900 | 0 | 0 | 1667200 | 631.157 | 0 | 0 | 0 | 42307.4 | 1624900 | 660 | 1596870 | 1564930.125
4647 | 2002-07-13 14:00 | 831 | 922 | 87 | 38.2 | 5.23 | 0 | 53.811 | 259.667 | 39.0848 | 0 | 831 | 715.552 | 90.7383 | 7.7858 | 715.552 | 84.9163 | 0.040639 | 705.237 | 81.7736 | 0.030623 | 763.43 | 763.425 | 1714450 | 55.1567 | 1701350 | 1480370 | 1448010 | 0 | 0 | 1427910 | 634.792 | 0 | 0 | 0 | 26059.9 | 1401850 | 660 | 1380240 | 1352636.625
4648 | 2002-07-13 15:00 | 660 | 873 | 81 | 38.45 | 4.7 | 0 | 41.5196 | 269.484 | 52.8705 | 0 | 660 | 527.24 | 83.9669 | 6.1837 | 527.24 | 78.5794 | 0.032277 | 509.929 | 75.6712 | 0.024321 | 568.056 | 568.053 | 1275700 | 51.5098 | 1244380 | 1099370 | 1074110 | 0 | 0 | 1063120 | 639.197 | 0 | 0 | 0 | 14984.2 | 1048140 | 660 | 1034210 | 1013525.3125
4649 | 2002-07-13 16:00 | 465 | 786 | 81 | 38.7 | 4.7 | 0 | 29.1968 | 277.483 | 66.7924 | 0 | 465 | 310.203 | 80.5403 | 4.3567 | 310.203 | 75.3727 | 0.02274 | 286.354 | 72.5832 | 0.017135 | 348.186 | 348.185 | 781936 | 46.7049 | 739544 | 666206 | 651185 | 0 | 0 | 647075 | 636.025 | 0 | 0 | 0 | 11673.7 | 635402 | 660 | 627141 | 614598.625
4650 | 2002-07-13 17:00 | 232 | 528 | 76 | 38.08 | 4.7 | 0 | 17.0856 | 284.984 | 80.6871 | 0 | 232 | 85.9255 | 67.5982 | 2.1737 | 85.9255 | 63.261 | 0.011346 | 63.6731 | 60.9198 | 0.0085493 | 120.863 | 120.861 | 271422 | 40.8586 | 237303 | 218416 | 213639 | 0 | 0 | 213154 | 610.787 | 0 | 0 | 0 | 20452.9 | 192701 | 659.999 | 187607 | 183854.7969
4651 | 2002-07-13 18:00 | 51 | 352 | 17 | 37.45 | 9.47 | 0 | 5.3971 | 292.722 | 90 | 0 | 51 | 0 | 13.1233 | 0.47783 | 0 | 12.2813 | 0.0024941 | 0 | 11.8268 | 0.0018794 | 11.4738 | 11.4734 | 25766.3 | 37.6448 | 15892.9 | 14799.8 | 14524.7 | 0 | 0 | 14521.3 | 496.028 | 0 | 0 | 0 | 14521.3 | 0 | 660 | 0 | 0
4652 | 2002-07-13 19:00 | 0 | 4 | 0 | 36.83 | 9.47 | 0
4653 | 2002-07-13 20:00 | 0 | 0 | 0 | 35.5 | 9.47 | 0
4654 | 2002-07-13 21:00 | 0 | 0 | 0 | 34.17 | 7.36 | 0
4655 | 2002-07-13 22:00 | 0 | 0 | 0 | 32.84 | 7.36 | 0
4656 | 2002-07-13 23:00 | 0 | 0 | 0 | 31.81 | 7.36 | 0
4657 | 2002-07-14 | 0 | 0 | 0 | 30.78 | 9.56 | 0
4658 | 2002-07-14 01:00 | 0 | 0 | 0 | 29.76 | 9.56 | 0
4659 | 2002-07-14 02:00 | 0 | 0 | 0 | 29.62 | 9.56 | 0
4660 | 2002-07-14 03:00 | 0 | 0 | 0 | 29.47 | 7.15 | 0
4661 | 2002-07-14 04:00 | 1 | 37 | 0 | 29.33 | 7.15 | 0 | -3.9502 | 60.2188 | 90 | 0 | 1 | 0 | 0 | 0.0093692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29.33 | 0 | 0 | 0 | 0 | 0 | 0 | 660 | 0 | 0 | 0 | 0 | 0 | 660 | 0 | 0
4662 | 2002-07-14 05:00 | 89 | 418 | 35 | 29.49 | 7.15 | 0 | 7.1859 | 68.6118 | 90 | 0 | 89 | 0 | 26.7294 | 0.83386 | 0 | 25.0144 | 0.0043525 | 0 | 24.0886 | 0.0032797 | 23.3691 | 23.3679 | 52478.3 | 29.9488 | 37728.9 | 36697.2 | 35885.8 | 0 | 0 | 35869.9 | 566.03 | 0 | 0 | 0 | 16803 | 19066.9 | 660 | 18364.1 | 17996.8652
4663 | 2002-07-14 06:00 | 289 | 708 | 58 | 29.65 | 3.03 | 0 | 18.9548 | 76.2891 | 78.4835 | 0 | 289 | 141.983 | 54.1705 | 2.7077 | 138.072 | 50.6948 | 0.014133 | 110.397 | 48.8187 | 0.01065 | 154.449 | 154.446 | 346851 | 33.6128 | 309643 | 296565 | 275293 | 0 | 0 | 274570 | 648.754 | 0 | 0 | 0 | 1042.31 | 273528 | 660 | 267672 | 262318.7812
4664 | 2002-07-14 07:00 | 498 | 826 | 71 | 29.81 | 3.03 | 0 | 31.1107 | 83.8359 | 64.5686 | 0 | 498 | 354.886 | 72.4648 | 4.6659 | 354.886 | 67.8153 | 0.024354 | 331.309 | 65.3055 | 0.018351 | 384.734 | 384.731 | 864010 | 39.6814 | 822490 | 768122 | 749256 | 0 | 0 | 744270 | 664.522 | 0 | 0 | 0 | 0 | 744270 | 664.522 | 734426 | 719737.625
4665 | 2002-07-14 08:00 | 692 | 892 | 78 | 31.89 | 3.03 | 0 | 43.4423 | 92.0433 | 50.6438 | 0 | 692 | 566.242 | 81.2489 | 6.4835 | 566.242 | 76.0359 | 0.033842 | 549.908 | 73.2218 | 0.0255 | 604.46 | 604.454 | 1357450 | 47.399 | 1329070 | 1199290 | 1171950 | 0 | 0 | 1159540 | 655.831 | 0 | 0 | 0 | 976.24 | 1158570 | 660 | 1142400 | 1119554.25
4666 | 2002-07-14 09:00 | 854 | 928 | 88 | 33.98 | 3.19 | 0 | 55.6859 | 102.422 | 36.8869 | 0 | 854 | 741.76 | 91.822 | 8.0013 | 741.76 | 85.9305 | 0.041764 | 732.477 | 82.7503 | 0.03147 | 790.801 | 790.794 | 1775920 | 54.0563 | 1765760 | 1545520 | 1512910 | 0 | 0 | 1491280 | 639.046 | 0 | 0 | 0 | 18111.5 | 1473170 | 660 | 1449830 | 1420837
4667 | 2002-07-14 10:00 | 967 | 946 | 95 | 36.06 | 3.19 | 0 | 67.2595 | 119.05 | 23.7684 | 0 | 967 | 865.303 | 98.5704 | 9.06 | 865.303 | 92.246 | 0.04729 | 861.293 | 88.832 | 0.035634 | 921.656 | 921.655 | 2069810 | 59.4586 | 2074600 | 1769770 | 1729340 | 0 | 0 | 1700200 | 627.323 | 0 | 0 | 0 | 57610.3 | 1642590 | 660 | 1613960 | 1581683.75
4668 | 2002-07-14 11:00 | 1024 | 920 | 133 | 36.66 | 3.19 | 0 | 75.9231 | 155.134 | 13.5042 | 0 | 1024 | 893.189 | 134.809 | 9.5941 | 893.189 | 126.159 | 0.050078 | 891.919 | 121.49 | 0.037735 | 983.043 | 983.037 | 2207650 | 61.6169 | 2219820 | 1874220 | 1834440 | 0 | 0 | 1801070 | 620.934 | 0 | 0 | 0 | 85854.2 | 1715220 | 660 | 1684080 | 1650402.625
4669 | 2002-07-14 12:00 | 956 | 710 | 271 | 37.27 | 6.81 | 0 | 74.9755 | 212.784 | 14.6631 | 0 | 956 | 686.146 | 283.01 | 8.957 | 686.146 | 264.851 | 0.046752 | 684.991 | 255.049 | 0.035229 | 911.874 | 911.857 | 2047810 | 55.566 | 2051440 | 1784800 | 1743860 | 0 | 0 | 1715420 | 640.887 | 0 | 0 | 0 | 21435.8 | 1693980 | 660 | 1663590 | 1630321.75
4670 | 2002-07-14 13:00 | 179 | 10 | 170 | 37.87 | 6.81 | 0 | 65.5155 | 244.306 | 25.7438 | 0 | 179 | 8.9078 | 158.081 | 1.6771 | 8.9078 | 147.938 | 0.0087538 | 8.8587 | 142.463 | 0.0065962 | 146.789 | 146.78 | 329631 | 40.8151 | 292902 | 270065 | 263594 | 0 | 0 | 262877 | 618.966 | 0 | 0 | 0 | 15525 | 247352 | 659.999 | 241624 | 236791.6875
4671 | 2002-07-14 14:00 | 212 | 17 | 198 | 37.95 | 6.81 | 0 | 53.7589 | 259.422 | 39.0284 | 0 | 212 | 13.4844 | 195.922 | 1.9863 | 13.4844 | 183.352 | 0.010368 | 13.2907 | 176.566 | 0.0078123 | 184.168 | 184.162 | 413583 | 41.6451 | 374080 | 344004 | 335529 | 0 | 0 | 334404 | 628.124 | 0 | 0 | 0 | 12443.9 | 321961 | 660 | 315947 | 309627.6562
4672 | 2002-07-14 15:00 | 663 | 694 | 203 | 38.03 | 7.98 | 0 | 41.4718 | 269.289 | 52.8333 | 0 | 663 | 419.633 | 201.814 | 6.2118 | 419.633 | 188.866 | 0.032424 | 405.884 | 181.876 | 0.024432 | 570.151 | 570.145 | 1280400 | 48.6524 | 1249250 | 1119740 | 1093200 | 0 | 0 | 1082120 | 647.822 | 0 | 0 | 0 | 3971.94 | 1078150 | 660 | 1063630 | 1042357.9375
4673 | 2002-07-14 16:00 | 463 | 808 | 69 | 38.11 | 7.98 | 0 | 29.1465 | 277.315 | 66.7705 | 0 | 463 | 319.066 | 70.0741 | 4.338 | 319.066 | 65.578 | 0.022643 | 294.571 | 63.151 | 0.017062 | 347.007 | 347.002 | 779282 | 44.575 | 736867 | 671078 | 656123 | 0 | 0 | 652050 | 643.799 | 0 | 0 | 0 | 5480.99 | 646569 | 660 | 638163 | 625400.1875
4674 | 2002-07-14 17:00 | 243 | 619 | 61 | 37.3 | 7.98 | 0 | 17.0286 | 284.834 | 80.6795 | 0 | 243 | 100.653 | 53.9801 | 2.2767 | 100.653 | 50.5166 | 0.011884 | 74.6119 | 48.647 | 0.0089546 | 119.57 | 119.568 | 268518 | 39.5277 | 234547 | 217450 | 212679 | 0 | 0 | 212206 | 614.991 | 0 | 0 | 0 | 16621.9 | 195584 | 659.999 | 190447 | 186638.0938
4675 | 2002-07-14 18:00 | 53 | 413 | 13 | 36.49 | 8.81 | 0 | 5.3299 | 292.582 | 90 | 0 | 53 | 0 | 11.1246 | 0.49657 | 0 | 10.4108 | 0.0025919 | 0 | 10.0255 | 0.0019531 | 9.7266 | 9.7263 | 21842.8 | 36.662 | 12843.3 | 12050.4 | 11830.7 | 0 | 0 | 11828.4 | 488.124 | 0 | 0 | 0 | 11828.4 | 0 | 660 | 0 | 0
4676 | 2002-07-14 19:00 | 0 | 3 | 0 | 35.68 | 8.81 | 0
4677 | 2002-07-14 20:00 | 0 | 0 | 0 | 34.57 | 8.81 | 0
4678 | 2002-07-14 21:00 | 0 | 0 | 0 | 33.46 | 5.21 | 0
4679 | 2002-07-14 22:00 | 0 | 0 | 0 | 32.34 | 5.21 | 0
4680 | 2002-07-14 23:00 | 0 | 0 | 0 | 31.44 | 5.21 | 0
4681 | 2002-07-15 | 0 | 0 | 0 | 30.54 | 9.15 | 0
4682 | 2002-07-15 01:00 | 0 | 0 | 0 | 29.64 | 9.15 | 0
4683 | 2002-07-15 02:00 | 0 | 0 | 0 | 28.74 | 9.15 | 0
4684 | 2002-07-15 03:00 | 0 | 0 | 0 | 27.84 | 7.55 | 0
4685 | 2002-07-15 04:00 | 1 | 30 | 1 | 26.95 | 7.55 | 0 | -4.0684 | 60.3228 | 90 | 0 | 1 | 0 | 1.0017 | 0.0093692 | 0 | 0.9374 | 0 | 0 | 0.9027 | 0 | 0.87562 | 0.87557 | 1966.32 | 26.9668 | 187.31 | 187.741 | 186.868 | 0 | 0 | 186.859 | 130.597 | 0 | 0 | 0 | 186.859 | 0 | 660 | 0 | 0
4686 | 2002-07-15 05:00 | 83 | 365 | 37 | 27.26 | 7.55 | 0 | 7.0778 | 68.7272 | 90 | 0 | 83 | 0 | 28.7246 | 0.77765 | 0 | 26.8816 | 0.004059 | 0 | 25.8867 | 0.0030586 | 25.1131 | 25.1113 | 56393.9 | 27.7407 | 41035.8 | 40416.4 | 39490.2 | 0 | 0 | 39471.7 | 578.156 | 0 | 0 | 0 | 12589.8 | 26882 | 660 | 25903.8 | 25385.7461
4687 | 2002-07-15 06:00 | 272 | 627 | 69 | 27.57 | 4.21 | 0 | 18.8544 | 76.4178 | 78.5236 | 0 | 272 | 124.982 | 62.5147 | 2.5484 | 121.321 | 58.5037 | 0.013302 | 96.8993 | 56.3385 | 0.010023 | 148.65 | 148.631 | 333791 | 31.0983 | 297045 | 288137 | 268877 | 0 | 0 | 268204 | 656.132 | 0 | 0 | 0 | 145.28 | 268059 | 660 | 262224 | 256979.9688
4688 | 2002-07-15 07:00 | 497 | 791 | 89 | 27.87 | 4.21 | 0 | 31.0153 | 83.983 | 64.5944 | 0 | 497 | 339.711 | 89.1458 | 4.6565 | 339.711 | 83.426 | 0.024305 | 317.105 | 80.3385 | 0.018315 | 385.538 | 385.535 | 865817 | 37.0221 | 824322 | 779811 | 760310 | 0 | 0 | 755323 | 674.232 | 0 | 0 | 0 | 0 | 755323 | 674.232 | 744966 | 730067.1875
4689 | 2002-07-15 08:00 | 679 | 858 | 90 | 29.72 | 4.21 | 0 | 43.348 | 92.2182 | 50.6534 | 0 | 679 | 544.022 | 93.1363 | 6.3617 | 544.022 | 87.1605 | 0.033206 | 528.32 | 83.9348 | 0.025021 | 593.911 | 593.909 | 1333770 | 43.8187 | 1304510 | 1197670 | 1168340 | 0 | 0 | 1156380 | 666.321 | 0 | 0 | 0 | 0 | 1156380 | 666.321 | 1139960 | 1117159.25
4690 | 2002-07-15 09:00 | 844 | 912 | 92 | 31.56 | 4.45 | 0 | 55.5863 | 102.64 | 36.8745 | 0 | 844 | 729.187 | 95.8701 | 7.9076 | 729.187 | 89.7189 | 0.041275 | 720.07 | 86.3985 | 0.031102 | 782.304 | 782.298 | 1756850 | 49.8414 | 1745770 | 1560130 | 1524740 | 0 | 0 | 1503760 | 654.044 | 0 | 0 | 0 | 1162.16 | 1502600 | 660 | 1478510 | 1448941.75
4691 | 2002-07-15 10:00 | 966 | 946 | 95 | 33.4 | 4.45 | 0 | 67.1414 | 119.323 | 23.7185 | 0 | 966 | 865.391 | 98.6512 | 9.0507 | 865.391 | 92.3216 | 0.047241 | 861.399 | 88.9048 | 0.035597 | 921.829 | 921.826 | 2070180 | 54.942 | 2074990 | 1811100 | 1770800 | 0 | 0 | 1741540 | 641.579 | 0 | 0 | 0 | 17221.1 | 1724320 | 660 | 1692860 | 1659000.625
4692 | 2002-07-15 11:00 | 1023 | 955 | 99 | 34.06 | 4.45 | 0 | 75.7683 | 155.282 | 13.3765 | 0 | 1023 | 927.395 | 102.008 | 9.5847 | 927.395 | 95.4627 | 0.050029 | 926.102 | 91.9297 | 0.037698 | 987.527 | 987.524 | 2217720 | 57.1373 | 2230440 | 1926910 | 1884560 | 0 | 0 | 1850820 | 634.813 | 0 | 0 | 0 | 31954.1 | 1818860 | 660 | 1783960 | 1748283.25
4693 | 2002-07-15 12:00 | 1012 | 949 | 98 | 34.71 | 6.02 | 0 | 74.8486 | 212.415 | 14.5219 | 0 | 1012 | 916.664 | 101.108 | 9.4817 | 916.664 | 94.6203 | 0.049491 | 915.152 | 91.1185 | 0.037292 | 976.118 | 976.112 | 2192090 | 55.312 | 2203420 | 1920840 | 1876190 | 0 | 0 | 1843560 | 642.613 | 0 | 0 | 0 | 17070.1 | 1826490 | 660 | 1791300 | 1755477.75
4694 | 2002-07-15 13:00 | 951 | 944 | 93 | 35.37 | 6.02 | 0 | 65.4392 | 243.969 | 25.6577 | 0 | 951 | 850.336 | 96.7485 | 8.9101 | 850.336 | 90.541 | 0.046508 | 845.686 | 87.1901 | 0.035045 | 904.923 | 904.921 | 2032230 | 54.4695 | 2035040 | 1780120 | 1737970 | 0 | 0 | 1709980 | 644.358 | 0 | 0 | 0 | 13737.4 | 1696250 | 660 | 1665780 | 1632463
4695 | 2002-07-15 14:00 | 817 | 893 | 97 | 35.73 | 6.02 | 0 | 53.7017 | 259.17 | 38.973 | 0 | 817 | 694.536 | 100.787 | 7.6547 | 694.536 | 94.3204 | 0.039955 | 684.595 | 90.8296 | 0.030107 | 752.191 | 752.191 | 1689230 | 51.6059 | 1674940 | 1483370 | 1451540 | 0 | 0 | 1432000 | 645.459 | 0 | 0 | 0 | 7549.31 | 1424450 | 660 | 1402300 | 1374256.625
4696 | 2002-07-15 15:00 | 662 | 880 | 80 | 36.09 | 5.34 | 0 | 41.4192 | 269.087 | 52.7978 | 0 | 662 | 531.913 | 83.1076 | 6.2024 | 531.913 | 77.7753 | 0.032375 | 514.522 | 74.8969 | 0.024395 | 571.76 | 571.757 | 1284020 | 48.6993 | 1252980 | 1122830 | 1096910 | 0 | 0 | 1085840 | 650.027 | 0 | 0 | 0 | 4299.81 | 1081540 | 659.999 | 1066950 | 1045612.25
4697 | 2002-07-15 16:00 | 456 | 597 | 165 | 36.45 | 5.34 | 0 | 29.0915 | 277.143 | 66.7509 | 0 | 456 | 236.25 | 155.829 | 4.2724 | 236.25 | 145.831 | 0.0223 | 218.137 | 140.434 | 0.016804 | 347.83 | 347.823 | 781121 | 44.1207 | 738726 | 674320 | 659020 | 0 | 0 | 654915 | 644.073 | 0 | 0 | 0 | 4386.68 | 650528 | 660 | 642072 | 629230.125
4698 | 2002-07-15 17:00 | 144 | 90 | 118 | 35.3 | 5.34 | 0 | 16.9667 | 284.679 | 80.6746 | 0 | 144 | 14.4375 | 103.427 | 1.3492 | 14.4375 | 96.7906 | 0.0070422 | 10.7045 | 93.2085 | 0.0053064 | 100.801 | 100.799 | 226369 | 37.523 | 194780 | 182371 | 177976 | 0 | 0 | 177644 | 613.939 | 0 | 0 | 0 | 14352.6 | 163291 | 660 | 158686 | 155512.2656
4699 | 2002-07-15 18:00 | 31 | 60 | 25 | 34.14 | 8.69 | 0 | 5.2576 | 292.438 | 90 | 0 | 31 | 0 | 20.4895 | 0.29045 | 0 | 19.1749 | 0.001516 | 0 | 18.4652 | 0.0011424 | 17.9124 | 17.9112 | 40224 | 34.4592 | 27529.8 | 26082.4 | 25536.6 | 0 | 0 | 25527.6 | 535.592 | 0 | 0 | 0 | 25527.6 | 0 | 660 | 0 | 0
4700 | 2002-07-15 19:00 | 0 | 0 | 0 | 32.99 | 8.69 | 0
4701 | 2002-07-15 20:00 | 0 | 0 | 0 | 31.63 | 8.69 | 0
4702 | 2002-07-15 21:00 | 0 | 0 | 0 | 30.27 | 5.94 | 0
4703 | 2002-07-15 22:00 | 0 | 0 | 0 | 28.9 | 5.94 | 0
4704 | 2002-07-15 23:00 | 0 | 0 | 0 | 27.79 | 5.94 | 0
4705 | 2002-07-16 | 0 | 0 | 0 | 26.68 | 7.31 | 0
4706 | 2002-07-16 01:00 | 0 | 0 | 0 | 25.57 | 7.31 | 0
4707 | 2002-07-16 02:00 | 0 | 0 | 0 | 25.11 | 7.31 | 0
4708 | 2002-07-16 03:00 | 0 | 0 | 0 | 24.66 | 3.45 | 0
4709 | 2002-07-16 04:00 | 1 | 19 | 1 | 24.2 | 3.45 | 0 | -4.189 | 60.4328 | 90 | 0 | 1 | 0 | 1.0018 | 0.0093692 | 0 | 0.9375 | 0 | 0 | 0.9028 | 0 | 0.87572 | 0.87568 | 1966.55 | 24.2219 | 187.346 | 187.176 | 186.311 | 0 | 0 | 186.303 | 130.476 | 0 | 0 | 0 | 186.303 | 0 | 660 | 0 | 0
4710 | 2002-07-16 05:00 | 86 | 250 | 55 | 24.56 | 3.45 | 0 | 6.9678 | 68.8488 | 90 | 0 | 86 | 0 | 42.6101 | 0.80575 | 0 | 39.8762 | 0.0042058 | 0 | 38.4004 | 0.0031691 | 37.2515 | 37.25 | 83654.3 | 25.4896 | 64536.7 | 64363.7 | 62829.7 | 0 | 0 | 62787.4 | 608.215 | 0 | 0 | 0 | 6581.85 | 56205.6 | 660 | 54259.3 | 53174.1367
4711 | 2002-07-16 06:00 | 122 | 60 | 103 | 24.91 | 3.32 | 0 | 18.7525 | 76.5528 | 78.5625 | 0 | 122 | 11.7197 | 103.048 | 1.143 | 11.355 | 96.436 | 0.0059663 | 9.0596 | 92.867 | 0.0044957 | 98.8732 | 98.8659 | 222028 | 27.3985 | 190712 | 188393 | 183335 | 0 | 0 | 183020 | 649.229 | 0 | 0 | 0 | 602.461 | 182417 | 660 | 177482 | 173932.8594
4712 | 2002-07-16 07:00 | 487 | 641 | 157 | 25.27 | 3.32 | 0 | 30.9186 | 84.137 | 64.6186 | 0 | 487 | 275.295 | 152.133 | 4.5628 | 275.295 | 142.372 | 0.023816 | 256.948 | 137.103 | 0.017946 | 382.246 | 382.238 | 858408 | 34.8911 | 816819 | 780546 | 761344 | 0 | 0 | 756440 | 680.798 | 0 | 0 | 0 | 0 | 756440 | 680.798 | 745820 | 730903.5
4713 | 2002-07-16 08:00 | 689 | 891 | 78 | 27.32 | 3.32 | 0 | 43.2524 | 92.4012 | 50.6608 | 0 | 689 | 565.253 | 81.3672 | 6.4554 | 565.253 | 76.1466 | 0.033695 | 548.931 | 73.3284 | 0.02539 | 603.617 | 603.612 | 1355560 | 42.5131 | 1327110 | 1226170 | 1197560 | 0 | 0 | 1185180 | 671.511 | 0 | 0 | 0 | 0 | 1185180 | 671.511 | 1167900 | 1144543.625
4714 | 2002-07-16 09:00 | 851 | 926 | 88 | 29.38 | 1.29 | 0 | 55.4848 | 102.869 | 36.8595 | 0 | 851 | 740.899 | 91.9629 | 7.9732 | 740.899 | 86.0624 | 0.041617 | 731.644 | 82.8773 | 0.03136 | 790.116 | 790.111 | 1774390 | 52.1481 | 1764160 | 1558820 | 1523640 | 0 | 0 | 1502220 | 646.22 | 0 | 0 | 0 | 7548.31 | 1494670 | 660 | 1470790 | 1441377
4715 | 2002-07-16 10:00 | 965 | 946 | 95 | 31.43 | 1.29 | 0 | 67.0204 | 119.61 | 23.6652 | 0 | 965 | 865.523 | 98.735 | 9.0413 | 865.523 | 92.4 | 0.047192 | 861.55 | 88.9804 | 0.035561 | 922.049 | 922.046 | 2070680 | 57.9999 | 2075510 | 1783760 | 1744630 | 0 | 0 | 1715300 | 630.939 | 0 | 0 | 0 | 42646.5 | 1672650 | 660 | 1643000 | 1610138.375
4716 | 2002-07-16 11:00 | 1022 | 955 | 99 | 32.52 | 1.29 | 0 | 75.6085 | 155.442 | 13.2432 | 0 | 1022 | 927.561 | 102.105 | 9.5753 | 927.561 | 95.5537 | 0.04998 | 926.294 | 92.0173 | 0.037661 | 987.798 | 987.794 | 2218330 | 60.9846 | 2231080 | 1889910 | 1849270 | 0 | 0 | 1815510 | 622.815 | 0 | 0 | 0 | 76093.2 | 1739420 | 660 | 1707420 | 1673276.375
4717 | 2002-07-16 12:00 | 1018 | 955 | 98 | 33.62 | 4.37 | 0 | 74.7148 | 212.048 | 14.3773 | 0 | 1018 | 923.868 | 101.201 | 9.5379 | 923.868 | 94.7077 | 0.049784 | 922.375 | 91.2026 | 0.037514 | 983.207 | 983.198 | 2208010 | 56.7167 | 2220200 | 1922020 | 1878570 | 0 | 0 | 1845320 | 637.247 | 0 | 0 | 0 | 27750.3 | 1817570 | 660 | 1782720 | 1747062.375
4718 | 2002-07-16 13:00 | 952 | 944 | 95 | 34.71 | 4.37 | 0 | 65.357 | 243.625 | 25.5715 | 0 | 952 | 850.517 | 98.817 | 8.9195 | 850.517 | 92.4767 | 0.046557 | 845.899 | 89.0542 | 0.035082 | 906.938 | 906.937 | 2036750 | 56.0152 | 2039800 | 1770530 | 1731010 | 0 | 0 | 1702710 | 637.359 | 0 | 0 | 0 | 25319.5 | 1677390 | 660 | 1647580 | 1614627.5
4719 | 2002-07-16 14:00 | 829 | 922 | 87 | 34.95 | 4.37 | 0 | 53.6393 | 258.912 | 38.9188 | 0 | 829 | 716.88 | 90.9457 | 7.7671 | 716.88 | 85.1105 | 0.040542 | 706.654 | 81.9606 | 0.030549 | 764.986 | 764.98 | 1717950 | 52.9205 | 1705020 | 1500370 | 1466480 | 0 | 0 | 1446400 | 643.727 | 0 | 0 | 0 | 11997.3 | 1434400 | 660 | 1412020 | 1383778.375
4720 | 2002-07-16 15:00 | 661 | 880 | 79 | 35.18 | 6.88 | 0 | 41.3617 | 268.88 | 52.7641 | 0 | 661 | 532.932 | 82.1855 | 6.1931 | 532.932 | 76.9123 | 0.032326 | 515.541 | 74.0658 | 0.024358 | 571.943 | 571.94 | 1284430 | 46.6046 | 1253410 | 1134960 | 1109970 | 0 | 0 | 1098750 | 653.616 | 0 | 0 | 0 | 720.65 | 1098030 | 660 | 1083110 | 1061446.875
4721 | 2002-07-16 16:00 | 455 | 791 | 71 | 35.42 | 6.88 | 0 | 29.0316 | 276.966 | 66.7335 | 0 | 455 | 312.56 | 71.0958 | 4.263 | 312.56 | 66.5342 | 0.022251 | 288.624 | 64.0718 | 0.016767 | 342.131 | 342.127 | 768332 | 42.2541 | 725838 | 668751 | 653837 | 0 | 0 | 649866 | 650.438 | 0 | 0 | 0 | 1683.74 | 648183 | 660 | 639756 | 626961.125
4722 | 2002-07-16 17:00 | 243 | 621 | 62 | 34.36 | 6.88 | 0 | 16.8999 | 284.52 | 80.6723 | 0 | 243 | 100.917 | 55.0391 | 2.2767 | 100.917 | 51.5077 | 0.011884 | 74.8312 | 49.6014 | 0.0089546 | 120.708 | 120.706 | 271075 | 36.7711 | 236973 | 223021 | 217920 | 0 | 0 | 217439 | 624.539 | 0 | 0 | 0 | 9548.14 | 207890 | 660 | 202584 | 198532.125
4723 | 2002-07-16 18:00 | 52 | 414 | 13 | 33.29 | 9.39 | 0 | 5.1802 | 292.29 | 90 | 0 | 52 | 0 | 11.1282 | 0.4872 | 0 | 10.4142 | 0.002543 | 0 | 10.0288 | 0.0019162 | 9.7298 | 9.7288 | 21848.3 | 33.456 | 12847.5 | 12277.8 | 12043.7 | 0 | 0 | 12041.4 | 500.015 | 0 | 0 | 0 | 12041.4 | 0 | 660 | 0 | 0
4724 | 2002-07-16 19:00 | 0 | 0 | 0 | 32.23 | 9.39 | 0
4725 | 2002-07-16 20:00 | 0 | 0 | 0 | 30.86 | 9.39 | 0
4726 | 2002-07-16 21:00 | 0 | 0 | 0 | 29.49 | 6.74 | 0
4727 | 2002-07-16 22:00 | 0 | 0 | 0 | 28.12 | 6.74 | 0
4728 | 2002-07-16 23:00 | 0 | 0 | 0 | 27.33 | 6.74 | 0
4729 | 2002-07-17 | 0 | 0 | 0 | 26.54 | 9.13 | 0
4730 | 2002-07-17 01:00 | 0 | 0 | 0 | 25.74 | 9.13 | 0
4731 | 2002-07-17 02:00 | 0 | 0 | 0 | 25.19 | 9.13 | 0
4732 | 2002-07-17 03:00 | 0 | 0 | 0 | 24.63 | 5.89 | 0
4733 | 2002-07-17 04:00 | 1 | 28 | 1 | 24.07 | 5.89 | 0 | -4.3119 | 60.5488 | 90 | 0 | 1 | 0 | 1.0019 | 0.0093692 | 0 | 0.9376 | 0 | 0 | 0.9029 | 0 | 0.87581 | 0.87579 | 1966.79 | 24.0886 | 187.406 | 187.206 | 186.328 | 0 | 0 | 186.32 | 130.477 | 0 | 0 | 0 | 186.32 | 0 | 660 | 0 | 0
4734 | 2002-07-17 05:00 | 82 | 388 | 35 | 24.45 | 5.89 | 0 | 6.8559 | 68.9764 | 90 | 0 | 82 | 0 | 27.0596 | 0.76828 | 0 | 25.3234 | 0.0040101 | 0 | 24.3862 | 0.0030217 | 23.6575 | 23.6565 | 53126.4 | 24.9535 | 38275 | 38283.8 | 37399.9 | 0 | 0 | 37383.7 | 585.387 | 0 | 0 | 0 | 9323.01 | 28060.7 | 660 | 27041.6 | 26500.7949
4735 | 2002-07-17 06:00 | 281 | 693 | 59 | 24.84 | 3.37 | 0 | 18.6491 | 76.6943 | 78.6002 | 0 | 281 | 137.221 | 55.2571 | 2.6328 | 132.654 | 51.7117 | 0.013742 | 105.73 | 49.7979 | 0.010355 | 150.872 | 150.873 | 338823 | 28.625 | 301940 | 296518 | 275968 | 0 | 0 | 275274 | 663.85 | 0 | 0 | 0 | 0 | 275274 | 663.85 | 269324 | 263937.2188
4736 | 2002-07-17 07:00 | 493 | 822 | 71 | 25.23 | 3.37 | 0 | 30.8205 | 84.298 | 64.6411 | 0 | 493 | 352.762 | 72.6139 | 4.619 | 352.762 | 67.9548 | 0.02411 | 329.217 | 65.4399 | 0.018167 | 382.835 | 382.829 | 859737 | 34.8342 | 818161 | 782057 | 763072 | 0 | 0 | 758146 | 680.966 | 0 | 0 | 0 | 0 | 758146 | 680.966 | 747495 | 732545.125
4737 | 2002-07-17 08:00 | 688 | 891 | 78 | 27.04 | 3.37 | 0 | 43.1553 | 92.5921 | 50.6662 | 0 | 688 | 565.283 | 81.4303 | 6.446 | 565.283 | 76.2055 | 0.033646 | 548.955 | 73.3852 | 0.025353 | 603.695 | 603.696 | 1355740 | 42.1851 | 1327300 | 1228260 | 1197090 | 0 | 0 | 1184770 | 672.739 | 0 | 0 | 0 | 0 | 1184770 | 672.739 | 1167440 | 1144087.25
4738 | 2002-07-17 09:00 | 828 | 843 | 134 | 28.86 | 2.07 | 0 | 55.3816 | 103.106 | 36.8419 | 0 | 828 | 674.89 | 140.986 | 7.7577 | 674.89 | 131.94 | 0.040493 | 666.47 | 127.057 | 0.030512 | 769.751 | 769.741 | 1728640 | 49.9119 | 1716210 | 1532910 | 1500460 | 0 | 0 | 1480010 | 652.252 | 0 | 0 | 0 | 2240.94 | 1477770 | 660 | 1454320 | 1425236
4739 | 2002-07-17 10:00 | 963 | 946 | 94 | 30.68 | 2.07 | 0 | 66.8965 | 119.908 | 23.6083 | 0 | 963 | 865.7 | 97.8277 | 9.0226 | 865.7 | 91.5509 | 0.047095 | 861.746 | 88.1627 | 0.035487 | 921.446 | 921.439 | 2069320 | 55.8808 | 2074080 | 1801740 | 1762480 | 0 | 0 | 1733140 | 637.509 | 0 | 0 | 0 | 24371.5 | 1708770 | 660 | 1677860 | 1644304.5
4740 | 2002-07-17 11:00 | 1013 | 942 | 103 | 31.73 | 2.07 | 0 | 75.4436 | 155.615 | 13.1044 | 0 | 1013 | 915.695 | 106.143 | 9.491 | 915.695 | 99.3322 | 0.04954 | 914.471 | 95.656 | 0.037329 | 979.859 | 979.854 | 2200500 | 58.5284 | 2212280 | 1897560 | 1854650 | 0 | 0 | 1821570 | 630.748 | 0 | 0 | 0 | 44707.9 | 1776860 | 660 | 1743510 | 1708638.375
4741 | 2002-07-17 12:00 | 1000 | 924 | 111 | 32.79 | 6.52 | 0 | 74.5742 | 211.683 | 14.2296 | 0 | 1000 | 893.927 | 114.058 | 9.3692 | 893.927 | 106.74 | 0.048904 | 892.513 | 102.79 | 0.03685 | 965.479 | 965.472 | 2168210 | 52.5241 | 2178240 | 1924990 | 1881070 | 0 | 0 | 1849080 | 651.75 | 0 | 0 | 0 | 4315.3 | 1844760 | 660 | 1808880 | 1772705.5
4742 | 2002-07-17 13:00 | 951 | 944 | 94 | 33.85 | 6.52 | 0 | 65.2686 | 243.275 | 25.4856 | 0 | 951 | 851.729 | 97.9072 | 8.9101 | 851.729 | 91.6253 | 0.046508 | 847.139 | 88.2343 | 0.035045 | 907.346 | 907.341 | 2037660 | 52.3959 | 2040750 | 1803580 | 1764730 | 0 | 0 | 1736220 | 647.897 | 0 | 0 | 0 | 5718.16 | 1730500 | 660 | 1698830 | 1664849.75
4743 | 2002-07-17 14:00 | 828 | 922 | 86 | 33.89 | 6.52 | 0 | 53.5716 | 258.647 | 38.8659 | 0 | 828 | 718.04 | 90.0213 | 7.7577 | 718.04 | 84.2454 | 0.040493 | 707.832 | 81.1275 | 0.030512 | 765.32 | 765.318 | 1718710 | 49.5329 | 1705810 | 1526460 | 1491490 | 0 | 0 | 1471470 | 655.087 | 0 | 0 | 0 | 1094.94 | 1470370 | 660 | 1447110 | 1418164.375
4744 | 2002-07-17 15:00 | 660 | 880 | 79 | 33.94 | 6.29 | 0 | 41.2992 | 268.668 | 52.7324 | 0 | 660 | 533.064 | 82.2532 | 6.1837 | 533.064 | 76.9757 | 0.032277 | 515.702 | 74.1269 | 0.024321 | 572.158 | 572.153 | 1284910 | 45.8083 | 1253900 | 1139840 | 1112890 | 0 | 0 | 1101770 | 658.434 | 0 | 0 | 0 | 72.6089 | 1101690 | 660.016 | 1086700 | 1064965
4745 | 2002-07-17 16:00 | 462 | 786 | 81 | 33.98 | 6.29 | 0 | 28.9669 | 276.784 | 66.7185 | 0 | 462 | 310.94 | 80.8789 | 4.3286 | 310.94 | 75.6896 | 0.022594 | 287.152 | 72.8884 | 0.017025 | 349.256 | 349.251 | 784326 | 41.2246 | 741951 | 687228 | 671406 | 0 | 0 | 667284 | 655.405 | 0 | 0 | 0 | 358.552 | 666926 | 660 | 658256 | 645090.4375
4746 | 2002-07-17 17:00 | 230 | 525 | 77 | 33.13 | 6.29 | 0 | 16.8281 | 284.357 | 80.6728 | 0 | 230 | 85.654 | 68.8644 | 2.1549 | 85.654 | 64.4459 | 0.011248 | 63.512 | 62.0608 | 0.0084756 | 121.814 | 121.812 | 273558 | 35.6568 | 239332 | 226597 | 221243 | 0 | 0 | 220753 | 628.873 | 0 | 0 | 0 | 7122.98 | 213630 | 660 | 208251 | 204085.9219
4747 | 2002-07-17 18:00 | 37 | 261 | 12 | 32.27 | 9.28 | 0 | 5.0976 | 292.139 | 90 | 0 | 37 | 0 | 10.2988 | 0.34666 | 0 | 9.638 | 0.0018094 | 0 | 9.2813 | 0.0013635 | 9.0042 | 9.0038 | 20220.3 | 32.4247 | 11601 | 11158.2 | 10946.3 | 0 | 0 | 10944.4 | 501.133 | 0 | 0 | 0 | 10944.4 | 0 | 660 | 0 | 0
4748 | 2002-07-17 19:00 | 0 | 0 | 0 | 31.41 | 9.28 | 0
4749 | 2002-07-17 20:00 | 0 | 0 | 0 | 30.19 | 9.28 | 0
4750 | 2002-07-17 21:00 | 0 | 0 | 0 | 28.98 | 5.72 | 0
4751 | 2002-07-17 22:00 | 0 | 0 | 0 | 27.77 | 5.72 | 0
4752 | 2002-07-17 23:00 | 0 | 0 | 0 | 26.94 | 5.72 | 0
4753 | 2002-07-18 | 0 | 0 | 0 | 26.1 | 7.21 | 0
4754 | 2002-07-18 01:00 | 0 | 0 | 0 | 25.27 | 7.21 | 0
4755 | 2002-07-18 02:00 | 0 | 0 | 0 | 24.42 | 7.21 | 0
4756 | 2002-07-18 03:00 | 0 | 0 | 0 | 23.58 | 5.54 | 0
4757 | 2002-07-18 04:00 | 1 | 21 | 1 | 22.73 | 5.54 | 0 | -4.437 | 60.6706 | 90 | 0 | 1 | 0 | 1.002 | 0.0093692 | 0 | 0.9377 | 0 | 0 | 0.903 | 0 | 0.87591 | 0.87587 | 1966.98 | 22.7491 | 187.437 | 186.942 | 186.063 | 0 | 0 | 186.055 | 130.436 | 0 | 0 | 0 | 186.055 | 0 | 660 | 0 | 0
4758 | 2002-07-18 05:00 | 76 | 319 | 38 | 23.12 | 5.54 | 0 | 6.7424 | 69.11 | 90 | 0 | 76 | 0 | 30.0794 | 0.71206 | 0 | 28.1494 | 0.0037167 | 0 | 27.1076 | 0.0028006 | 26.2971 | 26.2947 | 59051.1 | 23.6924 | 43291.1 | 43598.8 | 42564.4 | 0 | 0 | 42544.2 | 596.448 | 0 | 0 | 0 | 7219.2 | 35325 | 660 | 34057.6 | 33376.4258
4759 | 2002-07-18 06:00 | 276 | 662 | 65 | 23.51 | 2.49 | 0 | 18.5443 | 76.842 | 78.6366 | 0 | 276 | 130.719 | 59.0238 | 2.5859 | 126.085 | 55.2367 | 0.013498 | 100.393 | 53.1925 | 0.010171 | 148.988 | 148.986 | 334586 | 27.4722 | 297860 | 294178 | 274539 | 0 | 0 | 273863 | 668.297 | 0 | 0 | 0 | 0 | 273863 | 668.297 | 267816 | 262459.6562
4760 | 2002-07-18 07:00 | 491 | 821 | 71 | 23.9 | 2.49 | 0 | 30.7211 | 84.4659 | 64.6619 | 0 | 491 | 351.844 | 72.6687 | 4.6003 | 351.844 | 68.0061 | 0.024012 | 328.329 | 65.4892 | 0.018093 | 382.021 | 382.016 | 857912 | 34.0595 | 816313 | 783130 | 763580 | 0 | 0 | 758712 | 685.342 | 0 | 0 | 0 | 0 | 758712 | 685.342 | 747887 | 732929.1875
4761 | 2002-07-18 08:00 | 673 | 853 | 90 | 25.83 | 2.49 | 0 | 43.0568 | 92.791 | 50.6694 | 0 | 673 | 541.217 | 93.3492 | 6.3055 | 541.217 | 87.3598 | 0.032912 | 525.582 | 84.1266 | 0.0248 | 591.441 | 591.438 | 1328220 | 41.5589 | 1298750 | 1205280 | 1177590 | 0 | 0 | 1165690 | 673.342 | 0 | 0 | 0 | 0 | 1165690 | 673.342 | 1148730 | 1125753.75
4762 | 2002-07-18 09:00 | 839 | 907 | 94 | 27.75 | 4.27 | 0 | 55.2766 | 103.354 | 36.8217 | 0 | 839 | 725.597 | 98.0905 | 7.8608 | 725.597 | 91.7969 | 0.041031 | 716.556 | 88.3995 | 0.030917 | 780.837 | 780.83 | 1753550 | 46.2132 | 1742310 | 1584530 | 1548320 | 0 | 0 | 1527490 | 667.135 | 0 | 0 | 0 | 0 | 1527490 | 667.135 | 1502370 | 1472327.25
4763 | 2002-07-18 10:00 | 933 | 849 | 153 | 29.67 | 4.27 | 0 | 66.7698 | 120.218 | 23.5481 | 0 | 933 | 778.13 | 162.031 | 8.7415 | 778.13 | 151.634 | 0.045628 | 774.596 | 146.023 | 0.034381 | 893.033 | 893.026 | 2005520 | 50.7862 | 2006930 | 1787350 | 1745520 | 0 | 0 | 1718270 | 655.633 | 0 | 0 | 0 | 1101.71 | 1717170 | 660 | 1685970 | 1652248.375
4764 | 2002-07-18 11:00 | 1021 | 955 | 99 | 30.5 | 4.27 | 0 | 75.2739 | 155.801 | 12.9602 | 0 | 1021 | 929.03 | 102.31 | 9.566 | 929.03 | 95.7453 | 0.049931 | 927.816 | 92.2018 | 0.037624 | 989.453 | 989.444 | 2222030 | 53.8961 | 2234980 | 1962260 | 1917640 | 0 | 0 | 1883910 | 646.527 | 0 | 0 | 0 | 9168.28 | 1874750 | 660 | 1837720 | 1800969.375
4765 | 2002-07-18 12:00 | 1016 | 955 | 98 | 31.34 | 5.56 | 0 | 74.4267 | 211.32 | 14.0789 | 0 | 1016 | 924.36 | 101.398 | 9.5191 | 924.36 | 94.8923 | 0.049687 | 922.929 | 91.3804 | 0.03744 | 983.916 | 983.914 | 2209610 | 52.732 | 2221880 | 1961880 | 1915060 | 0 | 0 | 1881990 | 652.136 | 0 | 0 | 0 | 3818.68 | 1878170 | 660 | 1841020 | 1804197.125
4766 | 2002-07-18 13:00 | 925 | 859 | 146 | 32.17 | 5.56 | 0 | 65.1742 | 242.919 | 25.4 | 0 | 925 | 775.349 | 148.443 | 8.6665 | 775.349 | 138.918 | 0.045236 | 771.201 | 133.777 | 0.034086 | 877.862 | 877.856 | 1971430 | 51.2562 | 1971080 | 1751180 | 1710410 | 0 | 0 | 1684120 | 654.316 | 0 | 0 | 0 | 2338.38 | 1681780 | 660 | 1651810 | 1618775.75
4767 | 2002-07-18 14:00 | 809 | 880 | 102 | 32.25 | 5.56 | 0 | 53.4985 | 258.376 | 38.8144 | 0 | 809 | 685.31 | 105.961 | 7.5797 | 685.31 | 99.162 | 0.039564 | 675.6 | 95.492 | 0.029812 | 747.988 | 747.984 | 1679780 | 48.5125 | 1665050 | 1497090 | 1462320 | 0 | 0 | 1443130 | 656.609 | 0 | 0 | 0 | 198.161 | 1442930 | 660 | 1420340 | 1391929.375
4768 | 2002-07-18 15:00 | 659 | 880 | 79 | 32.33 | 8.38 | 0 | 41.2318 | 268.45 | 52.7026 | 0 | 659 | 533.225 | 82.3231 | 6.1743 | 533.225 | 77.0411 | 0.032228 | 515.888 | 74.1899 | 0.024284 | 572.399 | 572.392 | 1285450 | 42.7298 | 1254460 | 1157500 | 1130280 | 0 | 0 | 1119140 | 668.452 | 0 | 0 | 0 | 0 | 1119140 | 668.452 | 1103380 | 1081310.75
4769 | 2002-07-18 16:00 | 452 | 789 | 70 | 32.41 | 8.38 | 0 | 28.8972 | 276.598 | 66.706 | 0 | 452 | 312.602 | 70.2857 | 4.2349 | 312.602 | 65.776 | 0.022105 | 288.707 | 63.3417 | 0.016656 | 341.504 | 341.505 | 766930 | 38.6148 | 724429 | 679600 | 662657 | 0 | 0 | 658738 | 663.414 | 0 | 0 | 0 | 0 | 658738 | 663.414 | 650062 | 637060.9375
4770 | 2002-07-18 17:00 | 241 | 615 | 63 | 31.88 | 8.38 | 0 | 16.7514 | 284.19 | 80.6762 | 0 | 241 | 100.057 | 56.1079 | 2.258 | 100.057 | 52.5079 | 0.011786 | 74.1812 | 50.5647 | 0.0088809 | 121.012 | 121.008 | 271754 | 34.0786 | 237616 | 226854 | 222003 | 0 | 0 | 221518 | 633.528 | 0 | 0 | 0 | 5050.16 | 216467 | 660 | 211053 | 206832.2188
4771 | 2002-07-18 18:00 | 38 | 303 | 10 | 31.36 | 8.45 | 0 | 5.01 | 291.983 | 90 | 0 | 38 | 0 | 8.6261 | 0.35603 | 0 | 8.0726 | 0.0018584 | 0 | 7.7739 | 0.0014003 | 7.542 | 7.5414 | 16936.1 | 31.4964 | 9127.84 | 8839.67 | 8676 | 0 | 0 | 8674.78 | 493.581 | 0 | 0 | 0 | 8674.78 | 0 | 660 | 0 | 0
4772 | 2002-07-18 19:00 | 0 | 0 | 0 | 30.84 | 8.45 | 0
4773 | 2002-07-18 20:00 | 0 | 0 | 0 | 29.89 | 8.45 | 0
4774 | 2002-07-18 21:00 | 0 | 0 | 0 | 28.95 | 6.24 | 0
4775 | 2002-07-18 22:00 | 0 | 0 | 0 | 28 | 6.24 | 0
4776 | 2002-07-18 23:00 | 0 | 0 | 0 | 27.08 | 6.24 | 0
4777 | 2002-07-19 | 0 | 0 | 0 | 26.16 | 7.07 | 0
4778 | 2002-07-19 01:00 | 0 | 0 | 0 | 25.24 | 7.07 | 0
4779 | 2002-07-19 02:00 | 0 | 0 | 0 | 24.73 | 7.07 | 0
4780 | 2002-07-19 03:00 | 0 | 0 | 0 | 24.21 | 2.86 | 0
4781 | 2002-07-19 04:00 | 0 | 22 | 0 | 23.7 | 2.86 | 0
4782 | 2002-07-19 05:00 | 78 | 364 | 35 | 23.79 | 2.86 | 0 | 6.6271 | 69.2497 | 90 | 0 | 78 | 0 | 27.3007 | 0.7308 | 0 | 25.549 | 0.0038145 | 0 | 24.6034 | 0.0028743 | 23.8681 | 23.8667 | 53598.4 | 24.4093 | 38672.8 | 38796.6 | 37896.6 | 0 | 0 | 37880.1 | 588.185 | 0 | 0 | 0 | 8636.49 | 29243.6 | 660 | 28183.7 | 27620.0117
4783 | 2002-07-19 06:00 | 277 | 688 | 59 | 23.87 | 1.06 | 0 | 18.4381 | 76.9961 | 78.6716 | 0 | 277 | 135.393 | 55.3682 | 2.5953 | 130.309 | 51.8157 | 0.013546 | 103.655 | 49.898 | 0.010207 | 148.957 | 148.94 | 334483 | 28.2288 | 297792 | 292989 | 273215 | 0 | 0 | 272536 | 664.438 | 0 | 0 | 0 | 0 | 272536 | 664.438 | 266587 | 261254.9375
4784 | 2002-07-19 07:00 | 490 | 824 | 70 | 23.96 | 1.06 | 0 | 30.6205 | 84.6406 | 64.681 | 0 | 490 | 352.639 | 71.758 | 4.5909 | 352.639 | 67.1539 | 0.023963 | 329.042 | 64.6685 | 0.018057 | 381.916 | 381.913 | 857680 | 35.1369 | 816075 | 778920 | 760800 | 0 | 0 | 755889 | 679.727 | 0 | 0 | 0 | 0 | 755889 | 679.727 | 745317 | 730410.5
4785 | 2002-07-19 08:00 | 681 | 879 | 82 | 25.89 | 1.06 | 0 | 42.9571 | 92.9977 | 50.6706 | 0 | 681 | 557.096 | 85.5383 | 6.3804 | 557.096 | 80.05 | 0.033304 | 541.001 | 77.0874 | 0.025095 | 599.57 | 599.568 | 1346480 | 43.4366 | 1317680 | 1212020 | 1183360 | 0 | 0 | 1171130 | 667.266 | 0 | 0 | 0 | 0 | 1171130 | 667.266 | 1154350 | 1131264.5
4786 | 2002-07-19 09:00 | 848 | 926 | 88 | 27.82 | 2.01 | 0 | 55.1698 | 103.611 | 36.7989 | 0 | 848 | 741.386 | 92.1949 | 7.9451 | 741.386 | 86.2795 | 0.041471 | 732.161 | 83.0863 | 0.031249 | 790.821 | 790.816 | 1775970 | 49.5351 | 1765810 | 1580480 | 1543200 | 0 | 0 | 1521890 | 656.989 | 0 | 0 | 0 | 640.297 | 1521250 | 660 | 1496580 | 1466652.5
4787 | 2002-07-19 10:00 | 963 | 947 | 94 | 29.75 | 2.01 | 0 | 66.6402 | 120.539 | 23.4846 | 0 | 963 | 868.18 | 98.0087 | 9.0226 | 868.18 | 91.7203 | 0.047095 | 864.26 | 88.3258 | 0.035487 | 924.043 | 924.036 | 2075140 | 55.1233 | 2080210 | 1813990 | 1773730 | 0 | 0 | 1744320 | 640.861 | 0 | 0 | 0 | 18246.2 | 1726070 | 660 | 1694550 | 1660660.25
4788 | 2002-07-19 11:00 | 1020 | 956 | 98 | 30.72 | 2.01 | 0 | 75.0992 | 155.997 | 12.8106 | 0 | 1020 | 930.335 | 101.428 | 9.5566 | 930.335 | 94.9206 | 0.049882 | 929.147 | 91.4076 | 0.037587 | 989.975 | 989.971 | 2223220 | 57.9038 | 2236230 | 1924420 | 1880940 | 0 | 0 | 1847230 | 633.878 | 0 | 0 | 0 | 38062.2 | 1809160 | 660 | 1774620 | 1739131.25
4789 | 2002-07-19 12:00 | 1016 | 955 | 98 | 31.69 | 3.51 | 0 | 74.2725 | 210.962 | 13.9253 | 0 | 1016 | 925.676 | 101.502 | 9.5191 | 925.676 | 94.9895 | 0.049687 | 924.274 | 91.474 | 0.03744 | 985.312 | 985.311 | 2212760 | 56.1815 | 2225200 | 1931550 | 1888230 | 0 | 0 | 1854990 | 640.813 | 0 | 0 | 0 | 23663.4 | 1831330 | 660 | 1795960 | 1760037.125
4790 | 2002-07-19 13:00 | 949 | 944 | 93 | 32.66 | 3.51 | 0 | 65.0737 | 242.557 | 25.3149 | 0 | 949 | 853.282 | 97.0872 | 8.8914 | 853.282 | 90.8579 | 0.04641 | 848.75 | 87.4953 | 0.034971 | 908.192 | 908.188 | 2039550 | 55.2345 | 2042740 | 1780060 | 1740720 | 0 | 0 | 1712270 | 640.21 | 0 | 0 | 0 | 19861.1 | 1692410 | 660 | 1662080 | 1628834.75
4791 | 2002-07-19 14:00 | 827 | 922 | 87 | 33.26 | 3.51 | 0 | 53.4201 | 258.099 | 38.7644 | 0 | 827 | 718.529 | 91.1772 | 7.7484 | 718.529 | 85.3271 | 0.040444 | 708.38 | 82.1692 | 0.030475 | 766.862 | 766.859 | 1722170 | 52.3216 | 1709440 | 1508770 | 1475690 | 0 | 0 | 1455430 | 644.611 | 0 | 0 | 0 | 9429.96 | 1446000 | 660 | 1423340 | 1394870.25
4792 | 2002-07-19 15:00 | 651 | 864 | 82 | 33.86 | 5 | 0 | 41.1593 | 268.227 | 52.6749 | 0 | 651 | 524.201 | 85.3631 | 6.0994 | 524.201 | 79.886 | 0.031837 | 507.184 | 76.9295 | 0.02399 | 566.614 | 566.612 | 1272470 | 46.6347 | 1241030 | 1123460 | 1097160 | 0 | 0 | 1086250 | 655.589 | 0 | 0 | 0 | 660.535 | 1085590 | 660.174 | 1070910 | 1049490.75
4793 | 2002-07-19 16:00 | 460 | 813 | 68 | 34.47 | 5 | 0 | 28.8227 | 276.407 | 66.6959 | 0 | 460 | 321.675 | 69.4096 | 4.3098 | 321.675 | 64.9562 | 0.022496 | 297.103 | 62.5522 | 0.016951 | 348.882 | 348.879 | 783491 | 42.3357 | 741110 | 682638 | 666705 | 0 | 0 | 662597 | 651.651 | 0 | 0 | 0 | 1272.63 | 661324 | 660 | 652727 | 639672.375
4794 | 2002-07-19 17:00 | 239 | 615 | 62 | 33.9 | 5 | 0 | 16.6698 | 284.018 | 80.6823 | 0 | 239 | 99.9033 | 55.2758 | 2.2392 | 99.9033 | 51.7292 | 0.011688 | 74.0466 | 49.8147 | 0.0088072 | 120.154 | 120.154 | 269835 | 36.6089 | 235797 | 222101 | 216843 | 0 | 0 | 216368 | 625.88 | 0 | 0 | 0 | 9131.4 | 207237 | 660 | 201939 | 197900.1406
4795 | 2002-07-19 18:00 | 38 | 301 | 10 | 33.34 | 7.01 | 0 | 4.9172 | 291.824 | 90 | 0 | 38 | 0 | 8.6285 | 0.35603 | 0 | 8.0748 | 0.0018584 | 0 | 7.776 | 0.0014003 | 7.5441 | 7.5437 | 16941.2 | 33.4894 | 9131.68 | 8751.75 | 8592.23 | 0 | 0 | 8590.99 | 486.482 | 0 | 0 | 0 | 8590.99 | 0 | 660 | 0 | 0
4796 | 2002-07-19 19:00 | 0 | 0 | 0 | 32.78 | 7.01 | 0
4797 | 2002-07-19 20:00 | 0 | 0 | 0 | 31.52 | 7.01 | 0
4798 | 2002-07-19 21:00 | 0 | 0 | 0 | 30.27 | 5.57 | 0
4799 | 2002-07-19 22:00 | 0 | 0 | 0 | 29.01 | 5.57 | 0
4800 | 2002-07-19 23:00 | 0 | 0 | 0 | 27.83 | 5.57 | 0
4801 | 2002-07-20 | 0 | 0 | 0 | 26.64 | 5.48 | 0
4802 | 2002-07-20 01:00 | 0 | 0 | 0 | 25.46 | 5.48 | 0
4803 | 2002-07-20 02:00 | 0 | 0 | 0 | 24.67 | 5.48 | 0
4804 | 2002-07-20 03:00 | 0 | 0 | 0 | 23.87 | 1.88 | 0
4805 | 2002-07-20 04:00 | 0 | 20 | 0 | 23.08 | 1.88 | 0
4806 | 2002-07-20 05:00 | 76 | 358 | 34 | 23.26 | 1.88 | 0 | 6.5102 | 69.3953 | 90 | 0 | 76 | 0 | 26.4684 | 0.71206 | 0 | 24.7701 | 0.0037167 | 0 | 23.8534 | 0.0028006 | 23.1405 | 23.1385 | 51963.2 | 23.9009 | 37295.5 | 37518.7 | 36663.1 | 0 | 0 | 36647.6 | 588.02 | 0 | 0 | 0 | 8294.9 | 28352.7 | 660 | 27323.6 | 26777.1094
4807 | 2002-07-20 06:00 | 277 | 672 | 65 | 23.44 | 2.46 | 0 | 18.3306 | 77.1563 | 78.7053 | 0 | 277 | 132.024 | 59.1591 | 2.5953 | 126.795 | 55.3634 | 0.013546 | 100.765 | 53.3144 | 0.010207 | 149.467 | 149.456 | 335643 | 27.4226 | 298905 | 295265 | 276205 | 0 | 0 | 275518 | 667.748 | 0 | 0 | 0 | 0 | 275518 | 667.748 | 269475 | 264085.9375
4808 | 2002-07-20 07:00 | 487 | 820 | 70 | 23.62 | 2.46 | 0 | 30.5187 | 84.8221 | 64.6984 | 0 | 487 | 350.95 | 71.8172 | 4.5628 | 350.95 | 67.2093 | 0.023816 | 327.439 | 64.7219 | 0.017946 | 380.414 | 380.413 | 854313 | 33.757 | 812668 | 780725 | 760250 | 0 | 0 | 755413 | 684.511 | 0 | 0 | 0 | 0 | 755413 | 684.511 | 744667 | 729773.6875
4809 | 2002-07-20 08:00 | 685 | 890 | 80 | 25.98 | 2.46 | 0 | 42.856 | 93.212 | 50.6696 | 0 | 685 | 563.757 | 83.6258 | 6.4179 | 563.757 | 78.2602 | 0.033499 | 547.47 | 75.3638 | 0.025243 | 604.173 | 604.169 | 1356810 | 42.0796 | 1328400 | 1229910 | 1200100 | 0 | 0 | 1187740 | 673.314 | 0 | 0 | 0 | 0 | 1187740 | 673.314 | 1170320 | 1146910.5
4810 | 2002-07-20 09:00 | 841 | 918 | 89 | 28.35 | 2.54 | 0 | 55.0612 | 103.877 | 36.7735 | 0 | 841 | 734.794 | 93.278 | 7.8795 | 734.794 | 87.2931 | 0.041128 | 725.667 | 84.0624 | 0.030991 | 785.468 | 785.462 | 1763950 | 49.1694 | 1753220 | 1571920 | 1534470 | 0 | 0 | 1513450 | 657.602 | 0 | 0 | 0 | 342.372 | 1513100 | 660 | 1488700 | 1458921.5
4811 | 2002-07-20 10:00 | 962 | 947 | 94 | 30.71 | 2.54 | 0 | 66.5077 | 120.872 | 23.4179 | 0 | 962 | 868.489 | 98.1037 | 9.0132 | 868.489 | 91.8092 | 0.047046 | 864.591 | 88.4114 | 0.03545 | 924.447 | 924.44 | 2076060 | 55.2132 | 2081180 | 1814030 | 1774310 | 0 | 0 | 1744780 | 639.734 | 0 | 0 | 0 | 19395.3 | 1725380 | 660 | 1693890 | 1660008.625
4812 | 2002-07-20 11:00 | 1019 | 956 | 98 | 31.75 | 2.54 | 0 | 74.9196 | 156.205 | 12.6558 | 0 | 1019 | 930.674 | 101.538 | 9.5472 | 930.674 | 95.0231 | 0.049833 | 929.515 | 91.5064 | 0.037551 | 990.427 | 990.422 | 2224230 | 58.0021 | 2237300 | 1924410 | 1880700 | 0 | 0 | 1846900 | 632.68 | 0 | 0 | 0 | 38756.2 | 1808140 | 660 | 1773640 | 1738164.375
4813 | 2002-07-20 12:00 | 1015 | 955 | 98 | 32.79 | 4.65 | 0 | 74.1116 | 210.607 | 13.7692 | 0 | 1015 | 926.025 | 101.609 | 9.5098 | 926.025 | 95.0899 | 0.049638 | 924.655 | 91.5706 | 0.037403 | 985.775 | 985.769 | 2213790 | 55.5273 | 2226290 | 1938850 | 1895680 | 0 | 0 | 1862060 | 640.168 | 0 | 0 | 0 | 18956 | 1843110 | 660 | 1807290 | 1771148.75
4814 | 2002-07-20 13:00 | 949 | 944 | 94 | 33.83 | 4.65 | 0 | 64.967 | 242.191 | 25.2305 | 0 | 949 | 853.619 | 98.1777 | 8.8914 | 853.619 | 91.8785 | 0.04641 | 849.117 | 88.4781 | 0.034971 | 909.502 | 909.497 | 2042500 | 54.8081 | 2045850 | 1786620 | 1748730 | 0 | 0 | 1720170 | 641.037 | 0 | 0 | 0 | 17961.8 | 1702200 | 660 | 1671530 | 1638096.25
4815 | 2002-07-20 14:00 | 826 | 922 | 87 | 33.8 | 4.65 | 0 | 53.3362 | 257.817 | 38.7162 | 0 | 826 | 718.825 | 91.2596 | 7.739 | 718.825 | 85.4043 | 0.040395 | 708.703 | 82.2435 | 0.030438 | 767.247 | 767.245 | 1723040 | 51.4969 | 1710340 | 1515800 | 1481510 | 0 | 0 | 1461350 | 648.169 | 0 | 0 | 0 | 5903.56 | 1455450 | 659.999 | 1432550 | 1403900.75
4816 | 2002-07-20 15:00 | 658 | 880 | 80 | 33.77 | 4.91 | 0 | 41.0817 | 267.999 | 52.6495 | 0 | 658 | 533.63 | 83.4608 | 6.165 | 533.63 | 78.1058 | 0.032179 | 516.333 | 75.2152 | 0.024248 | 573.825 | 573.82 | 1288650 | 46.7831 | 1257780 | 1137910 | 1111160 | 0 | 0 | 1099980 | 655.887 | 0 | 0 | 0 | 705.077 | 1099280 | 660 | 1084330 | 1062643.25
4817 | 2002-07-20 16:00 | 458 | 812 | 67 | 33.74 | 4.91 | 0 | 28.7432 | 276.212 | 66.6884 | 0 | 458 | 321.764 | 68.508 | 4.2911 | 321.764 | 64.1124 | 0.022398 | 297.198 | 61.7397 | 0.016877 | 348.186 | 348.181 | 781924 | 41.6361 | 739530 | 683561 | 667868 | 0 | 0 | 663774 | 654.153 | 0 | 0 | 0 | 668.632 | 663105 | 660 | 654485 | 641395.375
4818 | 2002-07-20 17:00 | 236 | 611 | 61 | 33 | 4.91 | 0 | 16.5831 | 283.843 | 80.6914 | 0 | 236 | 99.1801 | 54.4438 | 2.2111 | 99.1801 | 50.9506 | 0.011541 | 73.481 | 49.0649 | 0.0086967 | 118.878 | 118.876 | 266966 | 35.6959 | 233075 | 220600 | 215440 | 0 | 0 | 214974 | 627.747 | 0 | 0 | 0 | 7613.92 | 207360 | 660 | 202060 | 198019.0312
4819 | 2002-07-20 18:00 | 37 | 296 | 10 | 32.27 | 13.15 | 0 | 4.8193 | 291.662 | 90 | 0 | 37 | 0 | 8.6308 | 0.34666 | 0 | 8.077 | 0.0018094 | 0 | 7.7781 | 0.0013635 | 7.5461 | 7.546 | 16946.4 | 32.3727 | 9135.65 | 8807.18 | 8643.8 | 0 | 0 | 8642.56 | 490.495 | 0 | 0 | 0 | 8642.56 | 0 | 660 | 0 | 0
4820 | 2002-07-20 19:00 | 0 | 0 | 0 | 31.53 | 13.15 | 0
4821 | 2002-07-20 20:00 | 0 | 0 | 0 | 29.39 | 13.15 | 0
4822 | 2002-07-20 21:00 | 0 | 0 | 0 | 27.24 | 7.52 | 0
4823 | 2002-07-20 22:00 | 0 | 0 | 0 | 25.1 | 7.52 | 0
4824 | 2002-07-20 23:00 | 0 | 0 | 0 | 24.18 | 7.52 | 0
4825 | 2002-07-21 | 0 | 0 | 0 | 23.27 | 8.94 | 0
4826 | 2002-07-21 01:00 | 0 | 0 | 0 | 22.35 | 8.94 | 0
4827 | 2002-07-21 02:00 | 0 | 0 | 0 | 21.52 | 8.94 | 0
4828 | 2002-07-21 03:00 | 0 | 0 | 0 | 20.69 | 4.19 | 0
4829 | 2002-07-21 04:00 | 0 | 19 | 0 | 19.86 | 4.19 | 0
4830 | 2002-07-21 05:00 | 77 | 390 | 32 | 20.22 | 4.19 | 0 | 6.3917 | 69.5469 | 90 | 0 | 77 | 0 | 24.6931 | 0.72143 | 0 | 23.1087 | 0.0037656 | 0 | 22.2535 | 0.0028375 | 21.5886 | 21.5877 | 48480.3 | 20.7331 | 34374.9 | 35173.2 | 34371.1 | 0 | 0 | 34357.9 | 594.624 | 0 | 0 | 0 | 5735.97 | 28621.9 | 660 | 27583.4 | 27031.7559
4831 | 2002-07-21 06:00 | 277 | 674 | 66 | 20.58 | 2.89 | 0 | 18.2218 | 77.3228 | 78.7376 | 0 | 277 | 131.786 | 60.1529 | 2.5953 | 126.289 | 56.2934 | 0.013546 | 100.272 | 54.21 | 0.010207 | 149.857 | 149.853 | 336536 | 24.4607 | 299773 | 300430 | 280903 | 0 | 0 | 280214 | 677.623 | 0 | 0 | 0 | 0 | 280214 | 677.623 | 273922 | 268443.4375
4832 | 2002-07-21 07:00 | 474 | 756 | 91 | 20.93 | 2.89 | 0 | 30.4157 | 85.0102 | 64.714 | 0 | 474 | 323.135 | 91.5844 | 4.441 | 323.135 | 85.7082 | 0.023181 | 301.466 | 82.5362 | 0.017467 | 372.499 | 372.497 | 836534 | 30.5766 | 794673 | 774769 | 754992 | 0 | 0 | 750363 | 695 | 0 | 0 | 0 | 0 | 750363 | 695 | 739295 | 724508.9375
4833 | 2002-07-21 08:00 | 668 | 850 | 91 | 23.43 | 2.89 | 0 | 42.7537 | 93.434 | 50.6666 | 0 | 668 | 538.738 | 94.5698 | 6.2586 | 538.738 | 88.502 | 0.032668 | 523.177 | 85.2266 | 0.024616 | 590.175 | 590.171 | 1325370 | 38.7136 | 1295800 | 1218710 | 1188380 | 0 | 0 | 1176640 | 684.6 | 0 | 0 | 0 | 0 | 1176640 | 684.6 | 1158910 | 1135728.875
4834 | 2002-07-21 09:00 | 823 | 873 | 108 | 25.93 | 6.42 | 0 | 54.9509 | 104.152 | 36.7458 | 0 | 823 | 699.836 | 112.18 | 7.7109 | 699.836 | 104.983 | 0.040248 | 691.159 | 101.097 | 0.030328 | 768.518 | 768.518 | 1725900 | 41.7392 | 1713340 | 1591230 | 1550490 | 0 | 0 | 1530460 | 681.096 | 0 | 0 | 0 | 0 | 1530460 | 681.096 | 1504750 | 1474651.875
4835 | 2002-07-21 10:00 | 952 | 897 | 131 | 28.42 | 6.42 | 0 | 66.3723 | 121.215 | 23.348 | 0 | 952 | 822.743 | 134.469 | 8.9195 | 822.743 | 125.841 | 0.046557 | 819.074 | 121.184 | 0.035082 | 912.084 | 912.078 | 2048300 | 47.1824 | 2051950 | 1859740 | 1814140 | 0 | 0 | 1785810 | 668.457 | 0 | 0 | 0 | 0 | 1785810 | 668.457 | 1751970 | 1716930.25
4836 | 2002-07-21 11:00 | 984 | 849 | 167 | 29.67 | 6.42 | 0 | 74.7353 | 156.424 | 12.4957 | 0 | 984 | 826.817 | 177.309 | 9.2193 | 826.817 | 165.932 | 0.048122 | 825.814 | 159.791 | 0.036261 | 956.073 | 956.059 | 2147070 | 49.3372 | 2155970 | 1934740 | 1890460 | 0 | 0 | 1859200 | 662.179 | 0 | 0 | 0 | 0 | 1859200 | 662.179 | 1822740 | 1786287.875
4837 | 2002-07-21 12:00 | 1014 | 919 | 132 | 30.92 | 5.08 | 0 | 73.944 | 210.258 | 13.6107 | 0 | 1014 | 892.027 | 134.893 | 9.5004 | 892.027 | 126.238 | 0.049589 | 890.739 | 121.566 | 0.037366 | 981.972 | 981.961 | 2205230 | 52.9442 | 2217260 | 1955720 | 1913750 | 0 | 0 | 1880340 | 648.223 | 0 | 0 | 0 | 6059.07 | 1874280 | 660 | 1837270 | 1800528
4838 | 2002-07-21 13:00 | 940 | 932 | 97 | 32.17 | 5.08 | 0 | 64.8541 | 241.82 | 25.147 | 0 | 940 | 842.992 | 101.266 | 8.8071 | 842.992 | 94.7682 | 0.04597 | 838.579 | 91.2609 | 0.034639 | 901.979 | 901.977 | 2025620 | 52.4002 | 2028080 | 1792180 | 1748940 | 0 | 0 | 1721150 | 650.5 | 0 | 0 | 0 | 4414 | 1716740 | 660 | 1685550 | 1651836
4839 | 2002-07-21 14:00 | 809 | 885 | 100 | 32.68 | 5.08 | 0 | 53.2468 | 257.529 | 38.6698 | 0 | 809 | 690.895 | 104.273 | 7.5797 | 690.895 | 97.5829 | 0.039564 | 681.194 | 93.9715 | 0.029812 | 751.94 | 751.936 | 1688650 | 49.545 | 1674340 | 1497940 | 1463450 | 0 | 0 | 1444090 | 654.226 | 0 | 0 | 0 | 1240.58 | 1442840 | 660 | 1420250 | 1391848.625
4840 | 2002-07-21 15:00 | 649 | 862 | 83 | 33.2 | 7.1 | 0 | 40.9991 | 267.766 | 52.6263 | 0 | 649 | 523.696 | 86.5069 | 6.0806 | 523.696 | 80.9565 | 0.031739 | 506.743 | 77.9603 | 0.023916 | 567.186 | 567.182 | 1273750 | 44.372 | 1242360 | 1137200 | 1110230 | 0 | 0 | 1099360 | 663.799 | 0 | 0 | 0 | 0 | 1099360 | 663.799 | 1084220 | 1062535.5
4841 | 2002-07-21 16:00 | 456 | 809 | 68 | 33.71 | 7.1 | 0 | 28.6587 | 276.013 | 66.6835 | 0 | 456 | 320.219 | 69.5383 | 4.2724 | 320.219 | 65.0766 | 0.0223 | 295.779 | 62.6681 | 0.016804 | 347.71 | 347.706 | 780862 | 40.5589 | 738462 | 686238 | 669721 | 0 | 0 | 665652 | 657.659 | 0 | 0 | 0 | 20.9115 | 665631 | 660 | 656978 | 643838
4842 | 2002-07-21 17:00 | 236 | 611 | 62 | 33.01 | 7.1 | 0 | 16.4915 | 283.665 | 80.7034 | 0 | 236 | 99.0192 | 55.4403 | 2.2111 | 99.0192 | 51.8831 | 0.011541 | 73.3226 | 49.963 | 0.0086967 | 119.595 | 119.592 | 268574 | 35.3657 | 234600 | 222442 | 217361 | 0 | 0 | 216889 | 629.872 | 0 | 0 | 0 | 7008.83 | 209880 | 660 | 204548 | 200456.7969
4843 | 2002-07-21 18:00 | 36 | 293 | 9 | 32.31 | 7.95 | 0 | 4.7163 | 291.496 | 90 | 0 | 36 | 0 | 7.7897 | 0.33729 | 0 | 7.2899 | 0.0017606 | 0 | 7.0202 | 0.0013266 | 6.8108 | 6.8106 | 15294.9 | 32.4371 | 7917.06 | 7641.55 | 7500.09 | 0 | 0 | 7499.13 | 483.716 | 0 | 0 | 0 | 7499.13 | 0 | 660 | 0 | 0
4844 | 2002-07-21 19:00 | 0 | 0 | 0 | 31.61 | 7.95 | 0
4845 | 2002-07-21 20:00 | 0 | 0 | 0 | 30.16 | 7.95 | 0
4846 | 2002-07-21 21:00 | 0 | 0 | 0 | 28.72 | 8.28 | 0
4847 | 2002-07-21 22:00 | 0 | 0 | 0 | 27.27 | 8.28 | 0
4848 | 2002-07-21 23:00 | 0 | 0 | 0 | 26.13 | 8.28 | 0
4849 | 2002-07-22 | 0 | 0 | 0 | 24.99 | 7.55 | 0
4850 | 2002-07-22 01:00 | 0 | 0 | 0 | 23.85 | 7.55 | 0
4851 | 2002-07-22 02:00 | 0 | 0 | 0 | 23.3 | 7.55 | 0
4852 | 2002-07-22 03:00 | 0 | 0 | 0 | 22.74 | 7.49 | 0
4853 | 2002-07-22 04:00 | 0 | 16 | 0 | 22.19 | 7.49 | 0
4854 | 2002-07-22 05:00 | 73 | 356 | 33 | 22.34 | 7.49 | 0 | 6.2718 | 69.7044 | 90 | 0 | 73 | 0 | 25.7615 | 0.68395 | 0 | 24.1086 | 0.00357 | 0 | 23.2164 | 0.0026901 | 22.5225 | 22.5217 | 50578.1 | 22.7728 | 36132.1 | 36571.2 | 35713.5 | 0 | 0 | 35699 | 590.359 | 0 | 0 | 0 | 7289.05 | 28409.9 | 660 | 27378.8 | 26831.2383
4855 | 2002-07-22 06:00 | 270 | 681 | 58 | 22.49 | 4.15 | 0 | 18.1118 | 77.4954 | 78.7684 | 0 | 270 | 132.827 | 54.6098 | 2.5297 | 126.963 | 51.1059 | 0.013204 | 100.719 | 49.2146 | 0.0099496 | 145.445 | 145.44 | 326630 | 25.9562 | 290284 | 288820 | 269903 | 0 | 0 | 269254 | 672.039 | 0 | 0 | 0 | 0 | 269254 | 672.039 | 263156 | 257892.6406
4856 | 2002-07-22 07:00 | 486 | 822 | 71 | 22.64 | 4.15 | 0 | 30.3116 | 85.205 | 64.7278 | 0 | 486 | 351.041 | 72.913 | 4.5534 | 351.041 | 68.2348 | 0.023767 | 327.479 | 65.7095 | 0.017909 | 381.411 | 381.408 | 856543 | 31.7298 | 814925 | 790353 | 770621 | 0 | 0 | 765736 | 690.757 | 0 | 0 | 0 | 0 | 765736 | 690.757 | 754604 | 739511.75
4857 | 2002-07-22 08:00 | 681 | 889 | 79 | 25.03 | 4.15 | 0 | 42.6501 | 93.6634 | 50.6614 | 0 | 681 | 563.245 | 82.7812 | 6.3804 | 563.245 | 77.4698 | 0.033304 | 546.98 | 74.6027 | 0.025095 | 602.959 | 602.957 | 1354090 | 39.3999 | 1325580 | 1242880 | 1212440 | 0 | 0 | 1200100 | 680.915 | 0 | 0 | 0 | 0 | 1200100 | 680.915 | 1182050 | 1158413.625
4858 | 2002-07-22 09:00 | 845 | 926 | 88 | 27.43 | 5.73 | 0 | 54.8388 | 104.436 | 36.7155 | 0 | 845 | 742.257 | 92.4513 | 7.917 | 742.257 | 86.5195 | 0.041324 | 733.073 | 83.3174 | 0.031138 | 791.928 | 791.923 | 1778450 | 44.4598 | 1768420 | 1621900 | 1581450 | 0 | 0 | 1560130 | 673.13 | 0 | 0 | 0 | 0 | 1560130 | 673.13 | 1533780 | 1503104.5
4859 | 2002-07-22 10:00 | 960 | 947 | 94 | 29.83 | 5.73 | 0 | 66.2341 | 121.569 | 23.2752 | 0 | 960 | 869.234 | 98.3022 | 8.9945 | 869.234 | 91.995 | 0.046948 | 865.384 | 88.5903 | 0.035376 | 925.389 | 925.387 | 2078190 | 49.7298 | 2083420 | 1865600 | 1819930 | 0 | 0 | 1790650 | 659.306 | 0 | 0 | 0 | -19.3867 | 1790670 | 660.599 | 1756800 | 1721666.25
4860 | 2002-07-22 11:00 | 1008 | 941 | 103 | 30.89 | 5.73 | 0 | 74.5461 | 156.653 | 12.3306 | 0 | 1008 | 917.287 | 106.716 | 9.4442 | 917.287 | 99.8692 | 0.049295 | 916.204 | 96.1731 | 0.037145 | 982.042 | 982.042 | 2205420 | 52.0082 | 2217460 | 1964870 | 1922400 | 0 | 0 | 1889000 | 651.185 | 0 | 0 | 0 | 3021.19 | 1885970 | 660 | 1848520 | 1811548.375
4861 | 2002-07-22 12:00 | 995 | 922 | 111 | 31.95 | 3.96 | 0 | 73.7697 | 209.913 | 13.45 | 0 | 995 | 895.441 | 114.661 | 9.3224 | 895.441 | 107.304 | 0.04866 | 894.179 | 103.333 | 0.036666 | 967.622 | 967.617 | 2173020 | 55.2999 | 2183320 | 1903180 | 1860390 | 0 | 0 | 1828100 | 640.736 | 0 | 0 | 0 | 17793.8 | 1810310 | 659.999 | 1775730 | 1740210.875
4862 | 2002-07-22 13:00 | 930 | 911 | 107 | 33.01 | 3.96 | 0 | 64.735 | 241.446 | 25.0646 | 0 | 930 | 824.354 | 111.285 | 8.7134 | 824.354 | 104.144 | 0.045481 | 820.069 | 100.29 | 0.034271 | 892.781 | 892.776 | 2004950 | 54.5538 | 2006330 | 1753970 | 1715620 | 0 | 0 | 1688090 | 640.919 | 0 | 0 | 0 | 16385.1 | 1671710 | 660 | 1642090 | 1609246.75
4863 | 2002-07-22 14:00 | 824 | 921 | 87 | 33.49 | 3.96 | 0 | 53.152 | 257.237 | 38.6253 | 0 | 824 | 719.516 | 91.4322 | 7.7202 | 719.516 | 85.5657 | 0.040297 | 709.443 | 82.399 | 0.030365 | 768.116 | 768.114 | 1724990 | 52.0256 | 1712390 | 1513650 | 1478800 | 0 | 0 | 1458520 | 645.694 | 0 | 0 | 0 | 7717.7 | 1450800 | 660 | 1428010 | 1399453.125
4864 | 2002-07-22 15:00 | 654 | 877 | 79 | 33.97 | 7.23 | 0 | 40.9113 | 267.529 | 52.6054 | 0 | 654 | 533.217 | 82.6243 | 6.1275 | 533.217 | 77.3229 | 0.031983 | 515.977 | 74.4613 | 0.0241 | 572.749 | 572.744 | 1286230 | 45.1588 | 1255280 | 1144730 | 1116930 | 0 | 0 | 1105850 | 661.994 | 0 | 0 | 0 | 0 | 1105850 | 661.994 | 1090680 | 1068861.75
4865 | 2002-07-22 16:00 | 440 | 752 | 80 | 34.45 | 7.23 | 0 | 28.5692 | 275.809 | 66.6813 | 0 | 440 | 297.989 | 80.3817 | 4.1225 | 297.989 | 75.2243 | 0.021518 | 275.249 | 72.4402 | 0.016214 | 337.274 | 337.271 | 757426 | 41.0387 | 714862 | 662581 | 647563 | 0 | 0 | 643725 | 655.103 | 0 | 0 | 0 | 571.397 | 643154 | 660 | 634793 | 622096.8125
4866 | 2002-07-22 17:00 | 235 | 604 | 64 | 33.84 | 7.23 | 0 | 16.3948 | 283.482 | 80.7184 | 0 | 235 | 97.7133 | 57.3576 | 2.2018 | 97.7133 | 53.6774 | 0.011492 | 72.3072 | 51.6909 | 0.0086598 | 120.287 | 120.285 | 270130 | 36.1898 | 236076 | 222866 | 217768 | 0 | 0 | 217291 | 626.651 | 0 | 0 | 0 | 8412.06 | 208879 | 660 | 203559 | 199488.2656
4867 | 2002-07-22 18:00 | 36 | 287 | 10 | 33.23 | 7.57 | 0 | 4.6081 | 291.327 | 90 | 0 | 36 | 0 | 8.6355 | 0.33729 | 0 | 8.0814 | 0.0017606 | 0 | 7.7823 | 0.0013266 | 7.5502 | 7.5495 | 16954.3 | 33.3743 | 9141.32 | 8766.29 | 8606.99 | 0 | 0 | 8605.75 | 487.062 | 0 | 0 | 0 | 8605.75 | 0 | 660 | 0 | 0
4868 | 2002-07-22 19:00 | 0 | 0 | 0 | 32.63 | 7.57 | 0
4869 | 2002-07-22 20:00 | 0 | 0 | 0 | 31.42 | 7.57 | 0
4870 | 2002-07-22 21:00 | 0 | 0 | 0 | 30.21 | 7.52 | 0
4871 | 2002-07-22 22:00 | 0 | 0 | 0 | 29.01 | 7.52 | 0
4872 | 2002-07-22 23:00 | 0 | 0 | 0 | 27.8 | 7.52 | 0
4873 | 2002-07-23 | 0 | 0 | 0 | 26.59 | 8.19 | 0
4874 | 2002-07-23 01:00 | 0 | 0 | 0 | 25.38 | 8.19 | 0
4875 | 2002-07-23 02:00 | 0 | 0 | 0 | 24.91 | 8.19 | 0
4876 | 2002-07-23 03:00 | 0 | 0 | 0 | 24.44 | 6.44 | 0
4877 | 2002-07-23 04:00 | 0 | 12 | 0 | 23.96 | 6.44 | 0
4878 | 2002-07-23 05:00 | 70 | 321 | 35 | 24.21 | 6.44 | 0 | 6.1504 | 69.8678 | 90 | 0 | 70 | 0 | 27.8388 | 0.65585 | 0 | 26.0526 | 0.0034233 | 0 | 25.0884 | 0.0025795 | 24.3382 | 24.3367 | 54654 | 24.71 | 39563.8 | 39625.4 | 38726.1 | 0 | 0 | 38708.9 | 587.627 | 0 | 0 | 0 | 8863.64 | 29845.3 | 660 | 28764.6 | 28189.3164
4879 | 2002-07-23 06:00 | 273 | 672 | 65 | 24.46 | 1.23 | 0 | 18.0007 | 77.674 | 78.7978 | 0 | 273 | 130.761 | 59.3903 | 2.5578 | 124.656 | 55.5797 | 0.013351 | 98.8059 | 53.5227 | 0.01006 | 147.769 | 147.769 | 331861 | 28.7354 | 295306 | 289794 | 271642 | 0 | 0 | 270968 | 663.421 | 0 | 0 | 0 | -10.4508 | 270979 | 663.735 | 265053 | 259751.8438
4880 | 2002-07-23 07:00 | 484 | 822 | 70 | 24.7 | 1.23 | 0 | 30.2065 | 85.4063 | 64.7399 | 0 | 484 | 351.142 | 72.0098 | 4.5347 | 351.142 | 67.3896 | 0.02367 | 327.555 | 64.8955 | 0.017836 | 380.694 | 380.69 | 854934 | 35.7144 | 813295 | 774132 | 755292 | 0 | 0 | 750448 | 678.955 | 0 | 0 | 0 | 0 | 750448 | 678.955 | 739981 | 725181.4375
4881 | 2002-07-23 08:00 | 680 | 889 | 79 | 26.94 | 1.23 | 0 | 42.5452 | 93.9003 | 50.6542 | 0 | 680 | 563.515 | 82.8602 | 6.3711 | 563.515 | 77.5437 | 0.033255 | 547.25 | 74.6739 | 0.025058 | 603.29 | 603.287 | 1354830 | 44.3947 | 1326350 | 1214440 | 1185500 | 0 | 0 | 1173140 | 664.804 | 0 | 0 | 0 | 0 | 1173140 | 664.804 | 1156430 | 1133305.5
4882 | 2002-07-23 09:00 | 844 | 926 | 88 | 29.18 | 1.49 | 0 | 54.725 | 104.729 | 36.6829 | 0 | 844 | 742.632 | 92.5421 | 7.9076 | 742.632 | 86.6044 | 0.041275 | 733.462 | 83.3993 | 0.031102 | 792.386 | 792.382 | 1779490 | 51.7089 | 1769500 | 1566980 | 1530960 | 0 | 0 | 1509500 | 649.623 | 0 | 0 | 0 | 5734.82 | 1503760 | 660 | 1479640 | 1450043.125
4883 | 2002-07-23 10:00 | 958 | 947 | 93 | 31.42 | 1.49 | 0 | 66.0929 | 121.933 | 23.1994 | 0 | 958 | 869.67 | 97.4049 | 8.9757 | 869.67 | 91.1552 | 0.04685 | 865.844 | 87.7816 | 0.035303 | 925.051 | 925.043 | 2077410 | 57.7208 | 2082600 | 1792460 | 1752250 | 0 | 0 | 1722840 | 632.543 | 0 | 0 | 0 | 39237.6 | 1683600 | 660 | 1653570 | 1620498.5
4884 | 2002-07-23 11:00 | 1014 | 956 | 95 | 32.57 | 1.49 | 0 | 74.3522 | 156.891 | 12.1605 | 0 | 1014 | 932.956 | 98.9012 | 9.5004 | 932.956 | 92.5555 | 0.049589 | 931.885 | 89.1301 | 0.037366 | 990.421 | 990.419 | 2224230 | 60.7295 | 2237300 | 1897760 | 1856780 | 0 | 0 | 1822910 | 623.736 | 0 | 0 | 0 | 72343.2 | 1750570 | 660 | 1718170 | 1683806.125
4885 | 2002-07-23 12:00 | 1012 | 955 | 98 | 33.73 | 2.62 | 0 | 73.5889 | 209.575 | 13.2875 | 0 | 1012 | 927.311 | 101.951 | 9.4817 | 927.311 | 95.4098 | 0.049491 | 926.035 | 91.8787 | 0.037292 | 987.413 | 987.406 | 2217460 | 59.7633 | 2230160 | 1901090 | 1859960 | 0 | 0 | 1826250 | 626.91 | 0 | 0 | 0 | 60199.1 | 1766050 | 660 | 1733100 | 1698433.75
4886 | 2002-07-23 13:00 | 946 | 904 | 130 | 34.89 | 2.62 | 0 | 64.6096 | 241.068 | 24.9835 | 0 | 946 | 818.73 | 133.852 | 8.8633 | 818.73 | 125.264 | 0.046263 | 814.504 | 120.628 | 0.03486 | 907.113 | 907.108 | 2037130 | 58.8063 | 2040200 | 1745940 | 1710100 | 0 | 0 | 1681580 | 627.441 | 0 | 0 | 0 | 53650.5 | 1627930 | 660 | 1599800 | 1567802.25
4887 | 2002-07-23 14:00 | 779 | 750 | 180 | 35.51 | 2.62 | 0 | 53.0515 | 256.939 | 38.5828 | 0 | 779 | 585.906 | 188.547 | 7.2986 | 585.906 | 176.449 | 0.038096 | 577.726 | 169.919 | 0.028706 | 725.243 | 725.232 | 1628690 | 54.631 | 1611610 | 1405160 | 1375140 | 0 | 0 | 1356960 | 634.326 | 0 | 0 | 0 | 25133.2 | 1331830 | 660 | 1311860 | 1285623.625
4888 | 2002-07-23 15:00 | 654 | 842 | 103 | 36.14 | 5.13 | 0 | 40.8183 | 267.287 | 52.587 | 0 | 654 | 512.135 | 107.369 | 6.1275 | 512.135 | 100.48 | 0.031983 | 495.594 | 96.761 | 0.0241 | 574.608 | 574.603 | 1290420 | 48.9859 | 1259600 | 1127200 | 1101170 | 0 | 0 | 1089890 | 646.508 | 0 | 0 | 0 | 4960.38 | 1084930 | 659.999 | 1070270 | 1048864.5
4889 | 2002-07-23 16:00 | 443 | 778 | 72 | 36.76 | 5.13 | 0 | 28.4748 | 275.602 | 66.6818 | 0 | 443 | 308.021 | 72.6873 | 4.1506 | 308.021 | 68.0235 | 0.021664 | 284.514 | 65.506 | 0.016325 | 339.536 | 339.529 | 762494 | 44.3505 | 719964 | 656294 | 641204 | 0 | 0 | 637305 | 643.514 | 0 | 0 | 0 | 5364.3 | 631941 | 660 | 623725 | 611250.875
4890 | 2002-07-23 17:00 | 233 | 602 | 63 | 36.04 | 5.13 | 0 | 16.2932 | 283.296 | 80.7364 | 0 | 233 | 97.5435 | 56.5271 | 2.183 | 97.5435 | 52.9003 | 0.011395 | 72.1233 | 50.9425 | 0.0085861 | 119.382 | 119.381 | 268098 | 38.7089 | 234148 | 218049 | 213023 | 0 | 0 | 212552 | 617.896 | 0 | 0 | 0 | 14204.9 | 198348 | 660 | 193171 | 189307.6094
4891 | 2002-07-23 18:00 | 35 | 283 | 10 | 35.31 | 6.16 | 0 | 4.4948 | 291.155 | 90 | 0 | 35 | 0 | 8.6378 | 0.32792 | 0 | 8.0836 | 0.0017117 | 0 | 7.7844 | 0.0012898 | 7.5521 | 7.5518 | 16959.4 | 35.468 | 9145.23 | 8672.14 | 8513.75 | 0 | 0 | 8512.5 | 479.426 | 0 | 0 | 0 | 8512.5 | 0 | 660 | 0 | 0
4892 | 2002-07-23 19:00 | 0 | 0 | 0 | 34.59 | 6.16 | 0
4893 | 2002-07-23 20:00 | 0 | 0 | 0 | 33.66 | 6.16 | 0
4894 | 2002-07-23 21:00 | 0 | 0 | 0 | 32.72 | 6.78 | 0
4895 | 2002-07-23 22:00 | 0 | 0 | 0 | 31.79 | 6.78 | 0
4896 | 2002-07-23 23:00 | 0 | 0 | 0 | 30.85 | 6.78 | 0
4897 | 2002-07-24 | 0 | 0 | 0 | 29.91 | 6.36 | 0
4898 | 2002-07-24 01:00 | 0 | 0 | 0 | 28.97 | 6.36 | 0
4899 | 2002-07-24 02:00 | 0 | 0 | 0 | 28.4 | 6.36 | 0
4900 | 2002-07-24 03:00 | 0 | 0 | 0 | 27.84 | 2.54 | 0
4901 | 2002-07-24 04:00 | 0 | 12 | 0 | 27.27 | 2.54 | 0
4902 | 2002-07-24 05:00 | 72 | 370 | 32 | 27.62 | 2.54 | 0 | 6.0277 | 70.037 | 90 | 0 | 72 | 0 | 25.0566 | 0.67458 | 0 | 23.4489 | 0.0035211 | 0 | 22.5811 | 0.0026532 | 21.9062 | 21.9053 | 49193.6 | 28.2006 | 34971.5 | 34354 | 33601 | 0 | 0 | 33587.2 | 568.714 | 0 | 0 | 0 | 14342.9 | 19244.2 | 660 | 18535.2 | 18164.4785
4903 | 2002-07-24 06:00 | 271 | 695 | 57 | 27.96 | 1.67 | 0 | 17.8884 | 77.8587 | 78.8256 | 0 | 271 | 135.017 | 53.8008 | 2.5391 | 128.4 | 50.3488 | 0.013253 | 101.692 | 48.4855 | 0.0099864 | 145.682 | 145.672 | 327150 | 32.052 | 290827 | 280650 | 262826 | 0 | 0 | 262172 | 652.002 | 0 | 0 | 0 | 553.513 | 261618 | 660 | 255834 | 250717.5312
4904 | 2002-07-24 07:00 | 482 | 821 | 70 | 28.31 | 1.67 | 0 | 30.1003 | 85.6141 | 64.7502 | 0 | 482 | 350.429 | 72.0791 | 4.516 | 350.429 | 67.4543 | 0.023572 | 326.874 | 64.9579 | 0.017762 | 380.095 | 380.096 | 853596 | 38.9872 | 811942 | 760771 | 741679 | 0 | 0 | 736844 | 668.111 | 0 | 0 | 0 | 0 | 736844 | 668.111 | 726966 | 712426.625
4905 | 2002-07-24 08:00 | 676 | 884 | 79 | 29.91 | 1.67 | 0 | 42.4392 | 94.1444 | 50.645 | 0 | 676 | 561.007 | 82.9417 | 6.3336 | 561.007 | 77.62 | 0.033059 | 544.823 | 74.7473 | 0.024911 | 601.007 | 601.002 | 1349690 | 46.7927 | 1321020 | 1195510 | 1169990 | 0 | 0 | 1157600 | 655.428 | 0 | 0 | 0 | 678.558 | 1156920 | 660 | 1140790 | 1117971.625
4906 | 2002-07-24 09:00 | 830 | 900 | 96 | 31.52 | 0.84 | 0 | 54.6094 | 105.031 | 36.648 | 0 | 830 | 722.38 | 100.637 | 7.7764 | 722.38 | 94.1796 | 0.040591 | 713.481 | 90.694 | 0.030586 | 780.08 | 780.072 | 1751850 | 54.6901 | 1740530 | 1518290 | 1485080 | 0 | 0 | 1464090 | 636.828 | 0 | 0 | 0 | 22081.4 | 1442010 | 660 | 1419440 | 1391053.625
4907 | 2002-07-24 10:00 | 947 | 928 | 100 | 33.12 | 0.84 | 0 | 65.9489 | 122.307 | 23.1208 | 0 | 947 | 853.026 | 104.503 | 8.8727 | 853.026 | 97.7981 | 0.046312 | 849.301 | 94.1786 | 0.034897 | 915.209 | 915.203 | 2055310 | 60.3038 | 2059330 | 1748880 | 1709910 | 0 | 0 | 1681130 | 624.127 | 0 | 0 | 0 | 69018.9 | 1612110 | 660 | 1584510 | 1552821.75
4908 | 2002-07-24 11:00 | 996 | 917 | 116 | 33.68 | 0.84 | 0 | 74.1537 | 157.138 | 11.9856 | 0 | 996 | 894.821 | 119.757 | 9.3317 | 894.821 | 112.074 | 0.048709 | 893.824 | 107.926 | 0.036703 | 971.733 | 971.726 | 2182250 | 62.5426 | 2193040 | 1842320 | 1803440 | 0 | 0 | 1770760 | 617.347 | 0 | 0 | 0 | 100718 | 1670050 | 660 | 1640480 | 1607674.125
4909 | 2002-07-24 12:00 | 992 | 917 | 115 | 34.24 | 3.4 | 0 | 73.4015 | 209.242 | 13.1233 | 0 | 992 | 891.234 | 118.851 | 9.2943 | 891.234 | 111.225 | 0.048513 | 890.039 | 107.109 | 0.036555 | 967.268 | 967.263 | 2172230 | 58.458 | 2182480 | 1872460 | 1833850 | 0 | 0 | 1801400 | 630.036 | 0 | 0 | 0 | 47167.1 | 1754240 | 660 | 1721710 | 1687274.875
4910 | 2002-07-24 13:00 | 926 | 906 | 109 | 34.8 | 3.4 | 0 | 64.4779 | 240.687 | 24.9039 | 0 | 926 | 821.162 | 113.494 | 8.6759 | 821.162 | 106.212 | 0.045285 | 816.953 | 102.281 | 0.034123 | 891.69 | 891.687 | 2002500 | 57.1258 | 2003760 | 1729160 | 1691620 | 0 | 0 | 1664150 | 632.551 | 0 | 0 | 0 | 35973.1 | 1628180 | 660 | 1600040 | 1568037
4911 | 2002-07-24 14:00 | 822 | 921 | 87 | 35.41 | 3.4 | 0 | 52.9455 | 256.638 | 38.5426 | 0 | 822 | 720.34 | 91.6149 | 7.7015 | 720.34 | 85.7367 | 0.040199 | 710.308 | 82.5636 | 0.030291 | 769.115 | 769.11 | 1727220 | 54.6667 | 1714730 | 1495790 | 1461950 | 0 | 0 | 1441690 | 638.476 | 0 | 0 | 0 | 21748.1 | 1419950 | 660 | 1397910 | 1369950.5
4912 | 2002-07-24 15:00 | 650 | 872 | 81 | 36.03 | 4.82 | 0 | 40.7201 | 267.041 | 52.5712 | 0 | 650 | 530.108 | 84.7759 | 6.09 | 530.108 | 79.3365 | 0.031788 | 513.003 | 76.4003 | 0.023953 | 571.745 | 571.739 | 1283980 | 49.0722 | 1252940 | 1120700 | 1095480 | 0 | 0 | 1084290 | 646.222 | 0 | 0 | 0 | 5423.5 | 1078860 | 659.999 | 1064330 | 1043040.1875
4913 | 2002-07-24 16:00 | 441 | 774 | 73 | 36.65 | 4.82 | 0 | 28.3753 | 275.391 | 66.6851 | 0 | 441 | 306.471 | 73.7616 | 4.1318 | 306.471 | 69.0289 | 0.021567 | 283.077 | 66.4742 | 0.016251 | 339.081 | 339.078 | 761484 | 44.3848 | 718946 | 655243 | 639936 | 0 | 0 | 636057 | 643.531 | 0 | 0 | 0 | 5251.13 | 630806 | 660 | 622605 | 610153.25
4914 | 2002-07-24 17:00 | 222 | 559 | 65 | 35.97 | 4.82 | 0 | 16.1865 | 283.106 | 80.7574 | 0 | 222 | 90.4575 | 58.4533 | 2.08 | 90.4575 | 54.7028 | 0.010857 | 66.8205 | 52.6783 | 0.0081808 | 115.922 | 115.921 | 260330 | 38.6143 | 226788 | 211263 | 206534 | 0 | 0 | 206090 | 616.599 | 0 | 0 | 0 | 14697.8 | 191392 | 659.999 | 186317 | 182591
4915 | 2002-07-24 18:00 | 33 | 259 | 10 | 35.28 | 7.25 | 0 | 4.3765 | 290.98 | 90 | 0 | 33 | 0 | 8.64 | 0.30918 | 0 | 8.0856 | 0.0016138 | 0 | 7.7864 | 0.0012161 | 7.554 | 7.5537 | 16963.5 | 35.4274 | 9148.23 | 8676.99 | 8522.22 | 0 | 0 | 8520.96 | 479.746 | 0 | 0 | 0 | 8520.96 | 0 | 660 | 0 | 0
4916 | 2002-07-24 19:00 | 0 | 0 | 0 | 34.6 | 7.25 | 0
4917 | 2002-07-24 20:00 | 0 | 0 | 0 | 33.63 | 7.25 | 0
4918 | 2002-07-24 21:00 | 0 | 0 | 0 | 32.65 | 6.05 | 0
4919 | 2002-07-24 22:00 | 0 | 0 | 0 | 31.68 | 6.05 | 0
4920 | 2002-07-24 23:00 | 0 | 0 | 0 | 30.61 | 6.05 | 0
4921 | 2002-07-25 | 0 | 0 | 0 | 29.54 | 7.56 | 0
4922 | 2002-07-25 01:00 | 0 | 0 | 0 | 28.47 | 7.56 | 0
4923 | 2002-07-25 02:00 | 0 | 0 | 0 | 27.8 | 7.56 | 0
4924 | 2002-07-25 03:00 | 0 | 0 | 0 | 27.14 | 5.98 | 0
4925 | 2002-07-25 04:00 | 0 | 10 | 0 | 26.48 | 5.98 | 0
4926 | 2002-07-25 05:00 | 70 | 367 | 31 | 26.82 | 5.98 | 0 | 5.9037 | 70.212 | 90 | 0 | 70 | 0 | 24.2253 | 0.65585 | 0 | 22.6709 | 0.0034233 | 0 | 21.8319 | 0.0025795 | 21.1794 | 21.1786 | 47561.9 | 27.2682 | 33607.9 | 33187.7 | 32466.1 | 0 | 0 | 32453.2 | 570.243 | 0 | 0 | 0 | 13168.5 | 19284.7 | 660 | 18574.2 | 18202.7441
4927 | 2002-07-25 06:00 | 269 | 693 | 57 | 27.17 | 2.95 | 0 | 17.7751 | 78.0493 | 78.8519 | 0 | 269 | 134.267 | 53.8748 | 2.5203 | 127.385 | 50.4181 | 0.013155 | 100.812 | 48.5521 | 0.0099127 | 144.893 | 144.893 | 325403 | 30.9074 | 289162 | 280671 | 262760 | 0 | 0 | 262115 | 656.351 | 0 | 0 | 0 | 164.628 | 261950 | 660 | 256167 | 251043.25
4928 | 2002-07-25 07:00 | 473 | 799 | 73 | 27.52 | 2.95 | 0 | 29.993 | 85.8282 | 64.7587 | 0 | 473 | 341.217 | 74.4266 | 4.4316 | 341.217 | 69.6512 | 0.023132 | 318.27 | 67.0735 | 0.01743 | 373.8 | 373.796 | 839449 | 37.1618 | 797620 | 753919 | 735548 | 0 | 0 | 730841 | 671.494 | 0 | 0 | 0 | 0 | 730841 | 671.494 | 720920 | 706501.625
4929 | 2002-07-25 08:00 | 677 | 889 | 78 | 29.5 | 2.95 | 0 | 42.3319 | 94.3957 | 50.6338 | 0 | 677 | 564.177 | 82.0251 | 6.343 | 564.177 | 76.7622 | 0.033108 | 547.912 | 73.9213 | 0.024948 | 603.203 | 603.202 | 1354640 | 45.0591 | 1326150 | 1210390 | 1180450 | 0 | 0 | 1168140 | 663.25 | 0 | 0 | 0 | 0 | 1168140 | 663.25 | 1151620 | 1128582.875
4930 | 2002-07-25 09:00 | 841 | 926 | 87 | 31.48 | 2.32 | 0 | 54.4921 | 105.341 | 36.6108 | 0 | 841 | 743.505 | 91.7255 | 7.8795 | 743.505 | 85.8402 | 0.041128 | 734.368 | 82.6634 | 0.030991 | 792.551 | 792.546 | 1779860 | 52.7972 | 1769900 | 1558920 | 1522440 | 0 | 0 | 1500970 | 645.354 | 0 | 0 | 0 | 9544.75 | 1491420 | 660 | 1467630 | 1438281.875
4931 | 2002-07-25 10:00 | 939 | 909 | 111 | 33.46 | 2.32 | 0 | 65.8019 | 122.691 | 23.0395 | 0 | 939 | 835.354 | 115.521 | 8.7977 | 835.354 | 108.109 | 0.045921 | 831.734 | 104.108 | 0.034602 | 907.8 | 907.795 | 2038680 | 57.877 | 2041830 | 1755630 | 1717150 | 0 | 0 | 1688880 | 632.576 | 0 | 0 | 0 | 42121.8 | 1646760 | 660 | 1617990 | 1585633
4932 | 2002-07-25 11:00 | 1015 | 956 | 98 | 34.09 | 2.32 | 0 | 73.9504 | 157.394 | 11.8059 | 0 | 1015 | 934.007 | 102.133 | 9.5098 | 934.007 | 95.5799 | 0.049638 | 932.998 | 92.0425 | 0.037403 | 994.325 | 994.319 | 2233000 | 60.8343 | 2246540 | 1904700 | 1862970 | 0 | 0 | 1828800 | 623.328 | 0 | 0 | 0 | 73343.8 | 1755460 | 660 | 1722890 | 1688429.25
4933 | 2002-07-25 12:00 | 1008 | 955 | 95 | 34.72 | 5.01 | 0 | 73.2077 | 208.916 | 12.9577 | 0 | 1008 | 929.381 | 99.2022 | 9.4442 | 929.381 | 92.8372 | 0.049295 | 928.167 | 89.4013 | 0.037145 | 987.077 | 987.072 | 2216710 | 56.9598 | 2229370 | 1927740 | 1885330 | 0 | 0 | 1851710 | 636.784 | 0 | 0 | 0 | 30201.2 | 1821510 | 660 | 1786510 | 1750780.375
4934 | 2002-07-25 13:00 | 933 | 925 | 100 | 35.35 | 5.01 | 0 | 64.3399 | 240.304 | 24.8259 | 0 | 933 | 838.738 | 104.688 | 8.7415 | 838.738 | 97.9706 | 0.045628 | 834.468 | 94.3448 | 0.034381 | 900.982 | 900.979 | 2023380 | 55.65 | 2025720 | 1761440 | 1720890 | 0 | 0 | 1693090 | 639.738 | 0 | 0 | 0 | 22223.9 | 1670870 | 660 | 1641280 | 1608453.875
4935 | 2002-07-25 14:00 | 821 | 921 | 87 | 35.69 | 5.01 | 0 | 52.8339 | 256.332 | 38.5047 | 0 | 821 | 720.8 | 91.71 | 7.6921 | 720.8 | 85.8257 | 0.04015 | 710.786 | 82.6493 | 0.030254 | 769.662 | 769.659 | 1728460 | 53.0312 | 1716030 | 1509330 | 1474140 | 0 | 0 | 1453970 | 644.778 | 0 | 0 | 0 | 11772.1 | 1442200 | 660 | 1419620 | 1391230.5
4936 | 2002-07-25 15:00 | 648 | 870 | 81 | 36.04 | 6.75 | 0 | 40.6168 | 266.791 | 52.558 | 0 | 648 | 529.515 | 84.8624 | 6.0713 | 529.515 | 79.4175 | 0.03169 | 512.442 | 76.4783 | 0.023879 | 571.276 | 571.271 | 1282930 | 47.5463 | 1251860 | 1128280 | 1102800 | 0 | 0 | 1091630 | 650.971 | 0 | 0 | 0 | 1814.96 | 1089820 | 660 | 1075060 | 1053559.625
4937 | 2002-07-25 16:00 | 438 | 771 | 72 | 36.39 | 6.75 | 0 | 28.2708 | 275.176 | 66.6913 | 0 | 438 | 305.762 | 72.8815 | 4.1037 | 305.762 | 68.2053 | 0.02142 | 282.413 | 65.681 | 0.01614 | 337.667 | 337.664 | 758306 | 43.1911 | 715748 | 656278 | 641296 | 0 | 0 | 637443 | 647.302 | 0 | 0 | 0 | 3063.14 | 634380 | 660 | 626133 | 613610.6875
4938 | 2002-07-25 17:00 | 227 | 587 | 64 | 35.62 | 6.75 | 0 | 16.0749 | 282.913 | 80.7816 | 0 | 227 | 94.3047 | 57.6237 | 2.1268 | 94.3047 | 53.9264 | 0.011101 | 69.5863 | 51.9306 | 0.008365 | 117.88 | 117.878 | 264723 | 37.9942 | 230949 | 215890 | 211060 | 0 | 0 | 210601 | 619.384 | 0 | 0 | 0 | 12798.9 | 197802 | 660 | 192633 | 188780.3594
4939 | 2002-07-25 18:00 | 32 | 269 | 9 | 34.86 | 9.16 | 0 | 4.2531 | 290.801 | 90 | 0 | 32 | 0 | 7.7995 | 0.29981 | 0 | 7.299 | 0.0015649 | 0 | 7.0289 | 0.0011792 | 6.8192 | 6.8187 | 15313.1 | 34.978 | 7930.3 | 7555.16 | 7414.89 | 0 | 0 | 7413.93 | 475.563 | 0 | 0 | 0 | 7413.93 | 0 | 660 | 0 | 0
4940 | 2002-07-25 19:00 | 0 | 0 | 0 | 34.09 | 9.16 | 0
4941 | 2002-07-25 20:00 | 0 | 0 | 0 | 32.77 | 9.16 | 0
4942 | 2002-07-25 21:00 | 0 | 0 | 0 | 31.46 | 8.39 | 0
4943 | 2002-07-25 22:00 | 0 | 0 | 0 | 30.14 | 8.39 | 0
4944 | 2002-07-25 23:00 | 0 | 0 | 0 | 29.04 | 8.39 | 0
4945 | 2002-07-26 | 0 | 0 | 0 | 27.94 | 9.55 | 0
4946 | 2002-07-26 01:00 | 0 | 0 | 0 | 26.84 | 9.55 | 0
4947 | 2002-07-26 02:00 | 0 | 0 | 0 | 26.02 | 9.55 | 0
4948 | 2002-07-26 03:00 | 0 | 0 | 0 | 25.21 | 7.38 | 0
4949 | 2002-07-26 04:00 | 0 | 7 | 0 | 24.39 | 7.38 | 0
4950 | 2002-07-26 05:00 | 67 | 346 | 31 | 24.63 | 7.38 | 0 | 5.7785 | 70.3927 | 90 | 0 | 67 | 0 | 24.3529 | 0.62774 | 0 | 22.7904 | 0.0032766 | 0 | 21.9469 | 0.002469 | 21.2909 | 21.2903 | 47812.9 | 25.042 | 33817.5 | 33808.8 | 33022.4 | 0 | 0 | 33009.4 | 578.24 | 0 | 0 | 0 | 10112.6 | 22896.9 | 660 | 22058.2 | 21617.0859
4951 | 2002-07-26 06:00 | 264 | 679 | 57 | 24.87 | 4.55 | 0 | 17.6608 | 78.2458 | 78.8767 | 0 | 264 | 131.632 | 53.9518 | 2.4735 | 124.551 | 50.4902 | 0.012911 | 98.4986 | 48.6216 | 0.0097285 | 142.716 | 142.726 | 320535 | 28.1836 | 284496 | 279947 | 262584 | 0 | 0 | 261956 | 664.66 | 0 | 0 | 0 | 0 | 261956 | 664.66 | 256071 | 250949.6562
4952 | 2002-07-26 07:00 | 464 | 770 | 80 | 25.11 | 4.55 | 0 | 29.8848 | 86.0487 | 64.7654 | 0 | 464 | 328.563 | 81.4035 | 4.3473 | 328.563 | 76.1805 | 0.022691 | 306.457 | 73.3611 | 0.017098 | 368.44 | 368.436 | 827414 | 33.6638 | 785449 | 754834 | 735966 | 0 | 0 | 731418 | 683.123 | 0 | 0 | 0 | 0 | 731418 | 683.123 | 721064 | 706642.375
4953 | 2002-07-26 08:00 | 659 | 842 | 93 | 27.24 | 4.55 | 0 | 42.2235 | 94.654 | 50.6205 | 0 | 659 | 534.357 | 96.9965 | 6.1743 | 534.357 | 90.773 | 0.032228 | 518.964 | 87.4135 | 0.024284 | 588.209 | 588.203 | 1320960 | 40.8961 | 1291230 | 1202040 | 1172160 | 0 | 0 | 1160470 | 676.744 | 0 | 0 | 0 | 0 | 1160470 | 676.744 | 1143450 | 1120584
4954 | 2002-07-26 09:00 | 816 | 870 | 109 | 29.36 | 2.49 | 0 | 54.373 | 105.659 | 36.5714 | 0 | 816 | 698.553 | 113.724 | 7.6453 | 698.553 | 106.427 | 0.039906 | 689.991 | 102.489 | 0.03007 | 768.734 | 768.728 | 1726370 | 49.8038 | 1713830 | 1531590 | 1496300 | 0 | 0 | 1476040 | 654.064 | 0 | 0 | 0 | 1373.35 | 1474670 | 660 | 1451300 | 1422273.625
4955 | 2002-07-26 10:00 | 953 | 946 | 92 | 31.49 | 2.49 | 0 | 65.652 | 123.083 | 22.9557 | 0 | 953 | 870.213 | 96.724 | 8.9289 | 870.213 | 90.518 | 0.046606 | 866.471 | 87.168 | 0.035118 | 925.064 | 925.061 | 2077460 | 56.0914 | 2082650 | 1807360 | 1765750 | 0 | 0 | 1736450 | 639.048 | 0 | 0 | 0 | 24480.7 | 1711970 | 660 | 1680950 | 1647332.125
4956 | 2002-07-26 11:00 | 1014 | 956 | 98 | 32.37 | 2.49 | 0 | 73.7426 | 157.658 | 11.6216 | 0 | 1014 | 934.593 | 102.261 | 9.5004 | 934.593 | 95.6997 | 0.049589 | 933.615 | 92.1579 | 0.037366 | 995.036 | 995.032 | 2234590 | 58.8322 | 2248220 | 1925790 | 1882520 | 0 | 0 | 1848480 | 630.884 | 0 | 0 | 0 | 47856.1 | 1800620 | 660 | 1766400 | 1731072.25
4957 | 2002-07-26 12:00 | 999 | 940 | 102 | 33.26 | 5.53 | 0 | 73.0075 | 208.596 | 12.7911 | 0 | 999 | 914.671 | 106.304 | 9.3598 | 914.671 | 99.4836 | 0.048855 | 913.508 | 95.8018 | 0.036813 | 979.066 | 979.059 | 2198730 | 54.5878 | 2210410 | 1933930 | 1891220 | 0 | 0 | 1858230 | 644.561 | 0 | 0 | 0 | 13157.9 | 1845070 | 660 | 1809180 | 1772997.125
4958 | 2002-07-26 13:00 | 942 | 945 | 92 | 34.14 | 5.53 | 0 | 64.1956 | 239.919 | 24.7498 | 0 | 942 | 857.42 | 96.7903 | 8.8258 | 857.42 | 90.5801 | 0.046068 | 853.084 | 87.2278 | 0.034713 | 912.136 | 912.132 | 2048410 | 54.0099 | 2052070 | 1799260 | 1758980 | 0 | 0 | 1730340 | 644.292 | 0 | 0 | 0 | 12023.7 | 1718310 | 660 | 1687070 | 1653327.875
4959 | 2002-07-26 14:00 | 820 | 921 | 87 | 34.56 | 5.53 | 0 | 52.7167 | 256.022 | 38.4692 | 0 | 820 | 721.293 | 91.8075 | 7.6828 | 721.293 | 85.917 | 0.040101 | 711.295 | 82.7372 | 0.030217 | 770.241 | 770.238 | 1729760 | 51.3389 | 1717380 | 1523300 | 1488610 | 0 | 0 | 1468210 | 647.929 | 0 | 0 | 0 | 5332.46 | 1462870 | 659.999 | 1439790 | 1410997.5
4960 | 2002-07-26 15:00 | 650 | 878 | 80 | 34.98 | 8.09 | 0 | 40.5082 | 266.538 | 52.5474 | 0 | 650 | 533.624 | 83.9556 | 6.09 | 533.624 | 78.5689 | 0.031788 | 516.43 | 75.6611 | 0.023953 | 574.351 | 574.346 | 1289830 | 45.6069 | 1259000 | 1145650 | 1117870 | 0 | 0 | 1106730 | 660.65 | 0 | 0 | 0 | 7.9273 | 1106720 | 660.839 | 1091580 | 1069752.875
4961 | 2002-07-26 16:00 | 446 | 801 | 67 | 35.4 | 8.09 | 0 | 28.1612 | 274.957 | 66.7004 | 0 | 446 | 317.635 | 68.0689 | 4.1787 | 317.635 | 63.7015 | 0.021811 | 293.365 | 61.3439 | 0.016435 | 344.084 | 344.082 | 772724 | 41.7664 | 730263 | 674505 | 657958 | 0 | 0 | 653979 | 653.655 | 0 | 0 | 0 | 643.361 | 653335 | 660 | 644842 | 631945.125
4962 | 2002-07-26 17:00 | 224 | 585 | 62 | 34.5 | 8.09 | 0 | 15.9583 | 282.717 | 80.8088 | 0 | 224 | 94.1167 | 55.8735 | 2.0987 | 94.1167 | 52.2885 | 0.010955 | 69.3613 | 50.3533 | 0.0082545 | 116.131 | 116.131 | 260800 | 36.6487 | 227233 | 213949 | 209310 | 0 | 0 | 208864 | 623.104 | 0 | 0 | 0 | 10164.1 | 198699 | 660 | 193518 | 189647.5156
4963 | 2002-07-26 18:00 | 32 | 265 | 9 | 33.61 | 8.75 | 0 | 4.1246 | 290.62 | 90 | 0 | 32 | 0 | 7.8017 | 0.29981 | 0 | 7.3011 | 0.0015649 | 0 | 7.0309 | 0.0011792 | 6.8212 | 6.8209 | 15317.9 | 33.7311 | 7933.88 | 7607.42 | 7466.92 | 0 | 0 | 7465.96 | 479.311 | 0 | 0 | 0 | 7465.96 | 0 | 660 | 0 | 0
4964 | 2002-07-26 19:00 | 0 | 0 | 0 | 32.71 | 8.75 | 0
4965 | 2002-07-26 20:00 | 0 | 0 | 0 | 31.37 | 8.75 | 0
4966 | 2002-07-26 21:00 | 0 | 0 | 0 | 30.03 | 7.12 | 0
4967 | 2002-07-26 22:00 | 0 | 0 | 0 | 28.68 | 7.12 | 0
4968 | 2002-07-26 23:00 | 0 | 0 | 0 | 27.68 | 7.12 | 0
4969 | 2002-07-27 | 0 | 0 | 0 | 26.67 | 9.08 | 0
4970 | 2002-07-27 01:00 | 0 | 0 | 0 | 25.67 | 9.08 | 0
4971 | 2002-07-27 02:00 | 0 | 0 | 0 | 24.95 | 9.08 | 0
4972 | 2002-07-27 03:00 | 0 | 0 | 0 | 24.23 | 5.78 | 0
4973 | 2002-07-27 04:00 | 0 | 5 | 0 | 23.51 | 5.78 | 0
4974 | 2002-07-27 05:00 | 65 | 341 | 30 | 23.52 | 5.78 | 0 | 5.6521 | 70.5791 | 90 | 0 | 65 | 0 | 23.5204 | 0.609 | 0 | 22.0113 | 0.0031788 | 0 | 21.1966 | 0.0023953 | 20.5631 | 20.562 | 46176.9 | 23.9607 | 32453.5 | 32636.9 | 31909.4 | 0 | 0 | 31897.4 | 580.185 | 0 | 0 | 0 | 9105.59 | 22791.8 | 660 | 21956.9 | 21517.7578
4975 | 2002-07-27 06:00 | 257 | 657 | 58 | 23.54 | 3.05 | 0 | 17.5456 | 78.4481 | 78.8998 | 0 | 257 | 127.088 | 54.9837 | 2.4079 | 119.886 | 51.4558 | 0.012568 | 94.7452 | 49.5515 | 0.0094705 | 139.977 | 139.969 | 314344 | 27.1265 | 278560 | 275524 | 258479 | 0 | 0 | 257870 | 664.261 | 0 | 0 | 0 | 0 | 257870 | 664.261 | 252018 | 246977.8281
4976 | 2002-07-27 07:00 | 463 | 775 | 78 | 23.55 | 3.05 | 0 | 29.7757 | 86.2754 | 64.7703 | 0 | 463 | 330.455 | 79.5518 | 4.338 | 330.455 | 74.4476 | 0.022643 | 308.214 | 71.6924 | 0.017062 | 368.526 | 368.521 | 827603 | 32.9929 | 785641 | 757394 | 737898 | 0 | 0 | 733354 | 685.775 | 0 | 0 | 0 | 0 | 733354 | 685.775 | 722875 | 708417.3125
4977 | 2002-07-27 08:00 | 664 | 792 | 133 | 25.52 | 3.05 | 0 | 42.1138 | 94.9193 | 50.6053 | 0 | 664 | 502.537 | 137.84 | 6.2212 | 502.537 | 128.996 | 0.032472 | 488.072 | 124.222 | 0.024469 | 593.949 | 593.944 | 1333850 | 40.7391 | 1304590 | 1215420 | 1186670 | 0 | 0 | 1174680 | 676.161 | 0 | 0 | 0 | 0 | 1174680 | 676.161 | 1157400 | 1134251.5
4978 | 2002-07-27 09:00 | 753 | 593 | 272 | 27.48 | 0.46 | 0 | 54.2521 | 105.985 | 36.5299 | 0 | 753 | 476.23 | 277.411 | 7.055 | 476.23 | 259.612 | 0.036825 | 470.408 | 250.004 | 0.027748 | 698.827 | 698.818 | 1569370 | 48.7761 | 1549650 | 1390600 | 1357990 | 0 | 0 | 1341420 | 656.311 | 0 | 0 | 0 | 873.428 | 1340540 | 660 | 1320380 | 1293969.5
4979 | 2002-07-27 10:00 | 954 | 887 | 148 | 29.45 | 0.46 | 0 | 65.4992 | 123.484 | 22.8694 | 0 | 954 | 816.131 | 151.654 | 8.9382 | 816.131 | 141.923 | 0.046655 | 812.65 | 136.671 | 0.035155 | 920.875 | 920.864 | 2068030 | 57.5128 | 2072720 | 1785720 | 1746970 | 0 | 0 | 1717780 | 632.985 | 0 | 0 | 0 | 38204.6 | 1679580 | 660 | 1649690 | 1616693.75
4980 | 2002-07-27 11:00 | 1013 | 956 | 98 | 30.66 | 0.46 | 0 | 73.5301 | 157.929 | 11.4328 | 0 | 1013 | 935.218 | 102.392 | 9.491 | 935.218 | 95.8223 | 0.04954 | 934.271 | 92.276 | 0.037329 | 995.787 | 995.781 | 2236270 | 61.0058 | 2249990 | 1905890 | 1865580 | 0 | 0 | 1831310 | 623.186 | 0 | 0 | 0 | 76674.5 | 1754630 | 660 | 1722090 | 1687646.875
4981 | 2002-07-27 12:00 | 982 | 870 | 152 | 31.86 | 3.2 | 0 | 72.801 | 208.284 | 12.6238 | 0 | 982 | 847.848 | 154.992 | 9.2006 | 847.848 | 145.048 | 0.048024 | 846.798 | 139.68 | 0.036187 | 956.919 | 956.91 | 2148980 | 56.1375 | 2157980 | 1873010 | 1832800 | 0 | 0 | 1801100 | 637.455 | 0 | 0 | 0 | 25169.3 | 1775940 | 660 | 1742620 | 1707766.75
4982 | 2002-07-27 13:00 | 898 | 835 | 148 | 33.07 | 3.2 | 0 | 64.0451 | 239.532 | 24.6758 | 0 | 898 | 757.962 | 158.494 | 8.4136 | 757.962 | 148.325 | 0.043916 | 754.154 | 142.836 | 0.033092 | 870.112 | 870.103 | 1954030 | 55.1452 | 1952780 | 1701630 | 1664040 | 0 | 0 | 1637980 | 639.043 | 0 | 0 | 0 | 20740.5 | 1617240 | 660 | 1589470 | 1557676.875
4983 | 2002-07-27 14:00 | 784 | 809 | 141 | 33.66 | 3.2 | 0 | 52.5938 | 255.708 | 38.4363 | 0 | 784 | 634.056 | 149.087 | 7.3455 | 634.056 | 139.521 | 0.038341 | 625.286 | 134.358 | 0.028891 | 736.882 | 736.877 | 1654840 | 52.3551 | 1638960 | 1445740 | 1412720 | 0 | 0 | 1394230 | 645.882 | 0 | 0 | 0 | 10294.7 | 1383940 | 660 | 1362760 | 1335501.5
4984 | 2002-07-27 15:00 | 648 | 841 | 103 | 34.26 | 6.25 | 0 | 40.3944 | 266.28 | 52.5397 | 0 | 648 | 511.5 | 107.897 | 6.0713 | 511.5 | 100.974 | 0.03169 | 495.026 | 97.2372 | 0.023879 | 574.518 | 574.514 | 1290210 | 46.2079 | 1259390 | 1142620 | 1115960 | 0 | 0 | 1104680 | 655.865 | 0 | 0 | 0 | 253.624 | 1104430 | 660 | 1089380 | 1067591.75
4985 | 2002-07-27 16:00 | 444 | 800 | 67 | 34.85 | 6.25 | 0 | 28.0466 | 274.735 | 66.7124 | 0 | 444 | 316.99 | 68.1663 | 4.1599 | 316.99 | 63.7926 | 0.021713 | 292.749 | 61.4317 | 0.016362 | 343.571 | 343.566 | 771561 | 41.995 | 729090 | 672635 | 656636 | 0 | 0 | 652656 | 651.705 | 0 | 0 | 0 | 1040.13 | 651616 | 660 | 643145 | 630282
4986 | 2002-07-27 17:00 | 224 | 598 | 60 | 33.75 | 6.25 | 0 | 15.8367 | 282.518 | 80.8392 | 0 | 224 | 95.6769 | 54.1225 | 2.0987 | 95.6769 | 50.6499 | 0.010955 | 70.4127 | 48.7754 | 0.0082545 | 115.62 | 115.62 | 259653 | 36.1545 | 226146 | 213485 | 208587 | 0 | 0 | 208146 | 624.668 | 0 | 0 | 0 | 9014.62 | 199132 | 660 | 193944 | 190065.125
4987 | 2002-07-27 18:00 | 31 | 267 | 8 | 32.64 | 10.45 | 0 | 3.9911 | 290.435 | 90 | 0 | 31 | 0 | 6.9569 | 0.29045 | 0 | 6.5105 | 0.001516 | 0 | 6.2696 | 0.0011424 | 6.0826 | 6.0822 | 13659 | 32.7372 | 6730.61 | 6500.57 | 6375.38 | 0 | 0 | 6374.67 | 476.71 | 0 | 0 | 0 | 6374.67 | 0 | 660 | 0 | 0
4988 | 2002-07-27 19:00 | 0 | 0 | 0 | 31.54 | 10.45 | 0
4989 | 2002-07-27 20:00 | 0 | 0 | 0 | 29.92 | 10.45 | 0
4990 | 2002-07-27 21:00 | 0 | 0 | 0 | 28.31 | 6.84 | 0
4991 | 2002-07-27 22:00 | 0 | 0 | 0 | 26.69 | 6.84 | 0
4992 | 2002-07-27 23:00 | 0 | 0 | 0 | 25.47 | 6.84 | 0
4993 | 2002-07-28 | 0 | 0 | 0 | 24.24 | 7.3 | 0
4994 | 2002-07-28 01:00 | 0 | 0 | 0 | 23.02 | 7.3 | 0
4995 | 2002-07-28 02:00 | 0 | 0 | 0 | 22.24 | 7.3 | 0
4996 | 2002-07-28 03:00 | 0 | 0 | 0 | 21.45 | 5.32 | 0
4997 | 2002-07-28 04:00 | 0 | 3 | 0 | 20.67 | 5.32 | 0
4998 | 2002-07-28 05:00 | 65 | 347 | 30 | 20.71 | 5.32 | 0 | 5.5246 | 70.7712 | 90 | 0 | 65 | 0 | 23.65 | 0.609 | 0 | 22.1326 | 0.0031788 | 0 | 21.3135 | 0.0023953 | 20.6764 | 20.6751 | 46431.1 | 21.1666 | 32665.1 | 33346.7 | 32586 | 0 | 0 | 32573.9 | 590.159 | 0 | 0 | 0 | 6328.25 | 26245.6 | 660 | 25289.6 | 24783.8555
4999 | 2002-07-28 06:00 | 261 | 677 | 57 | 20.74 | 2.49 | 0 | 17.4294 | 78.6562 | 78.9214 | 0 | 261 | 130.871 | 54.115 | 2.4454 | 123.113 | 50.6429 | 0.012764 | 97.234 | 48.7686 | 0.0096179 | 141.632 | 141.623 | 318060 | 24.5064 | 282156 | 282665 | 265145 | 0 | 0 | 264522 | 673.737 | 0 | 0 | 0 | 0 | 264522 | 673.737 | 258424 | 253255.4844
5000 | 2002-07-28 07:00 | 465 | 760 | 88 | 20.78 | 2.49 | 0 | 29.6656 | 86.5082 | 64.7734 | 0 | 465 | 324.641 | 89.4374 | 4.3567 | 324.641 | 83.6989 | 0.02274 | 302.788 | 80.6013 | 0.017135 | 371.904 | 371.901 | 835198 | 30.6705 | 793321 | 773119 | 752888 | 0 | 0 | 748269 | 693.81 | 0 | 0 | 0 | 0 | 748269 | 693.81 | 737276 | 722530.6875
5001 | 2002-07-28 08:00 | 673 | 847 | 106 | 23.11 | 2.49 | 0 | 42.003 | 95.1914 | 50.5881 | 0 | 673 | 537.954 | 111.496 | 6.3055 | 537.954 | 104.343 | 0.032912 | 522.486 | 100.481 | 0.0248 | 604.302 | 604.295 | 1357100 | 39.1808 | 1328700 | 1247080 | 1216860 | 0 | 0 | 1204480 | 682.549 | 0 | 0 | 0 | 0 | 1204480 | 682.549 | 1186260 | 1162539.25
5002 | 2002-07-28 09:00 | 808 | 825 | 140 | 25.43 | 2.37 | 0 | 54.1295 | 106.318 | 36.4862 | 0 | 808 | 662.771 | 148.666 | 7.5703 | 662.771 | 139.128 | 0.039515 | 654.692 | 133.979 | 0.029775 | 765.039 | 765.034 | 1718070 | 45.9387 | 1705140 | 1552480 | 1515710 | 0 | 0 | 1495810 | 668.08 | 0 | 0 | 0 | 0 | 1495810 | 668.08 | 1471600 | 1442169.625
5003 | 2002-07-28 10:00 | 908 | 829 | 155 | 27.76 | 2.37 | 0 | 65.3434 | 123.894 | 22.7807 | 0 | 908 | 763.911 | 165.897 | 8.5073 | 763.911 | 155.253 | 0.044405 | 760.68 | 149.507 | 0.03346 | 882.914 | 882.909 | 1982780 | 51.4287 | 1983020 | 1760290 | 1719930 | 0 | 0 | 1693070 | 651.128 | 0 | 0 | 0 | 2757.73 | 1690320 | 660 | 1660050 | 1626852.5
5004 | 2002-07-28 11:00 | 978 | 878 | 139 | 29.37 | 2.37 | 0 | 73.3131 | 158.208 | 11.2397 | 0 | 978 | 859.086 | 142.707 | 9.1631 | 859.086 | 133.551 | 0.047828 | 858.246 | 128.608 | 0.03604 | 957.284 | 957.275 | 2149790 | 55.0323 | 2158840 | 1884080 | 1840070 | 0 | 0 | 1808780 | 643.975 | 0 | 0 | 0 | 15803.2 | 1792980 | 660 | 1759040 | 1723857.25
5005 | 2002-07-28 12:00 | 981 | 899 | 125 | 30.98 | 0.52 | 0 | 72.5883 | 207.979 | 12.456 | 0 | 981 | 875.99 | 129.236 | 9.1912 | 875.99 | 120.944 | 0.047975 | 874.934 | 116.468 | 0.03615 | 961.695 | 961.692 | 2159720 | 60.1684 | 2169310 | 1844680 | 1802910 | 0 | 0 | 1771080 | 625.488 | 0 | 0 | 0 | 64686.5 | 1706400 | 660 | 1675570 | 1642060.25
5006 | 2002-07-28 13:00 | 915 | 856 | 147 | 32.58 | 0.52 | 0 | 63.8882 | 239.144 | 24.6041 | 0 | 915 | 777.638 | 150.937 | 8.5728 | 777.638 | 141.253 | 0.044747 | 773.755 | 136.025 | 0.033718 | 882.52 | 882.518 | 1981910 | 59.3654 | 1982100 | 1690680 | 1656180 | 0 | 0 | 1629200 | 624.826 | 0 | 0 | 0 | 61493.2 | 1567700 | 660 | 1541560 | 1510725.5
5007 | 2002-07-28 14:00 | 764 | 723 | 191 | 33.54 | 0.52 | 0 | 52.4653 | 255.391 | 38.406 | 0 | 764 | 566.24 | 200.484 | 7.1581 | 566.24 | 187.621 | 0.037363 | 558.422 | 180.677 | 0.028154 | 716.954 | 716.946 | 1610080 | 55.3001 | 1592170 | 1383230 | 1352430 | 0 | 0 | 1334760 | 632.389 | 0 | 0 | 0 | 29555.3 | 1305200 | 660 | 1285840 | 1260125
5008 | 2002-07-28 15:00 | 643 | 835 | 103 | 34.51 | 3.07 | 0 | 40.2754 | 266.019 | 52.5348 | 0 | 643 | 508.106 | 108.036 | 6.0244 | 508.106 | 101.104 | 0.031445 | 491.745 | 97.3622 | 0.023695 | 571.457 | 571.452 | 1283340 | 49.1334 | 1252270 | 1119730 | 1094750 | 0 | 0 | 1083570 | 645.705 | 0 | 0 | 0 | 5840.08 | 1077730 | 659.999 | 1063220 | 1041953.8125
5009 | 2002-07-28 16:00 | 427 | 749 | 76 | 35.47 | 3.07 | 0 | 27.927 | 274.51 | 66.7275 | 0 | 427 | 296.109 | 77.1056 | 4.0007 | 296.109 | 72.1584 | 0.020882 | 273.443 | 69.4878 | 0.015735 | 332.658 | 332.656 | 747063 | 43.9827 | 704441 | 643227 | 628338 | 0 | 0 | 624600 | 644.052 | 0 | 0 | 0 | 4925.85 | 619674 | 660 | 611619 | 599386.1875
5010 | 2002-07-28 17:00 | 215 | 560 | 63 | 34.73 | 3.07 | 0 | 15.7101 | 282.315 | 80.8727 | 0 | 215 | 89.0483 | 56.9775 | 2.0144 | 89.0483 | 53.3218 | 0.010514 | 65.4326 | 51.3484 | 0.0079228 | 113.285 | 113.282 | 254402 | 37.6289 | 221180 | 207116 | 202298 | 0 | 0 | 201876 | 619.032 | 0 | 0 | 0 | 12521.7 | 189354 | 660 | 184310 | 180623.6094
5011 | 2002-07-28 18:00 | 30 | 247 | 9 | 34 | 7.72 | 0 | 3.8525 | 290.248 | 90 | 0 | 30 | 0 | 7.8057 | 0.28108 | 0 | 7.3049 | 0.0014671 | 0 | 7.0346 | 0.0011055 | 6.8246 | 6.8243 | 15325.7 | 34.1292 | 7939.47 | 7597.03 | 7459.5 | 0 | 0 | 7458.54 | 478.702 | 0 | 0 | 0 | 7458.54 | 0 | 660 | 0 | 0
5012 | 2002-07-28 19:00 | 0 | 0 | 0 | 33.26 | 7.72 | 0
5013 | 2002-07-28 20:00 | 0 | 0 | 0 | 31.74 | 7.72 | 0
5014 | 2002-07-28 21:00 | 0 | 0 | 0 | 30.21 | 7.01 | 0
5015 | 2002-07-28 22:00 | 0 | 0 | 0 | 28.68 | 7.01 | 0
5016 | 2002-07-28 23:00 | 0 | 0 | 0 | 27.53 | 7.01 | 0
5017 | 2002-07-29 | 0 | 0 | 0 | 26.38 | 6.09 | 0
5018 | 2002-07-29 01:00 | 0 | 0 | 0 | 25.23 | 6.09 | 0
5019 | 2002-07-29 02:00 | 0 | 0 | 0 | 24.73 | 6.09 | 0
5020 | 2002-07-29 03:00 | 0 | 0 | 0 | 24.23 | 5.74 | 0
5021 | 2002-07-29 04:00 | 0 | 1 | 0 | 23.73 | 5.74 | 0
5022 | 2002-07-29 05:00 | 54 | 215 | 33 | 23.89 | 5.74 | 0 | 5.396 | 70.9688 | 90 | 0 | 54 | 0 | 25.3991 | 0.50594 | 0 | 23.7695 | 0.0026408 | 0 | 22.8898 | 0.0019899 | 22.205 | 22.2042 | 49865.1 | 24.3672 | 35533.9 | 35656.2 | 34852.8 | 0 | 0 | 34838.6 | 582.822 | 0 | 0 | 0 | 9076.65 | 25761.9 | 660 | 24822.8 | 24326.3477
5023 | 2002-07-29 06:00 | 261 | 621 | 76 | 24.05 | 2.27 | 0 | 17.3123 | 78.8699 | 78.9414 | 0 | 261 | 119.247 | 70.1724 | 2.4454 | 111.899 | 65.67 | 0.012764 | 88.3253 | 63.2396 | 0.0096179 | 147.027 | 147.023 | 330186 | 28.0177 | 293716 | 289247 | 273554 | 0 | 0 | 272877 | 664.759 | 0 | 0 | 0 | 0 | 272877 | 664.759 | 266916 | 261577.4531
5024 | 2002-07-29 07:00 | 467 | 798 | 73 | 24.21 | 2.27 | 0 | 29.5546 | 86.747 | 64.7747 | 0 | 467 | 340.422 | 74.8496 | 4.3754 | 340.422 | 70.0471 | 0.022838 | 317.504 | 67.4547 | 0.017209 | 373.427 | 373.422 | 838611 | 34.2875 | 796772 | 763493 | 744827 | 0 | 0 | 740133 | 680.948 | 0 | 0 | 0 | 0 | 740133 | 680.948 | 729736 | 715141
5025 | 2002-07-29 08:00 | 671 | 885 | 80 | 26.78 | 2.27 | 0 | 41.8911 | 95.4702 | 50.5691 | 0 | 671 | 562.173 | 84.3892 | 6.2867 | 562.173 | 78.9746 | 0.032815 | 546.026 | 76.0518 | 0.024727 | 603.44 | 603.435 | 1355160 | 43.0648 | 1326700 | 1222550 | 1194070 | 0 | 0 | 1181720 | 670.319 | 0 | 0 | 0 | 0 | 1181720 | 670.319 | 1164570 | 1141280
5026 | 2002-07-29 09:00 | 836 | 926 | 87 | 29.34 | 1.93 | 0 | 54.0051 | 106.66 | 36.4406 | 0 | 836 | 744.745 | 92.131 | 7.8327 | 744.745 | 86.2197 | 0.040884 | 735.695 | 83.0288 | 0.030807 | 794.192 | 794.187 | 1783540 | 51.2646 | 1773750 | 1574260 | 1538480 | 0 | 0 | 1516870 | 649.855 | 0 | 0 | 0 | 4315.6 | 1512560 | 659.999 | 1488160 | 1458401.5
5027 | 2002-07-29 10:00 | 952 | 947 | 93 | 31.9 | 1.93 | 0 | 65.1846 | 124.311 | 22.6899 | 0 | 952 | 873.14 | 98.0777 | 8.9195 | 873.14 | 91.7849 | 0.046557 | 869.478 | 88.388 | 0.035082 | 929.164 | 929.161 | 2086660 | 57.5508 | 2092340 | 1802520 | 1762830 | 0 | 0 | 1733050 | 632.568 | 0 | 0 | 0 | 37856.7 | 1695190 | 660 | 1664760 | 1631463.125
5028 | 2002-07-29 11:00 | 1010 | 956 | 97 | 33.53 | 1.93 | 0 | 73.0916 | 158.493 | 11.0424 | 0 | 1010 | 936.584 | 101.661 | 9.4629 | 936.584 | 95.1384 | 0.049393 | 935.701 | 91.6174 | 0.037219 | 996.535 | 996.531 | 2237950 | 61.0406 | 2251760 | 1907130 | 1866140 | 0 | 0 | 1831780 | 622.843 | 0 | 0 | 0 | 76581.5 | 1755200 | 660 | 1722630 | 1688180
5029 | 2002-07-29 12:00 | 1007 | 955 | 99 | 35.15 | 0.62 | 0 | 72.3694 | 207.681 | 12.2881 | 0 | 1007 | 930.924 | 103.721 | 9.4348 | 930.924 | 97.066 | 0.049246 | 929.833 | 93.4737 | 0.037108 | 992.643 | 992.634 | 2229200 | 65.0746 | 2242540 | 1859490 | 1820120 | 0 | 0 | 1786100 | 609.84 | 0 | 0 | 0 | 145221 | 1640870 | 660 | 1612310 | 1580061
5030 | 2002-07-29 13:00 | 939 | 945 | 92 | 36.77 | 0.62 | 0 | 63.7251 | 238.755 | 24.5349 | 0 | 939 | 859.306 | 97.1333 | 8.7977 | 859.306 | 90.901 | 0.045921 | 855.042 | 87.5368 | 0.034602 | 914.335 | 914.333 | 2053360 | 64.3341 | 2057280 | 1710580 | 1674780 | 0 | 0 | 1645910 | 610.118 | 0 | 0 | 0 | 134144 | 1511770 | 660 | 1487400 | 1457654.375
5031 | 2002-07-29 14:00 | 815 | 921 | 86 | 37.12 | 0.62 | 0 | 52.331 | 255.071 | 38.3786 | 0 | 815 | 721.974 | 91.1043 | 7.6359 | 721.974 | 85.2589 | 0.039857 | 712.024 | 82.1035 | 0.030033 | 770.333 | 770.327 | 1729960 | 60.3428 | 1717600 | 1455070 | 1424050 | 0 | 0 | 1403580 | 618.336 | 0 | 0 | 0 | 78966 | 1324620 | 660 | 1304820 | 1278719.125
5032 | 2002-07-29 15:00 | 641 | 868 | 81 | 37.46 | 4.05 | 0 | 40.1511 | 265.754 | 52.5328 | 0 | 641 | 528.302 | 85.2289 | 6.0057 | 528.302 | 79.7605 | 0.031348 | 511.293 | 76.8086 | 0.023621 | 570.482 | 570.479 | 1281150 | 51.1453 | 1250010 | 1106450 | 1082880 | 0 | 0 | 1071730 | 639.418 | 0 | 0 | 0 | 14210.2 | 1057520 | 660 | 1043400 | 1022535.3125
5033 | 2002-07-29 16:00 | 444 | 807 | 67 | 37.8 | 4.05 | 0 | 27.8024 | 274.281 | 66.7456 | 0 | 444 | 319.12 | 68.3663 | 4.1599 | 319.12 | 63.9798 | 0.021713 | 294.663 | 61.612 | 0.016362 | 345.602 | 345.598 | 776126 | 46.0906 | 733688 | 662977 | 648599 | 0 | 0 | 644523 | 636.434 | 0 | 0 | 0 | 10217.3 | 634306 | 660 | 626060 | 613538.6875
5034 | 2002-07-29 17:00 | 220 | 593 | 60 | 37.26 | 4.05 | 0 | 15.5786 | 282.11 | 80.9094 | 0 | 220 | 94.1299 | 54.3019 | 2.0612 | 94.1299 | 50.8178 | 0.010759 | 69.0478 | 48.9371 | 0.0081071 | 114.453 | 114.451 | 257028 | 40.0056 | 223663 | 206746 | 202149 | 0 | 0 | 201716 | 611.343 | 0 | 0 | 0 | 18917.6 | 182799 | 659.999 | 177858 | 174300.3906
5035 | 2002-07-29 18:00 | 29 | 257 | 8 | 36.72 | 7.6 | 0 | 3.709 | 290.058 | 90 | 0 | 29 | 0 | 6.9613 | 0.27171 | 0 | 6.5146 | 0.0014182 | 0 | 6.2735 | 0.0010687 | 6.0864 | 6.0857 | 13667 | 36.8361 | 6736.34 | 6375.39 | 6255.03 | 0 | 0 | 6254.31 | 462.808 | 0 | 0 | 0 | 6254.31 | 0 | 660 | 0 | 0
5036 | 2002-07-29 19:00 | 0 | 0 | 0 | 36.18 | 7.6 | 0
5037 | 2002-07-29 20:00 | 0 | 0 | 0 | 34.68 | 7.6 | 0
5038 | 2002-07-29 21:00 | 0 | 0 | 0 | 33.19 | 6.75 | 0
5039 | 2002-07-29 22:00 | 0 | 0 | 0 | 31.7 | 6.75 | 0
5040 | 2002-07-29 23:00 | 0 | 0 | 0 | 30.59 | 6.75 | 0
5041 | 2002-07-30 | 0 | 0 | 0 | 29.47 | 4.43 | 0
5042 | 2002-07-30 01:00 | 0 | 0 | 0 | 28.36 | 4.43 | 0
5043 | 2002-07-30 02:00 | 0 | 0 | 0 | 27.56 | 4.43 | 0
5044 | 2002-07-30 03:00 | 0 | 0 | 0 | 26.77 | 4.31 | 0
5045 | 2002-07-30 04:00 | 0 | 0 | 0 | 25.97 | 4.31 | 0
5046 | 2002-07-30 05:00 | 58 | 282 | 31 | 26.07 | 4.31 | 0 | 5.2665 | 71.1719 | 90 | 0 | 58 | 0 | 24.914 | 0.54341 | 0 | 23.3154 | 0.0028364 | 0 | 22.4525 | 0.0021373 | 21.781 | 21.7804 | 48913 | 26.5837 | 34736.8 | 34433.5 | 33661.1 | 0 | 0 | 33647.5 | 573.97 | 0 | 0 | 0 | 11978.8 | 21668.7 | 660 | 20873.5 | 20456.0449
5047 | 2002-07-30 06:00 | 260 | 662 | 64 | 26.17 | 2.75 | 0 | 17.1944 | 79.0893 | 78.9597 | 0 | 260 | 126.969 | 59.1338 | 2.436 | 118.799 | 55.3397 | 0.012715 | 93.7207 | 53.2916 | 0.0095811 | 142.611 | 142.591 | 320230 | 29.8971 | 284228 | 277271 | 261190 | 0 | 0 | 260558 | 658.128 | 0 | 0 | 0 | 82.4639 | 260476 | 660 | 254702 | 249607.5156
5048 | 2002-07-30 07:00 | 472 | 817 | 70 | 26.28 | 2.75 | 0 | 29.4428 | 86.9918 | 64.7743 | 0 | 472 | 348.54 | 72.5466 | 4.4223 | 348.54 | 67.8919 | 0.023083 | 325.077 | 65.3792 | 0.017393 | 378.759 | 378.756 | 850588 | 36.1802 | 808894 | 768228 | 749480 | 0 | 0 | 744654 | 675.71 | 0 | 0 | 0 | 0 | 744654 | 675.71 | 734389 | 719701.25
5049 | 2002-07-30 08:00 | 654 | 814 | 112 | 28.66 | 2.75 | 0 | 41.778 | 95.7556 | 50.5481 | 0 | 654 | 516.931 | 117.762 | 6.1275 | 516.931 | 110.206 | 0.031983 | 502.102 | 106.128 | 0.0241 | 590.006 | 589.997 | 1324980 | 44.0817 | 1295400 | 1187720 | 1159870 | 0 | 0 | 1148050 | 665.18 | 0 | 0 | 0 | 0 | 1148050 | 665.18 | 1131850 | 1109213.875
5050 | 2002-07-30 09:00 | 835 | 926 | 87 | 31.04 | 3.26 | 0 | 53.8788 | 107.009 | 36.3931 | 0 | 835 | 745.401 | 92.2386 | 7.8233 | 745.401 | 86.3204 | 0.040835 | 736.371 | 83.1258 | 0.03077 | 794.942 | 794.943 | 1785240 | 51.1285 | 1775530 | 1576920 | 1538810 | 0 | 0 | 1517290 | 652.277 | 0 | 0 | 0 | 3143.96 | 1514150 | 660 | 1489710 | 1459911.875
5051 | 2002-07-30 10:00 | 942 | 933 | 97 | 33.42 | 3.26 | 0 | 65.0228 | 124.737 | 22.5971 | 0 | 942 | 860.618 | 102.228 | 8.8258 | 860.618 | 95.6692 | 0.046068 | 857.04 | 92.1286 | 0.034713 | 920.727 | 920.72 | 2067700 | 56.6869 | 2072370 | 1793010 | 1756860 | 0 | 0 | 1727410 | 634.167 | 0 | 0 | 0 | 32639.5 | 1694770 | 660 | 1664350 | 1631065.875
5052 | 2002-07-30 11:00 | 1010 | 956 | 98 | 34.56 | 3.26 | 0 | 72.8656 | 158.784 | 10.8411 | 0 | 1010 | 937.325 | 102.802 | 9.4629 | 937.325 | 96.2059 | 0.049393 | 936.473 | 92.6454 | 0.037219 | 998.281 | 998.274 | 2241880 | 59.7867 | 2255900 | 1923090 | 1882420 | 0 | 0 | 1847920 | 626.875 | 0 | 0 | 0 | 60722.6 | 1787200 | 660 | 1753470 | 1718401.875
5053 | 2002-07-30 12:00 | 1005 | 955 | 98 | 35.7 | 4.94 | 0 | 72.1444 | 207.391 | 12.1205 | 0 | 1005 | 931.657 | 102.859 | 9.4161 | 931.657 | 96.2591 | 0.049149 | 930.595 | 92.6966 | 0.037035 | 992.629 | 992.623 | 2229170 | 58.1669 | 2242510 | 1927430 | 1883810 | 0 | 0 | 1849850 | 632.201 | 0 | 0 | 0 | 40495.4 | 1809350 | 660 | 1774800 | 1739307
5054 | 2002-07-30 13:00 | 938 | 945 | 93 | 36.84 | 4.94 | 0 | 63.5558 | 238.366 | 24.4684 | 0 | 938 | 858.988 | 98.2629 | 8.7883 | 858.988 | 91.9582 | 0.045872 | 854.75 | 88.5549 | 0.034566 | 915.039 | 915.033 | 2054930 | 57.5507 | 2058940 | 1773530 | 1734800 | 0 | 0 | 1705840 | 631.851 | 0 | 0 | 0 | 38753.2 | 1667090 | 660 | 1637630 | 1604878.375
5055 | 2002-07-30 14:00 | 814 | 921 | 87 | 36.89 | 4.94 | 0 | 52.1912 | 254.748 | 38.3541 | 0 | 814 | 721.599 | 92.2216 | 7.6265 | 721.599 | 86.3045 | 0.039808 | 711.67 | 83.1104 | 0.029996 | 770.966 | 770.962 | 1731390 | 54.3398 | 1719090 | 1502150 | 1470500 | 0 | 0 | 1449950 | 637.259 | 0 | 0 | 0 | 20921 | 1429030 | 660 | 1406770 | 1378637.625
5056 | 2002-07-30 15:00 | 638 | 866 | 81 | 36.93 | 7.27 | 0 | 40.0215 | 265.487 | 52.5339 | 0 | 638 | 526.873 | 85.3255 | 5.9776 | 526.873 | 79.8509 | 0.031201 | 509.909 | 76.8957 | 0.023511 | 569.223 | 569.221 | 1278330 | 48.0218 | 1247090 | 1121310 | 1095750 | 0 | 0 | 1084730 | 651.029 | 0 | 0 | 0 | 2907.25 | 1081820 | 659.999 | 1067230 | 1045882.4375
5057 | 2002-07-30 16:00 | 427 | 761 | 73 | 36.97 | 7.27 | 0 | 27.6727 | 274.05 | 66.7667 | 0 | 427 | 300.685 | 74.381 | 4.0007 | 300.685 | 69.6085 | 0.020882 | 277.607 | 67.0324 | 0.015735 | 334.316 | 334.312 | 750778 | 43.4844 | 708176 | 648316 | 633285 | 0 | 0 | 629510 | 646.006 | 0 | 0 | 0 | 3730.8 | 625779 | 659.999 | 617644 | 605290.75
5058 | 2002-07-30 17:00 | 217 | 576 | 63 | 36.32 | 7.27 | 0 | 15.4421 | 281.901 | 80.9492 | 0 | 217 | 90.9834 | 57.1658 | 2.0331 | 90.9834 | 53.4979 | 0.010612 | 66.614 | 51.518 | 0.0079965 | 114.596 | 114.592 | 257344 | 38.5529 | 223961 | 208685 | 204107 | 0 | 0 | 203673 | 616.4 | 0 | 0 | 0 | 14822.6 | 188851 | 660 | 183814 | 180138.1094
5059 | 2002-07-30 18:00 | 28 | 246 | 8 | 35.66 | 8.86 | 0 | 3.5605 | 289.865 | 90 | 0 | 28 | 0 | 6.9632 | 0.26234 | 0 | 6.5164 | 0.0013693 | 0 | 6.2752 | 0.0010318 | 6.088 | 6.0878 | 13671.6 | 35.7673 | 6739.72 | 6413.23 | 6291.42 | 0 | 0 | 6290.7 | 466.534 | 0 | 0 | 0 | 6290.7 | 0 | 660 | 0 | 0
5060 | 2002-07-30 19:00 | 0 | 0 | 0 | 35.01 | 8.86 | 0
5061 | 2002-07-30 20:00 | 0 | 0 | 0 | 33.43 | 8.86 | 0
5062 | 2002-07-30 21:00 | 0 | 0 | 0 | 31.85 | 7.11 | 0
5063 | 2002-07-30 22:00 | 0 | 0 | 0 | 30.27 | 7.11 | 0
5064 | 2002-07-30 23:00 | 0 | 0 | 0 | 29.12 | 7.11 | 0
5065 | 2002-07-31 | 0 | 0 | 0 | 27.98 | 7.36 | 0
5066 | 2002-07-31 01:00 | 0 | 0 | 0 | 26.83 | 7.36 | 0
5067 | 2002-07-31 02:00 | 0 | 0 | 0 | 26.17 | 7.36 | 0
5068 | 2002-07-31 03:00 | 0 | 0 | 0 | 25.51 | 6.44 | 0
5069 | 2002-07-31 04:00 | 0 | 0 | 0 | 24.86 | 6.44 | 0
5070 | 2002-07-31 05:00 | 50 | 200 | 31 | 25.02 | 6.44 | 0 | 5.136 | 71.3805 | 90 | 0 | 50 | 0 | 23.88 | 0.46846 | 0 | 22.3478 | 0.0024452 | 0 | 21.5207 | 0.0018425 | 20.8769 | 20.8767 | 46883.8 | 25.4489 | 33042.4 | 32960.4 | 32224.8 | 0 | 0 | 32212.4 | 575.753 | 0 | 0 | 0 | 10771.7 | 21440.7 | 660 | 20653.6 | 20240.5078
5071 | 2002-07-31 06:00 | 248 | 598 | 72 | 25.18 | 3.11 | 0 | 17.0756 | 79.3142 | 78.9764 | 0 | 248 | 114.611 | 66.687 | 2.3236 | 106.873 | 62.4083 | 0.012128 | 84.2706 | 60.0986 | 0.0091389 | 140.047 | 140.028 | 314474 | 28.7538 | 278660 | 273412 | 258367 | 0 | 0 | 257758 | 662.551 | 0 | 0 | 0 | 2.7251 | 257756 | 662.667 | 251936 | 246897.6875
5072 | 2002-07-31 07:00 | 459 | 783 | 75 | 25.34 | 3.11 | 0 | 29.3301 | 87.2424 | 64.7721 | 0 | 459 | 334.126 | 77.0589 | 4.3005 | 334.126 | 72.1146 | 0.022447 | 311.636 | 69.4457 | 0.016914 | 369.666 | 369.663 | 830171 | 34.7747 | 788237 | 753551 | 735535 | 0 | 0 | 730957 | 680.946 | 0 | 0 | 0 | 0 | 730957 | 680.946 | 720689 | 706275.4375
5073 | 2002-07-31 08:00 | 667 | 844 | 106 | 27.65 | 3.11 | 0 | 41.6637 | 96.0474 | 50.5254 | 0 | 667 | 536.509 | 111.952 | 6.2493 | 536.509 | 104.769 | 0.032619 | 521.138 | 100.891 | 0.024579 | 603.393 | 603.391 | 1355060 | 43.0499 | 1326590 | 1222540 | 1193080 | 0 | 0 | 1180750 | 670.083 | 0 | 0 | 0 | 0 | 1180750 | 670.083 | 1163630 | 1140360.375
5074 | 2002-07-31 09:00 | 811 | 840 | 134 | 29.96 | 3.33 | 0 | 53.7508 | 107.365 | 36.3437 | 0 | 811 | 676.181 | 143.259 | 7.5984 | 676.181 | 134.067 | 0.039661 | 668.016 | 129.106 | 0.029886 | 773.237 | 773.23 | 1736470 | 49.4096 | 1724420 | 1544110 | 1508190 | 0 | 0 | 1487740 | 655.708 | 0 | 0 | 0 | 719.948 | 1487020 | 660 | 1463350 | 1434081.125
5075 | 2002-07-31 10:00 | 870 | 672 | 262 | 32.27 | 3.33 | 0 | 64.858 | 125.169 | 22.5023 | 0 | 870 | 620.497 | 276.528 | 8.1512 | 620.497 | 258.785 | 0.042547 | 617.94 | 249.208 | 0.03206 | 841.165 | 841.163 | 1889040 | 53.4284 | 1884490 | 1655650 | 1616240 | 0 | 0 | 1592150 | 646.07 | 0 | 0 | 0 | 10446.9 | 1581710 | 660 | 1555110 | 1524003.375
5076 | 2002-07-31 11:00 | 999 | 904 | 138 | 33.41 | 3.33 | 0 | 72.6352 | 159.08 | 10.636 | 0 | 999 | 886.616 | 142.32 | 9.3598 | 886.616 | 133.188 | 0.048855 | 885.841 | 128.259 | 0.036813 | 983.713 | 983.706 | 2209160 | 58.1539 | 2221410 | 1909160 | 1865940 | 0 | 0 | 1832570 | 632.089 | 0 | 0 | 0 | 40554.9 | 1792020 | 660 | 1758110 | 1722950.625
5077 | 2002-07-31 12:00 | 1003 | 840 | 206 | 34.56 | 6.91 | 0 | 71.9134 | 207.109 | 11.9536 | 0 | 1003 | 820.247 | 217.667 | 9.3973 | 820.247 | 203.701 | 0.049051 | 819.338 | 196.162 | 0.036961 | 985.071 | 985.055 | 2212180 | 54.1991 | 2224600 | 1950230 | 1907270 | 0 | 0 | 1873810 | 645.04 | 0 | 0 | 0 | 11313.1 | 1862500 | 660 | 1825950 | 1789427.125
5078 | 2002-07-31 13:00 | 411 | 55 | 362 | 35.7 | 6.91 | 0 | 63.3801 | 237.977 | 24.4048 | 0 | 411 | 49.9126 | 374.419 | 3.8508 | 49.9126 | 350.396 | 0.0201 | 49.6677 | 337.428 | 0.015145 | 375.497 | 375.468 | 843203 | 43.1857 | 801450 | 735482 | 718164 | 0 | 0 | 713430 | 653.291 | 0 | 0 | 0 | 1478.87 | 711951 | 660 | 702696 | 688641.875
5079 | 2002-07-31 14:00 | 222 | 12 | 213 | 35.89 | 6.91 | 0 | 52.0456 | 254.423 | 38.3326 | 0 | 222 | 8.9535 | 198.251 | 2.08 | 8.9535 | 185.531 | 0.010857 | 8.8304 | 178.664 | 0.0081808 | 181.878 | 181.868 | 408431 | 39.5159 | 369069 | 343205 | 334684 | 0 | 0 | 333588 | 634.664 | 0 | 0 | 0 | 7422.95 | 326165 | 660 | 320155 | 313751.625
5080 | 2002-07-31 15:00 | 355 | 91 | 297 | 36.09 | 6.4 | 0 | 39.8867 | 265.216 | 52.538 | 0 | 355 | 55.012 | 306.188 | 3.3261 | 55.012 | 286.542 | 0.017361 | 53.2403 | 275.938 | 0.013082 | 319.315 | 319.297 | 717062 | 42.6667 | 674342 | 619642 | 604103 | 0 | 0 | 600691 | 647.833 | 0 | 0 | 0 | 2899.74 | 597792 | 660 | 590009 | 578208.375
5081 | 2002-07-31 16:00 | 218 | 61 | 190 | 36.29 | 6.4 | 0 | 27.5381 | 273.815 | 66.791 | 0 | 218 | 23.8665 | 192.234 | 2.0425 | 23.8665 | 179.9 | 0.010661 | 22.0318 | 173.242 | 0.0080334 | 189.423 | 189.413 | 425373 | 40.1914 | 385558 | 357377 | 348683 | 0 | 0 | 347484 | 632.585 | 0 | 0 | 0 | 8130.27 | 339354 | 660 | 333369 | 326701.6875
5082 | 2002-07-31 17:00 | 186 | 300 | 106 | 35.63 | 6.4 | 0 | 15.3007 | 281.69 | 80.9923 | 0 | 186 | 47.4651 | 93.9476 | 1.7427 | 47.4651 | 87.9197 | 0.0090962 | 34.6803 | 84.6659 | 0.0068542 | 115.772 | 115.77 | 259990 | 38.0146 | 226471 | 211656 | 206624 | 0 | 0 | 206183 | 618.942 | 0 | 0 | 0 | 12979.8 | 193203 | 660 | 188101 | 184339.4062
5083 | 2002-07-31 18:00 | 24 | 126 | 14 | 34.98 | 7.51 | 0 | 3.4072 | 289.67 | 90 | 0 | 24 | 0 | 10.7084 | 0.22486 | 0 | 10.0213 | 0.0011737 | 0 | 9.6504 | 0.00088441 | 9.3618 | 9.3615 | 21023.5 | 35.1597 | 12214.5 | 11565.6 | 11348.7 | 0 | 0 | 11346.6 | 491.685 | 0 | 0 | 0 | 11346.6 | 0 | 660 | 0 | 0
5084 | 2002-07-31 19:00 | 0 | 0 | 0 | 34.32 | 7.51 | 0
5085 | 2002-07-31 20:00 | 0 | 0 | 0 | 33.27 | 7.51 | 0
5086 | 2002-07-31 21:00 | 0 | 0 | 0 | 33.1 | 7.42 | 0
5087 | 2002-07-31 22:00 | 0 | 0 | 0 | 32.44 | 6.82 | 0
5088 | 2002-07-31 23:00 | 0 | 0 | 0 | 31.77 | 6.23 | 0
5089 | 2005-08-01 | 0 | 0 | 0 | 31.11 | 5.64 | 0
5090 | 2005-08-01 01:00 | 0 | 0 | 0 | 30.44 | 5.05 | 0
5091 | 2005-08-01 02:00 | 0 | 0 | 0 | 29.78 | 4.45 | 0
5092 | 2005-08-01 03:00 | 0 | 0 | 0 | 28.61 | 3.36 | 0
5093 | 2005-08-01 04:00 | 0 | 0 | 0 | 27.89 | 3.36 | 0
5094 | 2005-08-01 05:00 | 53 | 274 | 27 | 27.75 | 3.36 | 0 | 4.9664 | 71.6525 | 90 | 0 | 53 | 0 | 21.3129 | 0.49657 | 0 | 19.9454 | 0.0025919 | 0 | 19.2073 | 0.0019531 | 18.6329 | 18.6317 | 41842.1 | 28.2177 | 28861.7 | 28350.1 | 27758.6 | 0 | 0 | 27748.8 | 559.867 | 0 | 0 | 0 | 15527.1 | 12221.7 | 660 | 11766.3 | 11530.9375
5095 | 2005-08-01 06:00 | 248 | 637 | 62 | 27.62 | 2.05 | 0 | 16.9212 | 79.6071 | 78.9978 | 0 | 248 | 121.962 | 57.5261 | 2.3236 | 113.306 | 53.8351 | 0.012128 | 89.2861 | 51.8427 | 0.0091389 | 136.904 | 136.898 | 307443 | 31.3691 | 272010 | 263337 | 248531 | 0 | 0 | 247944 | 649.912 | 0 | 0 | 0 | 907.386 | 247036 | 660 | 241367 | 236539.1875
5096 | 2005-08-01 07:00 | 461 | 795 | 73 | 27.48 | 2.05 | 0 | 29.1831 | 87.5684 | 64.7694 | 0 | 461 | 339.191 | 75.2335 | 4.3192 | 339.191 | 70.4064 | 0.022545 | 316.364 | 67.8007 | 0.016988 | 372.656 | 372.654 | 836884 | 37.6855 | 795026 | 749553 | 731580 | 0 | 0 | 726887 | 668.969 | 0 | 0 | 0 | 0 | 726887 | 668.969 | 717112 | 702769.625
5097 | 2005-08-01 08:00 | 666 | 884 | 80 | 29.12 | 2.05 | 0 | 41.5143 | 96.4264 | 50.4964 | 0 | 666 | 562.411 | 84.7157 | 6.2399 | 562.411 | 79.2802 | 0.03257 | 546.326 | 76.3461 | 0.024542 | 604.016 | 604.011 | 1356450 | 45.6614 | 1328030 | 1208560 | 1179060 | 0 | 0 | 1166730 | 662.038 | 0 | 0 | 0 | 0 | 1166730 | 662.038 | 1150300 | 1127289.375
5098 | 2005-08-01 09:00 | 832 | 926 | 87 | 30.76 | 1.61 | 0 | 53.5829 | 107.826 | 36.2808 | 0 | 832 | 746.305 | 92.4918 | 7.7952 | 746.305 | 86.5574 | 0.040688 | 737.33 | 83.3539 | 0.030659 | 796.094 | 796.091 | 1787830 | 53.213 | 1778250 | 1563090 | 1525880 | 0 | 0 | 1504320 | 645.552 | 0 | 0 | 0 | 11111.4 | 1493200 | 660 | 1469370 | 1439986.125
5099 | 2005-08-01 10:00 | 933 | 915 | 107 | 32.4 | 1.61 | 0 | 64.6419 | 125.725 | 22.3817 | 0 | 933 | 845.213 | 112.556 | 8.7415 | 845.213 | 105.334 | 0.045628 | 841.77 | 101.436 | 0.034381 | 914.943 | 914.938 | 2054720 | 58.205 | 2058710 | 1767330 | 1728720 | 0 | 0 | 1699940 | 630.941 | 0 | 0 | 0 | 45163.2 | 1654780 | 660 | 1625740 | 1593224.5
5100 | 2005-08-01 11:00 | 1007 | 956 | 98 | 33.03 | 1.61 | 0 | 72.3348 | 159.457 | 10.3712 | 0 | 1007 | 938.398 | 103.129 | 9.4348 | 938.398 | 96.5117 | 0.049246 | 937.619 | 92.9398 | 0.037108 | 999.678 | 999.672 | 2245020 | 61.2248 | 2259210 | 1911680 | 1869900 | 0 | 0 | 1835360 | 622.21 | 0 | 0 | 0 | 78653.4 | 1756710 | 660 | 1724090 | 1689611.375
5101 | 2005-08-01 12:00 | 1003 | 956 | 98 | 33.66 | 3.81 | 0 | 71.6118 | 206.753 | 11.7409 | 0 | 1003 | 933.741 | 103.184 | 9.3973 | 933.741 | 96.5632 | 0.049051 | 932.743 | 92.9894 | 0.036961 | 994.997 | 994.991 | 2234500 | 57.9083 | 2248120 | 1934810 | 1892580 | 0 | 0 | 1858350 | 633.146 | 0 | 0 | 0 | 38846.1 | 1819510 | 660 | 1784580 | 1748890
5102 | 2005-08-01 13:00 | 936 | 945 | 94 | 34.28 | 3.81 | 0 | 63.1495 | 237.479 | 24.3258 | 0 | 936 | 859.959 | 99.5588 | 8.7696 | 859.959 | 93.1709 | 0.045774 | 855.77 | 89.7227 | 0.034492 | 917.161 | 917.159 | 2059710 | 56.6315 | 2063960 | 1786160 | 1745350 | 0 | 0 | 1716430 | 636.076 | 0 | 0 | 0 | 29248.8 | 1687180 | 660 | 1657030 | 1623886.75
5103 | 2005-08-01 14:00 | 808 | 916 | 88 | 34.53 | 3.81 | 0 | 51.8542 | 254.003 | 38.3072 | 0 | 808 | 718.404 | 93.486 | 7.5703 | 718.404 | 87.4877 | 0.039515 | 708.548 | 84.2499 | 0.029775 | 769.043 | 769.04 | 1727070 | 53.2718 | 1714570 | 1506200 | 1471210 | 0 | 0 | 1450980 | 642.721 | 0 | 0 | 0 | 13017.6 | 1437960 | 660 | 1415490 | 1387178.25
5104 | 2005-08-01 15:00 | 640 | 876 | 80 | 34.78 | 4.88 | 0 | 39.7098 | 264.865 | 52.5451 | 0 | 640 | 533.036 | 84.5508 | 5.9963 | 533.036 | 79.1259 | 0.031299 | 515.863 | 76.1975 | 0.023584 | 574.321 | 574.316 | 1289770 | 47.8298 | 1258930 | 1133100 | 1107540 | 0 | 0 | 1096250 | 650.245 | 0 | 0 | 0 | 2238.46 | 1094010 | 660 | 1079170 | 1057588.625
5105 | 2005-08-01 16:00 | 425 | 765 | 73 | 35.02 | 4.88 | 0 | 27.3616 | 273.511 | 66.8239 | 0 | 425 | 301.416 | 74.632 | 3.9819 | 301.416 | 69.8435 | 0.020784 | 278.193 | 67.2586 | 0.015661 | 335.104 | 335.101 | 752550 | 42.6343 | 709958 | 652754 | 637787 | 0 | 0 | 633981 | 647.943 | 0 | 0 | 0 | 2244.63 | 631737 | 660 | 623524 | 611053.625
5106 | 2005-08-01 17:00 | 208 | 553 | 63 | 34.58 | 4.88 | 0 | 15.1159 | 281.416 | 81.0492 | 0 | 208 | 86.5121 | 57.3866 | 1.9488 | 86.5121 | 53.7045 | 0.010172 | 63.0356 | 51.717 | 0.0076649 | 111.317 | 111.316 | 249986 | 37.1094 | 217007 | 203762 | 199184 | 0 | 0 | 198775 | 619.888 | 0 | 0 | 0 | 11771.2 | 187004 | 660 | 181996 | 178356.0312
5107 | 2005-08-01 18:00 | 26 | 228 | 8 | 34.13 | 6.46 | 0 | 3.2069 | 289.416 | 90 | 0 | 26 | 0 | 6.9664 | 0.2436 | 0 | 6.5194 | 0.0012715 | 0 | 6.2782 | 0.00095811 | 6.0907 | 6.0903 | 13677.3 | 34.255 | 6743.77 | 6465.26 | 6341.23 | 0 | 0 | 6340.51 | 471.693 | 0 | 0 | 0 | 6340.51 | 0 | 660 | 0 | 0
5108 | 2005-08-01 19:00 | 0 | 0 | 0 | 33.69 | 6.46 | 0
5109 | 2005-08-01 20:00 | 0 | 0 | 0 | 33.05 | 6.46 | 0
5110 | 2005-08-01 21:00 | 0 | 0 | 0 | 32.4 | 7.35 | 0
5111 | 2005-08-01 22:00 | 0 | 0 | 0 | 31.76 | 7.35 | 0
5112 | 2005-08-01 23:00 | 0 | 0 | 0 | 30.72 | 7.35 | 0
5113 | 2005-08-02 | 0 | 0 | 0 | 29.67 | 7.58 | 0
5114 | 2005-08-02 01:00 | 0 | 0 | 0 | 28.63 | 7.58 | 0
5115 | 2005-08-02 02:00 | 0 | 0 | 0 | 27.98 | 7.58 | 0
5116 | 2005-08-02 03:00 | 0 | 0 | 0 | 27.32 | 3.69 | 0
5117 | 2005-08-02 04:00 | 0 | 0 | 0 | 26.67 | 3.69 | 0
5118 | 2005-08-02 05:00 | 53 | 278 | 27 | 26.59 | 3.69 | 0 | 4.834 | 71.8733 | 90 | 0 | 53 | 0 | 21.4443 | 0.49657 | 0 | 20.0684 | 0.0025919 | 0 | 19.3256 | 0.0019531 | 18.7478 | 18.7472 | 42101.7 | 27.0505 | 29076.2 | 28747.9 | 28101.4 | 0 | 0 | 28091.5 | 564.312 | 0 | 0 | 0 | 13644.8 | 14446.8 | 660 | 13910.3 | 13632.1279
5119 | 2005-08-02 06:00 | 250 | 647 | 62 | 26.52 | 3.15 | 0 | 16.8007 | 79.8444 | 79.0107 | 0 | 250 | 123.987 | 57.6426 | 2.3423 | 114.846 | 53.9442 | 0.012226 | 90.4649 | 51.9477 | 0.0092126 | 138.149 | 138.163 | 310283 | 30.0369 | 274747 | 267800 | 252886 | 0 | 0 | 252284 | 653.786 | 0 | 0 | 0 | 449.714 | 251835 | 660 | 246130 | 241206.9375
5120 | 2005-08-02 07:00 | 459 | 792 | 74 | 26.44 | 3.15 | 0 | 29.0685 | 87.832 | 64.7632 | 0 | 459 | 337.856 | 76.3497 | 4.3005 | 337.856 | 71.451 | 0.022447 | 315.127 | 68.8066 | 0.016914 | 372.432 | 372.429 | 836382 | 35.9201 | 794519 | 755452 | 736771 | 0 | 0 | 732114 | 676.057 | 0 | 0 | 0 | 0 | 732114 | 676.057 | 722008 | 707568.1875
5121 | 2005-08-02 08:00 | 663 | 882 | 80 | 28.22 | 3.15 | 0 | 41.3974 | 96.7324 | 50.4697 | 0 | 663 | 561.144 | 84.8208 | 6.2118 | 561.144 | 79.3785 | 0.032424 | 545.119 | 76.4408 | 0.024432 | 602.937 | 602.933 | 1354030 | 43.5676 | 1325520 | 1218540 | 1190110 | 0 | 0 | 1177750 | 667.383 | 0 | 0 | 0 | 0 | 1177750 | 667.383 | 1160820 | 1137606
5122 | 2005-08-02 09:00 | 829 | 922 | 89 | 29.99 | 1.28 | 0 | 53.4507 | 108.198 | 36.2276 | 0 | 829 | 743.069 | 94.6365 | 7.7671 | 743.069 | 88.5644 | 0.040542 | 734.165 | 85.2867 | 0.030549 | 794.898 | 794.896 | 1785140 | 52.9113 | 1775430 | 1562940 | 1527040 | 0 | 0 | 1505320 | 643.892 | 0 | 0 | 0 | 10514.6 | 1494800 | 660 | 1470920 | 1441506.375
5123 | 2005-08-02 10:00 | 944 | 943 | 94 | 31.77 | 1.28 | 0 | 64.4702 | 126.173 | 22.2832 | 0 | 944 | 871.628 | 99.6271 | 8.8445 | 871.628 | 93.2348 | 0.046165 | 868.11 | 89.7842 | 0.034787 | 929.191 | 929.186 | 2086710 | 58.5637 | 2092390 | 1793270 | 1752800 | 0 | 0 | 1723180 | 630.834 | 0 | 0 | 0 | 47495.1 | 1675680 | 660 | 1645930 | 1613010.375
5124 | 2005-08-02 11:00 | 1003 | 953 | 98 | 32.55 | 1.28 | 0 | 72.0944 | 159.765 | 10.1581 | 0 | 1003 | 936.157 | 103.277 | 9.3973 | 936.157 | 96.6503 | 0.049051 | 935.412 | 93.0733 | 0.036961 | 997.666 | 997.662 | 2240500 | 61.3182 | 2254450 | 1906680 | 1867210 | 0 | 0 | 1832730 | 621.703 | 0 | 0 | 0 | 81549.2 | 1751180 | 660 | 1718760 | 1684384.375
5125 | 2005-08-02 12:00 | 999 | 952 | 99 | 33.34 | 3.8 | 0 | 71.3675 | 206.489 | 11.5771 | 0 | 999 | 930.458 | 104.338 | 9.3598 | 930.458 | 97.6433 | 0.048855 | 929.491 | 94.0296 | 0.036813 | 992.851 | 992.848 | 2229690 | 57.552 | 2243050 | 1933880 | 1891520 | 0 | 0 | 1857530 | 634.586 | 0 | 0 | 0 | 35342.5 | 1822180 | 660 | 1787160 | 1751413.875
5126 | 2005-08-02 13:00 | 932 | 941 | 95 | 34.13 | 3.8 | 0 | 62.9598 | 237.091 | 24.2695 | 0 | 932 | 856.672 | 100.701 | 8.7321 | 856.672 | 94.2402 | 0.045579 | 852.52 | 90.7525 | 0.034345 | 915.007 | 914.999 | 2054860 | 56.4435 | 2058860 | 1783390 | 1744480 | 0 | 0 | 1715650 | 636.25 | 0 | 0 | 0 | 28952.8 | 1686700 | 660 | 1656560 | 1623432.875
5127 | 2005-08-02 14:00 | 807 | 916 | 88 | 34.31 | 3.8 | 0 | 51.6958 | 253.672 | 38.293 | 0 | 807 | 719.111 | 93.6016 | 7.561 | 719.111 | 87.596 | 0.039466 | 709.255 | 84.3541 | 0.029738 | 769.83 | 769.824 | 1728830 | 53.0832 | 1716410 | 1509250 | 1475630 | 0 | 0 | 1455280 | 642.581 | 0 | 0 | 0 | 12590.4 | 1442690 | 660 | 1420100 | 1391697.625
5128 | 2005-08-02 15:00 | 635 | 871 | 80 | 34.5 | 5.95 | 0 | 39.5631 | 264.588 | 52.5564 | 0 | 635 | 529.776 | 84.6527 | 5.9495 | 529.776 | 79.2213 | 0.031054 | 512.696 | 76.2893 | 0.0234 | 571.338 | 571.334 | 1283070 | 46.6131 | 1252000 | 1133600 | 1108070 | 0 | 0 | 1096910 | 654.605 | 0 | 0 | 0 | 747.987 | 1096160 | 660 | 1081280 | 1059655.875
5129 | 2005-08-02 16:00 | 422 | 750 | 79 | 34.68 | 5.95 | 0 | 27.2157 | 273.27 | 66.8554 | 0 | 422 | 294.785 | 80.6348 | 3.9538 | 294.785 | 75.4611 | 0.020638 | 272.025 | 72.6683 | 0.015551 | 334.367 | 334.363 | 750894 | 41.769 | 708292 | 654054 | 638994 | 0 | 0 | 635220 | 651.438 | 0 | 0 | 0 | 1205.44 | 634015 | 660 | 625773 | 613257.25
5130 | 2005-08-02 17:00 | 189 | 440 | 75 | 34.22 | 5.95 | 0 | 14.9634 | 281.199 | 81.0996 | 0 | 189 | 68.3096 | 67.1894 | 1.7708 | 68.3096 | 62.8784 | 0.0092429 | 49.6493 | 60.5513 | 0.0069647 | 106.901 | 106.899 | 240068 | 36.4864 | 207654 | 195595 | 191059 | 0 | 0 | 190684 | 620.084 | 0 | 0 | 0 | 11011.8 | 179672 | 660 | 174781 | 171285.8438
5131 | 2005-08-02 18:00 | 23 | 178 | 9 | 33.75 | 7.87 | 0 | 3.0424 | 289.215 | 90 | 0 | 23 | 0 | 6.8854 | 0.21549 | 0 | 6.4436 | 0.0011248 | 0 | 6.2051 | 0.00084756 | 6.0198 | 6.0195 | 13518.3 | 33.8629 | 6629.71 | 6369.82 | 6247.83 | 0 | 0 | 6247.14 | 472.913 | 0 | 0 | 0 | 6247.14 | 0 | 660 | 0 | 0
5132 | 2005-08-02 19:00 | 0 | 0 | 0 | 33.29 | 7.87 | 0
5133 | 2005-08-02 20:00 | 0 | 0 | 0 | 32.41 | 7.87 | 0
5134 | 2005-08-02 21:00 | 0 | 0 | 0 | 31.53 | 5.7 | 0
5135 | 2005-08-02 22:00 | 0 | 0 | 0 | 30.65 | 5.7 | 0
5136 | 2005-08-02 23:00 | 0 | 0 | 0 | 29.63 | 5.7 | 0
5137 | 2005-08-03 | 0 | 0 | 0 | 28.62 | 5.39 | 0
5138 | 2005-08-03 01:00 | 0 | 0 | 0 | 27.6 | 5.39 | 0
5139 | 2005-08-03 02:00 | 0 | 0 | 0 | 26.67 | 5.39 | 0
5140 | 2005-08-03 03:00 | 0 | 0 | 0 | 25.74 | 2.83 | 0
5141 | 2005-08-03 04:00 | 0 | 0 | 0 | 24.8 | 2.83 | 0
5142 | 2005-08-03 05:00 | 44 | 167 | 29 | 24.87 | 2.83 | 0 | 4.7008 | 72.0994 | 90 | 0 | 44 | 0 | 22.4221 | 0.41225 | 0 | 20.9835 | 0.0021518 | 0 | 20.2069 | 0.0016214 | 19.6023 | 19.6005 | 44017.6 | 25.3796 | 30660.2 | 30595.3 | 29906.3 | 0 | 0 | 29895.5 | 572.577 | 0 | 0 | 0 | 11078.2 | 18817.2 | 660 | 18123.4 | 17760.9746
5143 | 2005-08-03 06:00 | 246 | 600 | 73 | 24.93 | 1.25 | 0 | 16.6796 | 80.0869 | 79.0219 | 0 | 246 | 114.783 | 68.0329 | 2.3048 | 105.943 | 63.6678 | 0.01203 | 83.4242 | 61.3115 | 0.0090652 | 140.402 | 140.404 | 315315 | 28.9868 | 279503 | 273885 | 259174 | 0 | 0 | 258556 | 659.428 | 0 | 0 | 0 | 236.67 | 258319 | 662.061 | 252517 | 247466.9688
5144 | 2005-08-03 07:00 | 463 | 809 | 71 | 24.99 | 1.25 | 0 | 28.9531 | 88.1012 | 64.7554 | 0 | 463 | 345.351 | 73.4967 | 4.338 | 345.351 | 68.7811 | 0.022643 | 322.13 | 66.2355 | 0.017062 | 376.731 | 376.726 | 846032 | 35.8751 | 804283 | 764933 | 746138 | 0 | 0 | 741368 | 676.715 | 0 | 0 | 0 | 0 | 741368 | 676.715 | 731111 | 716488.5
5145 | 2005-08-03 08:00 | 652 | 858 | 86 | 26.86 | 1.25 | 0 | 41.2793 | 97.0445 | 50.4413 | 0 | 652 | 546.387 | 90.9536 | 6.1087 | 546.387 | 85.1178 | 0.031885 | 530.81 | 81.9677 | 0.024026 | 594.417 | 594.414 | 1334900 | 44.0349 | 1305680 | 1197470 | 1170480 | 0 | 0 | 1158410 | 664.891 | 0 | 0 | 0 | 0 | 1158410 | 664.891 | 1142010 | 1119172.5
5146 | 2005-08-03 09:00 | 827 | 922 | 88 | 28.73 | 0.79 | 0 | 53.3166 | 108.576 | 36.1727 | 0 | 827 | 743.877 | 93.7414 | 7.7484 | 743.877 | 87.7268 | 0.040444 | 734.996 | 84.4801 | 0.030475 | 794.921 | 794.915 | 1785180 | 52.4207 | 1775470 | 1566780 | 1532560 | 0 | 0 | 1510710 | 644.109 | 0 | 0 | 0 | 9108.15 | 1501600 | 660 | 1477540 | 1447988.625
5147 | 2005-08-03 10:00 | 944 | 943 | 95 | 30.6 | 0.79 | 0 | 64.2954 | 126.627 | 22.1833 | 0 | 944 | 872.498 | 100.774 | 8.8445 | 872.498 | 94.3079 | 0.046165 | 869.011 | 90.8176 | 0.034787 | 931.067 | 931.062 | 2090930 | 58.3482 | 2096830 | 1799090 | 1761920 | 0 | 0 | 1731880 | 629.468 | 0 | 0 | 0 | 47383.1 | 1684500 | 660 | 1654440 | 1621347.375
5148 | 2005-08-03 11:00 | 996 | 907 | 136 | 31.6 | 0.79 | 0 | 71.8498 | 160.077 | 9.9419 | 0 | 996 | 891.441 | 141.04 | 9.3317 | 891.441 | 131.991 | 0.048709 | 890.761 | 127.106 | 0.036703 | 987.367 | 987.363 | 2217370 | 61.0262 | 2230060 | 1888620 | 1848640 | 0 | 0 | 1814930 | 622.603 | 0 | 0 | 0 | 77258.4 | 1737670 | 660 | 1705740 | 1671620.625
5149 | 2005-08-03 12:00 | 940 | 754 | 228 | 32.61 | 3.12 | 0 | 71.1175 | 206.234 | 11.4154 | 0 | 940 | 737.61 | 247.057 | 8.8071 | 737.61 | 231.205 | 0.04597 | 736.866 | 222.648 | 0.034639 | 930.762 | 930.749 | 2090220 | 56.3491 | 2096090 | 1816800 | 1775900 | 0 | 0 | 1746040 | 636.899 | 0 | 0 | 0 | 26677.8 | 1719370 | 660 | 1688080 | 1654321.375
5150 | 2005-08-03 13:00 | 930 | 901 | 130 | 33.62 | 3.12 | 0 | 62.764 | 236.705 | 24.2168 | 0 | 930 | 820.578 | 135.656 | 8.7134 | 820.578 | 126.952 | 0.045481 | 816.619 | 122.253 | 0.034271 | 910.74 | 910.731 | 2045260 | 56.8486 | 2048750 | 1770900 | 1732300 | 0 | 0 | 1703690 | 634.99 | 0 | 0 | 0 | 32427.7 | 1671260 | 660 | 1641660 | 1608822.625
5151 | 2005-08-03 14:00 | 795 | 774 | 189 | 33.95 | 3.12 | 0 | 51.5317 | 253.34 | 38.2822 | 0 | 795 | 607.561 | 200.122 | 7.4485 | 607.561 | 187.281 | 0.038879 | 599.239 | 180.35 | 0.029296 | 756.23 | 756.224 | 1698290 | 53.2378 | 1684430 | 1479680 | 1445440 | 0 | 0 | 1425890 | 642.488 | 0 | 0 | 0 | 13400.3 | 1412490 | 660 | 1390630 | 1362818.25
5152 | 2005-08-03 15:00 | 479 | 304 | 286 | 34.27 | 3.23 | 0 | 39.4112 | 264.309 | 52.571 | 0 | 479 | 184.761 | 278.509 | 4.4879 | 184.761 | 260.64 | 0.023425 | 178.799 | 250.993 | 0.017651 | 416.916 | 416.913 | 936283 | 44.8265 | 895911 | 816153 | 796894 | 0 | 0 | 791017 | 650.002 | 0 | 0 | 0 | 2258.77 | 788758 | 660 | 778504 | 762934.4375
5153 | 2005-08-03 16:00 | 408 | 602 | 134 | 34.6 | 3.23 | 0 | 27.0647 | 273.027 | 66.8901 | 0 | 408 | 236.362 | 132.306 | 3.8226 | 236.362 | 123.817 | 0.019953 | 218.07 | 119.234 | 0.015035 | 327.2 | 327.195 | 734793 | 42.8847 | 692114 | 635413 | 620859 | 0 | 0 | 617232 | 646.573 | 0 | 0 | 0 | 3103.66 | 614129 | 660 | 606145 | 594022.25
5154 | 2005-08-03 17:00 | 199 | 525 | 64 | 34.21 | 3.23 | 0 | 14.8061 | 280.979 | 81.1533 | 0 | 199 | 81.2441 | 58.5141 | 1.8645 | 81.2441 | 54.7597 | 0.0097319 | 58.8927 | 52.7331 | 0.0073332 | 108.284 | 108.282 | 243175 | 36.9518 | 210581 | 197864 | 193518 | 0 | 0 | 193131 | 619.259 | 0 | 0 | 0 | 11998.5 | 181133 | 660 | 176218 | 172693.9375
5155 | 2005-08-03 18:00 | 24 | 209 | 8 | 33.83 | 3.85 | 0 | 2.8732 | 289.011 | 90 | 0 | 24 | 0 | 6.0646 | 0.22486 | 0 | 5.6755 | 0.0011737 | 0 | 5.4654 | 0.00088441 | 5.3023 | 5.3022 | 11907.4 | 33.9589 | 5488.55 | 5289.47 | 5186.83 | 0 | 0 | 5186.33 | 462.236 | 0 | 0 | 0 | 5186.33 | 0 | 660 | 0 | 0
5156 | 2005-08-03 19:00 | 0 | 0 | 0 | 33.45 | 3.85 | 0
5157 | 2005-08-03 20:00 | 0 | 0 | 0 | 32.96 | 3.85 | 0
5158 | 2005-08-03 21:00 | 0 | 0 | 0 | 32.48 | 3.69 | 0
5159 | 2005-08-03 22:00 | 0 | 0 | 0 | 32 | 3.69 | 0
5160 | 2005-08-03 23:00 | 0 | 0 | 0 | 31.08 | 3.69 | 0
5161 | 2005-08-04 | 0 | 0 | 0 | 30.16 | 3.74 | 0
5162 | 2005-08-04 01:00 | 0 | 0 | 0 | 29.24 | 3.74 | 0
5163 | 2005-08-04 02:00 | 0 | 0 | 0 | 28.61 | 3.74 | 0
5164 | 2005-08-04 03:00 | 0 | 0 | 0 | 27.98 | 1.36 | 0
5165 | 2005-08-04 04:00 | 0 | 0 | 0 | 27.35 | 1.36 | 0
5166 | 2005-08-04 05:00 | 47 | 237 | 26 | 27.25 | 1.36 | 0 | 4.5668 | 72.3307 | 90 | 0 | 47 | 0 | 20.7379 | 0.44035 | 0 | 19.4073 | 0.0022985 | 0 | 18.689 | 0.001732 | 18.13 | 18.1291 | 40713.2 | 27.77 | 27932 | 27506.2 | 26909.6 | 0 | 0 | 26900.4 | 559.863 | 0 | 0 | 0 | 14975.1 | 11925.3 | 660 | 11480.7 | 11251.0889
5167 | 2005-08-04 06:00 | 248 | 648 | 63 | 27.15 | 0.83 | 0 | 16.5578 | 80.3347 | 79.0315 | 0 | 248 | 123.516 | 58.8212 | 2.3236 | 113.63 | 55.0472 | 0.012128 | 89.4516 | 53.0099 | 0.0091389 | 138.197 | 138.194 | 310352 | 31.2575 | 274840 | 266202 | 250856 | 0 | 0 | 250257 | 649.619 | 0 | 0 | 0 | 1142.45 | 249115 | 660 | 243438 | 238569.6875
5168 | 2005-08-04 07:00 | 461 | 809 | 70 | 27.04 | 0.83 | 0 | 28.8368 | 88.3758 | 64.7458 | 0 | 461 | 345.86 | 72.6282 | 4.3192 | 345.86 | 67.9683 | 0.022545 | 322.619 | 65.4528 | 0.016988 | 376.446 | 376.443 | 845398 | 38.2288 | 803640 | 755720 | 736929 | 0 | 0 | 732156 | 668.182 | 0 | 0 | 0 | 0 | 732156 | 668.182 | 722339 | 707891.875
5169 | 2005-08-04 08:00 | 652 | 861 | 85 | 28.79 | 0.83 | 0 | 41.16 | 97.3624 | 50.4113 | 0 | 652 | 549.002 | 90.0681 | 6.1087 | 549.002 | 84.2892 | 0.031885 | 533.378 | 81.1697 | 0.024026 | 596.134 | 596.127 | 1338750 | 46.5084 | 1309670 | 1186790 | 1159620 | 0 | 0 | 1147530 | 657.603 | 0 | 0 | 0 | 276.029 | 1147260 | 660 | 1131330 | 1108701.625
5170 | 2005-08-04 09:00 | 826 | 922 | 88 | 30.53 | 1.59 | 0 | 53.1805 | 108.961 | 36.1165 | 0 | 826 | 744.723 | 93.8628 | 7.739 | 744.723 | 87.8404 | 0.040395 | 735.865 | 84.5895 | 0.030438 | 795.87 | 795.863 | 1787300 | 53.0067 | 1777690 | 1564210 | 1530890 | 0 | 0 | 1508990 | 642.618 | 0 | 0 | 0 | 11933.7 | 1497060 | 660 | 1473120 | 1443654.875
5171 | 2005-08-04 10:00 | 936 | 934 | 97 | 32.27 | 1.59 | 0 | 64.1175 | 127.086 | 22.0823 | 0 | 936 | 864.135 | 102.937 | 8.7696 | 864.135 | 96.3324 | 0.045774 | 860.715 | 92.7672 | 0.034492 | 924.911 | 924.91 | 2077120 | 58.3912 | 2082290 | 1786080 | 1744840 | 0 | 0 | 1715560 | 631.584 | 0 | 0 | 0 | 45202.9 | 1670350 | 660 | 1640780 | 1607966
5172 | 2005-08-04 11:00 | 1001 | 918 | 132 | 32.89 | 1.59 | 0 | 71.6009 | 160.393 | 9.7229 | 0 | 1001 | 902.661 | 137.348 | 9.3786 | 902.661 | 128.535 | 0.048953 | 902.003 | 123.778 | 0.036887 | 995.044 | 995.038 | 2234600 | 60.9918 | 2248230 | 1904580 | 1863880 | 0 | 0 | 1829700 | 623.265 | 0 | 0 | 0 | 76152.9 | 1753550 | 660 | 1721040 | 1686623.625
5173 | 2005-08-04 12:00 | 950 | 714 | 277 | 33.51 | 0.59 | 0 | 70.8619 | 205.986 | 11.2563 | 0 | 950 | 698.668 | 295.683 | 8.9008 | 698.668 | 276.711 | 0.046459 | 697.983 | 266.47 | 0.035008 | 935.554 | 935.536 | 2100980 | 61.7705 | 2107430 | 1776610 | 1737820 | 0 | 0 | 1707620 | 618.936 | 0 | 0 | 0 | 89279.7 | 1618340 | 660 | 1590530 | 1558720
5174 | 2005-08-04 13:00 | 161 | 4 | 157 | 34.13 | 0.59 | 0 | 62.5621 | 236.32 | 24.1679 | 0 | 161 | 4.112 | 146.076 | 1.5084 | 4.112 | 136.703 | 0.0078736 | 4.0922 | 131.644 | 0.0059329 | 131.67 | 131.662 | 295679 | 38.1072 | 260401 | 243435 | 237503 | 0 | 0 | 236929 | 623.308 | 0 | 0 | 0 | 10672.2 | 226257 | 660 | 220731 | 216316.4375
5175 | 2005-08-04 14:00 | 139 | 0 | 139 | 34.74 | 0.59 | 0 | 51.3621 | 253.006 | 38.2748 | 0 | 139 | 0 | 128.865 | 1.3023 | 0 | 120.597 | 0.0067977 | 0 | 116.134 | 0.0051222 | 112.655 | 112.651 | 252986 | 38.1429 | 219854 | 205285 | 200218 | 0 | 0 | 199801 | 616.929 | 0 | 0 | 0 | 13726.1 | 186075 | 660 | 181082 | 177460.4375
5176 | 2005-08-04 15:00 | 615 | 566 | 257 | 35.34 | 1.68 | 0 | 39.2541 | 264.027 | 52.5889 | 0 | 615 | 343.725 | 255.082 | 5.7621 | 343.725 | 238.715 | 0.030076 | 332.622 | 229.88 | 0.022663 | 545.65 | 545.642 | 1225380 | 50.6573 | 1192380 | 1057490 | 1032610 | 0 | 0 | 1022520 | 640.946 | 0 | 0 | 0 | 12220.7 | 1010290 | 660 | 997098 | 977156.0625
5177 | 2005-08-04 16:00 | 410 | 738 | 76 | 35.95 | 1.68 | 0 | 26.9089 | 272.781 | 66.9281 | 0 | 410 | 289.213 | 77.9287 | 3.8414 | 289.213 | 72.9287 | 0.020051 | 266.774 | 70.2297 | 0.015109 | 326.908 | 326.903 | 734144 | 45.1269 | 691459 | 627579 | 613701 | 0 | 0 | 610079 | 638.986 | 0 | 0 | 0 | 8438.61 | 601641 | 660 | 593818 | 581941.375
5178 | 2005-08-04 17:00 | 201 | 547 | 62 | 35.67 | 1.68 | 0 | 14.6441 | 280.757 | 81.2101 | 0 | 201 | 84.0174 | 56.7533 | 1.8832 | 84.0174 | 53.1119 | 0.0098297 | 60.7277 | 51.1463 | 0.0074069 | 108.525 | 108.523 | 243714 | 38.7165 | 211089 | 196440 | 192114 | 0 | 0 | 191726 | 613.469 | 0 | 0 | 0 | 16320.2 | 175405 | 659.999 | 170586 | 167174.4531
5179 | 2005-08-04 18:00 | 23 | 213 | 7 | 35.39 | 4.07 | 0 | 2.6992 | 288.806 | 90 | 0 | 23 | 0 | 6.1197 | 0.21549 | 0 | 5.7271 | 0.0011248 | 0 | 5.5151 | 0.00084756 | 5.3505 | 5.3503 | 12015.4 | 35.5182 | 5564.05 | 5322.62 | 5220.71 | 0 | 0 | 5220.19 | 458.335 | 0 | 0 | 0 | 5220.19 | 0 | 660 | 0 | 0
5180 | 2005-08-04 19:00 | 0 | 0 | 0 | 35.11 | 4.07 | 0
5181 | 2005-08-04 20:00 | 0 | 0 | 0 | 34.48 | 4.07 | 0
5182 | 2005-08-04 21:00 | 0 | 0 | 0 | 33.86 | 5.09 | 0
5183 | 2005-08-04 22:00 | 0 | 0 | 0 | 33.23 | 5.09 | 0
5184 | 2005-08-04 23:00 | 0 | 0 | 0 | 32.42 | 5.09 | 0
5185 | 2005-08-05 | 0 | 0 | 0 | 31.61 | 3.55 | 0
5186 | 2005-08-05 01:00 | 0 | 0 | 0 | 30.8 | 3.55 | 0
5187 | 2005-08-05 02:00 | 0 | 0 | 0 | 30.04 | 3.55 | 0
5188 | 2005-08-05 03:00 | 0 | 0 | 0 | 29.27 | 2 | 0
5189 | 2005-08-05 04:00 | 0 | 0 | 0 | 28.51 | 2 | 0
5190 | 2005-08-05 05:00 | 30 | 52 | 25 | 28.46 | 2 | 0 | 4.4321 | 72.5671 | 90 | 0 | 30 | 0 | 20.4241 | 0.28108 | 0 | 19.1137 | 0.0014671 | 0 | 18.4063 | 0.0011055 | 17.8552 | 17.854 | 40095.4 | 28.9506 | 27424.1 | 26827 | 26244.3 | 0 | 0 | 26235.5 | 554.649 | 0 | 0 | 0 | 17016.2 | 9219.28 | 660 | 8874.06 | 8696.5771
5191 | 2005-08-05 06:00 | 47 | 0 | 47 | 28.4 | 1.19 | 0 | 16.4354 | 80.5876 | 79.0394 | 0 | 47 | 0 | 43.4208 | 0.44035 | 0 | 40.6349 | 0.0022985 | 0 | 39.131 | 0.001732 | 37.9588 | 37.9577 | 85243.7 | 29.5012 | 65928.5 | 64316.1 | 62747.1 | 0 | 0 | 62702.9 | 594.671 | 0 | 0 | 0 | 11653.3 | 51049.7 | 660 | 49266.2 | 48280.875
5192 | 2005-08-05 07:00 | 398 | 460 | 177 | 28.34 | 1.19 | 0 | 28.7198 | 88.6557 | 64.7347 | 0 | 398 | 196.295 | 171.819 | 3.729 | 196.295 | 160.795 | 0.019464 | 183.114 | 154.844 | 0.014666 | 327.834 | 327.833 | 736229 | 37.8506 | 693561 | 652888 | 637797 | 0 | 0 | 634183 | 664.661 | 0 | 0 | 0 | 0 | 634183 | 664.661 | 625791 | 613275.0625
5193 | 2005-08-05 08:00 | 573 | 572 | 197 | 30.01 | 1.19 | 0 | 41.0396 | 97.6861 | 50.3797 | 0 | 573 | 365.186 | 199.691 | 5.3686 | 365.186 | 186.878 | 0.028022 | 354.812 | 179.962 | 0.021115 | 518.752 | 518.744 | 1164970 | 45.0591 | 1130090 | 1030170 | 1005760 | 0 | 0 | 996636 | 657.216 | 0 | 0 | 0 | 93.4373 | 996543 | 660 | 983582 | 963910.5625
5194 | 2005-08-05 09:00 | 728 | 576 | 268 | 31.69 | 3.92 | 0 | 53.0426 | 109.352 | 36.0588 | 0 | 728 | 465.371 | 276.415 | 6.8208 | 465.371 | 258.68 | 0.035602 | 459.857 | 249.106 | 0.026827 | 687.72 | 687.707 | 1544410 | 48.3289 | 1523610 | 1370100 | 1338730 | 0 | 0 | 1322530 | 654.707 | 0 | 0 | 0 | 663.312 | 1321870 | 660 | 1302130 | 1276087.25
5195 | 2005-08-05 10:00 | 914 | 825 | 174 | 33.36 | 3.92 | 0 | 63.9365 | 127.551 | 21.9803 | 0 | 914 | 763.894 | 186.723 | 8.5635 | 763.894 | 174.743 | 0.044698 | 760.9 | 168.276 | 0.033681 | 901.333 | 901.329 | 2024160 | 55.1675 | 2026550 | 1766400 | 1726370 | 0 | 0 | 1698320 | 639.132 | 0 | 0 | 0 | 19276.4 | 1679040 | 660 | 1649170 | 1616187.25
5196 | 2005-08-05 11:00 | 917 | 674 | 280 | 33.73 | 3.92 | 0 | 71.3478 | 160.712 | 9.5012 | 0 | 917 | 663.089 | 299.27 | 8.5916 | 663.089 | 280.068 | 0.044845 | 662.628 | 269.703 | 0.033792 | 904.394 | 904.377 | 2031000 | 55.6112 | 2033740 | 1768770 | 1728040 | 0 | 0 | 1699860 | 638.032 | 0 | 0 | 0 | 21691 | 1678170 | 660 | 1648330 | 1615364.25
5197 | 2005-08-05 12:00 | 977 | 802 | 222 | 34.09 | 3.14 | 0 | 70.6009 | 205.746 | 11.1004 | 0 | 977 | 785.468 | 241.72 | 9.1537 | 785.468 | 226.211 | 0.047779 | 784.719 | 217.839 | 0.036003 | 972.516 | 972.507 | 2184000 | 58.8614 | 2194890 | 1879340 | 1839740 | 0 | 0 | 1806980 | 628.961 | 0 | 0 | 0 | 50738.3 | 1756250 | 660 | 1723640 | 1689172.125
5198 | 2005-08-05 13:00 | 423 | 119 | 318 | 34.46 | 3.14 | 0 | 62.3543 | 235.937 | 24.1229 | 0 | 423 | 108.181 | 315.19 | 3.9632 | 108.181 | 294.967 | 0.020687 | 107.664 | 284.051 | 0.015588 | 379.978 | 379.967 | 853312 | 44.1384 | 811676 | 741375 | 723464 | 0 | 0 | 718595 | 648.91 | 0 | 0 | 0 | 2476.13 | 716118 | 659.999 | 706809 | 692672.75
5199 | 2005-08-05 14:00 | 776 | 703 | 228 | 34.87 | 3.14 | 0 | 51.1868 | 252.671 | 38.271 | 0 | 776 | 552.146 | 238.507 | 7.2705 | 552.146 | 223.204 | 0.03795 | 544.589 | 214.943 | 0.028596 | 736.774 | 736.756 | 1654570 | 53.6364 | 1638680 | 1436210 | 1404410 | 0 | 0 | 1385760 | 639.196 | 0 | 0 | 0 | 17366.6 | 1368390 | 660 | 1347580 | 1320628.375
5200 | 2005-08-05 15:00 | 629 | 834 | 103 | 35.29 | 3.76 | 0 | 39.0919 | 263.743 | 52.6102 | 0 | 629 | 506.538 | 109.273 | 5.8932 | 506.538 | 102.262 | 0.030761 | 490.156 | 98.4775 | 0.023179 | 570.997 | 570.991 | 1282300 | 49.2511 | 1251200 | 1118120 | 1092920 | 0 | 0 | 1081770 | 645.649 | 0 | 0 | 0 | 5957.59 | 1075810 | 660 | 1061340 | 1040109.5625
5201 | 2005-08-05 16:00 | 426 | 665 | 126 | 35.71 | 3.76 | 0 | 26.7481 | 272.533 | 66.9693 | 0 | 426 | 260.776 | 125.126 | 3.9913 | 260.776 | 117.098 | 0.020833 | 240.486 | 112.764 | 0.015698 | 342.669 | 342.662 | 769533 | 44.0883 | 727050 | 663679 | 648824 | 0 | 0 | 644827 | 642.929 | 0 | 0 | 0 | 4679.96 | 640147 | 660 | 631826 | 619189
5202 | 2005-08-05 17:00 | 169 | 352 | 81 | 35.11 | 3.76 | 0 | 14.4774 | 280.533 | 81.2702 | 0 | 169 | 53.4256 | 72.7344 | 1.5834 | 53.4256 | 68.0677 | 0.0082648 | 38.4966 | 65.5485 | 0.0062277 | 100.93 | 100.926 | 226654 | 37.5777 | 195042 | 182562 | 178452 | 0 | 0 | 178118 | 614.098 | 0 | 0 | 0 | 14655.5 | 163463 | 660 | 158854 | 155677.25
5203 | 2005-08-05 18:00 | 19 | 134 | 9 | 34.52 | 2.61 | 0 | 2.5206 | 288.598 | 90 | 0 | 19 | 0 | 6.5509 | 0.17802 | 0 | 6.1306 | 0.00092918 | 0 | 5.9037 | 0.00070016 | 5.7272 | 5.727 | 12861.4 | 34.6711 | 6161 | 5904.4 | 5789.93 | 0 | 0 | 5789.32 | 466.404 | 0 | 0 | 0 | 5789.32 | 0 | 660 | 0 | 0
5204 | 2005-08-05 19:00 | 0 | 0 | 0 | 33.92 | 2.61 | 0
5205 | 2005-08-05 20:00 | 0 | 0 | 0 | 33.43 | 2.61 | 0
5206 | 2005-08-05 21:00 | 0 | 0 | 0 | 32.93 | 2.17 | 0
5207 | 2005-08-05 22:00 | 0 | 0 | 0 | 32.44 | 2.17 | 0
5208 | 2005-08-05 23:00 | 0 | 0 | 0 | 31.86 | 2.17 | 0
5209 | 2005-08-06 | 0 | 0 | 0 | 31.28 | 1.59 | 0
5210 | 2005-08-06 01:00 | 0 | 0 | 0 | 30.7 | 1.59 | 0
5211 | 2005-08-06 02:00 | 0 | 0 | 0 | 30.01 | 1.59 | 0
5212 | 2005-08-06 03:00 | 0 | 0 | 0 | 29.32 | 1.43 | 0
5213 | 2005-08-06 04:00 | 0 | 0 | 0 | 28.63 | 1.43 | 0
5214 | 2005-08-06 05:00 | 40 | 161 | 26 | 28.61 | 1.43 | 0 | 4.2969 | 72.8086 | 90 | 0 | 40 | 0 | 20.125 | 0.37477 | 0 | 18.8337 | 0.0019562 | 0 | 18.1367 | 0.001474 | 17.594 | 17.5939 | 39511.4 | 29.1122 | 26945 | 26334.7 | 25774.7 | 0 | 0 | 25766.1 | 553.451 | 0 | 0 | 0 | 17406.9 | 8359.23 | 660 | 8045.78 | 7884.8662
5215 | 2005-08-06 06:00 | 234 | 575 | 72 | 28.58 | 2.43 | 0 | 16.3124 | 80.8455 | 79.0456 | 0 | 234 | 109.602 | 67.513 | 2.1924 | 100.15 | 63.1812 | 0.011444 | 78.8057 | 60.8429 | 0.008623 | 135.468 | 135.444 | 304173 | 32.1964 | 268855 | 259186 | 245252 | 0 | 0 | 244667 | 642.833 | 0 | 0 | 0 | 1915.06 | 242752 | 660 | 237122 | 232379.4219
5216 | 2005-08-06 07:00 | 457 | 774 | 86 | 28.56 | 2.43 | 0 | 28.6021 | 88.9409 | 64.7219 | 0 | 457 | 330.925 | 88.7393 | 4.2817 | 330.925 | 83.0456 | 0.022349 | 308.723 | 79.9721 | 0.016841 | 377.05 | 377.047 | 846753 | 38.6274 | 805014 | 755570 | 737987 | 0 | 0 | 733196 | 667.579 | 0 | 0 | 0 | 0 | 733196 | 667.579 | 723387 | 708919.125
5217 | 2005-08-06 08:00 | 652 | 870 | 82 | 29.85 | 2.43 | 0 | 40.918 | 98.0154 | 50.3466 | 0 | 652 | 555.348 | 87.285 | 6.1087 | 555.348 | 81.6846 | 0.031885 | 539.603 | 78.6615 | 0.024026 | 599.74 | 599.738 | 1346860 | 45.8634 | 1318080 | 1198250 | 1169960 | 0 | 0 | 1157740 | 659.773 | 0 | 0 | 0 | -12.0172 | 1157750 | 660.366 | 1141590 | 1118755
5218 | 2005-08-06 09:00 | 823 | 921 | 89 | 31.14 | 1.43 | 0 | 52.9027 | 109.749 | 35.9999 | 0 | 823 | 744.496 | 95.1314 | 7.7109 | 744.496 | 89.0276 | 0.040248 | 735.708 | 85.7327 | 0.030328 | 796.827 | 796.823 | 1789460 | 53.8866 | 1779960 | 1559340 | 1524200 | 0 | 0 | 1502330 | 640.244 | 0 | 0 | 0 | 15626.8 | 1486700 | 660 | 1463030 | 1433772.875
5219 | 2005-08-06 10:00 | 940 | 944 | 94 | 32.44 | 1.43 | 0 | 63.7523 | 128.021 | 21.8774 | 0 | 940 | 875.328 | 100.175 | 8.8071 | 875.328 | 93.748 | 0.04597 | 871.932 | 90.2785 | 0.034639 | 933.378 | 933.377 | 2096130 | 59.0848 | 2102310 | 1797080 | 1756110 | 0 | 0 | 1726210 | 628.688 | 0 | 0 | 0 | 52592.1 | 1673620 | 660 | 1643940 | 1611058
5220 | 2005-08-06 11:00 | 985 | 892 | 143 | 33.03 | 1.43 | 0 | 71.0906 | 161.034 | 9.2772 | 0 | 985 | 878.391 | 148.476 | 9.2287 | 878.391 | 138.95 | 0.048171 | 877.809 | 133.807 | 0.036298 | 981.303 | 981.297 | 2203750 | 61.0427 | 2215700 | 1876180 | 1834570 | 0 | 0 | 1801460 | 623.588 | 0 | 0 | 0 | 76117.3 | 1725350 | 660 | 1693850 | 1659974
5221 | 2005-08-06 12:00 | 934 | 693 | 283 | 33.63 | 1.52 | 0 | 70.3344 | 205.514 | 10.948 | 0 | 934 | 678.741 | 302.272 | 8.7508 | 678.741 | 282.877 | 0.045677 | 678.112 | 272.408 | 0.034418 | 922.038 | 922.015 | 2070610 | 59.792 | 2075440 | 1767390 | 1730030 | 0 | 0 | 1700640 | 624.746 | 0 | 0 | 0 | 63924.1 | 1636710 | 660 | 1608290 | 1576123
5222 | 2005-08-06 13:00 | 161 | 4 | 157 | 34.23 | 1.52 | 0 | 62.1404 | 235.557 | 24.082 | 0 | 161 | 4.1306 | 146.094 | 1.5084 | 4.1306 | 136.721 | 0.0078736 | 4.1109 | 131.661 | 0.0059329 | 131.704 | 131.693 | 295748 | 37.9668 | 260465 | 243677 | 238012 | 0 | 0 | 237437 | 623.702 | 0 | 0 | 0 | 10540.1 | 226897 | 660 | 221364 | 216936.8906
5223 | 2005-08-06 14:00 | 138 | 0 | 138 | 34.66 | 1.52 | 0 | 51.0061 | 252.335 | 38.2709 | 0 | 138 | 0 | 127.944 | 1.293 | 0 | 119.735 | 0.0067488 | 0 | 115.304 | 0.0050853 | 111.85 | 111.848 | 251184 | 37.8337 | 218151 | 204030 | 198871 | 0 | 0 | 198461 | 618.015 | 0 | 0 | 0 | 13009.6 | 185452 | 660 | 180469 | 176859.2344
5224 | 2005-08-06 15:00 | 108 | 0 | 108 | 35.1 | 0.79 | 0 | 38.9245 | 263.457 | 52.6348 | 0 | 108 | 0 | 99.7479 | 1.0119 | 0 | 93.3479 | 0.0052816 | 0 | 89.8932 | 0.0039798 | 87.2002 | 87.1967 | 195821 | 37.6987 | 166242 | 155361 | 151663 | 0 | 0 | 151415 | 606.573 | 0 | 0 | 0 | 17532.5 | 133883 | 659.999 | 129871 | 127273.4531
5225 | 2005-08-06 16:00 | 70 | 0 | 70 | 35.53 | 0.79 | 0 | 26.5826 | 272.282 | 67.0138 | 0 | 70 | 0 | 64.5187 | 0.65585 | 0 | 60.3791 | 0.0034233 | 0 | 58.1445 | 0.0025795 | 56.4027 | 56.3996 | 126659 | 37.2109 | 102802 | 96105.1 | 93882 | 0 | 0 | 93780.9 | 587.361 | 0 | 0 | 0 | 23527.1 | 70253.8 | 659.999 | 67880.4 | 66522.8281
5226 | 2005-08-06 17:00 | 90 | 1 | 90 | 35.33 | 0.79 | 0 | 14.3059 | 280.306 | 81.3334 | 0 | 90 | 0 | 81.0189 | 0.84323 | 0 | 75.8206 | 0.0044014 | 0 | 73.0145 | 0.0033165 | 70.8273 | 70.8225 | 159050 | 37.4407 | 132279 | 123650 | 120690 | 0 | 0 | 120529 | 598.433 | 0 | 0 | 0 | 20437.9 | 100091 | 659.999 | 96888.9 | 94951.1484
5227 | 2005-08-06 18:00 | 10 | 0 | 10 | 35.13 | 3.23 | 0 | 2.3373 | 288.388 | 90 | 0 | 10 | 0 | 9.4017 | 0.093692 | 0 | 8.7984 | 0.00048904 | 0 | 8.4728 | 0.0003685 | 8.219 | 8.2185 | 18456.6 | 35.3381 | 10265.3 | 9727.26 | 9550.84 | 0 | 0 | 9549.3 | 485.7 | 0 | 0 | 0 | 9549.3 | 0 | 660 | 0 | 0
5228 | 2005-08-06 19:00 | 0 | 0 | 0 | 34.93 | 3.23 | 0
5229 | 2005-08-06 20:00 | 0 | 0 | 0 | 34.4 | 3.23 | 0
5230 | 2005-08-06 21:00 | 0 | 0 | 0 | 33.87 | 4.44 | 0
5231 | 2005-08-06 22:00 | 0 | 0 | 0 | 33.34 | 4.44 | 0
5232 | 2005-08-06 23:00 | 0 | 0 | 0 | 32.53 | 4.44 | 0
5233 | 2005-08-07 | 0 | 0 | 0 | 31.72 | 5.71 | 0
5234 | 2005-08-07 01:00 | 0 | 0 | 0 | 30.91 | 5.71 | 0
5235 | 2005-08-07 02:00 | 0 | 0 | 0 | 30.08 | 5.71 | 0
5236 | 2005-08-07 03:00 | 0 | 0 | 0 | 29.26 | 2.43 | 0
5237 | 2005-08-07 04:00 | 0 | 0 | 0 | 28.44 | 2.43 | 0
5238 | 2005-08-07 05:00 | 43 | 235 | 22 | 28.41 | 2.43 | 0 | 4.1609 | 73.055 | 90 | 0 | 43 | 0 | 17.2556 | 0.40288 | 0 | 16.1485 | 0.0021029 | 0 | 15.5508 | 0.0015846 | 15.0858 | 15.0853 | 33877.9 | 28.8128 | 22357.5 | 21891.5 | 21429.5 | 0 | 0 | 21423.3 | 545.67 | 0 | 0 | 0 | 17868.6 | 3554.71 | 660 | 3420.39 | 3351.9861
5239 | 2005-08-07 06:00 | 237 | 628 | 61 | 28.37 | 2.35 | 0 | 16.1887 | 81.1084 | 79.0502 | 0 | 237 | 119.909 | 57.3422 | 2.2205 | 109.17 | 53.663 | 0.01159 | 85.892 | 51.6769 | 0.0087335 | 133.45 | 133.441 | 299680 | 31.952 | 264671 | 255420 | 240403 | 0 | 0 | 239835 | 639.815 | 0 | 0 | 0 | 2321.32 | 237514 | 660 | 231948 | 227308.9688
5240 | 2005-08-07 07:00 | 445 | 772 | 76 | 28.34 | 2.35 | 0 | 28.4835 | 89.2312 | 64.7075 | 0 | 445 | 330.571 | 79.0134 | 4.1693 | 330.571 | 73.9437 | 0.021762 | 308.413 | 71.2071 | 0.016398 | 368.247 | 368.242 | 826982 | 38.2249 | 785011 | 738138 | 720772 | 0 | 0 | 716220 | 669.076 | 0 | 0 | 0 | 0 | 716220 | 669.076 | 706584 | 692452.5625
5241 | 2005-08-07 08:00 | 656 | 881 | 80 | 29.91 | 2.35 | 0 | 40.7952 | 98.3502 | 50.3121 | 0 | 656 | 562.995 | 85.3805 | 6.1462 | 562.995 | 79.9023 | 0.032081 | 547.065 | 76.9452 | 0.024174 | 605.313 | 605.31 | 1359370 | 46.1586 | 1331060 | 1208410 | 1180280 | 0 | 0 | 1167760 | 658.112 | 0 | 0 | 0 | -41.2301 | 1167810 | 660.419 | 1151430 | 1128399.125
5242 | 2005-08-07 09:00 | 822 | 921 | 89 | 31.47 | 0.98 | 0 | 52.7609 | 110.152 | 35.9399 | 0 | 822 | 745.445 | 95.2609 | 7.7015 | 745.445 | 89.1488 | 0.040199 | 736.681 | 85.8494 | 0.030291 | 797.884 | 797.881 | 1791840 | 54.9465 | 1782450 | 1553230 | 1518670 | 0 | 0 | 1496810 | 637.891 | 0 | 0 | 0 | 22683.2 | 1474120 | 660 | 1450770 | 1421750.5
5243 | 2005-08-07 10:00 | 937 | 944 | 93 | 33.03 | 0.98 | 0 | 63.5651 | 128.496 | 21.7739 | 0 | 937 | 875.307 | 99.2988 | 8.779 | 875.307 | 92.9276 | 0.045823 | 871.944 | 89.4884 | 0.034529 | 932.623 | 932.617 | 2094420 | 60.4709 | 2100510 | 1782730 | 1743000 | 0 | 0 | 1713030 | 623.235 | 0 | 0 | 0 | 70412.1 | 1642620 | 660 | 1614000 | 1581717.25
5244 | 2005-08-07 11:00 | 998 | 953 | 100 | 33.65 | 0.98 | 0 | 70.8292 | 161.358 | 9.0513 | 0 | 998 | 938.885 | 106.081 | 9.3505 | 938.885 | 99.2743 | 0.048806 | 938.293 | 95.6003 | 0.036777 | 1002.91 | 1002.91 | 2252290 | 63.1591 | 2266880 | 1899030 | 1857030 | 0 | 0 | 1822390 | 616.893 | 0 | 0 | 0 | 108283 | 1714110 | 660 | 1683010 | 1649353.125
5245 | 2005-08-07 12:00 | 992 | 952 | 99 | 34.27 | 3.26 | 0 | 70.0626 | 205.29 | 10.7999 | 0 | 992 | 933.108 | 105.121 | 9.2943 | 933.108 | 98.3761 | 0.048513 | 932.267 | 94.7353 | 0.036555 | 996.227 | 996.227 | 2237270 | 59.445 | 2251050 | 1922260 | 1882990 | 0 | 0 | 1848550 | 627.593 | 0 | 0 | 0 | 57660.6 | 1790890 | 660 | 1757030 | 1721886
5246 | 2005-08-07 13:00 | 894 | 844 | 150 | 34.89 | 3.26 | 0 | 61.9207 | 235.178 | 24.0455 | 0 | 894 | 770.078 | 163.01 | 8.3761 | 770.078 | 152.551 | 0.04372 | 766.419 | 146.905 | 0.032944 | 885.957 | 885.95 | 1989620 | 57.2783 | 1990210 | 1716000 | 1678120 | 0 | 0 | 1651120 | 632.912 | 0 | 0 | 0 | 37330.3 | 1613780 | 660 | 1586130 | 1554405
5247 | 2005-08-07 14:00 | 797 | 915 | 88 | 35.31 | 3.26 | 0 | 50.8198 | 251.998 | 38.2746 | 0 | 797 | 718.045 | 94.2127 | 7.4673 | 718.045 | 88.1678 | 0.038977 | 708.215 | 84.9048 | 0.02937 | 769.354 | 769.35 | 1727760 | 54.7517 | 1715290 | 1495640 | 1463210 | 0 | 0 | 1442790 | 636.196 | 0 | 0 | 0 | 23235.6 | 1419550 | 660 | 1397530 | 1369576.25
5248 | 2005-08-07 15:00 | 624 | 785 | 133 | 35.72 | 2.78 | 0 | 38.7521 | 263.17 | 52.6629 | 0 | 624 | 475.744 | 139.592 | 5.8464 | 475.744 | 130.635 | 0.030516 | 460.311 | 125.8 | 0.022995 | 568.55 | 568.548 | 1276810 | 50.5515 | 1245530 | 1105740 | 1080410 | 0 | 0 | 1069360 | 641.232 | 0 | 0 | 0 | 10801.6 | 1058550 | 660 | 1044420 | 1023532
5249 | 2005-08-07 16:00 | 355 | 463 | 149 | 36.13 | 2.78 | 0 | 26.4122 | 272.03 | 67.0616 | 0 | 355 | 180.49 | 144.757 | 3.3261 | 180.49 | 135.469 | 0.017361 | 166.36 | 130.455 | 0.013082 | 287.923 | 287.915 | 646582 | 43.6407 | 603823 | 551608 | 538496 | 0 | 0 | 535717 | 640.7 | 0 | 0 | 0 | 7105.36 | 528612 | 660 | 521551 | 511120.4375
5250 | 2005-08-07 17:00 | 179 | 438 | 71 | 35.6 | 2.78 | 0 | 14.1298 | 280.077 | 81.3999 | 0 | 179 | 66.1561 | 65.4807 | 1.6771 | 66.1561 | 61.2793 | 0.0087538 | 47.3437 | 59.0114 | 0.0065962 | 103.171 | 103.168 | 231690 | 38.2913 | 199770 | 186279 | 182204 | 0 | 0 | 181854 | 612.381 | 0 | 0 | 0 | 16180.2 | 165673 | 659.999 | 161025 | 157804.25
5251 | 2005-08-07 18:00 | 19 | 160 | 7 | 35.06 | 5.77 | 0 | 2.1494 | 288.175 | 90 | 0 | 19 | 0 | 5.3753 | 0.17802 | 0 | 5.0304 | 0.00092918 | 0 | 4.8442 | 0.00070016 | 4.6996 | 4.6994 | 10553.6 | 35.1608 | 4553.48 | 4384.6 | 4304.11 | 0 | 0 | 4303.74 | 446.989 | 0 | 0 | 0 | 4303.74 | 0 | 660 | 0 | 0
5252 | 2005-08-07 19:00 | 0 | 0 | 0 | 34.52 | 5.77 | 0
5253 | 2005-08-07 20:00 | 0 | 0 | 0 | 34.03 | 5.77 | 0
5254 | 2005-08-07 21:00 | 0 | 0 | 0 | 33.53 | 5.86 | 0
5255 | 2005-08-07 22:00 | 0 | 0 | 0 | 33.04 | 5.86 | 0
5256 | 2005-08-07 23:00 | 0 | 0 | 0 | 32.23 | 5.86 | 0
5257 | 2005-08-08 | 0 | 0 | 0 | 31.43 | 5.85 | 0
5258 | 2005-08-08 01:00 | 0 | 0 | 0 | 30.62 | 5.85 | 0
5259 | 2005-08-08 02:00 | 0 | 0 | 0 | 29.82 | 5.85 | 0
5260 | 2005-08-08 03:00 | 0 | 0 | 0 | 29.02 | 1.17 | 0
5261 | 2005-08-08 04:00 | 0 | 0 | 0 | 28.22 | 1.17 | 0
5262 | 2005-08-08 05:00 | 44 | 151 | 31 | 28.2 | 1.17 | 0 | 4.0245 | 73.3063 | 90 | 0 | 44 | 0 | 24.3672 | 0.41225 | 0 | 22.8037 | 0.0021518 | 0 | 21.9598 | 0.0016214 | 21.3026 | 21.3008 | 47836.2 | 28.8188 | 33836.6 | 33123 | 32408.1 | 0 | 0 | 32395 | 565.029 | 0 | 0 | 0 | 15559.7 | 16835.3 | 660 | 16212.6 | 15888.3545
5263 | 2005-08-08 06:00 | 105 | 25 | 98 | 28.19 | 0.77 | 0 | 16.0645 | 81.3761 | 79.0532 | 0 | 105 | 4.8037 | 98.3158 | 0.98377 | 4.3589 | 92.0077 | 0.0051349 | 3.4291 | 88.6025 | 0.0038693 | 89.2745 | 89.2689 | 200475 | 30.8541 | 170575 | 165463 | 161285 | 0 | 0 | 161028 | 632.223 | 0 | 0 | 0 | 4242.34 | 156785 | 660 | 152303 | 149256.6875
5264 | 2005-08-08 07:00 | 264 | 103 | 215 | 28.17 | 0.77 | 0 | 28.3642 | 89.5265 | 64.6916 | 0 | 264 | 44.0921 | 219.731 | 2.4735 | 44.0921 | 205.633 | 0.012911 | 41.1396 | 198.023 | 0.0097285 | 231.997 | 231.985 | 520980 | 35.0931 | 479278 | 456513 | 445238 | 0 | 0 | 443446 | 660.194 | 0 | 0 | 0 | 2.3095 | 443444 | 660.708 | 437311 | 428564.3438
5265 | 2005-08-08 08:00 | 477 | 280 | 294 | 29.67 | 0.77 | 0 | 40.6712 | 98.6903 | 50.2762 | 0 | 477 | 179.454 | 288.932 | 4.4691 | 179.454 | 270.394 | 0.023327 | 174.387 | 260.387 | 0.017578 | 421.747 | 421.732 | 947102 | 42.2557 | 906925 | 836845 | 816736 | 0 | 0 | 810749 | 659.633 | 0 | 0 | 0 | -29.3099 | 810779 | 660.566 | 800216 | 784211.1875
5266 | 2005-08-08 09:00 | 680 | 514 | 272 | 31.16 | 1.11 | 0 | 52.617 | 110.56 | 35.8788 | 0 | 680 | 416.043 | 281.378 | 6.3711 | 416.043 | 263.324 | 0.033255 | 411.172 | 253.579 | 0.025058 | 644.832 | 644.822 | 1448110 | 49.9676 | 1423270 | 1268760 | 1239110 | 0 | 0 | 1224860 | 646.494 | 0 | 0 | 0 | 4862.94 | 1220000 | 660 | 1202530 | 1178477.625
5267 | 2005-08-08 10:00 | 834 | 614 | 286 | 32.66 | 1.11 | 0 | 63.3746 | 128.975 | 21.6699 | 0 | 834 | 569.682 | 302.573 | 7.8139 | 569.682 | 283.159 | 0.040786 | 567.516 | 272.68 | 0.030733 | 815.02 | 815.008 | 1830300 | 56.4315 | 1822810 | 1576830 | 1541760 | 0 | 0 | 1518960 | 634.012 | 0 | 0 | 0 | 33121.6 | 1485840 | 660 | 1462190 | 1432949.75
5268 | 2005-08-08 11:00 | 870 | 609 | 297 | 33.48 | 1.11 | 0 | 70.5637 | 161.685 | 8.8237 | 0 | 870 | 600.436 | 316.883 | 8.1512 | 600.436 | 296.551 | 0.042547 | 600.076 | 285.576 | 0.03206 | 859.114 | 859.088 | 1929290 | 58.5372 | 1926780 | 1649950 | 1612950 | 0 | 0 | 1587620 | 628.035 | 0 | 0 | 0 | 50815.2 | 1536800 | 660 | 1511650 | 1481415.625
5269 | 2005-08-08 12:00 | 717 | 296 | 440 | 34.31 | 1.82 | 0 | 69.7856 | 205.073 | 10.6566 | 0 | 717 | 290.09 | 450.723 | 6.7177 | 290.09 | 421.804 | 0.035064 | 289.836 | 406.193 | 0.026422 | 675.174 | 675.167 | 1516250 | 53.0865 | 1494260 | 1311940 | 1281250 | 0 | 0 | 1265770 | 640.27 | 0 | 0 | 0 | 16806.1 | 1248970 | 660 | 1230860 | 1206245.125
5270 | 2005-08-08 13:00 | 922 | 722 | 287 | 35.13 | 1.82 | 0 | 61.6952 | 234.803 | 24.0135 | 0 | 922 | 658.81 | 302.568 | 8.6384 | 658.81 | 283.154 | 0.04509 | 655.689 | 272.675 | 0.033976 | 900.546 | 900.526 | 2022350 | 60.1738 | 2024650 | 1720240 | 1683160 | 0 | 0 | 1655150 | 623.237 | 0 | 0 | 0 | 69236.1 | 1585920 | 660 | 1559180 | 1527993.75
5271 | 2005-08-08 14:00 | 362 | 102 | 283 | 35.03 | 1.82 | 0 | 50.628 | 251.66 | 38.2821 | 0 | 362 | 80.2188 | 277.578 | 3.3917 | 80.2188 | 259.768 | 0.017703 | 79.1201 | 250.154 | 0.01334 | 319.409 | 319.4 | 717291 | 43.9126 | 674565 | 615915 | 601951 | 0 | 0 | 598492 | 641.199 | 0 | 0 | 0 | 5826.69 | 592665 | 660 | 584939 | 573239.875
5272 | 2005-08-08 15:00 | 109 | 0 | 109 | 34.93 | 3.58 | 0 | 38.5746 | 262.88 | 52.6945 | 0 | 109 | 0 | 100.682 | 1.0212 | 0 | 94.2223 | 0.0053305 | 0 | 90.7352 | 0.0040167 | 88.0171 | 88.0111 | 197651 | 37.1076 | 167944 | 157479 | 153826 | 0 | 0 | 153573 | 608.981 | 0 | 0 | 0 | 15906.7 | 137666 | 660 | 133572 | 130900.8672
5273 | 2005-08-08 16:00 | 401 | 498 | 181 | 34.84 | 3.58 | 0 | 26.2371 | 271.776 | 67.1127 | 0 | 401 | 193.543 | 174.428 | 3.7571 | 193.543 | 163.236 | 0.019611 | 178.338 | 157.195 | 0.014777 | 325.481 | 325.473 | 730932 | 42.8929 | 688242 | 631796 | 616876 | 0 | 0 | 613330 | 648.978 | 0 | 0 | 0 | 3115.15 | 610215 | 660 | 602282 | 590236.625
5274 | 2005-08-08 17:00 | 189 | 531 | 60 | 34.56 | 3.58 | 0 | 13.9491 | 279.846 | 81.4695 | 0 | 189 | 79.3794 | 55.2894 | 1.7708 | 79.3794 | 51.7419 | 0.0092429 | 56.5916 | 49.827 | 0.0069647 | 103.233 | 103.228 | 231823 | 37.1141 | 199895 | 187606 | 183332 | 0 | 0 | 182982 | 616.486 | 0 | 0 | 0 | 13105 | 169877 | 660 | 165153 | 161849.7969
5275 | 2005-08-08 18:00 | 20 | 190 | 7 | 34.29 | 5.4 | 0 | 1.957 | 287.961 | 90 | 0 | 20 | 0 | 5.4237 | 0.18738 | 0 | 5.0757 | 0.00097808 | 0 | 4.8879 | 0.00073701 | 4.742 | 4.7418 | 10648.9 | 34.3942 | 4618.45 | 4459.69 | 4380.86 | 0 | 0 | 4380.48 | 448.631 | 0 | 0 | 0 | 4380.48 | 0 | 660 | 0 | 0
5276 | 2005-08-08 19:00 | 0 | 0 | 0 | 34.01 | 5.4 | 0
5277 | 2005-08-08 20:00 | 0 | 0 | 0 | 33.41 | 5.4 | 0
5278 | 2005-08-08 21:00 | 0 | 0 | 0 | 32.81 | 3.85 | 0
5279 | 2005-08-08 22:00 | 0 | 0 | 0 | 32.21 | 3.85 | 0
5280 | 2005-08-08 23:00 | 0 | 0 | 0 | 31.34 | 3.85 | 0
5281 | 2005-08-09 | 0 | 0 | 0 | 30.48 | 3.49 | 0
5282 | 2005-08-09 01:00 | 0 | 0 | 0 | 29.61 | 3.49 | 0
5283 | 2005-08-09 02:00 | 0 | 0 | 0 | 28.83 | 3.49 | 0
5284 | 2005-08-09 03:00 | 0 | 0 | 0 | 28.05 | 2.02 | 0
5285 | 2005-08-09 04:00 | 0 | 0 | 0 | 27.27 | 2.02 | 0
5286 | 2005-08-09 05:00 | 35 | 166 | 21 | 27.13 | 2.02 | 0 | 3.8875 | 73.5625 | 90 | 0 | 35 | 0 | 16.1975 | 0.32792 | 0 | 15.1582 | 0.0017117 | 0 | 14.5972 | 0.0012898 | 14.1606 | 14.16 | 31799.6 | 27.5186 | 20683.8 | 20400.7 | 19970.1 | 0 | 0 | 19964.8 | 546.783 | 0 | 0 | 0 | 16100.2 | 3864.64 | 660 | 3718.69 | 3644.3132
5287 | 2005-08-09 06:00 | 232 | 587 | 70 | 26.98 | 0.87 | 0 | 15.9398 | 81.6486 | 79.0546 | 0 | 232 | 112.005 | 66.0806 | 2.1737 | 101.241 | 61.8407 | 0.011346 | 79.6428 | 59.552 | 0.0085493 | 135.027 | 135.032 | 303248 | 30.9827 | 268027 | 259941 | 244756 | 0 | 0 | 244183 | 648.657 | 0 | 0 | 0 | 1281.5 | 242902 | 660 | 237282 | 232536.7188
5288 | 2005-08-09 07:00 | 452 | 805 | 71 | 26.84 | 0.87 | 0 | 28.2441 | 89.8267 | 64.6742 | 0 | 452 | 344.397 | 74.3135 | 4.2349 | 344.397 | 69.5454 | 0.022105 | 321.361 | 66.9716 | 0.016656 | 376.699 | 376.693 | 845958 | 38.0061 | 804208 | 757078 | 739082 | 0 | 0 | 734303 | 669.795 | 0 | 0 | 0 | 0 | 734303 | 669.795 | 724398 | 709909.625
5289 | 2005-08-09 08:00 | 646 | 866 | 83 | 28.62 | 0.87 | 0 | 40.5459 | 99.0356 | 50.239 | 0 | 646 | 553.932 | 88.6609 | 6.0525 | 553.932 | 82.9723 | 0.031592 | 538.324 | 79.9015 | 0.023805 | 599.702 | 599.704 | 1346780 | 46.3967 | 1318000 | 1195040 | 1165700 | 0 | 0 | 1153490 | 658.199 | 0 | 0 | 0 | 49.5396 | 1153440 | 660.085 | 1137380 | 1114632.125
5290 | 2005-08-09 09:00 | 818 | 921 | 88 | 30.39 | 0.8 | 0 | 52.4711 | 110.974 | 35.8168 | 0 | 818 | 746.427 | 94.5036 | 7.664 | 746.427 | 88.4401 | 0.040004 | 737.724 | 85.1669 | 0.030144 | 798.233 | 798.227 | 1792610 | 54.1633 | 1783270 | 1560100 | 1528100 | 0 | 0 | 1506060 | 639.322 | 0 | 0 | 0 | 19047 | 1487020 | 660 | 1463340 | 1434074
5291 | 2005-08-09 10:00 | 936 | 944 | 95 | 32.17 | 0.8 | 0 | 63.181 | 129.458 | 21.5657 | 0 | 936 | 876.396 | 101.633 | 8.7696 | 876.396 | 95.112 | 0.045774 | 873.097 | 91.5919 | 0.034492 | 935.782 | 935.774 | 2101520 | 60.0399 | 2107990 | 1793140 | 1755300 | 0 | 0 | 1725010 | 624.49 | 0 | 0 | 0 | 66405 | 1658600 | 660 | 1629440 | 1596847.125
5292 | 2005-08-09 11:00 | 994 | 953 | 99 | 32.74 | 0.8 | 0 | 70.2943 | 162.013 | 8.595 | 0 | 994 | 939.998 | 105.399 | 9.313 | 939.998 | 98.636 | 0.048611 | 939.464 | 94.9856 | 0.036629 | 1003.45 | 1003.45 | 2253480 | 62.6253 | 2268140 | 1905390 | 1863620 | 0 | 0 | 1828900 | 618.191 | 0 | 0 | 0 | 99598.5 | 1729300 | 660 | 1697670 | 1663713.125
5293 | 2005-08-09 12:00 | 989 | 952 | 99 | 33.3 | 3.16 | 0 | 69.5035 | 204.865 | 10.5187 | 0 | 989 | 934.184 | 105.451 | 9.2662 | 934.184 | 98.685 | 0.048366 | 933.385 | 95.0327 | 0.036445 | 997.601 | 997.594 | 2240340 | 58.6768 | 2254290 | 1932590 | 1890490 | 0 | 0 | 1856130 | 631.18 | 0 | 0 | 0 | 46923.2 | 1809210 | 660 | 1774660 | 1739170.5
5294 | 2005-08-09 13:00 | 920 | 900 | 130 | 33.87 | 3.16 | 0 | 61.4639 | 234.43 | 23.9862 | 0 | 920 | 821.588 | 136.787 | 8.6197 | 821.588 | 128.011 | 0.044992 | 817.706 | 123.273 | 0.033902 | 912.782 | 912.776 | 2049870 | 57.0892 | 2053600 | 1772970 | 1736110 | 0 | 0 | 1707240 | 633.005 | 0 | 0 | 0 | 35735 | 1671500 | 660 | 1641890 | 1609053
5295 | 2005-08-09 14:00 | 745 | 725 | 186 | 33.7 | 3.16 | 0 | 50.4308 | 251.322 | 38.2935 | 0 | 745 | 569.146 | 198.798 | 6.9801 | 569.146 | 186.042 | 0.036434 | 561.345 | 179.157 | 0.027453 | 718.313 | 718.309 | 1613140 | 51.9723 | 1595360 | 1409600 | 1377840 | 0 | 0 | 1360190 | 644.802 | 0 | 0 | 0 | 9589.15 | 1350600 | 659.999 | 1330200 | 1303600.375
5296 | 2005-08-09 15:00 | 611 | 819 | 102 | 33.52 | 3.13 | 0 | 38.3921 | 262.589 | 52.7297 | 0 | 611 | 496.326 | 108.919 | 5.7246 | 496.326 | 101.93 | 0.02988 | 480.163 | 98.1578 | 0.022516 | 560.993 | 560.987 | 1259830 | 47.8187 | 1227970 | 1105030 | 1079280 | 0 | 0 | 1068550 | 650.222 | 0 | 0 | 0 | 2577.04 | 1065970 | 660 | 1051690 | 1030657.6875
5297 | 2005-08-09 16:00 | 391 | 706 | 80 | 33.35 | 3.13 | 0 | 26.0572 | 271.519 | 67.167 | 0 | 391 | 274.735 | 82.4726 | 3.6634 | 274.735 | 77.181 | 0.019121 | 253.072 | 74.3245 | 0.014408 | 317.588 | 317.583 | 713208 | 41.4447 | 670450 | 619868 | 605681 | 0 | 0 | 602283 | 651.513 | 0 | 0 | 0 | 1433.08 | 600850 | 660 | 593036 | 581175.75
5298 | 2005-08-09 17:00 | 185 | 517 | 61 | 33.39 | 3.13 | 0 | 13.7639 | 279.614 | 81.5424 | 0 | 185 | 76.6542 | 56.3264 | 1.7333 | 76.6542 | 52.7124 | 0.0090473 | 54.4279 | 50.7616 | 0.0068173 | 102.04 | 102.039 | 229153 | 35.9908 | 197386 | 186377 | 182055 | 0 | 0 | 181714 | 620.112 | 0 | 0 | 0 | 10745.1 | 170969 | 660 | 166226 | 162901.375
5299 | 2005-08-09 18:00 | 19 | 180 | 7 | 33.43 | 6.7 | 0 | 1.7602 | 287.745 | 90 | 0 | 19 | 0 | 5.4771 | 0.17802 | 0 | 5.1257 | 0.00092918 | 0 | 4.936 | 0.00070016 | 4.7886 | 4.7886 | 10753.9 | 33.5268 | 4690.28 | 4543.63 | 4461.11 | 0 | 0 | 4460.72 | 452.864 | 0 | 0 | 0 | 4460.72 | 0 | 660 | 0 | 0
5300 | 2005-08-09 19:00 | 0 | 0 | 0 | 33.47 | 6.7 | 0
5301 | 2005-08-09 20:00 | 0 | 0 | 0 | 32.72 | 6.7 | 0
5302 | 2005-08-09 21:00 | 0 | 0 | 0 | 31.97 | 5.9 | 0
5303 | 2005-08-09 22:00 | 0 | 0 | 0 | 31.22 | 5.9 | 0
5304 | 2005-08-09 23:00 | 0 | 0 | 0 | 30.32 | 5.9 | 0
5305 | 2005-08-10 | 0 | 0 | 0 | 29.43 | 8.55 | 0
5306 | 2005-08-10 01:00 | 0 | 0 | 0 | 28.54 | 8.55 | 0
5307 | 2005-08-10 02:00 | 0 | 0 | 0 | 27.7 | 8.55 | 0
5308 | 2005-08-10 03:00 | 0 | 0 | 0 | 26.87 | 5.72 | 0
5309 | 2005-08-10 04:00 | 0 | 0 | 0 | 26.03 | 5.72 | 0
5310 | 2005-08-10 05:00 | 40 | 155 | 27 | 25.95 | 5.72 | 0 | 3.75 | 73.8234 | 90 | 0 | 40 | 0 | 21.1556 | 0.37477 | 0 | 19.7983 | 0.0019562 | 0 | 19.0655 | 0.001474 | 18.495 | 18.4942 | 41533.1 | 26.348 | 28607.1 | 28395.3 | 27785.6 | 0 | 0 | 27776 | 565.821 | 0 | 0 | 0 | 12755.5 | 15020.5 | 660 | 14463.3 | 14174
5311 | 2005-08-10 06:00 | 190 | 324 | 101 | 25.86 | 2.81 | 0 | 15.8145 | 81.9258 | 79.0544 | 0 | 190 | 62.0098 | 92.8737 | 1.7801 | 55.8301 | 86.9148 | 0.0092918 | 43.92 | 83.6981 | 0.0070016 | 123.796 | 123.786 | 277993 | 29.0828 | 243691 | 238694 | 228142 | 0 | 0 | 227658 | 653.322 | 0 | 0 | 0 | 269.709 | 227388 | 660 | 221874 | 217436.2188
5312 | 2005-08-10 07:00 | 442 | 666 | 128 | 25.78 | 2.81 | 0 | 28.1232 | 90.1318 | 64.6553 | 0 | 442 | 285.152 | 129.306 | 4.1412 | 285.152 | 121.009 | 0.021616 | 266.102 | 116.531 | 0.016288 | 371.169 | 371.167 | 833546 | 35.4433 | 791654 | 754421 | 735664 | 0 | 0 | 731039 | 677.656 | 0 | 0 | 0 | 0 | 731039 | 677.656 | 720890 | 706472.5
5313 | 2005-08-10 08:00 | 625 | 779 | 120 | 26.84 | 2.81 | 0 | 40.4195 | 99.3859 | 50.2006 | 0 | 625 | 498.554 | 127.749 | 5.8558 | 498.554 | 119.552 | 0.030565 | 484.538 | 115.128 | 0.023031 | 581.699 | 581.693 | 1306330 | 41.9842 | 1276080 | 1181710 | 1153100 | 0 | 0 | 1141630 | 671.699 | 0 | 0 | 0 | 0 | 1141630 | 671.699 | 1125250 | 1102741.5
5314 | 2005-08-10 09:00 | 808 | 866 | 123 | 27.91 | 2.53 | 0 | 52.3232 | 111.392 | 35.7539 | 0 | 808 | 702.364 | 129.809 | 7.5703 | 702.364 | 121.48 | 0.039515 | 694.208 | 116.984 | 0.029775 | 786.885 | 786.88 | 1767130 | 48.7809 | 1756550 | 1577920 | 1541110 | 0 | 0 | 1519940 | 658.235 | 0 | 0 | 0 | 106.969 | 1519840 | 660.278 | 1495210 | 1465303.625
5315 | 2005-08-10 10:00 | 934 | 944 | 94 | 28.97 | 2.53 | 0 | 62.9842 | 129.944 | 21.4615 | 0 | 934 | 877.51 | 100.761 | 8.7508 | 877.51 | 94.2961 | 0.045677 | 874.242 | 90.8063 | 0.034418 | 936.13 | 936.124 | 2102300 | 53.7994 | 2108810 | 1851300 | 1808420 | 0 | 0 | 1778340 | 646.087 | 0 | 0 | 0 | 9895.51 | 1768450 | 660 | 1735410 | 1700697.625
5316 | 2005-08-10 11:00 | 993 | 953 | 99 | 30.35 | 2.53 | 0 | 70.0208 | 162.343 | 8.3654 | 0 | 993 | 941.128 | 105.567 | 9.3036 | 941.128 | 98.7938 | 0.048562 | 940.622 | 95.1375 | 0.036592 | 1004.72 | 1004.72 | 2256340 | 56.9987 | 2271150 | 1963760 | 1920470 | 0 | 0 | 1885640 | 637.08 | 0 | 0 | 0 | 29796.2 | 1855840 | 660 | 1819550 | 1783155.875
5317 | 2005-08-10 12:00 | 987 | 952 | 99 | 31.72 | 2.4 | 0 | 69.2164 | 204.664 | 10.3869 | 0 | 987 | 934.242 | 105.619 | 9.2474 | 934.242 | 98.8425 | 0.048268 | 933.464 | 95.1844 | 0.036371 | 997.824 | 997.821 | 2240860 | 58.4158 | 2254830 | 1935590 | 1891870 | 0 | 0 | 1857510 | 631.339 | 0 | 0 | 0 | 42922.1 | 1814590 | 660 | 1779840 | 1744246.5
5318 | 2005-08-10 13:00 | 918 | 940 | 95 | 33.1 | 2.4 | 0 | 61.2269 | 234.061 | 23.9637 | 0 | 918 | 857.994 | 101.844 | 8.6009 | 857.994 | 95.3095 | 0.044894 | 853.947 | 91.7822 | 0.033829 | 917.391 | 917.388 | 2060220 | 57.6439 | 2064500 | 1777450 | 1737270 | 0 | 0 | 1708350 | 632.679 | 0 | 0 | 0 | 38669.2 | 1669680 | 660 | 1640130 | 1607332
5319 | 2005-08-10 14:00 | 791 | 914 | 89 | 33.63 | 2.4 | 0 | 50.2283 | 250.984 | 38.3089 | 0 | 791 | 716.688 | 95.627 | 7.4111 | 716.688 | 89.4913 | 0.038683 | 706.855 | 86.1793 | 0.029149 | 769.271 | 769.265 | 1727580 | 54.211 | 1715100 | 1499550 | 1466650 | 0 | 0 | 1446340 | 639.414 | 0 | 0 | 0 | 19182.5 | 1427150 | 660 | 1404940 | 1376843.25
5320 | 2005-08-10 15:00 | 616 | 868 | 79 | 34.17 | 4.81 | 0 | 38.2046 | 262.297 | 52.7683 | 0 | 616 | 525.337 | 84.5202 | 5.7714 | 525.337 | 79.0972 | 0.030125 | 508.19 | 76.1699 | 0.0227 | 566.851 | 566.848 | 1272990 | 47.109 | 1241580 | 1121340 | 1095530 | 0 | 0 | 1084580 | 653.412 | 0 | 0 | 0 | 1212.82 | 1083360 | 660 | 1068740 | 1047363
5321 | 2005-08-10 16:00 | 402 | 760 | 70 | 34.7 | 4.81 | 0 | 25.8727 | 271.261 | 67.2247 | 0 | 402 | 294.526 | 72.7188 | 3.7664 | 294.526 | 68.0531 | 0.019659 | 271.211 | 65.5345 | 0.014814 | 326.658 | 326.656 | 733585 | 42.1563 | 690898 | 636630 | 621948 | 0 | 0 | 618357 | 650.55 | 0 | 0 | 0 | 2037.27 | 616320 | 660 | 608308 | 596141.4375
5322 | 2005-08-10 17:00 | 184 | 526 | 60 | 34.24 | 4.81 | 0 | 13.5742 | 279.379 | 81.6183 | 0 | 184 | 77.012 | 55.4928 | 1.7239 | 77.012 | 51.9323 | 0.0089984 | 54.4464 | 50.0103 | 0.0067805 | 101.33 | 101.326 | 227553 | 36.5529 | 195883 | 184386 | 180089 | 0 | 0 | 179753 | 617.885 | 0 | 0 | 0 | 12062.6 | 167690 | 660 | 163006 | 159745.4062
5323 | 2005-08-10 18:00 | 18 | 179 | 6 | 33.77 | 7.08 | 0 | 1.5589 | 287.526 | 90 | 0 | 18 | 0 | 4.64 | 0.16865 | 0 | 4.3423 | 0.00088028 | 0 | 4.1816 | 0.00066331 | 4.0568 | 4.0567 | 9110.38 | 33.85 | 3588.88 | 3495.44 | 3442.23 | 0 | 0 | 3441.98 | 429.505 | 0 | 0 | 0 | 3441.98 | 0 | 660 | 0 | 0
5324 | 2005-08-10 19:00 | 0 | 0 | 0 | 33.3 | 7.08 | 0
5325 | 2005-08-10 20:00 | 0 | 0 | 0 | 32.54 | 7.08 | 0
5326 | 2005-08-10 21:00 | 0 | 0 | 0 | 31.78 | 6.81 | 0
5327 | 2005-08-10 22:00 | 0 | 0 | 0 | 31.01 | 6.81 | 0
5328 | 2005-08-10 23:00 | 0 | 0 | 0 | 29.98 | 6.81 | 0
5329 | 2005-08-11 | 0 | 0 | 0 | 28.95 | 7.94 | 0
5330 | 2005-08-11 01:00 | 0 | 0 | 0 | 27.92 | 7.94 | 0
5331 | 2005-08-11 02:00 | 0 | 0 | 0 | 27.28 | 7.94 | 0
5332 | 2005-08-11 03:00 | 0 | 0 | 0 | 26.64 | 6.25 | 0
5333 | 2005-08-11 04:00 | 0 | 0 | 0 | 26 | 6.25 | 0
5334 | 2005-08-11 05:00 | 34 | 136 | 23 | 25.88 | 6.25 | 0 | 3.6121 | 74.089 | 90 | 0 | 34 | 0 | 17.9066 | 0.31855 | 0 | 16.7576 | 0.0016627 | 0 | 16.1375 | 0.0012529 | 15.6546 | 15.6544 | 35155.8 | 26.2056 | 23392 | 23237.9 | 22753.9 | 0 | 0 | 22747.3 | 556.861 | 0 | 0 | 0 | 13577.1 | 9170.22 | 660 | 8826.8 | 8650.2666
5335 | 2005-08-11 06:00 | 232 | 594 | 71 | 25.76 | 2.62 | 0 | 15.6887 | 82.2076 | 79.0525 | 0 | 232 | 113.07 | 67.3329 | 2.1737 | 101.417 | 63.0127 | 0.011346 | 79.7862 | 60.6807 | 0.0085493 | 136.261 | 136.25 | 305982 | 29.3523 | 270673 | 264703 | 248310 | 0 | 0 | 247733 | 655.737 | 0 | 0 | 0 | 173.739 | 247559 | 660 | 241908 | 237069.6875
5336 | 2005-08-11 07:00 | 448 | 804 | 70 | 25.64 | 2.62 | 0 | 28.0016 | 90.4415 | 64.635 | 0 | 448 | 344.899 | 73.6041 | 4.1974 | 344.899 | 68.8815 | 0.021909 | 321.888 | 66.3322 | 0.016509 | 376.59 | 376.586 | 845717 | 35.5688 | 803962 | 765749 | 747364 | 0 | 0 | 742583 | 676.903 | 0 | 0 | 0 | 0 | 742583 | 676.903 | 732301 | 717655.375
5337 | 2005-08-11 08:00 | 642 | 864 | 83 | 27.48 | 2.62 | 0 | 40.2917 | 99.7412 | 50.161 | 0 | 642 | 553.773 | 88.9172 | 6.015 | 553.773 | 83.2121 | 0.031397 | 538.241 | 80.1325 | 0.023658 | 599.845 | 599.841 | 1347090 | 43.295 | 1318320 | 1213460 | 1184300 | 0 | 0 | 1172140 | 669.977 | 0 | 0 | 0 | 0 | 1172140 | 669.977 | 1155210 | 1132105.25
5338 | 2005-08-11 09:00 | 806 | 902 | 94 | 29.31 | 3.11 | 0 | 52.1732 | 111.816 | 35.6904 | 0 | 806 | 732.113 | 100.913 | 7.5516 | 732.113 | 94.4379 | 0.039417 | 723.648 | 90.9428 | 0.029701 | 790.182 | 790.175 | 1774540 | 49.4771 | 1764320 | 1579600 | 1542110 | 0 | 0 | 1520780 | 656.129 | 0 | 0 | 0 | 596.006 | 1520190 | 660 | 1495560 | 1465643.875
5339 | 2005-08-11 10:00 | 933 | 944 | 95 | 31.14 | 3.11 | 0 | 62.7842 | 130.434 | 21.3575 | 0 | 933 | 877.612 | 101.938 | 8.7415 | 877.612 | 95.3971 | 0.045628 | 874.376 | 91.8665 | 0.034381 | 937.289 | 937.283 | 2104900 | 55.0616 | 2111550 | 1842190 | 1801140 | 0 | 0 | 1770790 | 640.789 | 0 | 0 | 0 | 17307 | 1753490 | 660 | 1720980 | 1686564.375
5340 | 2005-08-11 11:00 | 991 | 953 | 99 | 32.29 | 3.11 | 0 | 69.7434 | 162.674 | 8.1356 | 0 | 991 | 941.237 | 105.738 | 9.2849 | 941.237 | 98.9536 | 0.048464 | 940.759 | 95.2914 | 0.036519 | 1005 | 1005 | 2256980 | 57.9399 | 2271830 | 1955080 | 1910760 | 0 | 0 | 1875900 | 633.013 | 0 | 0 | 0 | 37740.2 | 1838160 | 660 | 1802530 | 1766480.25
5341 | 2005-08-11 12:00 | 985 | 952 | 98 | 33.43 | 3.69 | 0 | 68.9245 | 204.47 | 10.2617 | 0 | 985 | 935.382 | 104.77 | 9.2287 | 935.382 | 98.0474 | 0.048171 | 934.622 | 94.4187 | 0.036298 | 998.205 | 998.202 | 2241710 | 57.9494 | 2255730 | 1941010 | 1897130 | 0 | 0 | 1862870 | 633.772 | 0 | 0 | 0 | 38379 | 1824490 | 660 | 1789380 | 1753593.5
5342 | 2005-08-11 13:00 | 910 | 931 | 97 | 34.58 | 3.69 | 0 | 60.9843 | 233.695 | 23.9463 | 0 | 910 | 849.666 | 104.043 | 8.526 | 849.666 | 97.367 | 0.044503 | 845.665 | 93.7635 | 0.033534 | 911.279 | 911.272 | 2046490 | 56.9641 | 2050050 | 1771020 | 1732790 | 0 | 0 | 1704130 | 634.149 | 0 | 0 | 0 | 33579.5 | 1670550 | 660 | 1640970 | 1608153.25
5343 | 2005-08-11 14:00 | 788 | 914 | 88 | 35.01 | 3.69 | 0 | 50.0204 | 250.646 | 38.3283 | 0 | 788 | 716.623 | 94.7389 | 7.383 | 716.623 | 88.6602 | 0.038537 | 706.778 | 85.379 | 0.029038 | 768.421 | 768.417 | 1725670 | 53.8851 | 1713100 | 1500260 | 1466890 | 0 | 0 | 1446600 | 640.023 | 0 | 0 | 0 | 17126.7 | 1429470 | 660 | 1407200 | 1379059.125
5344 | 2005-08-11 15:00 | 614 | 867 | 80 | 35.45 | 4.58 | 0 | 38.0122 | 262.004 | 52.8106 | 0 | 614 | 524.134 | 85.6507 | 5.7527 | 524.134 | 80.1552 | 0.030027 | 506.984 | 77.1887 | 0.022626 | 566.67 | 566.667 | 1272590 | 48.5804 | 1241160 | 1112790 | 1087400 | 0 | 0 | 1076410 | 647.213 | 0 | 0 | 0 | 4373.4 | 1072040 | 660 | 1057640 | 1036483.3125
5345 | 2005-08-11 16:00 | 398 | 754 | 71 | 35.89 | 4.58 | 0 | 25.6836 | 271.002 | 67.2857 | 0 | 398 | 291.339 | 73.8359 | 3.729 | 291.339 | 69.0984 | 0.019464 | 268.181 | 66.5411 | 0.014666 | 324.695 | 324.691 | 729171 | 43.4135 | 686467 | 628502 | 613602 | 0 | 0 | 610047 | 644.622 | 0 | 0 | 0 | 4065.75 | 605982 | 660 | 598104 | 586141.6875
5346 | 2005-08-11 17:00 | 178 | 517 | 58 | 35.41 | 4.58 | 0 | 13.3801 | 279.143 | 81.6974 | 0 | 178 | 74.8806 | 53.7207 | 1.6677 | 74.8806 | 50.2739 | 0.0087049 | 52.6967 | 48.4133 | 0.0065594 | 98.0831 | 98.0817 | 220268 | 37.6827 | 189052 | 176823 | 172658 | 0 | 0 | 172343 | 612.94 | 0 | 0 | 0 | 15291.7 | 157052 | 659.999 | 152564 | 149512.5312
5347 | 2005-08-11 18:00 | 17 | 171 | 6 | 34.93 | 6.9 | 0 | 1.3534 | 287.306 | 90 | 0 | 17 | 0 | 4.6895 | 0.15928 | 0 | 4.3886 | 0.00083137 | 0 | 4.2262 | 0.00062646 | 4.1 | 4.1 | 9207.56 | 35.0118 | 3652.55 | 3541.34 | 3487.14 | 0 | 0 | 3486.88 | 428.014 | 0 | 0 | 0 | 3486.88 | 0 | 660 | 0 | 0
5348 | 2005-08-11 19:00 | 0 | 0 | 0 | 34.45 | 6.9 | 0
5349 | 2005-08-11 20:00 | 0 | 0 | 0 | 33.56 | 6.9 | 0
5350 | 2005-08-11 21:00 | 0 | 0 | 0 | 32.67 | 3.72 | 0
5351 | 2005-08-11 22:00 | 0 | 0 | 0 | 31.79 | 3.72 | 0
5352 | 2005-08-11 23:00 | 0 | 0 | 0 | 30.75 | 3.72 | 0
5353 | 2005-08-12 | 0 | 0 | 0 | 29.71 | 6.17 | 0
5354 | 2005-08-12 01:00 | 0 | 0 | 0 | 28.67 | 6.17 | 0
5355 | 2005-08-12 02:00 | 0 | 0 | 0 | 27.85 | 6.17 | 0
5356 | 2005-08-12 03:00 | 0 | 0 | 0 | 27.03 | 4.57 | 0
5357 | 2005-08-12 04:00 | 0 | 0 | 0 | 26.21 | 4.57 | 0
5358 | 2005-08-12 05:00 | 34 | 189 | 19 | 26.01 | 4.57 | 0 | 3.4737 | 74.3591 | 90 | 0 | 34 | 0 | 14.9626 | 0.31855 | 0 | 14.0025 | 0.0016627 | 0 | 13.4843 | 0.0012529 | 13.081 | 13.0804 | 29375.3 | 26.3133 | 18745.7 | 18613.1 | 18222.1 | 0 | 0 | 18217.7 | 545.827 | 0 | 0 | 0 | 14718.4 | 3499.34 | 660 | 3367.11 | 3299.7651
5359 | 2005-08-12 06:00 | 232 | 596 | 71 | 25.82 | 2.92 | 0 | 15.5624 | 82.4939 | 79.0492 | 0 | 232 | 114 | 67.4943 | 2.1737 | 101.826 | 63.1638 | 0.011346 | 80.1165 | 60.8261 | 0.0085493 | 136.723 | 136.706 | 307006 | 29.3532 | 271664 | 265666 | 249204 | 0 | 0 | 248613 | 649.737 | 0 | 0 | 0 | 394.664 | 248219 | 660 | 242567 | 237715.4531
5360 | 2005-08-12 07:00 | 437 | 750 | 86 | 25.63 | 2.92 | 0 | 27.8792 | 90.7557 | 64.6133 | 0 | 437 | 321.813 | 89.6941 | 4.0944 | 321.813 | 83.9392 | 0.021371 | 300.372 | 80.8326 | 0.016104 | 369.784 | 369.782 | 830438 | 35.1872 | 788508 | 752339 | 733620 | 0 | 0 | 729031 | 678.445 | 0 | 0 | 0 | 0 | 729031 | 678.445 | 718881 | 704503.8125
5361 | 2005-08-12 08:00 | 645 | 874 | 81 | 27.58 | 2.92 | 0 | 40.1627 | 100.101 | 50.1203 | 0 | 645 | 560.692 | 87.0148 | 6.0431 | 560.692 | 81.4317 | 0.031543 | 545.003 | 78.418 | 0.023768 | 604.741 | 604.736 | 1358080 | 43.2097 | 1329720 | 1224520 | 1194200 | 0 | 0 | 1181800 | 668.849 | 0 | 0 | 0 | 0 | 1181800 | 668.849 | 1164720 | 1141428.25
5362 | 2005-08-12 09:00 | 804 | 900 | 95 | 29.53 | 2.48 | 0 | 52.0212 | 112.244 | 35.6263 | 0 | 804 | 731.123 | 102.08 | 7.5328 | 731.123 | 95.5306 | 0.039319 | 722.705 | 91.9951 | 0.029628 | 790.288 | 790.284 | 1774780 | 50.561 | 1764560 | 1571470 | 1536380 | 0 | 0 | 1514930 | 651.831 | 0 | 0 | 0 | 2819.81 | 1512110 | 659.999 | 1487740 | 1457982.75
5363 | 2005-08-12 10:00 | 914 | 906 | 111 | 31.48 | 2.48 | 0 | 62.5809 | 130.926 | 21.2538 | 0 | 914 | 843.094 | 118.368 | 8.5635 | 843.094 | 110.773 | 0.044698 | 840.018 | 106.673 | 0.033681 | 918.323 | 918.319 | 2062320 | 55.9183 | 2066710 | 1794960 | 1755170 | 0 | 0 | 1726120 | 637.904 | 0 | 0 | 0 | 24042.3 | 1702070 | 660 | 1671400 | 1637972.25
5364 | 2005-08-12 11:00 | 987 | 953 | 97 | 32.44 | 2.48 | 0 | 69.4621 | 163.006 | 7.906 | 0 | 987 | 941.374 | 103.867 | 9.2474 | 941.374 | 97.2025 | 0.048268 | 940.923 | 93.6051 | 0.036371 | 1003.53 | 1003.52 | 2253650 | 59.1456 | 2268320 | 1940110 | 1898570 | 0 | 0 | 1863750 | 629.058 | 0 | 0 | 0 | 52284.3 | 1811470 | 660 | 1776840 | 1741305.75
5365 | 2005-08-12 12:00 | 983 | 952 | 98 | 33.4 | 3.32 | 0 | 68.6277 | 204.284 | 10.1438 | 0 | 983 | 935.499 | 104.941 | 9.2099 | 935.499 | 98.2074 | 0.048073 | 934.756 | 94.5728 | 0.036224 | 998.484 | 998.478 | 2242330 | 58.532 | 2256380 | 1935830 | 1894170 | 0 | 0 | 1859720 | 631.176 | 0 | 0 | 0 | 45628 | 1814090 | 660 | 1779360 | 1743776.625
5366 | 2005-08-12 13:00 | 913 | 941 | 93 | 34.36 | 3.32 | 0 | 60.7362 | 233.332 | 23.934 | 0 | 913 | 859.135 | 100.1 | 8.5541 | 859.135 | 93.677 | 0.04465 | 855.093 | 90.2101 | 0.033644 | 916.977 | 916.971 | 2059290 | 57.4405 | 2063520 | 1778460 | 1740750 | 0 | 0 | 1711650 | 632.233 | 0 | 0 | 0 | 38293.7 | 1673360 | 660 | 1643680 | 1610808.125
5367 | 2005-08-12 14:00 | 785 | 913 | 88 | 34.71 | 3.32 | 0 | 49.8073 | 250.308 | 38.3519 | 0 | 785 | 715.556 | 94.8753 | 7.3548 | 715.556 | 88.7879 | 0.03839 | 705.711 | 85.5019 | 0.028927 | 767.505 | 767.5 | 1723610 | 54.0282 | 1710940 | 1497270 | 1464120 | 0 | 0 | 1443870 | 639.164 | 0 | 0 | 0 | 18156 | 1425710 | 660 | 1403540 | 1375466
5368 | 2005-08-12 15:00 | 611 | 867 | 79 | 35.07 | 6.48 | 0 | 37.815 | 261.709 | 52.8565 | 0 | 611 | 523.93 | 84.7551 | 5.7246 | 523.93 | 79.3171 | 0.02988 | 506.742 | 76.3816 | 0.022516 | 565.651 | 565.648 | 1270300 | 46.6614 | 1238790 | 1121280 | 1095240 | 0 | 0 | 1084310 | 654.045 | 0 | 0 | 0 | 787.727 | 1083520 | 660 | 1068890 | 1047515.6875
5369 | 2005-08-12 16:00 | 405 | 763 | 76 | 35.42 | 6.48 | 0 | 25.4899 | 270.74 | 67.35 | 0 | 405 | 294.407 | 78.9164 | 3.7945 | 294.407 | 73.853 | 0.019806 | 270.903 | 71.1197 | 0.014924 | 331.776 | 331.77 | 745070 | 42.2187 | 702438 | 647143 | 631793 | 0 | 0 | 628096 | 650.917 | 0 | 0 | 0 | 1747.48 | 626349 | 660 | 618206 | 605842.125
5370 | 2005-08-12 17:00 | 177 | 512 | 60 | 34.67 | 6.48 | 0 | 13.1816 | 278.904 | 81.7796 | 0 | 177 | 73.3598 | 55.6996 | 1.6583 | 73.3598 | 52.1258 | 0.008656 | 51.3742 | 50.1967 | 0.0065225 | 98.5301 | 98.5292 | 221272 | 36.6891 | 189992 | 178680 | 174619 | 0 | 0 | 174301 | 615.91 | 0 | 0 | 0 | 12936.4 | 161365 | 660 | 156795 | 153659.3438
5371 | 2005-08-12 18:00 | 16 | 165 | 6 | 33.93 | 8.07 | 0 | 1.1436 | 287.084 | 90 | 0 | 16 | 0 | 4.7446 | 0.14991 | 0 | 4.4402 | 0.00078247 | 0 | 4.2758 | 0.0005896 | 4.1481 | 4.1478 | 9314.96 | 34.0068 | 3723.12 | 3620.66 | 3564.07 | 0 | 0 | 3563.8 | 432.134 | 0 | 0 | 0 | 3563.8 | 0 | 660 | 0 | 0
5372 | 2005-08-12 19:00 | 0 | 0 | 0 | 33.18 | 8.07 | 0
5373 | 2005-08-12 20:00 | 0 | 0 | 0 | 31.96 | 8.07 | 0
5374 | 2005-08-12 21:00 | 0 | 0 | 0 | 30.73 | 6.69 | 0
5375 | 2005-08-12 22:00 | 0 | 0 | 0 | 29.5 | 6.69 | 0
5376 | 2005-08-12 23:00 | 0 | 0 | 0 | 28.3 | 6.69 | 0
5377 | 2005-08-13 | 0 | 0 | 0 | 27.1 | 6.48 | 0
5378 | 2005-08-13 01:00 | 0 | 0 | 0 | 25.91 | 6.48 | 0
5379 | 2005-08-13 02:00 | 0 | 0 | 0 | 24.82 | 6.48 | 0
5380 | 2005-08-13 03:00 | 0 | 0 | 0 | 23.74 | 4.7 | 0
5381 | 2005-08-13 04:00 | 0 | 0 | 0 | 22.65 | 4.7 | 0
5382 | 2005-08-13 05:00 | 31 | 170 | 17 | 22.51 | 4.7 | 0 | 3.335 | 74.6338 | 90 | 0 | 31 | 0 | 13.187 | 0.29045 | 0 | 12.3409 | 0.001516 | 0 | 11.8841 | 0.0011424 | 11.5287 | 11.5283 | 25889.6 | 22.775 | 15989.6 | 16175.6 | 15851.3 | 0 | 0 | 15847.9 | 548.301 | 0 | 0 | 0 | 10871.9 | 4976.04 | 660 | 4788.44 | 4692.6738
5383 | 2005-08-13 06:00 | 220 | 597 | 60 | 22.37 | 3.56 | 0 | 15.4355 | 82.7845 | 79.0443 | 0 | 220 | 114.25 | 57.272 | 2.0612 | 101.614 | 53.5974 | 0.010759 | 79.961 | 51.6138 | 0.0081071 | 127.635 | 127.63 | 286622 | 25.532 | 252282 | 251419 | 234945 | 0 | 0 | 234436 | 662.4 | 0 | 0 | 0 | 297.964 | 234138 | 667.185 | 228476 | 223906.1094
5384 | 2005-08-13 07:00 | 439 | 786 | 73 | 22.23 | 3.56 | 0 | 27.756 | 91.0745 | 64.5903 | 0 | 439 | 337.22 | 76.9266 | 4.1131 | 337.22 | 71.9909 | 0.021469 | 314.786 | 69.3265 | 0.016177 | 372.605 | 372.601 | 836771 | 31.4611 | 794912 | 771849 | 752261 | 0 | 0 | 747609 | 690.728 | 0 | 0 | 0 | 0 | 747609 | 690.728 | 736742 | 722006.625
5385 | 2005-08-13 08:00 | 643 | 873 | 81 | 24.29 | 3.56 | 0 | 40.0324 | 100.466 | 50.0787 | 0 | 643 | 560.702 | 87.1456 | 6.0244 | 560.702 | 81.5542 | 0.031445 | 545.051 | 78.5359 | 0.023695 | 604.902 | 604.894 | 1358430 | 39.2762 | 1330090 | 1247850 | 1216970 | 0 | 0 | 1204570 | 681.913 | 0 | 0 | 0 | 0 | 1204570 | 681.913 | 1186380 | 1162653.75
5386 | 2005-08-13 09:00 | 790 | 836 | 133 | 26.35 | 0.59 | 0 | 51.867 | 112.676 | 35.5617 | 0 | 790 | 679.477 | 145.155 | 7.4017 | 679.477 | 135.842 | 0.038634 | 671.688 | 130.814 | 0.029112 | 778.455 | 778.452 | 1748200 | 49.8653 | 1736710 | 1551660 | 1514160 | 0 | 0 | 1493530 | 654.884 | 0 | 0 | 0 | 984.095 | 1492550 | 659.999 | 1468730 | 1439356.375
5387 | 2005-08-13 10:00 | 882 | 796 | 178 | 28.41 | 0.59 | 0 | 62.3745 | 131.421 | 21.1508 | 0 | 882 | 741.057 | 192.953 | 8.2637 | 741.057 | 180.572 | 0.043133 | 738.38 | 173.89 | 0.032502 | 884.933 | 884.926 | 1987310 | 55.1417 | 1987780 | 1732360 | 1693080 | 0 | 0 | 1666160 | 639.542 | 0 | 0 | 0 | 19636.5 | 1646520 | 660 | 1617760 | 1585406.25
5388 | 2005-08-13 11:00 | 988 | 918 | 132 | 29.67 | 0.59 | 0 | 69.1769 | 163.338 | 7.6773 | 0 | 988 | 907.61 | 139.293 | 9.2568 | 907.61 | 130.356 | 0.048317 | 907.199 | 125.531 | 0.036408 | 1001.78 | 1001.78 | 2249730 | 59.9316 | 2264190 | 1928680 | 1887000 | 0 | 0 | 1852350 | 627.145 | 0 | 0 | 0 | 61487.9 | 1790870 | 660 | 1757000 | 1721862.25
5389 | 2005-08-13 12:00 | 981 | 952 | 98 | 30.93 | 2.02 | 0 | 68.3263 | 204.105 | 10.0339 | 0 | 981 | 935.643 | 105.114 | 9.1912 | 935.643 | 98.3693 | 0.047975 | 934.916 | 94.7287 | 0.03615 | 998.79 | 998.782 | 2243010 | 58.3374 | 2257100 | 1938320 | 1896390 | 0 | 0 | 1861970 | 632.148 | 0 | 0 | 0 | 43529.6 | 1818440 | 660 | 1783550 | 1747882.75
5390 | 2005-08-13 13:00 | 903 | 926 | 98 | 32.19 | 2.02 | 0 | 60.4827 | 232.973 | 23.9271 | 0 | 903 | 845.568 | 105.385 | 8.4604 | 845.568 | 98.6232 | 0.04416 | 841.593 | 94.9732 | 0.033276 | 908.502 | 908.504 | 2040260 | 57.1201 | 2043490 | 1763810 | 1722860 | 0 | 0 | 1694640 | 636.067 | 0 | 0 | 0 | 33485.9 | 1661160 | 660 | 1631900 | 1599263.5
5391 | 2005-08-13 14:00 | 784 | 914 | 88 | 32.33 | 2.02 | 0 | 49.589 | 249.97 | 38.3797 | 0 | 784 | 716.567 | 95.0136 | 7.3455 | 716.567 | 88.9174 | 0.038341 | 706.691 | 85.6266 | 0.028891 | 768.576 | 768.57 | 1726010 | 53.4202 | 1713460 | 1504050 | 1473160 | 0 | 0 | 1452690 | 639.834 | 0 | 0 | 0 | 15975.5 | 1436710 | 659.999 | 1414270 | 1385987.25
5392 | 2005-08-13 15:00 | 608 | 866 | 79 | 32.47 | 3.62 | 0 | 37.6129 | 261.413 | 52.906 | 0 | 608 | 522.76 | 84.875 | 5.6965 | 522.76 | 79.4293 | 0.029734 | 505.561 | 76.4897 | 0.022405 | 564.611 | 564.604 | 1267960 | 46.4028 | 1236370 | 1120480 | 1094780 | 0 | 0 | 1083970 | 656.856 | 0 | 0 | 0 | 537.332 | 1083430 | 660 | 1068810 | 1047430.25
5393 | 2005-08-13 16:00 | 401 | 783 | 66 | 32.6 | 3.62 | 0 | 25.2917 | 270.478 | 67.4175 | 0 | 401 | 301.115 | 69.0925 | 3.7571 | 301.115 | 64.6594 | 0.019611 | 276.965 | 62.2664 | 0.014777 | 329.068 | 329.065 | 738994 | 40.7204 | 696332 | 646303 | 630707 | 0 | 0 | 627073 | 655.552 | 0 | 0 | 0 | 337.314 | 626736 | 660 | 618588 | 606216.6875
5394 | 2005-08-13 17:00 | 174 | 506 | 60 | 32.13 | 3.62 | 0 | 12.9789 | 278.664 | 81.8648 | 0 | 174 | 71.8283 | 55.8041 | 1.6302 | 71.8283 | 52.2236 | 0.0085093 | 50.0404 | 50.2909 | 0.0064119 | 97.3275 | 97.3244 | 218566 | 34.5317 | 187457 | 178362 | 174282 | 0 | 0 | 173972 | 622.636 | 0 | 0 | 0 | 8707.2 | 165264 | 660 | 160623 | 157410.7188
5395 | 2005-08-13 18:00 | 15 | 159 | 5 | 31.66 | 6.26 | 0 | 0.92958 | 286.861 | 90 | 0 | 15 | 0 | 3.8979 | 0.14054 | 0 | 3.6478 | 0.00073356 | 0 | 3.5128 | 0.00055276 | 3.408 | 3.4078 | 7653.05 | 31.7308 | 2661.69 | 2627.98 | 2596.38 | 0 | 0 | 2596.22 | 409.215 | 0 | 0 | 0 | 2596.22 | 0 | 660 | 0 | 0
5396 | 2005-08-13 19:00 | 0 | 0 | 0 | 31.19 | 6.26 | 0
5397 | 2005-08-13 20:00 | 0 | 0 | 0 | 30.26 | 6.26 | 0
5398 | 2005-08-13 21:00 | 0 | 0 | 0 | 29.32 | 4.69 | 0
5399 | 2005-08-13 22:00 | 0 | 0 | 0 | 28.39 | 4.69 | 0
5400 | 2005-08-13 23:00 | 0 | 0 | 0 | 27.31 | 4.69 | 0
5401 | 2005-08-14 | 0 | 0 | 0 | 26.24 | 3.4 | 0
5402 | 2005-08-14 01:00 | 0 | 0 | 0 | 25.17 | 3.4 | 0
5403 | 2005-08-14 02:00 | 0 | 0 | 0 | 24.24 | 3.4 | 0
5404 | 2005-08-14 03:00 | 0 | 0 | 0 | 23.31 | 5.86 | 0
5405 | 2005-08-14 04:00 | 0 | 0 | 0 | 22.38 | 5.86 | 0
5406 | 2005-08-14 05:00 | 27 | 129 | 17 | 22.29 | 5.86 | 0 | 3.1958 | 74.9128 | 90 | 0 | 27 | 0 | 13.1431 | 0.25297 | 0 | 12.2998 | 0.0013204 | 0 | 11.8446 | 0.00099496 | 11.4903 | 11.4899 | 25803.5 | 22.535 | 15922.1 | 16127.1 | 15792.1 | 0 | 0 | 15788.8 | 548.886 | 0 | 0 | 0 | 10616.6 | 5172.22 | 660 | 4977.28 | 4877.7354
5407 | 2005-08-14 06:00 | 222 | 524 | 83 | 22.2 | 1.13 | 0 | 15.3083 | 83.0795 | 79.0378 | 0 | 222 | 100.118 | 79.1238 | 2.08 | 88.6308 | 74.0471 | 0.010857 | 69.7582 | 71.3067 | 0.0081808 | 136.841 | 136.833 | 307287 | 26.1856 | 271846 | 270078 | 254197 | 0 | 0 | 253610 | 663.955 | 0 | 0 | 0 | 177.465 | 253432 | 666.373 | 247592 | 242640.2344
5408 | 2005-08-14 07:00 | 442 | 802 | 70 | 22.12 | 1.13 | 0 | 27.6321 | 91.3976 | 64.566 | 0 | 442 | 344.471 | 74.0647 | 4.1412 | 344.471 | 69.3126 | 0.021616 | 321.59 | 66.7474 | 0.016288 | 376.703 | 376.699 | 845966 | 33.0925 | 804215 | 774988 | 755879 | 0 | 0 | 751116 | 686.15 | 0 | 0 | 0 | 0 | 751116 | 686.15 | 740369 | 725561.5625
5409 | 2005-08-14 08:00 | 643 | 878 | 80 | 24.27 | 1.13 | 0 | 39.9008 | 100.835 | 50.0361 | 0 | 643 | 563.741 | 86.2567 | 6.0244 | 563.741 | 80.7223 | 0.031445 | 548.044 | 77.7349 | 0.023695 | 607.029 | 607.026 | 1363230 | 41.9514 | 1335060 | 1236830 | 1206090 | 0 | 0 | 1193640 | 673.867 | 0 | 0 | 0 | 0 | 1193640 | 673.867 | 1176070 | 1152547.125
5410 | 2005-08-14 09:00 | 810 | 921 | 88 | 26.41 | 6.52 | 0 | 51.7106 | 113.113 | 35.4968 | 0 | 810 | 748.912 | 95.1983 | 7.5891 | 748.912 | 89.0902 | 0.039612 | 740.364 | 85.7931 | 0.029849 | 801.402 | 801.401 | 1799740 | 42.7905 | 1790750 | 1655420 | 1614940 | 0 | 0 | 1593080 | 678.803 | 0 | 0 | 0 | 0 | 1593080 | 678.803 | 1565500 | 1534192.375
5411 | 2005-08-14 10:00 | 902 | 854 | 148 | 28.56 | 6.52 | 0 | 62.1648 | 131.919 | 21.0487 | 0 | 902 | 795.764 | 163.09 | 8.451 | 795.764 | 152.626 | 0.044111 | 792.92 | 146.977 | 0.033239 | 911.733 | 911.726 | 2047500 | 47.1955 | 2051110 | 1858870 | 1815220 | 0 | 0 | 1786750 | 667.763 | 0 | 0 | 0 | 0 | 1786750 | 667.763 | 1752880 | 1717825.625
5412 | 2005-08-14 11:00 | 986 | 953 | 99 | 29.64 | 6.52 | 0 | 68.888 | 163.671 | 7.4502 | 0 | 986 | 942.794 | 106.262 | 9.238 | 942.794 | 99.4444 | 0.048219 | 942.393 | 95.764 | 0.036334 | 1007.05 | 1007.04 | 2261570 | 50.2238 | 2276670 | 2035260 | 1989080 | 0 | 0 | 1954360 | 660.757 | 0 | 0 | 0 | 9.54 | 1954350 | 661.156 | 1914200 | 1875915
5413 | 2005-08-14 12:00 | 979 | 952 | 98 | 30.71 | 4.23 | 0 | 68.0203 | 203.933 | 9.9326 | 0 | 979 | 935.813 | 105.289 | 9.1725 | 935.813 | 98.5331 | 0.047877 | 935.101 | 94.8864 | 0.036076 | 999.123 | 999.121 | 2243770 | 54.3969 | 2257900 | 1977660 | 1932870 | 0 | 0 | 1898570 | 645.693 | 0 | 0 | 0 | 11412.6 | 1887160 | 660 | 1849660 | 1812663
5414 | 2005-08-14 13:00 | 910 | 941 | 94 | 31.79 | 4.23 | 0 | 60.2239 | 232.618 | 23.9257 | 0 | 910 | 859.339 | 101.44 | 8.526 | 859.339 | 94.9313 | 0.044503 | 855.299 | 91.418 | 0.033534 | 918.348 | 918.344 | 2062360 | 53.5618 | 2066750 | 1816240 | 1774960 | 0 | 0 | 1745950 | 646.148 | 0 | 0 | 0 | 9404.46 | 1736540 | 660 | 1704650 | 1670556.375
5415 | 2005-08-14 14:00 | 781 | 913 | 88 | 31.52 | 4.23 | 0 | 49.3655 | 249.633 | 38.4117 | 0 | 781 | 715.544 | 95.1538 | 7.3174 | 715.544 | 89.0485 | 0.038194 | 705.662 | 85.7529 | 0.02878 | 767.7 | 767.7 | 1724060 | 49.7204 | 1711420 | 1530070 | 1492950 | 0 | 0 | 1472920 | 655.78 | 0 | 0 | 0 | 972.339 | 1471950 | 660 | 1448650 | 1419673.25
5416 | 2005-08-14 15:00 | 605 | 670 | 198 | 31.25 | 6.88 | 0 | 37.4061 | 261.117 | 52.9591 | 0 | 605 | 403.599 | 203.788 | 5.6684 | 403.599 | 190.713 | 0.029587 | 390.279 | 183.655 | 0.022294 | 556.738 | 556.729 | 1250270 | 42.3708 | 1218090 | 1125640 | 1097770 | 0 | 0 | 1087250 | 668.331 | 0 | 0 | 0 | 0 | 1087250 | 668.331 | 1072140 | 1050695.25
5417 | 2005-08-14 16:00 | 199 | 57 | 175 | 30.98 | 6.88 | 0 | 25.089 | 270.214 | 67.4884 | 0 | 199 | 21.6706 | 177.522 | 1.8645 | 21.6706 | 166.132 | 0.0097319 | 19.9241 | 159.984 | 0.0073332 | 174.518 | 174.504 | 391892 | 34.4658 | 353004 | 336875 | 328483 | 0 | 0 | 327480 | 651.286 | 0 | 0 | 0 | 981.023 | 326499 | 660 | 320488 | 314078.6875
5418 | 2005-08-14 17:00 | 158 | 236 | 105 | 30.84 | 6.88 | 0 | 12.7719 | 278.423 | 81.9531 | 0 | 158 | 33.5602 | 93.8138 | 1.4803 | 33.5602 | 87.7945 | 0.0077269 | 23.251 | 84.5453 | 0.0058223 | 104.568 | 104.564 | 234824 | 32.9287 | 202721 | 194602 | 189857 | 0 | 0 | 189500 | 631.795 | 0 | 0 | 0 | 5003.05 | 184497 | 660 | 179529 | 175938.3438
5419 | 2005-08-14 18:00 | 13 | 72 | 9 | 30.69 | 5.53 | 0 | 0.7115 | 286.635 | 90 | 0 | 13 | 0 | 7.1127 | 0.1218 | 0 | 6.6563 | 0.00063575 | 0 | 6.41 | 0.00047905 | 6.2181 | 6.2177 | 13963.5 | 30.8254 | 6949.7 | 6770.39 | 6640.52 | 0 | 0 | 6639.78 | 484.134 | 0 | 0 | 0 | 6639.78 | 0 | 660 | 0 | 0
5420 | 2005-08-14 19:00 | 0 | 0 | 0 | 30.54 | 5.53 | 0
5421 | 2005-08-14 20:00 | 0 | 0 | 0 | 30.02 | 5.53 | 0
5422 | 2005-08-14 21:00 | 0 | 0 | 0 | 29.51 | 5.82 | 0
5423 | 2005-08-14 22:00 | 0 | 0 | 0 | 28.99 | 5.82 | 0
5424 | 2005-08-14 23:00 | 0 | 0 | 0 | 28.42 | 5.82 | 0
5425 | 2005-08-15 | 0 | 0 | 0 | 27.86 | 1.42 | 0
5426 | 2005-08-15 01:00 | 0 | 0 | 0 | 27.29 | 1.42 | 0
5427 | 2005-08-15 02:00 | 0 | 0 | 0 | 26.63 | 1.42 | 0
5428 | 2005-08-15 03:00 | 0 | 0 | 0 | 25.97 | 4.54 | 0
5429 | 2005-08-15 04:00 | 0 | 0 | 0 | 25.31 | 4.54 | 0
5430 | 2005-08-15 05:00 | 30 | 184 | 16 | 24.89 | 4.54 | 0 | 3.0564 | 75.1963 | 90 | 0 | 30 | 0 | 12.4447 | 0.28108 | 0 | 11.6462 | 0.0014671 | 0 | 11.2152 | 0.0011055 | 10.8798 | 10.8791 | 24431.7 | 25.1427 | 14848.8 | 14837.5 | 14539.6 | 0 | 0 | 14536.7 | 536.05 | 0 | 0 | 0 | 13771.9 | 764.758 | 660 | 735.734 | 721.0197
5431 | 2005-08-15 06:00 | 226 | 628 | 61 | 24.47 | 5.92 | 0 | 15.1805 | 83.3786 | 79.0299 | 0 | 226 | 119.907 | 58.5368 | 2.1174 | 105.622 | 54.781 | 0.011052 | 83.1508 | 52.7536 | 0.0083282 | 131.835 | 131.828 | 296049 | 27.2704 | 261329 | 258223 | 240031 | 0 | 0 | 239486 | 654.241 | 0 | 0 | 0 | 369.234 | 239117 | 663.389 | 233499 | 228828.8125
5432 | 2005-08-15 07:00 | 440 | 801 | 70 | 24.04 | 5.92 | 0 | 27.5073 | 91.7249 | 64.5406 | 0 | 440 | 344.372 | 74.2237 | 4.1225 | 344.372 | 69.4613 | 0.021518 | 321.536 | 66.8906 | 0.016214 | 376.789 | 376.787 | 846170 | 32.0439 | 804423 | 779014 | 758836 | 0 | 0 | 754084 | 689.254 | 0 | 0 | 0 | 0 | 754084 | 689.254 | 743177 | 728313.8125
5433 | 2005-08-15 08:00 | 641 | 878 | 79 | 24.75 | 5.92 | 0 | 39.7678 | 101.208 | 49.9927 | 0 | 641 | 564.818 | 85.3657 | 6.0057 | 564.818 | 79.8885 | 0.031348 | 549.13 | 76.9318 | 0.023621 | 607.303 | 607.298 | 1363840 | 37.6505 | 1335700 | 1262660 | 1231780 | 0 | 0 | 1219280 | 687.363 | 0 | 0 | 0 | 0 | 1219280 | 687.363 | 1200530 | 1176515.5
5434 | 2005-08-15 09:00 | 808 | 921 | 87 | 25.46 | 4.36 | 0 | 51.5521 | 113.553 | 35.4318 | 0 | 808 | 750.122 | 94.3107 | 7.5703 | 750.122 | 88.2595 | 0.039515 | 741.597 | 84.9931 | 0.029775 | 801.822 | 801.818 | 1800680 | 44.3082 | 1791730 | 1644560 | 1605090 | 0 | 0 | 1583180 | 674.077 | 0 | 0 | 0 | 0 | 1583180 | 674.077 | 1556070 | 1524948.875
5435 | 2005-08-15 10:00 | 926 | 944 | 94 | 26.17 | 4.36 | 0 | 61.9519 | 132.418 | 20.9476 | 0 | 926 | 880.413 | 101.542 | 8.6759 | 880.413 | 95.0267 | 0.045285 | 877.298 | 91.5098 | 0.034123 | 939.777 | 939.774 | 2110490 | 48.261 | 2117430 | 1909640 | 1864810 | 0 | 0 | 1834500 | 663.937 | 0 | 0 | 0 | 0 | 1834500 | 663.937 | 1798950 | 1762969.375
5436 | 2005-08-15 11:00 | 984 | 953 | 99 | 27.01 | 4.36 | 0 | 68.5954 | 164.003 | 7.2253 | 0 | 984 | 943.016 | 106.441 | 9.2193 | 943.016 | 99.6117 | 0.048122 | 942.638 | 95.9251 | 0.036261 | 1007.44 | 1007.44 | 2262440 | 50.6916 | 2277590 | 2031430 | 1982350 | 0 | 0 | 1947690 | 658.607 | 0 | 0 | 0 | -14.4422 | 1947700 | 660.393 | 1907820 | 1869661.125
5437 | 2005-08-15 12:00 | 977 | 850 | 192 | 27.84 | 3.99 | 0 | 67.7098 | 203.767 | 9.8407 | 0 | 977 | 835.914 | 208.763 | 9.1537 | 835.914 | 195.368 | 0.047779 | 835.29 | 188.138 | 0.036003 | 992.76 | 992.754 | 2229480 | 51.7493 | 2242840 | 1989960 | 1941660 | 0 | 0 | 1908120 | 656.258 | 0 | 0 | 0 | 1284.93 | 1906830 | 660 | 1868570 | 1831194.375
5438 | 2005-08-15 13:00 | 591 | 238 | 385 | 28.68 | 3.99 | 0 | 59.9599 | 232.267 | 23.93 | 0 | 591 | 217.51 | 394.079 | 5.5372 | 217.51 | 368.795 | 0.028902 | 216.487 | 355.146 | 0.021778 | 554.505 | 554.501 | 1245270 | 42.0345 | 1212940 | 1122590 | 1096060 | 0 | 0 | 1085630 | 669.46 | 0 | 0 | 0 | 0 | 1085630 | 669.46 | 1070490 | 1049077.5
5439 | 2005-08-15 14:00 | 771 | 588 | 327 | 29.15 | 3.99 | 0 | 49.137 | 249.296 | 38.448 | 0 | 771 | 459.791 | 335.508 | 7.2237 | 459.791 | 313.982 | 0.037705 | 453.426 | 302.361 | 0.028412 | 733.141 | 733.125 | 1646410 | 46.8064 | 1630160 | 1477570 | 1442230 | 0 | 0 | 1423850 | 661.588 | 0 | 0 | 0 | -6.5885 | 1423860 | 661.635 | 1401660 | 1373626.125
5440 | 2005-08-15 15:00 | 320 | 91 | 265 | 29.61 | 5.24 | 0 | 37.1946 | 260.82 | 53.0159 | 0 | 320 | 54.7334 | 272.768 | 2.9981 | 54.7334 | 255.267 | 0.015649 | 52.921 | 245.82 | 0.011792 | 289.79 | 289.774 | 650760 | 36.0421 | 608008 | 577061 | 562028 | 0 | 0 | 559220 | 664.994 | 0 | 0 | 0 | 0 | 559220 | 664.994 | 551682 | 540648.5
5441 | 2005-08-15 16:00 | 389 | 564 | 151 | 30.08 | 5.24 | 0 | 24.882 | 269.948 | 67.5625 | 0 | 389 | 215.897 | 148.061 | 3.6446 | 215.897 | 138.561 | 0.019024 | 198.409 | 133.433 | 0.014335 | 321.9 | 321.892 | 722889 | 37.2251 | 680164 | 642198 | 626656 | 0 | 0 | 623194 | 668.044 | 0 | 0 | 0 | 0 | 623194 | 668.044 | 614842 | 602544.875
5442 | 2005-08-15 17:00 | 165 | 498 | 56 | 29.67 | 5.24 | 0 | 12.5607 | 278.18 | 82.0444 | 0 | 165 | 69.3704 | 52.2477 | 1.5459 | 69.3704 | 48.8954 | 0.0080692 | 47.7785 | 47.0858 | 0.0060803 | 92.0243 | 92.0227 | 206660 | 31.7126 | 176329 | 170290 | 166221 | 0 | 0 | 165946 | 630.513 | 0 | 0 | 0 | 4989.74 | 160956 | 660 | 156394 | 153266.3906
5443 | 2005-08-15 18:00 | 13 | 147 | 5 | 29.26 | 3.41 | 0 | 0.48939 | 286.408 | 90 | 0 | 13 | 0 | 4.0027 | 0.1218 | 0 | 3.7459 | 0.00063575 | 0 | 3.6073 | 0.00047905 | 3.4995 | 3.4994 | 7858.83 | 29.3476 | 2789.07 | 2765.68 | 2730.71 | 0 | 0 | 2730.54 | 419.475 | 0 | 0 | 0 | 2730.54 | 0 | 660 | 0 | 0
5444 | 2005-08-15 19:00 | 0 | 0 | 0 | 28.85 | 3.41 | 0
5445 | 2005-08-15 20:00 | 0 | 0 | 0 | 28.57 | 3.41 | 0
5446 | 2005-08-15 21:00 | 0 | 0 | 0 | 28.29 | 3.74 | 0
5447 | 2005-08-15 22:00 | 0 | 0 | 0 | 28.01 | 3.74 | 0
5448 | 2005-08-15 23:00 | 0 | 0 | 0 | 27.52 | 3.74 | 0
5449 | 2005-08-16 | 0 | 0 | 0 | 27.02 | 3.05 | 0
5450 | 2005-08-16 01:00 | 0 | 0 | 0 | 26.53 | 3.05 | 0
5451 | 2005-08-16 02:00 | 0 | 0 | 0 | 25.93 | 3.05 | 0
5452 | 2005-08-16 03:00 | 0 | 0 | 0 | 25.32 | 3.38 | 0
5453 | 2005-08-16 04:00 | 0 | 0 | 0 | 24.72 | 3.38 | 0
5454 | 2005-08-16 05:00 | 29 | 207 | 13 | 24.51 | 3.38 | 0 | 2.9166 | 75.4839 | 90 | 0 | 29 | 0 | 9.8099 | 0.27171 | 0 | 9.1805 | 0.0014182 | 0 | 8.8407 | 0.0010687 | 8.5765 | 8.5759 | 19259.4 | 24.725 | 10871.2 | 10885.6 | 10676.4 | 0 | 0 | 10674.8 | 526.059 | 0 | 0 | 0 | 10674.8 | 0 | 660 | 0 | 0
5455 | 2005-08-16 06:00 | 213 | 587 | 60 | 24.3 | 2.65 | 0 | 15.0523 | 83.6819 | 79.0206 | 0 | 213 | 112.205 | 57.7518 | 1.9956 | 98.3362 | 54.0463 | 0.010417 | 77.437 | 52.0461 | 0.0078491 | 125.606 | 125.587 | 282030 | 27.6045 | 247947 | 244547 | 227894 | 0 | 0 | 227399 | 651.918 | 0 | 0 | 0 | 1067.25 | 226332 | 661.194 | 220883 | 216465.4219
5456 | 2005-08-16 07:00 | 417 | 705 | 92 | 24.09 | 2.65 | 0 | 27.3818 | 92.0563 | 64.5139 | 0 | 417 | 304.065 | 95.6916 | 3.907 | 304.065 | 89.5518 | 0.020393 | 283.936 | 86.2376 | 0.015367 | 359.083 | 359.08 | 806402 | 33.5384 | 764222 | 734788 | 716663 | 0 | 0 | 712337 | 682.697 | 0 | 0 | 0 | 0 | 712337 | 682.697 | 702268 | 688222.4375
5457 | 2005-08-16 08:00 | 640 | 839 | 105 | 25.28 | 2.65 | 0 | 39.6335 | 101.585 | 49.9486 | 0 | 640 | 539.698 | 113.953 | 5.9963 | 539.698 | 106.641 | 0.031299 | 524.746 | 102.694 | 0.023584 | 608.64 | 608.634 | 1366830 | 41.2949 | 1338800 | 1244200 | 1212900 | 0 | 0 | 1200420 | 676.866 | 0 | 0 | 0 | 0 | 1200420 | 676.866 | 1182560 | 1158910.75
5458 | 2005-08-16 09:00 | 802 | 910 | 91 | 26.47 | 0.85 | 0 | 51.3913 | 113.998 | 35.3666 | 0 | 802 | 741.972 | 98.586 | 7.5141 | 741.972 | 92.2605 | 0.039221 | 733.576 | 88.846 | 0.029554 | 797.779 | 797.776 | 1791610 | 50.1499 | 1782220 | 1590470 | 1551760 | 0 | 0 | 1530100 | 655.025 | 0 | 0 | 0 | 1096.49 | 1529000 | 660 | 1504090 | 1474012
5459 | 2005-08-16 10:00 | 898 | 852 | 149 | 27.66 | 0.85 | 0 | 61.7357 | 132.919 | 20.8479 | 0 | 898 | 794.714 | 164.666 | 8.4136 | 794.714 | 154.101 | 0.043916 | 791.93 | 148.398 | 0.033092 | 912.15 | 912.148 | 2048450 | 54.7348 | 2052120 | 1792650 | 1754650 | 0 | 0 | 1725850 | 640.686 | 0 | 0 | 0 | 17447.8 | 1708400 | 660 | 1677500 | 1643953.125
5460 | 2005-08-16 11:00 | 982 | 953 | 99 | 28.36 | 0.85 | 0 | 68.299 | 164.335 | 7.0036 | 0 | 982 | 943.264 | 106.622 | 9.2006 | 943.264 | 99.7807 | 0.048024 | 942.909 | 96.0879 | 0.036187 | 1007.86 | 1007.86 | 2263390 | 58.2757 | 2278590 | 1957520 | 1914350 | 0 | 0 | 1879370 | 632.987 | 0 | 0 | 0 | 41968.2 | 1837400 | 660 | 1801800 | 1765768.5
5461 | 2005-08-16 12:00 | 976 | 953 | 98 | 29.05 | 4.1 | 0 | 67.395 | 203.609 | 9.7588 | 0 | 976 | 937.302 | 105.644 | 9.1444 | 937.302 | 98.8658 | 0.047731 | 936.614 | 95.2068 | 0.035966 | 1000.9 | 1000.9 | 2247760 | 52.982 | 2262100 | 1995220 | 1950790 | 0 | 0 | 1916250 | 649.528 | 0 | 0 | 0 | 5335.11 | 1910920 | 660 | 1872490 | 1835042.25
5462 | 2005-08-16 13:00 | 904 | 940 | 93 | 29.74 | 4.1 | 0 | 59.6907 | 231.92 | 23.9399 | 0 | 904 | 858.588 | 100.728 | 8.4698 | 858.588 | 94.2653 | 0.044209 | 854.548 | 90.7766 | 0.033313 | 916.997 | 916.995 | 2059340 | 51.6659 | 2063570 | 1830390 | 1787520 | 0 | 0 | 1758820 | 654.227 | 0 | 0 | 0 | 2692.5 | 1756130 | 660 | 1723530 | 1689058.625
5463 | 2005-08-16 14:00 | 775 | 912 | 88 | 30.14 | 4.1 | 0 | 48.9036 | 248.96 | 38.4886 | 0 | 775 | 713.553 | 95.4395 | 7.2611 | 713.553 | 89.316 | 0.037901 | 703.65 | 86.0104 | 0.028559 | 765.998 | 765.993 | 1720220 | 48.4553 | 1707400 | 1535870 | 1498920 | 0 | 0 | 1478900 | 658.751 | 0 | 0 | 0 | 49.3253 | 1478850 | 660.129 | 1455370 | 1426265.75
5464 | 2005-08-16 15:00 | 595 | 855 | 81 | 30.53 | 5.47 | 0 | 36.9785 | 260.522 | 53.0763 | 0 | 595 | 513.347 | 87.2823 | 5.5747 | 513.347 | 81.6821 | 0.029098 | 496.289 | 78.6591 | 0.021926 | 557.721 | 557.717 | 1252490 | 42.7266 | 1220380 | 1125840 | 1099740 | 0 | 0 | 1089190 | 668.371 | 0 | 0 | 0 | 0 | 1089190 | 668.371 | 1074040 | 1052555
5465 | 2005-08-16 16:00 | 375 | 723 | 73 | 30.92 | 5.47 | 0 | 24.6707 | 269.682 | 67.6398 | 0 | 375 | 275.248 | 76.4585 | 3.5135 | 275.248 | 71.5528 | 0.018339 | 252.834 | 68.9047 | 0.013819 | 312.1 | 312.098 | 700894 | 37.7452 | 658108 | 619689 | 604879 | 0 | 0 | 601608 | 663.089 | 0 | 0 | 0 | 0 | 601608 | 663.089 | 593692 | 581818.5
5466 | 2005-08-16 17:00 | 162 | 492 | 56 | 30.51 | 5.47 | 0 | 12.3455 | 277.936 | 82.1386 | 0 | 162 | 67.8109 | 52.3497 | 1.5178 | 67.8109 | 48.9908 | 0.0079225 | 46.4126 | 47.1777 | 0.0059698 | 90.7884 | 90.7846 | 203879 | 32.4953 | 173735 | 167079 | 163267 | 0 | 0 | 162999 | 626.681 | 0 | 0 | 0 | 6363.88 | 156635 | 660 | 152155 | 149111.6094
5467 | 2005-08-16 18:00 | 12 | 141 | 4 | 30.1 | 5.2 | 0 | 0.26333 | 286.18 | 90 | 0 | 12 | 0 | 3.1439 | 0.11243 | 0 | 2.9422 | 0.00058685 | 0 | 2.8333 | 0.0004422 | 2.7487 | 2.7486 | 6172.55 | 30.1612 | 1795.83 | 1791.1 | 1774.51 | 0 | 0 | 1774.42 | 374.476 | 0 | 0 | 0 | 1774.42 | 0 | 660 | 0 | 0
5468 | 2005-08-16 19:00 | 0 | 0 | 0 | 29.68 | 5.2 | 0
5469 | 2005-08-16 20:00 | 0 | 0 | 0 | 29.05 | 5.2 | 0
5470 | 2005-08-16 21:00 | 0 | 0 | 0 | 28.41 | 4.04 | 0
5471 | 2005-08-16 22:00 | 0 | 0 | 0 | 27.77 | 4.04 | 0
5472 | 2005-08-16 23:00 | 0 | 0 | 0 | 27.01 | 4.04 | 0
5473 | 2005-08-17 | 0 | 0 | 0 | 26.26 | 3.32 | 0
5474 | 2005-08-17 01:00 | 0 | 0 | 0 | 25.5 | 3.32 | 0
5475 | 2005-08-17 02:00 | 0 | 0 | 0 | 24.86 | 3.32 | 0
5476 | 2005-08-17 03:00 | 0 | 0 | 0 | 24.22 | 2.26 | 0
5477 | 2005-08-17 04:00 | 0 | 0 | 0 | 23.58 | 2.26 | 0
5478 | 2005-08-17 05:00 | 27 | 195 | 12 | 23.68 | 2.26 | 0 | 2.7765 | 75.7757 | 90 | 0 | 27 | 0 | 8.9976 | 0.25297 | 0 | 8.4203 | 0.0013204 | 0 | 8.1087 | 0.00099496 | 7.8664 | 7.8659 | 17664.8 | 23.8924 | 9671.23 | 9721.97 | 9535.59 | 0 | 0 | 9534.27 | 522.714 | 0 | 0 | 0 | 9534.27 | 0 | 660 | 0 | 0
5479 | 2005-08-17 06:00 | 215 | 617 | 55 | 23.77 | 4.83 | 0 | 14.9236 | 83.9892 | 79.0099 | 0 | 215 | 118.442 | 53.1582 | 2.0144 | 103.252 | 49.7474 | 0.010514 | 81.3344 | 47.9063 | 0.0079228 | 125.371 | 125.365 | 281531 | 26.6279 | 247556 | 245354 | 227517 | 0 | 0 | 227029 | 656.387 | 0 | 0 | 0 | 1181.92 | 225847 | 663.947 | 220364 | 215956.8281
5480 | 2005-08-17 07:00 | 433 | 790 | 71 | 23.87 | 4.83 | 0 | 27.2555 | 92.3916 | 64.4862 | 0 | 433 | 340.476 | 75.5616 | 4.0569 | 340.443 | 70.7134 | 0.021175 | 317.946 | 68.0963 | 0.015956 | 374.477 | 374.474 | 840975 | 32.4067 | 799165 | 772595 | 752744 | 0 | 0 | 748039 | 687.184 | 0 | 0 | 0 | 0 | 748039 | 687.184 | 737298 | 722551.6875
5481 | 2005-08-17 08:00 | 638 | 878 | 80 | 25.28 | 4.83 | 0 | 39.4978 | 101.967 | 49.9037 | 0 | 638 | 565.04 | 86.6633 | 5.9776 | 565.04 | 81.1028 | 0.031201 | 549.428 | 78.1013 | 0.023511 | 608.726 | 608.723 | 1367030 | 39.1567 | 1339010 | 1256970 | 1225940 | 0 | 0 | 1213390 | 682.731 | 0 | 0 | 0 | 0 | 1213390 | 682.731 | 1194980 | 1171077.625
5482 | 2005-08-17 09:00 | 805 | 921 | 87 | 26.68 | 3.51 | 0 | 51.2283 | 114.446 | 35.3015 | 0 | 805 | 751.59 | 94.6037 | 7.5422 | 751.59 | 88.5337 | 0.039368 | 743.124 | 85.2571 | 0.029664 | 803.558 | 803.55 | 1804570 | 46.6536 | 1795810 | 1630080 | 1590530 | 0 | 0 | 1568520 | 665.943 | 0 | 0 | 0 | 0 | 1568520 | 665.943 | 1542150 | 1511308.25
5483 | 2005-08-17 10:00 | 896 | 851 | 149 | 28.09 | 3.51 | 0 | 61.5163 | 133.421 | 20.7497 | 0 | 896 | 794.75 | 164.947 | 8.3948 | 794.75 | 154.364 | 0.043818 | 791.994 | 148.651 | 0.033018 | 912.457 | 912.455 | 2049140 | 50.7706 | 2052840 | 1828700 | 1786010 | 0 | 0 | 1757490 | 655.125 | 0 | 0 | 0 | 769.177 | 1756720 | 660 | 1724100 | 1689621.375
5484 | 2005-08-17 11:00 | 967 | 893 | 141 | 28.78 | 3.51 | 0 | 67.9991 | 164.666 | 6.7859 | 0 | 967 | 884.634 | 149.15 | 9.06 | 884.634 | 139.581 | 0.04729 | 884.322 | 134.415 | 0.035634 | 988.21 | 988.2 | 2219250 | 53.3433 | 2232040 | 1964950 | 1920190 | 0 | 0 | 1886600 | 648.958 | 0 | 0 | 0 | 6714.34 | 1879890 | 660 | 1842670 | 1805813.375
5485 | 2005-08-17 12:00 | 934 | 832 | 169 | 29.49 | 3.99 | 0 | 67.0759 | 203.457 | 9.6874 | 0 | 934 | 818.755 | 186.423 | 8.7508 | 818.755 | 174.462 | 0.045677 | 818.163 | 168.005 | 0.034418 | 956.617 | 956.611 | 2148300 | 52.5288 | 2157270 | 1906180 | 1864990 | 0 | 0 | 1833390 | 649.785 | 0 | 0 | 0 | 5088.67 | 1828300 | 660 | 1793050 | 1757187
5486 | 2005-08-17 13:00 | 902 | 899 | 129 | 30.18 | 3.99 | 0 | 59.4165 | 231.577 | 23.9557 | 0 | 902 | 820.563 | 137.453 | 8.451 | 820.563 | 128.634 | 0.044111 | 816.696 | 123.873 | 0.033239 | 912.385 | 912.376 | 2048970 | 52.1535 | 2052660 | 1816270 | 1776320 | 0 | 0 | 1747570 | 649.734 | 0 | 0 | 0 | 4727.73 | 1742850 | 660 | 1710730 | 1676512.125
5487 | 2005-08-17 14:00 | 772 | 911 | 88 | 30.62 | 3.99 | 0 | 48.6652 | 248.625 | 38.5336 | 0 | 772 | 712.586 | 95.5851 | 7.233 | 712.586 | 89.4522 | 0.037754 | 702.667 | 86.1416 | 0.028448 | 765.172 | 765.168 | 1718380 | 49.0481 | 1705470 | 1529700 | 1493790 | 0 | 0 | 1473790 | 656.643 | 0 | 0 | 0 | 411.905 | 1473380 | 660 | 1450040 | 1421043
5488 | 2005-08-17 15:00 | 596 | 863 | 79 | 31.06 | 5.64 | 0 | 36.7579 | 260.224 | 53.1404 | 0 | 596 | 518.229 | 85.3705 | 5.5841 | 518.229 | 79.8929 | 0.029147 | 500.944 | 76.9362 | 0.021963 | 560.565 | 560.558 | 1258870 | 43.1847 | 1226970 | 1129470 | 1102470 | 0 | 0 | 1091800 | 666.208 | 0 | 0 | 0 | 0 | 1091800 | 666.208 | 1076690 | 1055158.75
5489 | 2005-08-17 16:00 | 371 | 713 | 75 | 31.5 | 5.64 | 0 | 24.4552 | 269.414 | 67.7204 | 0 | 371 | 271.079 | 78.5746 | 3.476 | 271.079 | 73.5331 | 0.018143 | 248.883 | 70.8117 | 0.013671 | 310.117 | 310.115 | 696437 | 38.2077 | 653644 | 614059 | 598914 | 0 | 0 | 595702 | 662.72 | 0 | 0 | 0 | -13.393 | 595716 | 662.99 | 587869 | 576111.4375
5490 | 2005-08-17 17:00 | 159 | 483 | 57 | 31.12 | 5.64 | 0 | 12.1263 | 277.69 | 82.2357 | 0 | 159 | 65.5979 | 53.3961 | 1.4897 | 65.5979 | 49.9701 | 0.0077758 | 44.5998 | 48.1208 | 0.0058592 | 89.9446 | 89.9427 | 201988 | 33.0654 | 171973 | 164874 | 161025 | 0 | 0 | 160761 | 624.066 | 0 | 0 | 0 | 7307.11 | 153454 | 660 | 149036 | 146055.3125
5491 | 2005-08-17 18:00 | 11 | 133 | 4 | 30.74 | 6.88 | 0 | 0.033422 | 285.949 | 90 | 0 | 11 | 0 | 3.1932 | 0.10306 | 0 | 2.9884 | 0.00053795 | 0 | 2.8778 | 0.00040535 | 2.7918 | 2.7917 | 6269.44 | 30.7958 | 1849.33 | 1842.63 | 1825.17 | 0 | 0 | 1825.07 | 376.516 | 0 | 0 | 0 | 1825.07 | 0 | 660 | 0 | 0
5492 | 2005-08-17 19:00 | 0 | 0 | 0 | 30.36 | 6.88 | 0
5493 | 2005-08-17 20:00 | 0 | 0 | 0 | 29.49 | 6.88 | 0
5494 | 2005-08-17 21:00 | 0 | 0 | 0 | 28.61 | 7.94 | 0
5495 | 2005-08-17 22:00 | 0 | 0 | 0 | 27.74 | 7.94 | 0
5496 | 2005-08-17 23:00 | 0 | 0 | 0 | 26.88 | 7.94 | 0
5497 | 2005-08-18 | 0 | 0 | 0 | 26.01 | 7.04 | 0
5498 | 2005-08-18 01:00 | 0 | 0 | 0 | 25.15 | 7.04 | 0
5499 | 2005-08-18 02:00 | 0 | 0 | 0 | 24.67 | 7.04 | 0
5500 | 2005-08-18 03:00 | 0 | 0 | 0 | 24.19 | 4.36 | 0
5501 | 2005-08-18 04:00 | 0 | 0 | 0 | 23.71 | 4.36 | 0
5502 | 2005-08-18 05:00 | 25 | 165 | 13 | 23.47 | 4.36 | 0 | 2.6362 | 76.0715 | 90 | 0 | 25 | 0 | 9.9485 | 0.23423 | 0 | 9.3102 | 0.0012226 | 0 | 8.9656 | 0.00092126 | 8.6976 | 8.6968 | 19530.8 | 23.6744 | 11076.9 | 11149.1 | 10928.7 | 0 | 0 | 10927 | 530.501 | 0 | 0 | 0 | 10927 | 0 | 660 | 0 | 0
5503 | 2005-08-18 06:00 | 219 | 585 | 69 | 23.23 | 4.59 | 0 | 14.7945 | 84.3003 | 78.9977 | 0 | 219 | 112.108 | 66.6336 | 2.0519 | 97.2298 | 62.3582 | 0.01071 | 76.6181 | 60.0504 | 0.0080702 | 132.576 | 132.62 | 297822 | 26.3009 | 262991 | 261105 | 242277 | 0 | 0 | 241735 | 662.232 | 0 | 0 | 0 | 356.822 | 241379 | 666.677 | 235674 | 230960.6875
5504 | 2005-08-18 07:00 | 431 | 788 | 71 | 22.99 | 4.59 | 0 | 27.1283 | 92.7309 | 64.4574 | 0 | 431 | 340.419 | 75.7294 | 4.0381 | 340.361 | 70.8705 | 0.021078 | 317.911 | 68.2476 | 0.015883 | 374.589 | 374.587 | 841225 | 31.664 | 799418 | 775513 | 757311 | 0 | 0 | 752596 | 690.626 | 0 | 0 | 0 | 0 | 752596 | 690.626 | 741660 | 726826.25
5505 | 2005-08-18 08:00 | 636 | 878 | 79 | 24.39 | 4.59 | 0 | 39.3607 | 102.352 | 49.8583 | 0 | 636 | 566.204 | 85.7738 | 5.9588 | 566.204 | 80.2704 | 0.031103 | 550.6 | 77.2996 | 0.023437 | 609.086 | 609.079 | 1367840 | 38.4939 | 1339850 | 1261650 | 1230960 | 0 | 0 | 1218360 | 684.053 | 0 | 0 | 0 | 0 | 1218360 | 684.053 | 1199780 | 1175784.375
5506 | 2005-08-18 09:00 | 797 | 908 | 91 | 25.79 | 3.12 | 0 | 51.0631 | 114.897 | 35.2366 | 0 | 797 | 741.341 | 98.8948 | 7.4673 | 741.341 | 92.5495 | 0.038977 | 733.026 | 89.1244 | 0.02937 | 797.515 | 797.509 | 1791000 | 46.1308 | 1781580 | 1621100 | 1581050 | 0 | 0 | 1559440 | 668.033 | 0 | 0 | 0 | 0 | 1559440 | 668.033 | 1533290 | 1502620.125
5507 | 2005-08-18 10:00 | 907 | 916 | 105 | 27.18 | 3.12 | 0 | 61.2936 | 133.924 | 20.6533 | 0 | 907 | 855.619 | 113.365 | 8.4979 | 855.619 | 106.091 | 0.044356 | 852.68 | 102.165 | 0.033423 | 926.232 | 926.225 | 2080070 | 50.8037 | 2085400 | 1857630 | 1814790 | 0 | 0 | 1785250 | 654.831 | 0 | 0 | 0 | 891.356 | 1784350 | 660 | 1750730 | 1715716.125
5508 | 2005-08-18 11:00 | 965 | 926 | 110 | 28.01 | 3.12 | 0 | 67.6956 | 164.997 | 6.5734 | 0 | 965 | 918.068 | 118.268 | 9.0413 | 918.068 | 110.68 | 0.047192 | 917.765 | 106.584 | 0.035561 | 993.653 | 993.647 | 2231480 | 53.3534 | 2244940 | 1976320 | 1933700 | 0 | 0 | 1899670 | 648.667 | 0 | 0 | 0 | 7442.52 | 1892230 | 660 | 1854530 | 1817438.75
5509 | 2005-08-18 12:00 | 971 | 953 | 97 | 28.85 | 4.04 | 0 | 66.7527 | 203.31 | 9.6273 | 0 | 971 | 937.834 | 104.974 | 9.0975 | 937.834 | 98.2388 | 0.047486 | 937.164 | 94.6031 | 0.035782 | 1000.85 | 1000.85 | 2247650 | 52.8752 | 2261990 | 1996150 | 1951050 | 0 | 0 | 1916530 | 649.704 | 0 | 0 | 0 | 4742.21 | 1911790 | 660 | 1873330 | 1835862
5510 | 2005-08-18 13:00 | 899 | 940 | 93 | 29.68 | 4.04 | 0 | 59.1373 | 231.239 | 23.9775 | 0 | 899 | 857.93 | 101.054 | 8.4229 | 857.93 | 94.5699 | 0.043965 | 853.878 | 91.0699 | 0.033128 | 916.632 | 916.626 | 2058510 | 51.6835 | 2062700 | 1829430 | 1786760 | 0 | 0 | 1757940 | 652.684 | 0 | 0 | 0 | 2522.28 | 1755410 | 660 | 1722840 | 1688386.75
5511 | 2005-08-18 14:00 | 769 | 911 | 88 | 29.69 | 4.04 | 0 | 48.422 | 248.292 | 38.583 | 0 | 769 | 711.636 | 95.7323 | 7.2049 | 711.636 | 89.59 | 0.037607 | 701.7 | 86.2743 | 0.028338 | 764.362 | 764.356 | 1716540 | 48.0383 | 1703540 | 1535490 | 1499980 | 0 | 0 | 1479980 | 659.682 | 0 | 0 | 0 | 22.527 | 1479960 | 660.84 | 1456420 | 1427294
5512 | 2005-08-18 15:00 | 578 | 827 | 86 | 29.71 | 6.84 | 0 | 36.5327 | 259.926 | 53.2081 | 0 | 578 | 494.999 | 92.6216 | 5.4154 | 494.999 | 86.6788 | 0.028267 | 478.424 | 83.4709 | 0.021299 | 545.059 | 545.056 | 1224060 | 40.6254 | 1191010 | 1109680 | 1082130 | 0 | 0 | 1072100 | 674.7 | 0 | 0 | 0 | 0 | 1072100 | 674.7 | 1056970 | 1035832.9375
5513 | 2005-08-18 16:00 | 375 | 734 | 73 | 29.73 | 6.84 | 0 | 24.2355 | 269.146 | 67.8041 | 0 | 375 | 277.933 | 76.7193 | 3.5135 | 277.933 | 71.7968 | 0.018339 | 255.044 | 69.1397 | 0.013819 | 314.471 | 314.471 | 706222 | 36.0277 | 663447 | 630007 | 614757 | 0 | 0 | 611452 | 670.1 | 0 | 0 | 0 | 0 | 611452 | 670.1 | 603194 | 591130.3125
5514 | 2005-08-18 17:00 | 148 | 438 | 57 | 29.37 | 6.84 | 0 | 11.9031 | 277.443 | 82.3357 | 0 | 148 | 58.8413 | 53.5005 | 1.3866 | 58.8413 | 50.0678 | 0.0072378 | 39.7236 | 48.2148 | 0.0054538 | 85.3056 | 85.3036 | 191569 | 31.0783 | 162283 | 157222 | 153598 | 0 | 0 | 153361 | 628.692 | 0 | 0 | 0 | 5173.27 | 148188 | 660 | 143874 | 140996.9844
5515 | 2005-08-18 18:00 | 10 | 117 | 4 | 29.02 | 6.18 | 0 | -0.20026 | 285.717 | 90 | 0 | 10 | 0 | 2.9909 | 0.093692 | 0 | 2.799 | 0 | 0 | 2.6954 | 0 | 2.6145 | 2.6144 | 5871.31 | 29.0746 | 1633.18 | 1631.88 | 1617.88 | 0 | 0 | 1617.8 | 365.324 | 0 | 0 | 0 | 1617.8 | 0 | 660 | 0 | 0
5516 | 2005-08-18 19:00 | 0 | 0 | 0 | 28.66 | 6.18 | 0
5517 | 2005-08-18 20:00 | 0 | 0 | 0 | 28.02 | 6.18 | 0
5518 | 2005-08-18 21:00 | 0 | 0 | 0 | 27.37 | 4.62 | 0
5519 | 2005-08-18 22:00 | 0 | 0 | 0 | 26.73 | 4.62 | 0
5520 | 2005-08-18 23:00 | 0 | 0 | 0 | 25.78 | 4.62 | 0
5521 | 2005-08-19 | 0 | 0 | 0 | 24.83 | 6.09 | 0
5522 | 2005-08-19 01:00 | 0 | 0 | 0 | 23.88 | 6.09 | 0
5523 | 2005-08-19 02:00 | 0 | 0 | 0 | 23.37 | 6.09 | 0
5524 | 2005-08-19 03:00 | 0 | 0 | 0 | 22.86 | 4.18 | 0
5525 | 2005-08-19 04:00 | 0 | 0 | 0 | 22.36 | 4.18 | 0
5526 | 2005-08-19 05:00 | 25 | 192 | 11 | 22.05 | 4.18 | 0 | 2.4956 | 76.3713 | 90 | 0 | 25 | 0 | 8.2456 | 0.23423 | 0 | 7.7165 | 0.0012226 | 0 | 7.431 | 0.00092126 | 7.2089 | 7.2091 | 16189.7 | 22.2215 | 8574.99 | 8683.5 | 8511.64 | 0 | 0 | 8510.59 | 522.202 | 0 | 0 | 0 | 8510.59 | 0 | 660 | 0 | 0
5527 | 2005-08-19 06:00 | 217 | 640 | 54 | 21.74 | 0.28 | 0 | 14.6649 | 84.6153 | 78.9843 | 0 | 217 | 123.025 | 53.7792 | 2.0331 | 106.088 | 50.3287 | 0.010612 | 83.6323 | 48.466 | 0.0079965 | 128.143 | 128.121 | 287718 | 25.6923 | 253522 | 252321 | 233202 | 0 | 0 | 232681 | 652.856 | 0 | 0 | 0 | 596.364 | 232085 | 665.383 | 226527 | 221996.2031
5528 | 2005-08-19 07:00 | 426 | 776 | 73 | 21.44 | 0.28 | 0 | 27.0003 | 93.0739 | 64.4276 | 0 | 426 | 335.627 | 77.9246 | 3.9913 | 335.562 | 72.9248 | 0.020833 | 313.471 | 70.2259 | 0.015698 | 372.201 | 372.196 | 835860 | 32.9214 | 793993 | 765706 | 746495 | 0 | 0 | 741848 | 686 | 0 | 0 | 0 | 0 | 741848 | 686 | 731239 | 716614.5
5529 | 2005-08-19 08:00 | 621 | 840 | 90 | 22.93 | 0.28 | 0 | 39.2222 | 102.741 | 49.8125 | 0 | 621 | 541.885 | 97.1706 | 5.8183 | 541.885 | 90.936 | 0.03037 | 526.992 | 87.5705 | 0.022884 | 596.147 | 596.142 | 1338780 | 41.3197 | 1309700 | 1216830 | 1186250 | 0 | 0 | 1174260 | 675.637 | 0 | 0 | 0 | 0 | 1174260 | 675.637 | 1157010 | 1133865.625
5530 | 2005-08-19 09:00 | 789 | 893 | 96 | 24.43 | 2.31 | 0 | 50.8956 | 115.351 | 35.1721 | 0 | 789 | 729.997 | 104.211 | 7.3923 | 729.997 | 97.5242 | 0.038585 | 721.845 | 93.9149 | 0.029075 | 791.315 | 791.309 | 1777080 | 45.7281 | 1766980 | 1610790 | 1572360 | 0 | 0 | 1551000 | 669.147 | 0 | 0 | 0 | 0 | 1551000 | 669.147 | 1525070 | 1494570.125
5531 | 2005-08-19 10:00 | 905 | 916 | 104 | 25.92 | 2.31 | 0 | 61.0677 | 134.427 | 20.5591 | 0 | 905 | 856.938 | 112.524 | 8.4792 | 856.938 | 105.304 | 0.044258 | 854.023 | 101.407 | 0.033349 | 926.799 | 926.794 | 2081350 | 50.8646 | 2086740 | 1858280 | 1817610 | 0 | 0 | 1787880 | 653.317 | 0 | 0 | 0 | 1088.15 | 1786790 | 659.999 | 1753080 | 1718015
5532 | 2005-08-19 11:00 | 946 | 854 | 159 | 27.24 | 2.31 | 0 | 67.3886 | 165.326 | 6.3672 | 0 | 946 | 847.272 | 176.996 | 8.8633 | 847.272 | 165.639 | 0.046263 | 847.009 | 159.509 | 0.03486 | 976.356 | 976.352 | 2192640 | 53.5185 | 2203990 | 1938320 | 1894630 | 0 | 0 | 1861860 | 647.955 | 0 | 0 | 0 | 7805.17 | 1854060 | 659.999 | 1817830 | 1781470.25
5533 | 2005-08-19 12:00 | 965 | 907 | 135 | 28.56 | 1.32 | 0 | 66.4254 | 203.17 | 9.5791 | 0 | 965 | 892.953 | 143.749 | 9.0413 | 892.953 | 134.526 | 0.047192 | 892.321 | 129.547 | 0.035561 | 991.247 | 991.239 | 2226070 | 57.0663 | 2239230 | 1935150 | 1891640 | 0 | 0 | 1857770 | 636.194 | 0 | 0 | 0 | 30323 | 1827450 | 660 | 1792220 | 1756377.5
5534 | 2005-08-19 13:00 | 882 | 909 | 105 | 29.88 | 1.32 | 0 | 58.8533 | 230.904 | 24.0054 | 0 | 882 | 829.349 | 113.598 | 8.2637 | 829.349 | 106.31 | 0.043133 | 825.423 | 102.375 | 0.032502 | 899.995 | 899.988 | 2021140 | 55.7621 | 2023360 | 1758260 | 1719580 | 0 | 0 | 1691590 | 637.367 | 0 | 0 | 0 | 23790.1 | 1667800 | 660 | 1638310 | 1605547.5
5535 | 2005-08-19 14:00 | 755 | 888 | 94 | 30.53 | 1.32 | 0 | 48.1741 | 247.959 | 38.6368 | 0 | 755 | 692.885 | 102.072 | 7.0738 | 692.885 | 95.5229 | 0.036923 | 683.177 | 91.9877 | 0.027822 | 751.937 | 751.933 | 1688650 | 52.1543 | 1674340 | 1478680 | 1444200 | 0 | 0 | 1424870 | 645.724 | 0 | 0 | 0 | 8349.04 | 1416520 | 660 | 1394560 | 1366671.25
5536 | 2005-08-19 15:00 | 581 | 842 | 82 | 31.18 | 4.97 | 0 | 36.3032 | 259.627 | 53.2794 | 0 | 581 | 503.934 | 88.6929 | 5.4435 | 503.934 | 83.0022 | 0.028413 | 486.99 | 79.9303 | 0.02141 | 549.933 | 549.932 | 1235010 | 43.6028 | 1202320 | 1104390 | 1078050 | 0 | 0 | 1067840 | 665.638 | 0 | 0 | 0 | 0 | 1067840 | 665.638 | 1053240 | 1032179.375
5537 | 2005-08-19 16:00 | 374 | 755 | 66 | 31.83 | 4.97 | 0 | 24.0117 | 268.876 | 67.891 | 0 | 374 | 284.874 | 69.8452 | 3.5041 | 284.874 | 65.3638 | 0.01829 | 261.273 | 62.9447 | 0.013782 | 314.504 | 314.502 | 706288 | 38.9345 | 663512 | 621152 | 606650 | 0 | 0 | 603315 | 659.02 | 0 | 0 | 0 | -1.1057 | 603316 | 660.177 | 595466 | 583556.4375
5538 | 2005-08-19 17:00 | 152 | 472 | 56 | 31.47 | 4.97 | 0 | 11.6762 | 277.194 | 82.4386 | 0 | 152 | 62.42 | 52.6594 | 1.4241 | 62.42 | 49.2807 | 0.0074334 | 41.8232 | 47.4569 | 0.0056013 | 86.6071 | 86.6054 | 194494 | 33.4264 | 165000 | 157859 | 154336 | 0 | 0 | 154092 | 621.445 | 0 | 0 | 0 | 8540.44 | 145551 | 660 | 141292 | 138465.6719
5539 | 2005-08-19 18:00 | 10 | 121 | 4 | 31.11 | 4.34 | 0 | -0.43763 | 285.484 | 90 | 0 | 10 | 0 | 2.9976 | 0.093692 | 0 | 2.8053 | 0 | 0 | 2.7014 | 0 | 2.6204 | 2.6204 | 5884.64 | 31.1717 | 1640.34 | 1637.36 | 1622.76 | 0 | 0 | 1622.68 | 362.329 | 0 | 0 | 0 | 1622.68 | 0 | 660 | 0 | 0
5540 | 2005-08-19 19:00 | 0 | 0 | 0 | 30.75 | 4.34 | 0
5541 | 2005-08-19 20:00 | 0 | 0 | 0 | 29.88 | 4.34 | 0
5542 | 2005-08-19 21:00 | 0 | 0 | 0 | 29 | 5.56 | 0
5543 | 2005-08-19 22:00 | 0 | 0 | 0 | 28.12 | 5.56 | 0
5544 | 2005-08-19 23:00 | 0 | 0 | 0 | 27.22 | 5.56 | 0
5545 | 2005-08-20 | 0 | 0 | 0 | 26.32 | 4.24 | 0
5546 | 2005-08-20 01:00 | 0 | 0 | 0 | 25.42 | 4.24 | 0
5547 | 2005-08-20 02:00 | 0 | 0 | 0 | 24.82 | 4.24 | 0
5548 | 2005-08-20 03:00 | 0 | 0 | 0 | 24.21 | 5.25 | 0
5549 | 2005-08-20 04:00 | 0 | 0 | 0 | 23.61 | 5.25 | 0
5550 | 2005-08-20 05:00 | 22 | 172 | 9 | 23.23 | 5.25 | 0 | 2.3547 | 76.675 | 90 | 0 | 22 | 0 | 7.0967 | 0.20612 | 0 | 6.6414 | 0.0010759 | 0 | 6.3956 | 0.00081071 | 6.2045 | 6.2042 | 13932.9 | 23.3676 | 6927.66 | 6975.13 | 6843.04 | 0 | 0 | 6842.31 | 506.966 | 0 | 0 | 0 | 6842.31 | 0 | 660 | 0 | 0
5551 | 2005-08-20 06:00 | 212 | 613 | 57 | 22.84 | 2.98 | 0 | 14.5349 | 84.9339 | 78.9696 | 0 | 212 | 118.167 | 55.5698 | 1.9863 | 101.293 | 52.0044 | 0.010368 | 79.8873 | 50.0797 | 0.0078123 | 126.076 | 126.06 | 283092 | 26.0852 | 249091 | 247501 | 227589 | 0 | 0 | 227093 | 651.938 | 0 | 0 | 0 | 404.439 | 226689 | 664.665 | 221196 | 216771.8594
5552 | 2005-08-20 07:00 | 423 | 774 | 73 | 22.46 | 2.98 | 0 | 26.8715 | 93.4205 | 64.3969 | 0 | 423 | 334.625 | 78.0997 | 3.9632 | 334.479 | 73.0887 | 0.020687 | 312.502 | 70.3837 | 0.015588 | 371.414 | 371.413 | 834099 | 32.0213 | 792217 | 767218 | 747269 | 0 | 0 | 742660 | 689.249 | 0 | 0 | 0 | 0 | 742660 | 689.249 | 731919 | 717280.6875
5553 | 2005-08-20 08:00 | 633 | 877 | 80 | 24.35 | 2.98 | 0 | 39.0822 | 103.133 | 49.7662 | 0 | 633 | 566.572 | 87.0874 | 5.9307 | 566.572 | 81.4997 | 0.030956 | 551.042 | 78.4835 | 0.023326 | 610.663 | 610.658 | 1371390 | 40.0701 | 1343530 | 1255840 | 1224420 | 0 | 0 | 1211780 | 679.278 | 0 | 0 | 0 | 0 | 1211780 | 679.278 | 1193570 | 1169696.375
5554 | 2005-08-20 09:00 | 793 | 907 | 91 | 26.24 | 3.36 | 0 | 50.7258 | 115.809 | 35.108 | 0 | 793 | 741.85 | 99.2113 | 7.4298 | 741.85 | 92.8457 | 0.038781 | 733.601 | 89.4096 | 0.029222 | 798.349 | 798.343 | 1792880 | 46.2815 | 1783550 | 1621760 | 1583330 | 0 | 0 | 1561550 | 667.351 | 0 | 0 | 0 | 0 | 1561550 | 667.351 | 1535350 | 1504647.25
5555 | 2005-08-20 10:00 | 917 | 944 | 94 | 28.13 | 3.36 | 0 | 60.8385 | 134.931 | 20.4671 | 0 | 917 | 882.962 | 102.371 | 8.5916 | 882.962 | 95.8031 | 0.044845 | 879.987 | 92.2575 | 0.033792 | 943.11 | 943.107 | 2117990 | 51.8057 | 2125330 | 1884320 | 1839490 | 0 | 0 | 1809090 | 653.773 | 0 | 0 | 0 | 2111.2 | 1806980 | 660 | 1772520 | 1737072
5556 | 2005-08-20 11:00 | 975 | 953 | 99 | 29.23 | 3.36 | 0 | 67.0782 | 165.655 | 6.1686 | 0 | 975 | 945.595 | 107.362 | 9.135 | 945.595 | 100.473 | 0.047682 | 945.319 | 96.755 | 0.035929 | 1010.85 | 1010.84 | 2270100 | 54.6061 | 2285670 | 2000140 | 1953570 | 0 | 0 | 1918530 | 645.602 | 0 | 0 | 0 | 11598.4 | 1906930 | 660 | 1868660 | 1831284.375
5557 | 2005-08-20 12:00 | 953 | 926 | 108 | 30.33 | 3.78 | 0 | 66.0943 | 203.036 | 9.5432 | 0 | 953 | 911.5 | 116.681 | 8.9289 | 911.5 | 109.195 | 0.046606 | 910.861 | 105.153 | 0.035118 | 985.568 | 985.561 | 2213330 | 54.3959 | 2225800 | 1949310 | 1906160 | 0 | 0 | 1872730 | 645.281 | 0 | 0 | 0 | 11821.2 | 1860910 | 660 | 1824420 | 1787927.625
5558 | 2005-08-20 13:00 | 887 | 926 | 98 | 31.43 | 3.78 | 0 | 58.5647 | 230.575 | 24.0394 | 0 | 887 | 844.517 | 106.571 | 8.3105 | 844.517 | 99.7331 | 0.043378 | 840.507 | 96.0421 | 0.032686 | 908.484 | 908.48 | 2040210 | 53.6137 | 2043440 | 1795080 | 1754740 | 0 | 0 | 1726330 | 645.46 | 0 | 0 | 0 | 10043.2 | 1716290 | 660 | 1685110 | 1651411.5
5559 | 2005-08-20 14:00 | 763 | 911 | 87 | 32.28 | 3.78 | 0 | 47.9216 | 247.628 | 38.695 | 0 | 763 | 710.843 | 94.9943 | 7.1487 | 710.843 | 88.8993 | 0.037314 | 700.846 | 85.6092 | 0.028117 | 762.889 | 762.886 | 1713250 | 50.9085 | 1700090 | 1510990 | 1476480 | 0 | 0 | 1456460 | 648.925 | 0 | 0 | 0 | 4190.92 | 1452270 | 660 | 1429450 | 1400861.375
5560 | 2005-08-20 15:00 | 585 | 861 | 78 | 33.13 | 5.74 | 0 | 36.0694 | 259.328 | 53.3544 | 0 | 585 | 513.974 | 84.7319 | 5.481 | 513.974 | 79.2954 | 0.028609 | 496.616 | 76.3607 | 0.021557 | 555.809 | 555.804 | 1248190 | 45.0745 | 1215930 | 1109030 | 1082060 | 0 | 0 | 1071640 | 661.42 | 0 | 0 | 0 | 0 | 1071640 | 661.42 | 1057180 | 1036034.5
5561 | 2005-08-20 16:00 | 366 | 733 | 70 | 33.98 | 5.74 | 0 | 23.7839 | 268.606 | 67.981 | 0 | 366 | 275.174 | 73.9885 | 3.4291 | 275.174 | 69.2412 | 0.017899 | 252.234 | 66.6786 | 0.013487 | 309.358 | 309.357 | 694739 | 40.6282 | 651945 | 605125 | 590235 | 0 | 0 | 587026 | 653.336 | 0 | 0 | 0 | 651.123 | 586375 | 660 | 578712 | 567137.875
5562 | 2005-08-20 17:00 | 146 | 465 | 53 | 33.32 | 5.74 | 0 | 11.4454 | 276.944 | 82.5442 | 0 | 146 | 60.8154 | 49.924 | 1.3679 | 60.8154 | 46.7208 | 0.00714 | 40.4227 | 44.9917 | 0.0053801 | 82.8572 | 82.8568 | 186075 | 35.1006 | 157187 | 148991 | 145767 | 0 | 0 | 145543 | 613.606 | 0 | 0 | 0 | 12448.8 | 133094 | 660 | 129100 | 126517.7188
5563 | 2005-08-20 18:00 | 9 | 115 | 3 | 32.66 | 5.03 | 0 | -0.67859 | 285.249 | 90 | 0 | 9 | 0 | 2.3239 | 0.084323 | 0 | 2.1748 | 0 | 0 | 2.0943 | 0 | 2.0315 | 2.0314 | 4561.98 | 32.7057 | 999.612 | 1004.44 | 998.227 | 0 | 0 | 998.182 | 297.819 | 0 | 0 | 0 | 998.182 | 0 | 660 | 0 | 0
5564 | 2005-08-20 19:00 | 0 | 0 | 0 | 32 | 5.03 | 0
5565 | 2005-08-20 20:00 | 0 | 0 | 0 | 31.39 | 5.03 | 0
5566 | 2005-08-20 21:00 | 0 | 0 | 0 | 30.77 | 6.41 | 0
5567 | 2005-08-20 22:00 | 0 | 0 | 0 | 30.16 | 6.41 | 0
5568 | 2005-08-20 23:00 | 0 | 0 | 0 | 29.21 | 6.41 | 0
5569 | 2005-08-21 | 0 | 0 | 0 | 28.27 | 7.23 | 0
5570 | 2005-08-21 01:00 | 0 | 0 | 0 | 27.33 | 7.23 | 0
5571 | 2005-08-21 02:00 | 0 | 0 | 0 | 26.64 | 7.23 | 0
5572 | 2005-08-21 03:00 | 0 | 0 | 0 | 25.95 | 7.14 | 0
5573 | 2005-08-21 04:00 | 0 | 0 | 0 | 25.26 | 7.14 | 0
5574 | 2005-08-21 05:00 | 17 | 70 | 12 | 24.94 | 7.14 | 0 | 2.2137 | 76.9824 | 90 | 0 | 17 | 0 | 9.3062 | 0.15928 | 0 | 8.709 | 0.00083137 | 0 | 8.3867 | 0.00062646 | 8.1357 | 8.1353 | 18269.8 | 25.0998 | 10124.8 | 10119.4 | 9924.54 | 0 | 0 | 9923.1 | 520.663 | 0 | 0 | 0 | 9923.1 | 0 | 660 | 0 | 0
5575 | 2005-08-21 06:00 | 210 | 522 | 80 | 24.61 | 5.05 | 0 | 14.4044 | 85.2561 | 78.9536 | 0 | 210 | 100.129 | 77.577 | 1.9675 | 85.2822 | 72.5995 | 0.01027 | 67.2915 | 69.9126 | 0.0077386 | 133.096 | 133.057 | 298807 | 27.6001 | 263841 | 260286 | 241914 | 0 | 0 | 241375 | 660.825 | 0 | 0 | 0 | 82.8034 | 241292 | 662.568 | 235658 | 230944.6719
5576 | 2005-08-21 07:00 | 413 | 724 | 87 | 24.28 | 5.05 | 0 | 26.7417 | 93.7706 | 64.3654 | 0 | 413 | 313.438 | 91.7962 | 3.8695 | 313.196 | 85.9064 | 0.020197 | 292.659 | 82.7271 | 0.015219 | 364.139 | 364.131 | 817743 | 32.463 | 775685 | 749626 | 728619 | 0 | 0 | 724215 | 687.965 | 0 | 0 | 0 | 0 | 724215 | 687.965 | 713788 | 699511.75
5577 | 2005-08-21 08:00 | 606 | 778 | 117 | 26.37 | 5.05 | 0 | 38.9408 | 103.529 | 49.7197 | 0 | 606 | 503.013 | 127.186 | 5.6777 | 503.013 | 119.025 | 0.029636 | 489.263 | 114.62 | 0.022331 | 585.788 | 585.783 | 1315520 | 39.534 | 1285600 | 1204470 | 1175810 | 0 | 0 | 1164110 | 678.392 | 0 | 0 | 0 | 0 | 1164110 | 678.392 | 1146940 | 1124001.25
5578 | 2005-08-21 09:00 | 795 | 877 | 118 | 28.46 | 3.46 | 0 | 50.5536 | 116.268 | 35.0445 | 0 | 795 | 717.754 | 126.957 | 7.4485 | 717.754 | 118.811 | 0.038879 | 709.807 | 114.414 | 0.029296 | 799.523 | 799.519 | 1795520 | 48.399 | 1786320 | 1607870 | 1570270 | 0 | 0 | 1548450 | 660.451 | 0 | 0 | 0 | -1.4748 | 1548450 | 661.304 | 1522880 | 1492422.75
5579 | 2005-08-21 10:00 | 893 | 895 | 114 | 30.56 | 3.46 | 0 | 60.6062 | 135.435 | 20.3777 | 0 | 893 | 838.146 | 123.145 | 8.3667 | 838.146 | 115.244 | 0.043671 | 835.348 | 110.979 | 0.032907 | 917.969 | 917.959 | 2061510 | 53.4528 | 2065850 | 1816390 | 1775840 | 0 | 0 | 1746750 | 645.075 | 0 | 0 | 0 | 9129.52 | 1737620 | 660 | 1705690 | 1671575.625
5580 | 2005-08-21 11:00 | 949 | 901 | 123 | 31.41 | 3.46 | 0 | 66.7644 | 165.981 | 5.9791 | 0 | 949 | 894.02 | 132.127 | 8.8914 | 894.02 | 123.649 | 0.04641 | 893.776 | 119.073 | 0.034971 | 982.497 | 982.49 | 2206420 | 55.9121 | 2218520 | 1928270 | 1885840 | 0 | 0 | 1852570 | 639.967 | 0 | 0 | 0 | 21956.4 | 1830610 | 660 | 1795270 | 1759364.125
5581 | 2005-08-21 12:00 | 965 | 952 | 99 | 32.27 | 5.11 | 0 | 65.7593 | 202.908 | 9.5201 | 0 | 965 | 936.66 | 107.6 | 9.0413 | 936.66 | 100.696 | 0.047192 | 936.006 | 96.9695 | 0.035561 | 1002.02 | 1002.01 | 2250280 | 54.7002 | 2264760 | 1980810 | 1937810 | 0 | 0 | 1903050 | 643.111 | 0 | 0 | 0 | 13770.3 | 1889280 | 660 | 1851690 | 1814657.75
5582 | 2005-08-21 13:00 | 892 | 939 | 94 | 33.13 | 5.11 | 0 | 58.2714 | 230.249 | 24.0797 | 0 | 892 | 856.573 | 102.596 | 8.3574 | 856.573 | 96.0128 | 0.043623 | 852.491 | 92.4595 | 0.03287 | 916.634 | 916.628 | 2058520 | 53.6488 | 2062700 | 1811900 | 1771380 | 0 | 0 | 1742440 | 645.127 | 0 | 0 | 0 | 10212 | 1732230 | 660 | 1700490 | 1666477
5583 | 2005-08-21 14:00 | 760 | 910 | 88 | 33.38 | 5.11 | 0 | 47.6645 | 247.298 | 38.7577 | 0 | 760 | 708.896 | 96.184 | 7.1206 | 708.896 | 90.0127 | 0.037167 | 698.887 | 86.6814 | 0.028006 | 762.028 | 762.025 | 1711320 | 50.438 | 1698070 | 1512720 | 1477830 | 0 | 0 | 1457880 | 650.311 | 0 | 0 | 0 | 2699.33 | 1455180 | 659.999 | 1432290 | 1403642.25
5584 | 2005-08-21 15:00 | 582 | 860 | 78 | 33.63 | 4.89 | 0 | 35.8313 | 259.029 | 53.433 | 0 | 582 | 512.92 | 84.8628 | 5.4529 | 512.92 | 79.4179 | 0.028462 | 495.519 | 76.4787 | 0.021447 | 554.858 | 554.854 | 1246070 | 46.2294 | 1213740 | 1100750 | 1074910 | 0 | 0 | 1064480 | 656.796 | 0 | 0 | 0 | 504.366 | 1063970 | 660 | 1049730 | 1028738.125
5585 | 2005-08-21 16:00 | 355 | 703 | 74 | 33.88 | 4.89 | 0 | 23.5523 | 268.335 | 68.0741 | 0 | 355 | 262.59 | 78.1097 | 3.3261 | 262.59 | 73.098 | 0.017361 | 240.558 | 70.3927 | 0.013082 | 301.635 | 301.628 | 677379 | 40.7293 | 634573 | 588594 | 574757 | 0 | 0 | 571696 | 651.213 | 0 | 0 | 0 | 1208.23 | 570488 | 660 | 562987 | 551727.5
5586 | 2005-08-21 17:00 | 143 | 457 | 53 | 33.44 | 4.89 | 0 | 11.211 | 276.694 | 82.6525 | 0 | 143 | 59.2001 | 50.0256 | 1.3398 | 59.2001 | 46.8159 | 0.0069933 | 39.0147 | 45.0832 | 0.0052696 | 81.5802 | 81.5789 | 183205 | 35.2925 | 154529 | 146305 | 142923 | 0 | 0 | 142708 | 612.771 | 0 | 0 | 0 | 12896 | 129812 | 660 | 125890 | 123372.4766
5587 | 2005-08-21 18:00 | 8 | 108 | 3 | 32.99 | 4.68 | 0 | -0.92305 | 285.013 | 90 | 0 | 8 | 0 | 2.3289 | 0.074954 | 0 | 2.1794 | 0 | 0 | 2.0988 | 0 | 2.0358 | 2.0357 | 4571.72 | 33.0369 | 1003.83 | 1008.78 | 1002.48 | 0 | 0 | 1002.44 | 298.292 | 0 | 0 | 0 | 1002.44 | 0 | 660 | 0 | 0
5588 | 2005-08-21 19:00 | 0 | 0 | 0 | 32.54 | 4.68 | 0
5589 | 2005-08-21 20:00 | 0 | 0 | 0 | 31.9 | 4.68 | 0
5590 | 2005-08-21 21:00 | 0 | 0 | 0 | 31.26 | 6.45 | 0
5591 | 2005-08-21 22:00 | 0 | 0 | 0 | 30.62 | 6.45 | 0
5592 | 2005-08-21 23:00 | 0 | 0 | 0 | 29.81 | 6.45 | 0
5593 | 2005-08-22 | 0 | 0 | 0 | 28.99 | 5.26 | 0
5594 | 2005-08-22 01:00 | 0 | 0 | 0 | 28.18 | 5.26 | 0
5595 | 2005-08-22 02:00 | 0 | 0 | 0 | 27.39 | 5.26 | 0
5596 | 2005-08-22 03:00 | 0 | 0 | 0 | 26.61 | 3.55 | 0
5597 | 2005-08-22 04:00 | 0 | 0 | 0 | 25.83 | 3.55 | 0
5598 | 2005-08-22 05:00 | 20 | 175 | 8 | 25.7 | 3.55 | 0 | 2.0724 | 77.2935 | 90 | 0 | 20 | 0 | 6.2808 | 0.18738 | 0 | 5.8778 | 0.00097808 | 0 | 5.6603 | 0.00073701 | 5.4912 | 5.491 | 12331.3 | 25.8361 | 5785.98 | 5766.82 | 5662.98 | 0 | 0 | 5662.45 | 488.294 | 0 | 0 | 0 | 5662.45 | 0 | 660 | 0 | 0
5599 | 2005-08-22 06:00 | 208 | 621 | 54 | 25.57 | 3.99 | 0 | 14.2734 | 85.5818 | 78.9365 | 0 | 208 | 119.863 | 53.0426 | 1.9488 | 101.465 | 49.6393 | 0.010172 | 80.1008 | 47.8021 | 0.0076649 | 124.073 | 124.048 | 278574 | 28.5575 | 244869 | 240302 | 220472 | 0 | 0 | 220001 | 649.983 | 0 | 0 | 0 | 1176.96 | 218824 | 660.236 | 213519 | 209248.4688
5600 | 2005-08-22 07:00 | 426 | 796 | 69 | 25.45 | 3.99 | 0 | 26.6112 | 94.1241 | 64.3331 | 0 | 426 | 345.209 | 74.3861 | 3.9913 | 344.742 | 69.6134 | 0.020833 | 322.183 | 67.037 | 0.015698 | 377.559 | 377.556 | 847888 | 34.543 | 806180 | 771602 | 749300 | 0 | 0 | 744529 | 679.781 | 0 | 0 | 0 | 0 | 744529 | 679.781 | 734114 | 719431.4375
5601 | 2005-08-22 08:00 | 629 | 877 | 80 | 27.39 | 3.99 | 0 | 38.7979 | 103.928 | 49.6729 | 0 | 629 | 567.028 | 87.3795 | 5.8932 | 567.028 | 81.773 | 0.030761 | 551.57 | 78.7467 | 0.023179 | 611.43 | 611.424 | 1373100 | 42.1154 | 1345310 | 1245470 | 1217810 | 0 | 0 | 1205100 | 673.768 | 0 | 0 | 0 | 0 | 1205100 | 673.768 | 1187290 | 1163545.75
5602 | 2005-08-22 09:00 | 788 | 904 | 92 | 29.33 | 3.92 | 0 | 50.3791 | 116.731 | 34.9818 | 0 | 788 | 740.323 | 100.574 | 7.383 | 740.323 | 94.1208 | 0.038537 | 732.161 | 90.6375 | 0.029038 | 798.142 | 798.135 | 1792410 | 48.6407 | 1783060 | 1603040 | 1566180 | 0 | 0 | 1544450 | 660.19 | 0 | 0 | 0 | 66.5984 | 1544390 | 660.547 | 1518970 | 1488592.75
5603 | 2005-08-22 10:00 | 890 | 892 | 116 | 31.28 | 3.92 | 0 | 60.3705 | 135.939 | 20.2911 | 0 | 890 | 835.174 | 125.39 | 8.3386 | 835.174 | 117.345 | 0.043525 | 832.411 | 113.002 | 0.032797 | 917.083 | 917.078 | 2059520 | 53.4685 | 2063760 | 1814400 | 1773200 | 0 | 0 | 1744140 | 644.887 | 0 | 0 | 0 | 9073.01 | 1735070 | 660 | 1703230 | 1669161.625
5604 | 2005-08-22 11:00 | 953 | 919 | 113 | 31.7 | 3.92 | 0 | 66.4473 | 166.306 | 5.8002 | 0 | 953 | 911.646 | 122.173 | 8.9289 | 911.646 | 114.334 | 0.046606 | 911.412 | 110.103 | 0.035118 | 990.903 | 990.893 | 2225290 | 55.6744 | 2238420 | 1948060 | 1903570 | 0 | 0 | 1869900 | 641.804 | 0 | 0 | 0 | 19369.4 | 1850530 | 660 | 1814430 | 1778142
5605 | 2005-08-22 12:00 | 945 | 919 | 111 | 32.12 | 3.43 | 0 | 65.4206 | 202.785 | 9.5104 | 0 | 945 | 904.497 | 120.173 | 8.8539 | 904.497 | 112.462 | 0.046214 | 903.867 | 108.3 | 0.034824 | 981.836 | 981.834 | 2204950 | 56.6543 | 2216970 | 1919770 | 1876960 | 0 | 0 | 1843780 | 637.276 | 0 | 0 | 0 | 27503.3 | 1816280 | 660 | 1781470 | 1745841.5
5606 | 2005-08-22 13:00 | 888 | 938 | 94 | 32.54 | 3.43 | 0 | 57.9736 | 229.928 | 24.1262 | 0 | 888 | 854.728 | 102.767 | 8.3199 | 854.728 | 96.1737 | 0.043427 | 850.638 | 92.6144 | 0.032723 | 914.986 | 914.979 | 2054810 | 55.4037 | 2058810 | 1792660 | 1752630 | 0 | 0 | 1723790 | 639.823 | 0 | 0 | 0 | 20682.1 | 1703100 | 660 | 1672390 | 1638946.5
5607 | 2005-08-22 14:00 | 757 | 909 | 88 | 32.73 | 3.43 | 0 | 47.4029 | 246.97 | 38.8249 | 0 | 757 | 708.018 | 96.3378 | 7.0925 | 708.018 | 90.1566 | 0.03702 | 697.979 | 86.82 | 0.027896 | 761.282 | 761.279 | 1709640 | 51.753 | 1696310 | 1501330 | 1468970 | 0 | 0 | 1449010 | 646.296 | 0 | 0 | 0 | 7669.2 | 1441340 | 660 | 1418790 | 1390410.375
5608 | 2005-08-22 15:00 | 558 | 784 | 102 | 32.91 | 5.54 | 0 | 35.5892 | 258.73 | 53.5152 | 0 | 558 | 465.904 | 111.189 | 5.228 | 465.904 | 104.055 | 0.027289 | 450.022 | 100.204 | 0.020563 | 533.739 | 533.732 | 1198630 | 44.5293 | 1164770 | 1064860 | 1040800 | 0 | 0 | 1031090 | 659.379 | 0 | 0 | 0 | 8.0839 | 1031080 | 660.487 | 1017460 | 997107.9375
5609 | 2005-08-22 16:00 | 370 | 701 | 92 | 33.1 | 5.54 | 0 | 23.3168 | 268.063 | 68.1703 | 0 | 370 | 261.168 | 95.3497 | 3.4666 | 261.168 | 89.2319 | 0.018094 | 239.109 | 85.9295 | 0.013635 | 315.301 | 315.296 | 708078 | 39.964 | 665308 | 619663 | 605010 | 0 | 0 | 601671 | 656.135 | 0 | 0 | 0 | 281.808 | 601389 | 660 | 593568 | 581696.8125
5610 | 2005-08-22 17:00 | 140 | 445 | 55 | 32.49 | 5.54 | 0 | 10.973 | 276.442 | 82.7634 | 0 | 140 | 56.2507 | 52.0245 | 1.3117 | 56.2507 | 48.6865 | 0.0068466 | 36.7356 | 46.8847 | 0.005159 | 81.1167 | 81.1121 | 182157 | 34.2558 | 153559 | 146213 | 142842 | 0 | 0 | 142629 | 615.566 | 0 | 0 | 0 | 10904.9 | 131724 | 660 | 127760 | 125204.3203
5611 | 2005-08-22 18:00 | 7 | 101 | 3 | 31.88 | 6.05 | 0 | -1.1709 | 284.776 | 90 | 0 | 7 | 0 | 2.1917 | 0.065585 | 0 | 2.0511 | 0 | 0 | 1.9751 | 0 | 1.9159 | 1.9158 | 4302.45 | 31.9204 | 890.433 | 895.165 | 890.087 | 0 | 0 | 890.047 | 282.861 | 0 | 0 | 0 | 890.047 | 0 | 660 | 0 | 0
5612 | 2005-08-22 19:00 | 0 | 0 | 0 | 31.27 | 6.05 | 0
5613 | 2005-08-22 20:00 | 0 | 0 | 0 | 30.59 | 6.05 | 0
5614 | 2005-08-22 21:00 | 0 | 0 | 0 | 29.92 | 8.47 | 0
5615 | 2005-08-22 22:00 | 0 | 0 | 0 | 29.24 | 8.47 | 0
5616 | 2005-08-22 23:00 | 0 | 0 | 0 | 28.37 | 8.47 | 0
5617 | 2005-08-23 | 0 | 0 | 0 | 27.49 | 7.58 | 0
5618 | 2005-08-23 01:00 | 0 | 0 | 0 | 26.62 | 7.58 | 0
5619 | 2005-08-23 02:00 | 0 | 0 | 0 | 26.11 | 7.58 | 0
5620 | 2005-08-23 03:00 | 0 | 0 | 0 | 25.6 | 7.59 | 0
5621 | 2005-08-23 04:00 | 0 | 0 | 0 | 25.1 | 7.59 | 0
5622 | 2005-08-23 05:00 | 17 | 145 | 7 | 24.97 | 7.59 | 0 | 1.931 | 77.6082 | 90 | 0 | 17 | 0 | 5.06 | 0.15928 | 0 | 4.7353 | 0.00083137 | 0 | 4.5601 | 0.00062646 | 4.4239 | 4.4237 | 9934.48 | 25.0545 | 4135.05 | 4134.16 | 4069.04 | 0 | 0 | 4068.73 | 464.81 | 0 | 0 | 0 | 4068.73 | 0 | 660 | 0 | 0
5623 | 2005-08-23 06:00 | 192 | 537 | 60 | 24.85 | 4.3 | 0 | 14.142 | 85.9108 | 78.9182 | 0 | 192 | 103.844 | 58.9788 | 1.7989 | 87.2973 | 55.1946 | 0.0093896 | 68.9535 | 53.1519 | 0.0070753 | 118.449 | 118.446 | 265993 | 27.6452 | 232775 | 229507 | 211151 | 0 | 0 | 210728 | 654.491 | 0 | 0 | 0 | 440.773 | 210287 | 660.739 | 205044 | 200942.7656
5624 | 2005-08-23 07:00 | 424 | 762 | 84 | 24.73 | 4.3 | 0 | 26.4797 | 94.4808 | 64.3001 | 0 | 424 | 330.68 | 89.7072 | 3.9726 | 329.977 | 83.9515 | 0.020735 | 308.43 | 80.8445 | 0.015624 | 377.611 | 377.596 | 847978 | 33.641 | 806287 | 774978 | 752652 | 0 | 0 | 747870 | 681.653 | 0 | 0 | 0 | 0 | 747870 | 681.653 | 737338 | 722590.875
5625 | 2005-08-23 08:00 | 621 | 825 | 106 | 26.49 | 4.3 | 0 | 38.6534 | 104.33 | 49.6261 | 0 | 621 | 534.101 | 116.506 | 5.8183 | 534.101 | 109.031 | 0.03037 | 519.58 | 104.996 | 0.022884 | 605.86 | 605.862 | 1360610 | 40.7879 | 1332350 | 1241150 | 1209500 | 0 | 0 | 1197110 | 678.095 | 0 | 0 | 0 | 0 | 1197110 | 678.095 | 1179260 | 1155677.125
5626 | 2005-08-23 09:00 | 761 | 805 | 143 | 28.25 | 6.55 | 0 | 50.2023 | 117.195 | 34.92 | 0 | 761 | 659.54 | 157.902 | 7.13 | 659.54 | 147.771 | 0.037216 | 652.299 | 142.302 | 0.028043 | 770.79 | 770.78 | 1730970 | 43.9744 | 1718660 | 1579610 | 1544710 | 0 | 0 | 1524290 | 672.461 | 0 | 0 | 0 | 0 | 1524290 | 672.461 | 1499080 | 1469096.875
5627 | 2005-08-23 10:00 | 865 | 799 | 173 | 30 | 6.55 | 0 | 60.1317 | 136.442 | 20.2077 | 0 | 865 | 748.877 | 191.097 | 8.1044 | 748.877 | 178.836 | 0.042302 | 746.421 | 172.217 | 0.031876 | 891.11 | 891.096 | 2001180 | 48.1789 | 2002370 | 1805890 | 1764080 | 0 | 0 | 1736950 | 664.279 | 0 | 0 | 0 | 0 | 1736950 | 664.279 | 1704950 | 1670848.375
5628 | 2005-08-23 11:00 | 949 | 914 | 115 | 30.54 | 6.55 | 0 | 66.1269 | 166.629 | 5.6336 | 0 | 949 | 907.625 | 124.438 | 8.8914 | 907.625 | 116.454 | 0.04641 | 907.404 | 112.144 | 0.034971 | 988.996 | 988.989 | 2221010 | 50.716 | 2233900 | 1992000 | 1944030 | 0 | 0 | 1910710 | 659.136 | 0 | 0 | 0 | 87.2669 | 1910620 | 660.509 | 1872200 | 1834759
5629 | 2005-08-23 12:00 | 940 | 914 | 113 | 31.07 | 6.1 | 0 | 65.0784 | 202.667 | 9.5143 | 0 | 940 | 899.369 | 122.438 | 8.8071 | 899.369 | 114.582 | 0.04597 | 898.742 | 110.341 | 0.034639 | 978.844 | 978.837 | 2198220 | 51.6235 | 2209880 | 1961760 | 1916730 | 0 | 0 | 1883810 | 654.651 | 0 | 0 | 0 | 1761.64 | 1882050 | 660 | 1844750 | 1807852.5
5630 | 2005-08-23 13:00 | 885 | 940 | 92 | 31.61 | 6.1 | 0 | 57.6715 | 229.612 | 24.1791 | 0 | 885 | 856.134 | 100.852 | 8.2918 | 856.134 | 94.3811 | 0.04328 | 852.017 | 90.8881 | 0.032613 | 914.65 | 914.645 | 2054060 | 50.8156 | 2058020 | 1833040 | 1793040 | 0 | 0 | 1764080 | 653.144 | 0 | 0 | 0 | 1211.98 | 1762870 | 659.999 | 1730030 | 1695428.5
5631 | 2005-08-23 14:00 | 753 | 909 | 87 | 31.99 | 6.1 | 0 | 47.137 | 246.644 | 38.8966 | 0 | 753 | 707.158 | 95.4513 | 7.055 | 707.158 | 89.3269 | 0.036825 | 697.085 | 86.021 | 0.027748 | 759.64 | 759.638 | 1705950 | 47.9408 | 1692450 | 1526170 | 1490760 | 0 | 0 | 1471110 | 661.132 | 0 | 0 | 0 | 28.5673 | 1471080 | 661.786 | 1447730 | 1418771.125
5632 | 2005-08-23 15:00 | 573 | 854 | 79 | 32.38 | 8.99 | 0 | 35.3429 | 258.431 | 53.601 | 0 | 573 | 506.756 | 86.1587 | 5.3686 | 506.756 | 80.6306 | 0.028022 | 489.394 | 77.6465 | 0.021115 | 550.05 | 550.045 | 1235260 | 42.0007 | 1202580 | 1113210 | 1086220 | 0 | 0 | 1075960 | 669.35 | 0 | 0 | 0 | 0 | 1075960 | 669.35 | 1061020 | 1039796.125
5633 | 2005-08-23 16:00 | 367 | 746 | 74 | 32.76 | 8.99 | 0 | 23.0775 | 267.79 | 68.2694 | 0 | 367 | 276.754 | 78.3754 | 3.4385 | 276.754 | 73.3467 | 0.017948 | 253.217 | 70.6322 | 0.013524 | 314.147 | 314.142 | 705480 | 38.2546 | 662702 | 622487 | 607936 | 0 | 0 | 604612 | 661.436 | 0 | 0 | 0 | -18.1356 | 604630 | 661.802 | 596715 | 584780.6875
5634 | 2005-08-23 17:00 | 131 | 385 | 59 | 32.06 | 8.99 | 0 | 10.7316 | 276.189 | 82.877 | 0 | 131 | 47.9464 | 54.4772 | 1.2274 | 47.9464 | 50.9818 | 0.0064064 | 31.0106 | 49.095 | 0.0048274 | 77.7071 | 77.7055 | 174507 | 33.4191 | 146491 | 140100 | 136822 | 0 | 0 | 136627 | 616.846 | 0 | 0 | 0 | 9917.39 | 126710 | 660 | 122858 | 120401.0078
5635 | 2005-08-23 18:00 | 6 | 83 | 2 | 31.36 | 8.43 | 0 | -1.4221 | 284.537 | 90 | 0 | 6 | 0 | 1.4987 | 0.056215 | 0 | 1.4025 | 0 | 0 | 1.3506 | 0 | 1.3101 | 1.3101 | 2942.16 | 31.3837 | 418.461 | 421.391 | 419.385 | 0 | 0 | 419.366 | 194.673 | 0 | 0 | 0 | 419.366 | 0 | 660 | 0 | 0
5636 | 2005-08-23 19:00 | 0 | 0 | 0 | 30.66 | 8.43 | 0
5637 | 2005-08-23 20:00 | 0 | 0 | 0 | 29.87 | 8.43 | 0
5638 | 2005-08-23 21:00 | 0 | 0 | 0 | 29.08 | 9.41 | 0
5639 | 2005-08-23 22:00 | 0 | 0 | 0 | 28.29 | 9.41 | 0
5640 | 2005-08-23 23:00 | 0 | 0 | 0 | 27.53 | 9.41 | 0
5641 | 2005-08-24 | 0 | 0 | 0 | 26.77 | 7.25 | 0
5642 | 2005-08-24 01:00 | 0 | 0 | 0 | 26.01 | 7.25 | 0
5643 | 2005-08-24 02:00 | 0 | 0 | 0 | 25.53 | 7.25 | 0
5644 | 2005-08-24 03:00 | 0 | 0 | 0 | 25.05 | 9.53 | 0
5645 | 2005-08-24 04:00 | 0 | 0 | 0 | 24.57 | 9.53 | 0
5646 | 2005-08-24 05:00 | 17 | 157 | 6 | 24.53 | 9.53 | 0 | 1.7894 | 77.9263 | 90 | 0 | 17 | 0 | 4.5858 | 0.15928 | 0 | 4.2915 | 0.00083137 | 0 | 4.1327 | 0.00062646 | 4.0093 | 4.0092 | 9003.54 | 24.5978 | 3518.97 | 3522.35 | 3472.94 | 0 | 0 | 3472.7 | 452.726 | 0 | 0 | 0 | 3472.7 | 0 | 660 | 0 | 0
5647 | 2005-08-24 06:00 | 203 | 612 | 54 | 24.49 | 5.9 | 0 | 14.0101 | 86.2431 | 78.8988 | 0 | 203 | 118.504 | 53.3986 | 1.902 | 98.9621 | 49.9724 | 0.0099275 | 78.2115 | 48.123 | 0.0074806 | 122.552 | 122.523 | 275146 | 27.096 | 241645 | 238895 | 218131 | 0 | 0 | 217667 | 647.83 | 0 | 0 | 0 | 377.326 | 217290 | 660.569 | 212001 | 207761.3281
5648 | 2005-08-24 07:00 | 422 | 794 | 69 | 24.45 | 5.9 | 0 | 26.3473 | 94.8406 | 64.2664 | 0 | 422 | 345.345 | 74.7425 | 3.9538 | 344.402 | 69.9468 | 0.020638 | 321.961 | 67.3582 | 0.015551 | 377.655 | 377.643 | 848081 | 32.4824 | 806416 | 779304 | 756489 | 0 | 0 | 751722 | 686.05 | 0 | 0 | 0 | 0 | 751722 | 686.05 | 740970 | 726150.75
5649 | 2005-08-24 08:00 | 613 | 844 | 88 | 26.14 | 5.9 | 0 | 38.5074 | 104.735 | 49.5792 | 0 | 613 | 546.738 | 95.9323 | 5.7433 | 546.738 | 89.7771 | 0.029978 | 531.915 | 86.4545 | 0.022589 | 599.84 | 599.835 | 1347070 | 38.8984 | 1318300 | 1238950 | 1208120 | 0 | 0 | 1195960 | 683.693 | 0 | 0 | 0 | 0 | 1195960 | 683.693 | 1177870 | 1154310.875
5650 | 2005-08-24 09:00 | 788 | 872 | 120 | 27.83 | 5.68 | 0 | 50.023 | 117.661 | 34.8592 | 0 | 788 | 715.296 | 129.591 | 7.383 | 715.296 | 121.277 | 0.038537 | 707.475 | 116.788 | 0.029038 | 799.564 | 799.563 | 1795620 | 45.0797 | 1786420 | 1633730 | 1592680 | 0 | 0 | 1570910 | 670.671 | 0 | 0 | 0 | 0 | 1570910 | 670.671 | 1544300 | 1513415.5
5651 | 2005-08-24 10:00 | 855 | 745 | 212 | 29.51 | 5.68 | 0 | 59.8897 | 136.945 | 20.1275 | 0 | 855 | 697.906 | 236.363 | 8.0107 | 697.906 | 221.197 | 0.041813 | 695.636 | 213.011 | 0.031507 | 881.418 | 881.408 | 1979420 | 48.5254 | 1979490 | 1782100 | 1738720 | 0 | 0 | 1712200 | 662.764 | 0 | 0 | 0 | -68.4903 | 1712270 | 663.207 | 1681160 | 1647537.375
5652 | 2005-08-24 11:00 | 961 | 909 | 134 | 30.04 | 5.68 | 0 | 65.8033 | 166.949 | 5.4812 | 0 | 961 | 902.51 | 143.95 | 9.0038 | 902.51 | 134.714 | 0.046997 | 902.302 | 129.728 | 0.035413 | 1001.1 | 1001.09 | 2248200 | 51.6374 | 2262570 | 2008790 | 1963640 | 0 | 0 | 1929070 | 653.62 | 0 | 0 | 0 | 1491.3 | 1927580 | 660 | 1888490 | 1850721.5
5653 | 2005-08-24 12:00 | 954 | 951 | 96 | 30.57 | 9.44 | 0 | 64.7326 | 202.554 | 9.5322 | 0 | 954 | 935.673 | 105.046 | 8.9382 | 935.673 | 98.3062 | 0.046655 | 935.018 | 94.668 | 0.035155 | 998.83 | 998.822 | 2243090 | 47.5597 | 2257180 | 2043550 | 1997770 | 0 | 0 | 1963410 | 667.349 | 0 | 0 | 0 | 0 | 1963410 | 667.349 | 1922870 | 1884413.25
5654 | 2005-08-24 13:00 | 859 | 854 | 141 | 31.1 | 9.44 | 0 | 57.3651 | 229.3 | 24.2384 | 0 | 859 | 777.444 | 158.176 | 8.0482 | 777.444 | 148.027 | 0.042009 | 773.686 | 142.549 | 0.031654 | 888.779 | 888.772 | 1995960 | 46.2178 | 1996870 | 1817830 | 1774340 | 0 | 0 | 1747380 | 670.37 | 0 | 0 | 0 | 0 | 1747380 | 670.37 | 1714870 | 1680571.125
5655 | 2005-08-24 14:00 | 715 | 793 | 137 | 31.07 | 9.44 | 0 | 46.8669 | 246.319 | 38.9727 | 0 | 715 | 615.763 | 151.146 | 6.699 | 615.763 | 141.448 | 0.034966 | 606.949 | 136.214 | 0.026348 | 720.894 | 720.884 | 1618930 | 43.3321 | 1601410 | 1475700 | 1439100 | 0 | 0 | 1421480 | 674.569 | 0 | 0 | 0 | 0 | 1421480 | 674.569 | 1398800 | 1370827.25
5656 | 2005-08-24 15:00 | 554 | 789 | 100 | 31.04 | 7.92 | 0 | 35.0927 | 258.132 | 53.6902 | 0 | 554 | 467.621 | 109.522 | 5.1905 | 467.621 | 102.495 | 0.027093 | 451.518 | 98.7019 | 0.020415 | 533.733 | 533.727 | 1198620 | 41.0215 | 1164760 | 1083050 | 1057070 | 0 | 0 | 1047440 | 672.958 | 0 | 0 | 0 | 0 | 1047440 | 672.958 | 1032880 | 1012217.5
5657 | 2005-08-24 16:00 | 357 | 733 | 72 | 31.01 | 7.92 | 0 | 22.8346 | 267.517 | 68.3716 | 0 | 357 | 270.689 | 76.516 | 3.3448 | 270.689 | 71.6066 | 0.017459 | 247.503 | 68.9565 | 0.013156 | 306.979 | 306.977 | 689393 | 36.7509 | 646592 | 611770 | 596638 | 0 | 0 | 593474 | 665.054 | 0 | 0 | 0 | 0 | 593474 | 665.054 | 585587 | 573875.1875
5658 | 2005-08-24 17:00 | 128 | 383 | 58 | 30.4 | 7.92 | 0 | 10.4867 | 275.935 | 82.9931 | 0 | 128 | 46.9171 | 53.6455 | 1.1993 | 46.9171 | 50.2035 | 0.0062597 | 30.033 | 48.3455 | 0.0047168 | 76.0317 | 76.0301 | 170745 | 31.8219 | 143022 | 137964 | 134645 | 0 | 0 | 134459 | 619.728 | 0 | 0 | 0 | 7487.5 | 126971 | 660 | 123114 | 120651.2578
5659 | 2005-08-24 18:00 | 6 | 79 | 3 | 29.78 | 6.78 | 0 | -1.6765 | 284.296 | 90 | 0 | 6 | 0 | 2.2025 | 0.056215 | 0 | 2.0612 | 0 | 0 | 1.9849 | 0 | 1.9253 | 1.9252 | 4323.57 | 29.8187 | 899.003 | 902.47 | 897.534 | 0 | 0 | 897.495 | 284.604 | 0 | 0 | 0 | 897.495 | 0 | 660 | 0 | 0
5660 | 2005-08-24 19:00 | 0 | 0 | 0 | 29.17 | 6.78 | 0
5661 | 2005-08-24 20:00 | 0 | 0 | 0 | 28.68 | 6.78 | 0
5662 | 2005-08-24 21:00 | 0 | 0 | 0 | 28.19 | 6.89 | 0
5663 | 2005-08-24 22:00 | 0 | 0 | 0 | 27.71 | 6.89 | 0
5664 | 2005-08-24 23:00 | 0 | 0 | 0 | 27.54 | 6.89 | 0
5665 | 2005-08-25 | 0 | 0 | 0 | 27.37 | 9.46 | 0
5666 | 2005-08-25 01:00 | 0 | 0 | 0 | 27.2 | 9.46 | 0
5667 | 2005-08-25 02:00 | 0 | 0 | 0 | 26.32 | 9.46 | 0
5668 | 2005-08-25 03:00 | 0 | 0 | 0 | 25.43 | 7.04 | 0
5669 | 2005-08-25 04:00 | 0 | 0 | 0 | 24.55 | 7.04 | 0
5670 | 2005-08-25 05:00 | 16 | 156 | 5 | 24.42 | 7.04 | 0 | 1.6476 | 78.2479 | 90 | 0 | 16 | 0 | 4.4099 | 0.14991 | 0 | 4.1269 | 0.00078247 | 0 | 3.9742 | 0.0005896 | 3.8555 | 3.8554 | 8658.16 | 24.4962 | 3295.18 | 3298.76 | 3253.79 | 0 | 0 | 3253.58 | 447.332 | 0 | 0 | 0 | 3253.58 | 0 | 660 | 0 | 0
5671 | 2005-08-25 06:00 | 204 | 625 | 53 | 24.3 | 3.51 | 0 | 13.8778 | 86.5785 | 78.8783 | 0 | 204 | 121.437 | 52.615 | 1.9113 | 100.705 | 49.2391 | 0.0099764 | 79.6361 | 47.4168 | 0.0075175 | 123.249 | 123.248 | 276771 | 27.3635 | 243261 | 240106 | 218578 | 0 | 0 | 218120 | 654.657 | 0 | 0 | 0 | 726.838 | 217393 | 661.199 | 212103 | 207860.5625
5672 | 2005-08-25 07:00 | 420 | 793 | 69 | 24.17 | 3.51 | 0 | 26.214 | 95.2033 | 64.2322 | 0 | 420 | 345.437 | 74.9238 | 3.9351 | 344.26 | 70.1166 | 0.02054 | 321.878 | 67.5216 | 0.015477 | 377.733 | 377.715 | 848243 | 33.5587 | 806598 | 775537 | 751646 | 0 | 0 | 746878 | 681.396 | 0 | 0 | 0 | 0 | 746878 | 681.396 | 736370 | 721642.5
5673 | 2005-08-25 08:00 | 623 | 750 | 158 | 25.72 | 3.51 | 0 | 38.3598 | 105.142 | 49.5325 | 0 | 623 | 486.294 | 170.49 | 5.837 | 486.294 | 159.551 | 0.030467 | 473.144 | 153.646 | 0.022958 | 608.009 | 608.004 | 1365430 | 40.833 | 1337350 | 1245560 | 1213520 | 0 | 0 | 1201040 | 677.762 | 0 | 0 | 0 | 0 | 1201040 | 677.762 | 1183120 | 1159460.625
5674 | 2005-08-25 09:00 | 550 | 300 | 321 | 27.26 | 3.4 | 0 | 49.8413 | 118.129 | 34.7997 | 0 | 550 | 246.047 | 329.308 | 5.1531 | 246.047 | 308.179 | 0.026897 | 243.367 | 296.773 | 0.020268 | 523.956 | 523.953 | 1176670 | 40.3786 | 1142150 | 1065080 | 1039880 | 0 | 0 | 1030590 | 673.661 | 0 | 0 | 0 | 0 | 1030590 | 673.661 | 1016320 | 995991.375
5675 | 2005-08-25 10:00 | 908 | 840 | 184 | 28.8 | 3.4 | 0 | 59.6445 | 137.446 | 20.051 | 0 | 908 | 788.17 | 202.723 | 8.5073 | 788.17 | 189.716 | 0.044405 | 785.627 | 182.695 | 0.03346 | 939.305 | 939.297 | 2109420 | 52.3179 | 2116310 | 1871550 | 1828430 | 0 | 0 | 1798180 | 651.314 | 0 | 0 | 0 | 3886.77 | 1794290 | 660 | 1760300 | 1725094.625
5676 | 2005-08-25 11:00 | 909 | 762 | 217 | 29.62 | 3.4 | 0 | 65.4767 | 167.268 | 5.3449 | 0 | 909 | 757.306 | 244.572 | 8.5166 | 757.306 | 228.88 | 0.044454 | 757.141 | 220.409 | 0.033497 | 948.256 | 948.244 | 2129510 | 53.3619 | 2137470 | 1880780 | 1839070 | 0 | 0 | 1808000 | 646.218 | 0 | 0 | 0 | 8079.57 | 1799930 | 660 | 1765730 | 1730413.125
5677 | 2005-08-25 12:00 | 933 | 873 | 148 | 30.43 | 3.1 | 0 | 64.3835 | 202.446 | 9.5642 | 0 | 933 | 858.469 | 158.244 | 8.7415 | 858.469 | 148.09 | 0.045628 | 857.864 | 142.61 | 0.034381 | 970.493 | 970.49 | 2179480 | 55.2155 | 2190120 | 1909960 | 1866540 | 0 | 0 | 1834000 | 640.786 | 0 | 0 | 0 | 17062.6 | 1816930 | 660 | 1782100 | 1746462.5
5678 | 2005-08-25 13:00 | 854 | 880 | 116 | 31.24 | 3.1 | 0 | 57.0547 | 228.992 | 24.3041 | 0 | 854 | 801.48 | 126.05 | 8.0013 | 801.48 | 117.962 | 0.041764 | 797.583 | 113.597 | 0.03147 | 883.875 | 883.869 | 1984950 | 53.8133 | 1985290 | 1741780 | 1702350 | 0 | 0 | 1675560 | 644.544 | 0 | 0 | 0 | 11589.5 | 1663970 | 660 | 1634620 | 1601929
5679 | 2005-08-25 14:00 | 727 | 859 | 103 | 31.76 | 3.1 | 0 | 46.5926 | 245.996 | 39.0533 | 0 | 727 | 667.011 | 112.328 | 6.8114 | 667.011 | 105.121 | 0.035553 | 657.415 | 101.23 | 0.02679 | 735.912 | 735.905 | 1652660 | 50.5544 | 1636680 | 1456670 | 1422430 | 0 | 0 | 1404000 | 651.533 | 0 | 0 | 0 | 3708.31 | 1400290 | 660 | 1378720 | 1351150
5680 | 2005-08-25 15:00 | 562 | 812 | 98 | 32.29 | 5.75 | 0 | 34.8387 | 257.834 | 53.783 | 0 | 562 | 479.901 | 107.666 | 5.2655 | 479.901 | 100.758 | 0.027484 | 463.284 | 97.0287 | 0.02071 | 543.524 | 543.518 | 1220600 | 43.9629 | 1187440 | 1088740 | 1063150 | 0 | 0 | 1053120 | 663.087 | 0 | 0 | 0 | -24.3124 | 1053140 | 663.412 | 1038940 | 1018165
5681 | 2005-08-25 16:00 | 357 | 742 | 72 | 32.81 | 5.75 | 0 | 22.5882 | 267.244 | 68.4766 | 0 | 357 | 272.22 | 76.649 | 3.3448 | 272.22 | 71.7311 | 0.017459 | 248.732 | 69.0763 | 0.013156 | 308.287 | 308.285 | 692331 | 39.4309 | 649533 | 606490 | 591784 | 0 | 0 | 588605 | 658.091 | 0 | 0 | 0 | 91.8763 | 588513 | 660 | 580829 | 569212.125
5682 | 2005-08-25 17:00 | 127 | 388 | 57 | 32.35 | 5.75 | 0 | 10.2386 | 275.68 | 83.1116 | 0 | 127 | 47.2328 | 54.238 | 1.1899 | 47.2328 | 50.758 | 0.0062108 | 29.9036 | 48.8795 | 0.00468 | 76.4241 | 76.4225 | 171626 | 33.9913 | 143834 | 137120 | 133892 | 0 | 0 | 133704 | 613.879 | 0 | 0 | 0 | 11201.4 | 122503 | 660 | 118748 | 116372.9688
5683 | 2005-08-25 18:00 | 5 | 76 | 2 | 31.89 | 6.69 | 0 | -1.9339 | 284.055 | 90 | 0 | 5 | 0 | 1.424 | 0.046846 | 0 | 1.3326 | 0 | 0 | 1.2833 | 0 | 1.2448 | 1.2447 | 2795.34 | 31.9152 | 377.816 | 380.714 | 378.977 | 0 | 0 | 378.961 | 185.08 | 0 | 0 | 0 | 378.961 | 0 | 660 | 0 | 0
5684 | 2005-08-25 19:00 | 0 | 0 | 0 | 31.43 | 6.69 | 0
5685 | 2005-08-25 20:00 | 0 | 0 | 0 | 30.89 | 6.69 | 0
5686 | 2005-08-25 21:00 | 0 | 0 | 0 | 30.34 | 5.94 | 0
5687 | 2005-08-25 22:00 | 0 | 0 | 0 | 29.8 | 5.94 | 0
5688 | 2005-08-25 23:00 | 0 | 0 | 0 | 29.1 | 5.94 | 0
5689 | 2005-08-26 | 0 | 0 | 0 | 28.41 | 7.45 | 0
5690 | 2005-08-26 01:00 | 0 | 0 | 0 | 27.71 | 7.45 | 0
5691 | 2005-08-26 02:00 | 0 | 0 | 0 | 27.14 | 7.45 | 0
5692 | 2005-08-26 03:00 | 0 | 0 | 0 | 26.57 | 5.29 | 0
5693 | 2005-08-26 04:00 | 0 | 0 | 0 | 25.99 | 5.29 | 0
5694 | 2005-08-26 05:00 | 14 | 145 | 4 | 25.86 | 5.29 | 0 | 1.5056 | 78.5727 | 90 | 0 | 14 | 0 | 3.5458 | 0.13117 | 0 | 3.3183 | 0.00068466 | 0 | 3.1955 | 0.0005159 | 3.1001 | 3.1 | 6961.79 | 25.9286 | 2245.5 | 2243.26 | 2219.22 | 0 | 0 | 2219.11 | 407.67 | 0 | 0 | 0 | 2219.11 | 0 | 660 | 0 | 0
5695 | 2005-08-26 06:00 | 198 | 593 | 56 | 25.73 | 3.81 | 0 | 13.7449 | 86.9169 | 78.8569 | 0 | 198 | 115.5 | 55.6965 | 1.8551 | 95.1115 | 52.1229 | 0.009683 | 75.26 | 50.1939 | 0.0072964 | 121.697 | 121.697 | 273289 | 28.6958 | 239884 | 235214 | 214653 | 0 | 0 | 214206 | 649.922 | 0 | 0 | 0 | 982.962 | 213224 | 660 | 207996 | 203835.8438
5696 | 2005-08-26 07:00 | 401 | 711 | 88 | 25.6 | 3.81 | 0 | 26.0798 | 95.569 | 64.1976 | 0 | 401 | 309.901 | 93.9552 | 3.7571 | 308.546 | 87.9268 | 0.019611 | 288.53 | 84.6727 | 0.014777 | 362.021 | 362.005 | 812965 | 34.4222 | 770925 | 738108 | 713106 | 0 | 0 | 708766 | 677.71 | 0 | 0 | 0 | 0 | 708766 | 677.71 | 698925 | 684946.125
5697 | 2005-08-26 08:00 | 621 | 836 | 104 | 27.19 | 3.81 | 0 | 38.2106 | 105.552 | 49.486 | 0 | 621 | 542.977 | 115.146 | 5.8183 | 542.977 | 107.758 | 0.03037 | 528.335 | 103.77 | 0.022884 | 613.165 | 613.162 | 1377010 | 42.133 | 1349370 | 1249130 | 1217350 | 0 | 0 | 1204620 | 672.865 | 0 | 0 | 0 | 0 | 1204620 | 672.865 | 1186870 | 1163128.25
5698 | 2005-08-26 09:00 | 788 | 920 | 87 | 28.78 | 3.55 | 0 | 49.6572 | 118.599 | 34.7414 | 0 | 788 | 755.767 | 96.0107 | 7.383 | 755.767 | 89.8504 | 0.038537 | 747.569 | 86.5251 | 0.029038 | 809.1 | 809.099 | 1817030 | 48.8385 | 1808880 | 1624880 | 1588930 | 0 | 0 | 1566470 | 658.317 | 0 | 0 | 0 | 50.1408 | 1566420 | 660 | 1540310 | 1509507
5699 | 2005-08-26 10:00 | 905 | 944 | 94 | 30.37 | 3.55 | 0 | 59.3961 | 137.946 | 19.9784 | 0 | 905 | 885.546 | 103.424 | 8.4792 | 885.546 | 96.7884 | 0.044258 | 882.711 | 93.2064 | 0.033349 | 946.672 | 946.667 | 2125980 | 53.839 | 2133750 | 1873070 | 1830370 | 0 | 0 | 1799580 | 646.1 | 0 | 0 | 0 | 9825.18 | 1789760 | 660 | 1755930 | 1720814.625
5700 | 2005-08-26 11:00 | 940 | 908 | 118 | 31.49 | 3.55 | 0 | 65.1469 | 167.583 | 5.2267 | 0 | 940 | 902.13 | 128.188 | 8.8071 | 902.13 | 119.963 | 0.04597 | 901.941 | 115.524 | 0.034639 | 986.975 | 986.969 | 2216480 | 55.9581 | 2229120 | 1937150 | 1895110 | 0 | 0 | 1861430 | 638.907 | 0 | 0 | 0 | 22673.2 | 1838750 | 660 | 1803110 | 1767043.125
5701 | 2005-08-26 12:00 | 929 | 903 | 119 | 32.61 | 4.62 | 0 | 64.0311 | 202.342 | 9.6106 | 0 | 929 | 888.324 | 129.258 | 8.704 | 888.324 | 120.964 | 0.045432 | 887.692 | 116.488 | 0.034234 | 974.087 | 974.085 | 2187550 | 55.1218 | 2198630 | 1918410 | 1874810 | 0 | 0 | 1842030 | 641.152 | 0 | 0 | 0 | 16398.3 | 1825630 | 660 | 1790470 | 1754662.25
5702 | 2005-08-26 13:00 | 868 | 923 | 97 | 33.73 | 4.62 | 0 | 56.7402 | 228.689 | 24.3762 | 0 | 868 | 839.842 | 106.61 | 8.1325 | 839.842 | 99.7698 | 0.042449 | 835.732 | 96.0774 | 0.031986 | 903.886 | 903.881 | 2029880 | 54.6194 | 2032570 | 1776570 | 1735470 | 0 | 0 | 1707310 | 641.196 | 0 | 0 | 0 | 15109.9 | 1692200 | 660 | 1661880 | 1628638.25
5703 | 2005-08-26 14:00 | 743 | 908 | 87 | 34.02 | 4.62 | 0 | 46.3143 | 245.675 | 39.1383 | 0 | 743 | 703.613 | 95.9218 | 6.9613 | 703.613 | 89.7673 | 0.036336 | 693.436 | 86.445 | 0.02738 | 756.511 | 756.507 | 1698920 | 51.5035 | 1685090 | 1493170 | 1460220 | 0 | 0 | 1440510 | 646.738 | 0 | 0 | 0 | 6651.92 | 1433860 | 660 | 1411490 | 1383258.75
5704 | 2005-08-26 15:00 | 563 | 854 | 78 | 34.31 | 5.45 | 0 | 34.5809 | 257.536 | 53.8793 | 0 | 563 | 503.731 | 85.5384 | 5.2749 | 503.731 | 80.0501 | 0.027533 | 486.191 | 77.0875 | 0.020747 | 546.4 | 546.398 | 1227070 | 46.2745 | 1194120 | 1082590 | 1057420 | 0 | 0 | 1047330 | 656.778 | 0 | 0 | 0 | 583.292 | 1046750 | 660 | 1032840 | 1012187.0625
5705 | 2005-08-26 16:00 | 349 | 747 | 65 | 34.59 | 5.45 | 0 | 22.3383 | 266.97 | 68.5844 | 0 | 349 | 272.832 | 69.7498 | 3.2699 | 272.832 | 65.2745 | 0.017067 | 249.113 | 62.8587 | 0.012861 | 302.625 | 302.62 | 679609 | 41.2165 | 636801 | 589228 | 575715 | 0 | 0 | 572644 | 650.919 | 0 | 0 | 0 | 1806.13 | 570838 | 660 | 563334 | 552066.8125
5706 | 2005-08-26 17:00 | 112 | 292 | 61 | 34.2 | 5.45 | 0 | 9.9873 | 275.424 | 83.2325 | 0 | 112 | 34.6531 | 56.5073 | 1.0494 | 34.6531 | 52.8817 | 0.0054773 | 21.6823 | 50.9246 | 0.0041272 | 70.4327 | 70.4296 | 158167 | 35.7422 | 131464 | 124069 | 121296 | 0 | 0 | 121136 | 604.264 | 0 | 0 | 0 | 16317.7 | 104818 | 660 | 101494 | 99464.5391
5707 | 2005-08-26 18:00 | 4 | 54 | 2 | 33.8 | 7.89 | 0 | -2.1944 | 283.812 | 90 | 0 | 4 | 0 | 1.4277 | 0.037477 | 0 | 1.3361 | 0 | 0 | 1.2867 | 0 | 1.2481 | 1.248 | 2802.69 | 33.8234 | 379.806 | 383.488 | 381.716 | 0 | 0 | 381.699 | 185.677 | 0 | 0 | 0 | 381.699 | 0 | 660 | 0 | 0
5708 | 2005-08-26 19:00 | 0 | 0 | 0 | 33.4 | 7.89 | 0
5709 | 2005-08-26 20:00 | 0 | 0 | 0 | 32.43 | 7.89 | 0
5710 | 2005-08-26 21:00 | 0 | 0 | 0 | 31.46 | 6.04 | 0
5711 | 2005-08-26 22:00 | 0 | 0 | 0 | 30.49 | 6.04 | 0
5712 | 2005-08-26 23:00 | 0 | 0 | 0 | 29.77 | 6.04 | 0
5713 | 2005-08-27 | 0 | 0 | 0 | 29.04 | 7.13 | 0
5714 | 2005-08-27 01:00 | 0 | 0 | 0 | 28.31 | 7.13 | 0
5715 | 2005-08-27 02:00 | 0 | 0 | 0 | 27.57 | 7.13 | 0
5716 | 2005-08-27 03:00 | 0 | 0 | 0 | 26.84 | 7.77 | 0
5717 | 2005-08-27 04:00 | 0 | 0 | 0 | 26.1 | 7.77 | 0
5718 | 2005-08-27 05:00 | 13 | 147 | 3 | 25.93 | 7.77 | 0 | 1.3635 | 78.9006 | 90 | 0 | 13 | 0 | 2.6738 | 0.1218 | 0 | 2.5023 | 0.00063575 | 0 | 2.4096 | 0.00047905 | 2.3378 | 2.3377 | 5249.81 | 25.9741 | 1316.18 | 1316.65 | 1307.64 | 0 | 0 | 1307.58 | 340.335 | 0 | 0 | 0 | 1307.58 | 0 | 660 | 0 | 0
5719 | 2005-08-27 06:00 | 199 | 602 | 57 | 25.76 | 4.97 | 0 | 13.6116 | 87.2583 | 78.8346 | 0 | 199 | 116.841 | 56.8512 | 1.8645 | 95.5066 | 53.2036 | 0.0097319 | 75.6214 | 51.2345 | 0.0073332 | 123.057 | 123.063 | 276355 | 28.54 | 242831 | 238308 | 217260 | 0 | 0 | 216805 | 651.271 | 0 | 0 | 0 | 1026.35 | 215778 | 660.689 | 210517 | 206306.9375
5720 | 2005-08-27 07:00 | 406 | 734 | 85 | 25.59 | 4.97 | 0 | 25.9445 | 95.9373 | 64.1625 | 0 | 406 | 319.767 | 91.4954 | 3.8039 | 318.013 | 85.6249 | 0.019855 | 297.429 | 82.456 | 0.014961 | 368.503 | 368.487 | 827525 | 33.914 | 785656 | 754064 | 727080 | 0 | 0 | 722571 | 678.26 | 0 | 0 | 0 | 0 | 722571 | 678.26 | 712518 | 698267.5
5721 | 2005-08-27 08:00 | 611 | 821 | 105 | 27.62 | 4.97 | 0 | 38.0598 | 105.965 | 49.4398 | 0 | 611 | 533.712 | 116.408 | 5.7246 | 533.712 | 108.939 | 0.02988 | 519.359 | 104.907 | 0.022516 | 605.56 | 605.55 | 1359910 | 41.2992 | 1331620 | 1237500 | 1206830 | 0 | 0 | 1194410 | 675.374 | 0 | 0 | 0 | 0 | 1194410 | 675.374 | 1176750 | 1153216
5722 | 2005-08-27 09:00 | 750 | 822 | 126 | 29.65 | 2.96 | 0 | 49.4706 | 119.07 | 34.6847 | 0 | 750 | 675.084 | 141.557 | 7.0269 | 675.084 | 132.474 | 0.036678 | 667.789 | 127.571 | 0.027638 | 771.527 | 771.524 | 1732650 | 49.5377 | 1720410 | 1539510 | 1503530 | 0 | 0 | 1483170 | 654.421 | 0 | 0 | 0 | 820.959 | 1482350 | 660 | 1458790 | 1429613.625
5723 | 2005-08-27 10:00 | 862 | 835 | 146 | 31.67 | 2.96 | 0 | 59.1445 | 138.445 | 19.9099 | 0 | 862 | 784.197 | 164.774 | 8.0763 | 784.197 | 154.201 | 0.042155 | 781.704 | 148.494 | 0.031765 | 902.323 | 902.313 | 2026370 | 54.929 | 2028870 | 1770510 | 1730850 | 0 | 0 | 1702800 | 640.91 | 0 | 0 | 0 | 17901.3 | 1684900 | 660 | 1654830 | 1621728.875
5724 | 2005-08-27 11:00 | 902 | 801 | 179 | 32.91 | 2.96 | 0 | 64.8142 | 167.897 | 5.1284 | 0 | 902 | 795.756 | 199.978 | 8.451 | 795.756 | 187.147 | 0.044111 | 795.596 | 180.221 | 0.033239 | 946.575 | 946.568 | 2125750 | 57.3098 | 2133510 | 1840660 | 1802390 | 0 | 0 | 1771340 | 633.348 | 0 | 0 | 0 | 36387.9 | 1734950 | 660 | 1703120 | 1669052.875
5725 | 2005-08-27 12:00 | 875 | 731 | 221 | 34.15 | 3.73 | 0 | 63.6756 | 202.243 | 9.6715 | 0 | 875 | 719.298 | 249.033 | 8.1981 | 719.298 | 233.055 | 0.042791 | 718.779 | 224.43 | 0.032244 | 914.944 | 914.929 | 2054700 | 56.5648 | 2058690 | 1782140 | 1744180 | 0 | 0 | 1715240 | 635.363 | 0 | 0 | 0 | 30743.6 | 1684490 | 660 | 1654430 | 1621342.625
5726 | 2005-08-27 13:00 | 835 | 844 | 133 | 35.39 | 3.73 | 0 | 56.4218 | 228.391 | 24.4548 | 0 | 835 | 767.012 | 143.744 | 7.8233 | 767.012 | 134.521 | 0.040835 | 763.233 | 129.543 | 0.03077 | 866.022 | 866.015 | 1944860 | 56.6065 | 1943140 | 1680710 | 1643260 | 0 | 0 | 1617440 | 634.207 | 0 | 0 | 0 | 32076.6 | 1585370 | 660 | 1558650 | 1527472.625
5727 | 2005-08-27 14:00 | 708 | 824 | 115 | 36.21 | 3.73 | 0 | 46.032 | 245.356 | 39.2277 | 0 | 708 | 638.242 | 129.233 | 6.6334 | 638.242 | 120.941 | 0.034624 | 628.958 | 116.465 | 0.02609 | 723.086 | 723.075 | 1623840 | 53.9246 | 1606540 | 1405740 | 1374200 | 0 | 0 | 1356200 | 637.05 | 0 | 0 | 0 | 19723.9 | 1336480 | 659.999 | 1316410 | 1290078.625
5728 | 2005-08-27 15:00 | 545 | 814 | 86 | 37.03 | 6.66 | 0 | 34.3194 | 257.239 | 53.979 | 0 | 545 | 478.764 | 95.6463 | 5.1062 | 478.764 | 89.5095 | 0.026653 | 461.996 | 86.1968 | 0.020083 | 531.767 | 531.764 | 1194200 | 47.8023 | 1160210 | 1043660 | 1018780 | 0 | 0 | 1009210 | 649.949 | 0 | 0 | 0 | 3316.23 | 1005890 | 659.999 | 992782 | 972926.0625
5729 | 2005-08-27 16:00 | 331 | 689 | 72 | 37.86 | 6.66 | 0 | 22.0851 | 266.695 | 68.6951 | 0 | 331 | 250.284 | 76.3079 | 3.1012 | 250.284 | 71.4118 | 0.016187 | 228.356 | 68.7689 | 0.012198 | 288.223 | 288.22 | 647266 | 43.6987 | 604501 | 552085 | 539398 | 0 | 0 | 536600 | 639.399 | 0 | 0 | 0 | 7512.58 | 529087 | 660 | 522022 | 511581.2812
5730 | 2005-08-27 17:00 | 117 | 394 | 50 | 37.01 | 6.66 | 0 | 9.7328 | 275.167 | 83.3558 | 0 | 117 | 45.856 | 47.7822 | 1.0962 | 45.856 | 44.7164 | 0.0057218 | 28.3327 | 43.0615 | 0.0043115 | 69.2565 | 69.2548 | 155528 | 38.4129 | 129046 | 119949 | 117333 | 0 | 0 | 117179 | 594.617 | 0 | 0 | 0 | 23836.8 | 93342.4 | 659.999 | 90318.2 | 88511.8672
5731 | 2005-08-27 18:00 | 4 | 68 | 2 | 36.17 | 7.5 | 0 | -2.4578 | 283.568 | 90 | 0 | 4 | 0 | 1.4315 | 0.037477 | 0 | 1.3397 | 0 | 0 | 1.2901 | 0 | 1.2514 | 1.2513 | 2810.04 | 36.194 | 381.805 | 386.434 | 384.629 | 0 | 0 | 384.612 | 186.235 | 0 | 0 | 0 | 384.612 | 0 | 660 | 0 | 0
5732 | 2005-08-27 19:00 | 0 | 0 | 0 | 35.32 | 7.5 | 0
5733 | 2005-08-27 20:00 | 0 | 0 | 0 | 34.39 | 7.5 | 0
5734 | 2005-08-27 21:00 | 0 | 0 | 0 | 33.45 | 9.35 | 0
5735 | 2005-08-27 22:00 | 0 | 0 | 0 | 32.51 | 9.35 | 0
5736 | 2005-08-27 23:00 | 0 | 0 | 0 | 31.71 | 9.35 | 0
5737 | 2005-08-28 | 0 | 0 | 0 | 30.9 | 7.49 | 0
5738 | 2005-08-28 01:00 | 0 | 0 | 0 | 30.09 | 7.49 | 0
5739 | 2005-08-28 02:00 | 0 | 0 | 0 | 29.45 | 7.49 | 0
5740 | 2005-08-28 03:00 | 0 | 0 | 0 | 28.81 | 5.59 | 0
5741 | 2005-08-28 04:00 | 0 | 0 | 0 | 28.18 | 5.59 | 0
5742 | 2005-08-28 05:00 | 12 | 138 | 3 | 27.83 | 5.59 | 0 | 1.2212 | 79.2317 | 90 | 0 | 12 | 0 | 2.6744 | 0.11243 | 0 | 2.5028 | 0.00058685 | 0 | 2.4102 | 0.0004422 | 2.3383 | 2.3384 | 5251.34 | 27.8807 | 1317.19 | 1318.46 | 1308.88 | 0 | 0 | 1308.82 | 338.817 | 0 | 0 | 0 | 1308.82 | 0 | 660 | 0 | 0
5743 | 2005-08-28 06:00 | 195 | 594 | 56 | 27.49 | 4.03 | 0 | 13.4778 | 87.6025 | 78.8114 | 0 | 195 | 115.723 | 56.0786 | 1.827 | 93.8718 | 52.4805 | 0.0095363 | 74.3766 | 50.5382 | 0.0071858 | 121.174 | 121.164 | 272088 | 30.4004 | 238790 | 232115 | 212019 | 0 | 0 | 211572 | 641.316 | 0 | 0 | 0 | 1801.08 | 209771 | 660 | 204597 | 200504.6719
5744 | 2005-08-28 07:00 | 403 | 733 | 84 | 27.14 | 4.03 | 0 | 25.8083 | 96.3083 | 64.1271 | 0 | 403 | 319.743 | 90.6984 | 3.7758 | 317.58 | 84.8791 | 0.019708 | 297.071 | 81.7377 | 0.014851 | 367.459 | 367.434 | 825166 | 35.966 | 783299 | 744471 | 716841 | 0 | 0 | 712350 | 670.015 | 0 | 0 | 0 | 247.323 | 712103 | 672.237 | 702410 | 688361.4375
5745 | 2005-08-28 08:00 | 589 | 763 | 120 | 29.34 | 4.03 | 0 | 37.9074 | 106.379 | 49.394 | 0 | 589 | 496.838 | 131.901 | 5.5185 | 496.838 | 123.438 | 0.028805 | 483.512 | 118.869 | 0.021705 | 584.331 | 584.324 | 1312240 | 43.3758 | 1282200 | 1179550 | 1150440 | 0 | 0 | 1138890 | 667.665 | 0 | 0 | 0 | 0 | 1138890 | 667.665 | 1122760 | 1100302.625
5746 | 2005-08-28 09:00 | 761 | 859 | 110 | 31.54 | 4.29 | 0 | 49.2816 | 119.541 | 34.6295 | 0 | 761 | 706.76 | 120.258 | 7.13 | 706.76 | 112.542 | 0.037216 | 699.152 | 108.377 | 0.028043 | 783.331 | 783.324 | 1759150 | 50.038 | 1748180 | 1560780 | 1524900 | 0 | 0 | 1503800 | 652.772 | 0 | 0 | 0 | 1605.08 | 1502200 | 660 | 1478120 | 1448556.625
5747 | 2005-08-28 10:00 | 859 | 810 | 167 | 33.74 | 4.29 | 0 | 58.8898 | 138.941 | 19.8457 | 0 | 859 | 760.244 | 186.656 | 8.0482 | 760.244 | 174.68 | 0.042009 | 757.844 | 168.215 | 0.031654 | 898.308 | 898.299 | 2017350 | 54.9531 | 2019380 | 1761990 | 1724710 | 0 | 0 | 1696850 | 640.253 | 0 | 0 | 0 | 19358.5 | 1677490 | 660 | 1647670 | 1614718
5748 | 2005-08-28 11:00 | 948 | 903 | 135 | 34.77 | 4.29 | 0 | 64.4786 | 168.207 | 5.052 | 0 | 948 | 897.406 | 145.992 | 8.882 | 897.406 | 136.625 | 0.046361 | 897.231 | 131.568 | 0.034934 | 997.97 | 997.966 | 2241180 | 58.3367 | 2255160 | 1936740 | 1894960 | 0 | 0 | 1860510 | 631.467 | 0 | 0 | 0 | 43564.8 | 1816950 | 660 | 1782120 | 1746475
5749 | 2005-08-28 12:00 | 911 | 869 | 136 | 35.81 | 2.71 | 0 | 63.317 | 202.148 | 9.7467 | 0 | 911 | 854.851 | 147.039 | 8.5354 | 854.851 | 137.605 | 0.044552 | 854.225 | 132.512 | 0.033571 | 957.168 | 957.16 | 2149530 | 60.8954 | 2158570 | 1828670 | 1788920 | 0 | 0 | 1757350 | 623.141 | 0 | 0 | 0 | 75839 | 1681510 | 660 | 1651550 | 1618523.25
5750 | 2005-08-28 13:00 | 840 | 866 | 122 | 36.84 | 2.71 | 0 | 56.0997 | 228.096 | 24.5398 | 0 | 840 | 786.913 | 132.833 | 7.8701 | 786.913 | 124.31 | 0.041079 | 783.006 | 119.71 | 0.030954 | 875.664 | 875.656 | 1966490 | 59.7894 | 1965880 | 1673110 | 1637590 | 0 | 0 | 1611080 | 623.736 | 0 | 0 | 0 | 65764.8 | 1545320 | 660 | 1519890 | 1489494.625
5751 | 2005-08-28 14:00 | 726 | 885 | 93 | 37.39 | 2.71 | 0 | 45.746 | 245.039 | 39.3215 | 0 | 726 | 683.684 | 102.519 | 6.8021 | 683.684 | 95.941 | 0.035504 | 673.68 | 92.3903 | 0.026753 | 743.114 | 743.111 | 1668840 | 56.8656 | 1653600 | 1425800 | 1393830 | 0 | 0 | 1374890 | 629.438 | 0 | 0 | 0 | 40837.6 | 1334050 | 660 | 1314030 | 1287750.625
5752 | 2005-08-28 15:00 | 552 | 844 | 79 | 37.94 | 3.9 | 0 | 34.0544 | 256.942 | 54.082 | 0 | 552 | 495.508 | 86.8542 | 5.1718 | 495.508 | 81.2815 | 0.026995 | 478.05 | 78.2733 | 0.020341 | 539.653 | 539.652 | 1211920 | 51.0139 | 1178490 | 1043200 | 1019730 | 0 | 0 | 1009790 | 637.971 | 0 | 0 | 0 | 14808.6 | 994978 | 660 | 982041 | 962400.25
5753 | 2005-08-28 16:00 | 341 | 727 | 70 | 38.5 | 3.9 | 0 | 21.8286 | 266.421 | 68.8085 | 0 | 341 | 263.46 | 75.0481 | 3.1949 | 263.46 | 70.2329 | 0.016676 | 240.192 | 67.6336 | 0.012566 | 298.603 | 298.6 | 670578 | 45.7341 | 627774 | 567505 | 554932 | 0 | 0 | 551911 | 633.452 | 0 | 0 | 0 | 12963.1 | 538948 | 659.999 | 531777 | 521141.7188
5754 | 2005-08-28 17:00 | 103 | 208 | 68 | 37.59 | 3.9 | 0 | 9.4754 | 274.909 | 83.4813 | 0 | 103 | 24.1366 | 62.3401 | 0.96503 | 24.1366 | 58.3403 | 0.0050371 | 14.7131 | 56.1811 | 0.0037956 | 68.7711 | 68.7691 | 154438 | 39.256 | 128051 | 118443 | 115867 | 0 | 0 | 115714 | 591.121 | 0 | 0 | 0 | 26639.1 | 89075.2 | 659.999 | 86166.5 | 84443.1328
5755 | 2005-08-28 18:00 | 3 | 34 | 2 | 36.68 | 5.36 | 0 | -2.7239 | 283.323 | 90 | 0 | 3 | 0 | 1.5719 | 0.028108 | 0 | 1.471 | 0 | 0 | 1.4166 | 0 | 1.3741 | 1.374 | 3085.67 | 36.7103 | 460.064 | 465.666 | 463.462 | 0 | 0 | 463.442 | 204.176 | 0 | 0 | 0 | 463.442 | 0 | 660 | 0 | 0
5756 | 2005-08-28 19:00 | 0 | 0 | 0 | 35.77 | 5.36 | 0
5757 | 2005-08-28 20:00 | 0 | 0 | 0 | 34.86 | 5.36 | 0
5758 | 2005-08-28 21:00 | 0 | 0 | 0 | 33.95 | 6.02 | 0
5759 | 2005-08-28 22:00 | 0 | 0 | 0 | 33.04 | 6.02 | 0
5760 | 2005-08-28 23:00 | 0 | 0 | 0 | 32.12 | 6.02 | 0
5761 | 2005-08-29 | 0 | 0 | 0 | 31.21 | 6.67 | 0
5762 | 2005-08-29 01:00 | 0 | 0 | 0 | 30.3 | 6.67 | 0
5763 | 2005-08-29 02:00 | 0 | 0 | 0 | 29.76 | 6.67 | 0
5764 | 2005-08-29 03:00 | 0 | 0 | 0 | 29.22 | 6.23 | 0
5765 | 2005-08-29 04:00 | 0 | 0 | 0 | 28.68 | 6.23 | 0
5766 | 2005-08-29 05:00 | 10 | 136 | 1 | 28.63 | 6.23 | 0 | 1.0788 | 79.5656 | 90 | 0 | 10 | 0 | 0.90207 | 0.093692 | 0 | 0.84419 | 0.00048904 | 0 | 0.81295 | 0.0003685 | 0.78892 | 0.78889 | 1771.64 | 28.6464 | 152.136 | 152.787 | 152.01 | 0 | 0 | 152.004 | 118.963 | 0 | 0 | 0 | 152.004 | 0 | 660 | 0 | 0
5767 | 2005-08-29 06:00 | 195 | 598 | 56 | 28.58 | 3.77 | 0 | 13.3435 | 87.9493 | 78.7874 | 0 | 195 | 117.114 | 56.2731 | 1.827 | 94.2304 | 52.6625 | 0.0095363 | 74.712 | 50.7135 | 0.0071858 | 121.67 | 121.672 | 273226 | 31.553 | 239916 | 231821 | 210606 | 0 | 0 | 210162 | 640.829 | 0 | 0 | 0 | 2252.72 | 207910 | 660 | 202766 | 198710.4219
5768 | 2005-08-29 07:00 | 400 | 730 | 83 | 28.53 | 3.77 | 0 | 25.6711 | 96.6817 | 64.0915 | 0 | 400 | 319.73 | 89.8999 | 3.7477 | 317.142 | 84.1318 | 0.019562 | 296.708 | 81.0181 | 0.01474 | 366.408 | 366.398 | 822844 | 37.4828 | 780989 | 736844 | 708519 | 0 | 0 | 704001 | 660.703 | 0 | 0 | 0 | 2696.94 | 701304 | 668.134 | 691902 | 678064
5769 | 2005-08-29 08:00 | 614 | 835 | 103 | 30.22 | 3.77 | 0 | 37.7532 | 106.796 | 49.3487 | 0 | 614 | 543.71 | 114.819 | 5.7527 | 543.71 | 107.452 | 0.030027 | 529.165 | 103.475 | 0.022626 | 613.683 | 613.682 | 1378170 | 45.2151 | 1350580 | 1231920 | 1204380 | 0 | 0 | 1191550 | 662.901 | 0 | 0 | 0 | 0 | 1191550 | 662.901 | 1174550 | 1151059.125
5770 | 2005-08-29 09:00 | 769 | 891 | 96 | 31.91 | 4.58 | 0 | 49.0901 | 120.014 | 34.5762 | 0 | 769 | 733.228 | 105.96 | 7.2049 | 733.228 | 99.1614 | 0.037607 | 725.363 | 95.4915 | 0.028338 | 796.257 | 796.252 | 1788180 | 50.3601 | 1778620 | 1585700 | 1548880 | 0 | 0 | 1527280 | 654.587 | 0 | 0 | 0 | 1887.92 | 1525400 | 660 | 1500600 | 1470589.25
5771 | 2005-08-29 10:00 | 876 | 894 | 114 | 33.6 | 4.58 | 0 | 58.632 | 139.436 | 19.7863 | 0 | 876 | 839.749 | 124.84 | 8.2074 | 839.749 | 116.83 | 0.04284 | 837.115 | 112.507 | 0.032281 | 921.164 | 921.158 | 2068690 | 54.9443 | 2073410 | 1809690 | 1770230 | 0 | 0 | 1740900 | 640.467 | 0 | 0 | 0 | 17851.1 | 1723050 | 660 | 1691640 | 1657808.25
5772 | 2005-08-29 11:00 | 912 | 825 | 171 | 34.12 | 4.58 | 0 | 64.1402 | 168.514 | 4.9991 | 0 | 912 | 820.325 | 192.505 | 8.5447 | 820.325 | 180.154 | 0.044601 | 820.169 | 173.486 | 0.033607 | 963.878 | 963.874 | 2164620 | 56.4541 | 2174460 | 1884520 | 1842070 | 0 | 0 | 1810070 | 637.49 | 0 | 0 | 0 | 26523.9 | 1783540 | 660 | 1749950 | 1714948.125
5773 | 2005-08-29 12:00 | 925 | 879 | 144 | 34.63 | 8.11 | 0 | 62.9555 | 202.057 | 9.8362 | 0 | 925 | 863.994 | 155.358 | 8.6665 | 863.994 | 145.39 | 0.045236 | 863.349 | 140.009 | 0.034086 | 973.291 | 973.282 | 2185740 | 52.6156 | 2196720 | 1940640 | 1894900 | 0 | 0 | 1862460 | 651.409 | 0 | 0 | 0 | 3951.64 | 1858500 | 660 | 1822100 | 1785662.875
5774 | 2005-08-29 13:00 | 862 | 889 | 128 | 35.15 | 8.11 | 0 | 55.7739 | 227.807 | 24.6313 | 0 | 862 | 806.958 | 139.168 | 8.0763 | 806.958 | 130.239 | 0.042155 | 802.919 | 125.419 | 0.031765 | 900.518 | 900.513 | 2022320 | 51.7909 | 2024610 | 1794530 | 1754790 | 0 | 0 | 1726810 | 650.542 | 0 | 0 | 0 | 3756.99 | 1723060 | 660 | 1691640 | 1657811.375
5775 | 2005-08-29 14:00 | 704 | 810 | 127 | 35.26 | 8.11 | 0 | 45.4562 | 244.724 | 39.4196 | 0 | 704 | 625.414 | 142.122 | 6.5959 | 625.414 | 133.003 | 0.034429 | 616.206 | 128.081 | 0.025943 | 721.983 | 721.979 | 1621390 | 48.6017 | 1603980 | 1441170 | 1407690 | 0 | 0 | 1389940 | 657.493 | 0 | 0 | 0 | 385.772 | 1389560 | 660 | 1368240 | 1340879.25
5776 | 2005-08-29 15:00 | 545 | 806 | 97 | 35.37 | 6.91 | 0 | 33.7859 | 256.645 | 54.1884 | 0 | 545 | 471.388 | 107.375 | 5.1062 | 471.388 | 100.485 | 0.026653 | 454.676 | 96.7664 | 0.020083 | 534.919 | 534.91 | 1201280 | 46.0345 | 1167500 | 1059530 | 1035240 | 0 | 0 | 1025530 | 655.575 | 0 | 0 | 0 | 679.496 | 1024850 | 660 | 1011380 | 991148.1875
5777 | 2005-08-29 16:00 | 324 | 689 | 70 | 35.48 | 6.91 | 0 | 21.569 | 266.146 | 68.9246 | 0 | 324 | 248.456 | 75.1807 | 3.0356 | 248.456 | 70.357 | 0.015845 | 226.332 | 67.7531 | 0.01194 | 285.275 | 285.27 | 640644 | 41.1675 | 597897 | 553123 | 540470 | 0 | 0 | 537731 | 647.531 | 0 | 0 | 0 | 2523.63 | 535208 | 660 | 528077 | 517515.125
5778 | 2005-08-29 17:00 | 109 | 360 | 51 | 34.66 | 6.91 | 0 | 9.2151 | 274.651 | 83.609 | 0 | 109 | 40.3154 | 48.934 | 1.0212 | 40.3154 | 45.7943 | 0.0053305 | 24.2222 | 44.0994 | 0.0040167 | 66.2759 | 66.2732 | 148833 | 35.9813 | 122926 | 115822 | 113298 | 0 | 0 | 113157 | 600.171 | 0 | 0 | 0 | 17882.3 | 95274.6 | 659.999 | 92198.9 | 90354.8828
5779 | 2005-08-29 18:00 | 3 | 55 | 1 | 33.84 | 9.36 | 0 | -2.9928 | 283.076 | 90 | 0 | 3 | 0 | 0.72984 | 0.028108 | 0 | 0.68301 | 0 | 0 | 0.65774 | 0 | 0.638 | 0.63796 | 1432.71 | 33.8509 | 99.5435 | 100.579 | 99.9805 | 0 | 0 | 99.9764 | 98.1327 | 0 | 0 | 0 | 99.9764 | 0 | 660 | 0 | 0
5780 | 2005-08-29 19:00 | 0 | 0 | 0 | 33.02 | 9.36 | 0
5781 | 2005-08-29 20:00 | 0 | 0 | 0 | 32.06 | 9.36 | 0
5782 | 2005-08-29 21:00 | 0 | 0 | 0 | 31.1 | 9.4 | 0
5783 | 2005-08-29 22:00 | 0 | 0 | 0 | 30.14 | 9.4 | 0
5784 | 2005-08-29 23:00 | 0 | 0 | 0 | 29.28 | 9.4 | 0
5785 | 2005-08-30 | 0 | 0 | 0 | 28.43 | 11.11 | 0
5786 | 2005-08-30 01:00 | 0 | 0 | 0 | 27.57 | 11.11 | 0
5787 | 2005-08-30 02:00 | 0 | 0 | 0 | 26.96 | 11.11 | 0
5788 | 2005-08-30 03:00 | 0 | 0 | 0 | 26.35 | 8.25 | 0
5789 | 2005-08-30 04:00 | 0 | 0 | 0 | 25.74 | 8.25 | 0
5790 | 2005-08-30 05:00 | 9 | 132 | 1 | 25.2 | 8.25 | 0 | 0.93616 | 79.9025 | 90 | 0 | 9 | 0 | 0.90267 | 0.084323 | 0 | 0.84476 | 0.00044014 | 0 | 0.81349 | 0.00033165 | 0.78941 | 0.78938 | 1772.74 | 25.2145 | 152.323 | 152.362 | 151.608 | 0 | 0 | 151.601 | 118.414 | 0 | 0 | 0 | 151.601 | 0 | 660 | 0 | 0
5791 | 2005-08-30 06:00 | 192 | 593 | 56 | 24.67 | 7.04 | 0 | 13.2087 | 88.2987 | 78.7626 | 0 | 192 | 115.988 | 56.4697 | 1.7989 | 92.5641 | 52.8465 | 0.0093896 | 73.4426 | 50.8907 | 0.0070753 | 120.61 | 120.586 | 270791 | 27.0543 | 237608 | 234942 | 213132 | 0 | 0 | 212699 | 656.919 | 0 | 0 | 0 | 211.224 | 212488 | 662.568 | 207237 | 203092.5156
5792 | 2005-08-30 07:00 | 394 | 716 | 85 | 24.13 | 7.04 | 0 | 25.5328 | 97.0574 | 64.0557 | 0 | 394 | 313.638 | 91.8761 | 3.6915 | 310.652 | 85.9812 | 0.019268 | 290.681 | 82.799 | 0.014519 | 362.29 | 362.261 | 813548 | 31.2929 | 771620 | 749635 | 719328 | 0 | 0 | 714944 | 681.014 | 0 | 0 | 0 | 1046.97 | 713897 | 685.009 | 703724 | 689649.125
5793 | 2005-08-30 08:00 | 593 | 817 | 95 | 26.13 | 7.04 | 0 | 37.5974 | 107.214 | 49.304 | 0 | 593 | 532.23 | 106.732 | 5.556 | 532.23 | 99.8834 | 0.029 | 518.029 | 96.1868 | 0.021852 | 595.81 | 595.809 | 1338040 | 37.9108 | 1308930 | 1235760 | 1204990 | 0 | 0 | 1192990 | 686.082 | 0 | 0 | 0 | 0 | 1192990 | 686.082 | 1174850 | 1151350
5794 | 2005-08-30 09:00 | 729 | 747 | 167 | 28.13 | 3.95 | 0 | 48.8961 | 120.487 | 34.5247 | 0 | 729 | 614.479 | 187.588 | 6.8302 | 614.479 | 175.552 | 0.035651 | 607.912 | 169.055 | 0.026864 | 753.684 | 753.671 | 1692550 | 46.329 | 1678430 | 1525170 | 1488760 | 0 | 0 | 1469420 | 666 | 0 | 0 | 0 | 0 | 1469420 | 666 | 1445940 | 1417020.875
5795 | 2005-08-30 10:00 | 873 | 860 | 142 | 30.13 | 3.95 | 0 | 58.3712 | 139.928 | 19.7317 | 0 | 873 | 808.113 | 161.496 | 8.1793 | 808.113 | 151.135 | 0.042693 | 805.593 | 145.541 | 0.03217 | 922.631 | 922.626 | 2071980 | 52.4088 | 2076880 | 1835610 | 1795950 | 0 | 0 | 1766570 | 649.3 | 0 | 0 | 0 | 5421.03 | 1761150 | 660 | 1728370 | 1693804.25
5796 | 2005-08-30 11:00 | 916 | 871 | 136 | 31.31 | 3.95 | 0 | 63.799 | 168.819 | 4.9712 | 0 | 916 | 866.052 | 147.533 | 8.5822 | 866.052 | 138.067 | 0.044796 | 865.889 | 132.957 | 0.033755 | 968.913 | 968.904 | 2175920 | 54.7063 | 2186370 | 1911510 | 1870280 | 0 | 0 | 1837730 | 641.925 | 0 | 0 | 0 | 15163.1 | 1822570 | 660 | 1787530 | 1751775.75
5797 | 2005-08-30 12:00 | 920 | 876 | 144 | 32.49 | 1.91 | 0 | 62.5912 | 201.969 | 9.9399 | 0 | 920 | 861.004 | 155.635 | 8.6197 | 861.004 | 145.649 | 0.044992 | 860.348 | 140.259 | 0.033902 | 970.621 | 970.614 | 2179760 | 59.321 | 2190420 | 1871020 | 1830020 | 0 | 0 | 1797480 | 627.64 | 0 | 0 | 0 | 55049.3 | 1742430 | 660 | 1710330 | 1676119.75
5798 | 2005-08-30 13:00 | 820 | 824 | 142 | 33.67 | 1.91 | 0 | 55.4446 | 227.521 | 24.7291 | 0 | 820 | 747.742 | 160.836 | 7.6828 | 747.742 | 150.516 | 0.040101 | 743.967 | 144.946 | 0.030217 | 862.275 | 862.261 | 1936410 | 57.5057 | 1934260 | 1665270 | 1628570 | 0 | 0 | 1602970 | 631.386 | 0 | 0 | 0 | 40777.1 | 1562200 | 660 | 1536230 | 1505505.625
5799 | 2005-08-30 14:00 | 690 | 783 | 135 | 34.18 | 1.91 | 0 | 45.1629 | 244.411 | 39.5221 | 0 | 690 | 603.733 | 150.54 | 6.4648 | 603.733 | 140.881 | 0.033744 | 594.786 | 135.667 | 0.025427 | 708.565 | 708.561 | 1591240 | 53.767 | 1572480 | 1376680 | 1344670 | 0 | 0 | 1327450 | 637.383 | 0 | 0 | 0 | 18455.5 | 1308990 | 660 | 1289550 | 1263755.75
5800 | 2005-08-30 15:00 | 539 | 802 | 96 | 34.69 | 3.27 | 0 | 33.5141 | 256.349 | 54.2981 | 0 | 539 | 468.215 | 106.532 | 5.05 | 468.215 | 99.6972 | 0.026359 | 451.509 | 96.0074 | 0.019862 | 531.11 | 531.106 | 1192720 | 48.1024 | 1158680 | 1040680 | 1016550 | 0 | 0 | 1007010 | 649.424 | 0 | 0 | 0 | 4418.25 | 1002590 | 659.999 | 989532 | 969741.5625
5801 | 2005-08-30 16:00 | 326 | 715 | 66 | 35.2 | 3.27 | 0 | 21.3063 | 265.87 | 69.0432 | 0 | 326 | 255.929 | 71.2916 | 3.0544 | 255.929 | 66.7174 | 0.015943 | 232.947 | 64.2482 | 0.012013 | 288.291 | 288.289 | 647422 | 42.4803 | 604655 | 555682 | 542982 | 0 | 0 | 540178 | 643.103 | 0 | 0 | 0 | 4682.16 | 535495 | 660 | 528361 | 517794.0625
5802 | 2005-08-30 17:00 | 86 | 106 | 69 | 34.7 | 3.27 | 0 | 8.9521 | 274.392 | 83.7387 | 0 | 86 | 11.9149 | 62.7148 | 0.80575 | 11.9149 | 58.6909 | 0.0042058 | 7.0483 | 56.5188 | 0.0031691 | 61.6631 | 61.6584 | 138469 | 36.2571 | 113493 | 106730 | 104317 | 0 | 0 | 104196 | 596.514 | 0 | 0 | 0 | 19623.4 | 84572.1 | 659.999 | 81787.6 | 80151.8125
5803 | 2005-08-30 18:00 | 2 | 15 | 2 | 34.21 | 3.29 | 0 | -3.2642 | 282.829 | 90 | 0 | 2 | 0 | 1.9719 | 0.018738 | 0 | 1.8454 | 0 | 0 | 1.7771 | 0 | 1.7237 | 1.7238 | 3871.16 | 34.2535 | 722.383 | 728.295 | 724.372 | 0 | 0 | 724.34 | 255.243 | 0 | 0 | 0 | 724.34 | 0 | 660 | 0 | 0
5804 | 2005-08-30 19:00 | 0 | 0 | 0 | 33.72 | 3.29 | 0
5805 | 2005-08-30 20:00 | 0 | 0 | 0 | 32.69 | 3.29 | 0
5806 | 2005-08-30 21:00 | 0 | 0 | 0 | 31.67 | 6.18 | 0
5807 | 2005-08-30 22:00 | 0 | 0 | 0 | 30.65 | 6.18 | 0
5808 | 2005-08-30 23:00 | 0 | 0 | 0 | 29.53 | 6.18 | 0
5809 | 2005-08-31 | 0 | 0 | 0 | 28.4 | 3.82 | 0
5810 | 2005-08-31 01:00 | 0 | 0 | 0 | 27.28 | 3.82 | 0
5811 | 2005-08-31 02:00 | 0 | 0 | 0 | 26.49 | 3.82 | 0
5812 | 2005-08-31 03:00 | 0 | 0 | 0 | 25.71 | 2.2 | 0
5813 | 2005-08-31 04:00 | 0 | 0 | 0 | 24.92 | 2.2 | 0
5814 | 2005-08-31 05:00 | 8 | 128 | 0 | 23.98 | 2.2 | 0 | 0.79342 | 80.242 | 90 | 0 | 8 | 0 | 0 | 0.074954 | 0 | 0 | 0.00039123 | 0 | 0 | 0.0002948 | 0.00028596 | 0.00028404 | 0.63843 | 23.98 | 0.0037889 | 0.0037852 | 0.0037633 | 0 | 0 | 0.0037632 | 7.6738 | 0 | 0 | 0 | 0.0037632 | 0 | 660 | 0 | 0
5815 | 2005-08-31 06:00 | 187 | 594 | 52 | 23.04 | 1.66 | 0 | 13.0733 | 88.6506 | 78.7372 | 0 | 187 | 116.566 | 52.7796 | 1.752 | 92.1944 | 49.3932 | 0.0091451 | 73.202 | 47.5651 | 0.006891 | 117.151 | 117.123 | 263017 | 26.3323 | 230308 | 228402 | 206466 | 0 | 0 | 206059 | 658.376 | 0 | 0 | 0 | 213.225 | 205846 | 663.603 | 200665 | 196651.7656
5816 | 2005-08-31 07:00 | 395 | 725 | 84 | 22.1 | 1.66 | 0 | 25.3935 | 97.4353 | 64.0198 | 0 | 395 | 317.692 | 91.0994 | 3.7008 | 314.214 | 85.2543 | 0.019317 | 294.06 | 82.0991 | 0.014556 | 364.889 | 364.855 | 819371 | 32.356 | 777530 | 751554 | 718837 | 0 | 0 | 714417 | 677.523 | 0 | 0 | 0 | 946.816 | 713470 | 681.257 | 703437 | 689368.125
5817 | 2005-08-31 08:00 | 580 | 777 | 108 | 24.48 | 1.66 | 0 | 37.4399 | 107.635 | 49.2601 | 0 | 580 | 506.703 | 120.451 | 5.4341 | 506.703 | 112.723 | 0.028364 | 493.218 | 108.551 | 0.021373 | 583.737 | 583.73 | 1310910 | 40.8885 | 1280820 | 1192290 | 1163260 | 0 | 0 | 1151770 | 677.365 | 0 | 0 | 0 | 0 | 1151770 | 677.365 | 1134900 | 1112205.5
5818 | 2005-08-31 09:00 | 745 | 807 | 139 | 26.86 | 1.47 | 0 | 48.6996 | 120.961 | 34.4753 | 0 | 745 | 664.974 | 156.095 | 6.9801 | 664.974 | 146.08 | 0.036434 | 657.891 | 140.673 | 0.027453 | 774.634 | 774.626 | 1739620 | 48.9137 | 1727710 | 1550770 | 1516470 | 0 | 0 | 1495940 | 657.789 | 0 | 0 | 0 | 335.496 | 1495600 | 660 | 1471710 | 1442273.125
5819 | 2005-08-31 10:00 | 808 | 641 | 265 | 29.24 | 1.47 | 0 | 58.1073 | 140.417 | 19.6822 | 0 | 808 | 602.181 | 292.383 | 7.5703 | 602.181 | 273.623 | 0.039515 | 600.313 | 263.497 | 0.029775 | 837.924 | 837.919 | 1881750 | 53.0957 | 1876830 | 1651510 | 1613670 | 0 | 0 | 1589600 | 645.243 | 0 | 0 | 0 | 9759.12 | 1579840 | 660 | 1553300 | 1522234.5
5820 | 2005-08-31 11:00 | 920 | 833 | 177 | 30.85 | 1.47 | 0 | 63.4552 | 169.12 | 4.9692 | 0 | 920 | 827.431 | 199.302 | 8.6197 | 827.431 | 186.514 | 0.044992 | 827.275 | 179.611 | 0.033902 | 976.713 | 976.703 | 2193420 | 58.6568 | 2204820 | 1889830 | 1848480 | 0 | 0 | 1815610 | 631.067 | 0 | 0 | 0 | 47413 | 1768190 | 660 | 1735160 | 1700455.75
5821 | 2005-08-31 12:00 | 867 | 740 | 214 | 32.46 | 2.99 | 0 | 62.2242 | 201.886 | 10.0575 | 0 | 867 | 726.697 | 243.36 | 8.1231 | 726.697 | 227.746 | 0.0424 | 726.13 | 219.317 | 0.031949 | 917.115 | 917.113 | 2059610 | 56.0536 | 2063860 | 1791220 | 1749450 | 0 | 0 | 1720570 | 637.829 | 0 | 0 | 0 | 23965.7 | 1696600 | 660 | 1666120 | 1632797.125
5822 | 2005-08-31 13:00 | 823 | 821 | 150 | 34.07 | 2.99 | 0 | 55.112 | 227.24 | 24.8333 | 0 | 823 | 744.594 | 169.401 | 7.7109 | 744.594 | 158.532 | 0.040248 | 740.801 | 152.665 | 0.030328 | 866.691 | 866.684 | 1946360 | 56.3662 | 1944710 | 1684110 | 1645540 | 0 | 0 | 1619810 | 635.89 | 0 | 0 | 0 | 29106.2 | 1590700 | 660 | 1563810 | 1532532.75
5823 | 2005-08-31 14:00 | 717 | 853 | 116 | 34.44 | 2.99 | 0 | 44.866 | 244.1 | 39.6288 | 0 | 717 | 656.155 | 131.177 | 6.7177 | 656.155 | 122.76 | 0.035064 | 646.366 | 118.217 | 0.026422 | 741.671 | 741.661 | 1665580 | 53.5199 | 1650200 | 1447260 | 1415490 | 0 | 0 | 1396580 | 639.694 | 0 | 0 | 0 | 16669 | 1379910 | 660 | 1358830 | 1331651.875
5824 | 2005-08-31 15:00 | 543 | 762 | 125 | 34.8 | 4.52 | 0 | 33.239 | 256.054 | 54.4109 | 0 | 543 | 443.802 | 136.922 | 5.0875 | 443.802 | 128.137 | 0.026555 | 427.862 | 123.395 | 0.02001 | 534.739 | 534.732 | 1200870 | 47.239 | 1167090 | 1052830 | 1028480 | 0 | 0 | 1018780 | 651.651 | 0 | 0 | 0 | 2301.33 | 1016480 | 660 | 1003160 | 983097.25
5825 | 2005-08-31 16:00 | 299 | 592 | 86 | 35.16 | 4.52 | 0 | 21.0407 | 265.595 | 69.1644 | 0 | 299 | 211.017 | 90.9502 | 2.8014 | 211.017 | 85.1146 | 0.014622 | 191.905 | 81.9646 | 0.011018 | 265.664 | 265.658 | 596603 | 41.3398 | 554081 | 511852 | 499758 | 0 | 0 | 497396 | 644.772 | 0 | 0 | 0 | 3912.21 | 493484 | 660 | 486806 | 477069.5
5826 | 2005-08-31 17:00 | 85 | 395 | 24 | 34.16 | 4.52 | 0 | 8.6864 | 274.132 | 83.8705 | 0 | 85 | 43.1275 | 23.9625 | 0.79638 | 43.1275 | 22.4251 | 0.0041569 | 25.0886 | 21.5951 | 0.0031323 | 45.2863 | 45.2849 | 101698 | 35.2134 | 80441.8 | 76001.6 | 74404.4 | 0 | 0 | 74339.7 | 582.941 | 0 | 0 | 0 | 21387.7 | 52952 | 659.999 | 51108.1 | 50085.9219
5827 | 2005-08-31 18:00 | 2 | 51 | 1 | 33.15 | 5.61 | 0 | -3.538 | 282.58 | 90 | 0 | 2 | 0 | 0.69957 | 0.018738 | 0 | 0.65469 | 0 | 0 | 0.63046 | 0 | 0.61154 | 0.61152 | 1373.32 | 33.1633 | 91.4843 | 92.3632 | 91.7511 | 0 | 0 | 91.7474 | 94.6796 | 0 | 0 | 0 | 91.7474 | 0 | 660 | 0 | 0
5828 | 2005-08-31 19:00 | 0 | 0 | 0 | 32.14 | 5.61 | 0
5829 | 2005-08-31 20:00 | 0 | 0 | 0 | 30.8 | 5.61 | 0
5830 | 2005-08-31 21:00 | 0 | 0 | 0 | 30.58 | 5.83 | 0
5831 | 2005-08-31 22:00 | 0 | 0 | 0 | 29.85 | 5.56 | 0
5832 | 2005-08-31 23:00 | 0 | 0 | 0 | 29.13 | 5.28 | 0
5833 | 2006-09-01 | 0 | 0 | 0 | 28.4 | 5 | 0
5834 | 2006-09-01 01:00 | 0 | 0 | 0 | 27.68 | 4.72 | 0
5835 | 2006-09-01 02:00 | 0 | 0 | 0 | 26.95 | 4.45 | 0
5836 | 2006-09-01 03:00 | 0 | 0 | 0 | 25.73 | 3.67 | 0
5837 | 2006-09-01 04:00 | 0 | 0 | 0 | 25.25 | 3.67 | 0
5838 | 2006-09-01 05:00 | 7 | 108 | 1 | 25.01 | 3.67 | 0 | 0.68442 | 80.5011 | 90 | 0 | 7 | 0 | 0.90369 | 0.065585 | 0 | 0.84571 | 0.00034233 | 0 | 0.81441 | 0.00025795 | 0.79023 | 0.7902 | 1774.6 | 25.0294 | 152.645 | 152.65 | 151.891 | 0 | 0 | 151.885 | 118.493 | 0 | 0 | 0 | 151.885 | 0 | 660 | 0 | 0
5839 | 2006-09-01 06:00 | 188 | 591 | 55 | 24.77 | 2.96 | 0 | 12.9696 | 88.9187 | 78.7182 | 0 | 188 | 115.933 | 55.8499 | 1.7614 | 91.095 | 52.2665 | 0.009194 | 72.3678 | 50.3321 | 0.0069279 | 119.026 | 119.014 | 267263 | 27.8378 | 234312 | 230672 | 209499 | 0 | 0 | 209075 | 654.462 | 0 | 0 | 0 | 387.91 | 208687 | 660.767 | 203518 | 199447.8125
5840 | 2006-09-01 07:00 | 404 | 787 | 68 | 24.53 | 2.96 | 0 | 25.2865 | 97.723 | 63.9933 | 0 | 404 | 344.913 | 75.1665 | 3.7852 | 340.696 | 70.3436 | 0.019757 | 318.881 | 67.7403 | 0.014887 | 375.037 | 375.029 | 842226 | 34.1972 | 800703 | 767353 | 731721 | 0 | 0 | 727022 | 669.646 | 0 | 0 | 0 | 1729.97 | 725292 | 676.035 | 715282 | 700975.875
5841 | 2006-09-01 08:00 | 608 | 872 | 79 | 26.74 | 2.96 | 0 | 37.3186 | 107.954 | 49.228 | 0 | 608 | 569.839 | 87.8516 | 5.6965 | 569.839 | 82.2149 | 0.029734 | 554.702 | 79.1722 | 0.022405 | 614.88 | 614.877 | 1380860 | 42.5897 | 1353360 | 1250120 | 1220190 | 0 | 0 | 1207330 | 671.237 | 0 | 0 | 0 | 0 | 1207330 | 671.237 | 1189600 | 1165803.625
5842 | 2006-09-01 09:00 | 775 | 920 | 86 | 28.95 | 1.47 | 0 | 48.5483 | 121.32 | 34.44 | 0 | 775 | 758.133 | 95.9179 | 7.2611 | 758.133 | 89.7637 | 0.037901 | 750.076 | 86.4416 | 0.028559 | 811.45 | 811.444 | 1822290 | 52.0519 | 1814410 | 1604390 | 1566490 | 0 | 0 | 1543990 | 648.346 | 0 | 0 | 0 | 6026.2 | 1537960 | 660 | 1512770 | 1482514.625
5843 | 2006-09-01 10:00 | 892 | 944 | 94 | 31.17 | 1.47 | 0 | 57.9046 | 140.786 | 19.6489 | 0 | 892 | 887.115 | 104.486 | 8.3574 | 887.115 | 97.7818 | 0.043623 | 884.373 | 94.1629 | 0.03287 | 949.212 | 949.209 | 2131690 | 58.1941 | 2139770 | 1837780 | 1795490 | 0 | 0 | 1764560 | 632.259 | 0 | 0 | 0 | 42108.5 | 1722450 | 660 | 1691060 | 1657237.625
5844 | 2006-09-01 11:00 | 946 | 954 | 97 | 32.38 | 1.47 | 0 | 63.1924 | 169.344 | 4.9862 | 0 | 946 | 947.633 | 107.562 | 8.8633 | 947.633 | 100.661 | 0.046263 | 947.453 | 96.9355 | 0.03486 | 1013.09 | 1013.09 | 2275140 | 61.2228 | 2290990 | 1938920 | 1899770 | 0 | 0 | 1864150 | 622.235 | 0 | 0 | 0 | 80632.4 | 1783510 | 660 | 1749920 | 1714921.625
5845 | 2006-09-01 12:00 | 934 | 951 | 97 | 33.59 | 2.93 | 0 | 61.9442 | 201.823 | 10.1552 | 0 | 934 | 933.594 | 107.604 | 8.7508 | 933.594 | 100.7 | 0.045677 | 932.852 | 96.9734 | 0.034418 | 998.964 | 998.959 | 2243410 | 59.3915 | 2257520 | 1928350 | 1886280 | 0 | 0 | 1851900 | 629.164 | 0 | 0 | 0 | 55011.3 | 1796890 | 660 | 1762800 | 1727546.625
5846 | 2006-09-01 13:00 | 856 | 937 | 91 | 34.81 | 2.93 | 0 | 54.8579 | 227.029 | 24.9159 | 0 | 856 | 848.449 | 101.342 | 8.02 | 848.449 | 94.8397 | 0.041862 | 844.095 | 91.3297 | 0.031544 | 907.393 | 907.388 | 2037760 | 58.2464 | 2040860 | 1751510 | 1714290 | 0 | 0 | 1685820 | 629.463 | 0 | 0 | 0 | 46798.3 | 1639030 | 660 | 1610520 | 1578312.5
5847 | 2006-09-01 14:00 | 720 | 904 | 85 | 34.89 | 2.93 | 0 | 44.6391 | 243.865 | 39.712 | 0 | 720 | 695.214 | 94.7467 | 6.7458 | 695.214 | 88.6676 | 0.035211 | 684.787 | 85.3861 | 0.026532 | 747.094 | 747.092 | 1677780 | 54.1862 | 1662960 | 1453700 | 1420820 | 0 | 0 | 1401590 | 637.093 | 0 | 0 | 0 | 19879.3 | 1381710 | 660 | 1360580 | 1333368.5
5848 | 2006-09-01 15:00 | 515 | 797 | 81 | 34.98 | 0.89 | 0 | 33.0288 | 255.83 | 54.498 | 0 | 515 | 462.403 | 91.2444 | 4.8251 | 462.403 | 85.39 | 0.025186 | 445.711 | 82.2297 | 0.018978 | 512.121 | 512.115 | 1150080 | 50.1399 | 1114760 | 990597 | 967526 | 0 | 0 | 958623 | 640.286 | 0 | 0 | 0 | 12190.7 | 946432 | 660 | 934129 | 915446.3125
5849 | 2006-09-01 16:00 | 312 | 713 | 58 | 35.07 | 0.89 | 0 | 20.8378 | 265.385 | 69.2573 | 0 | 312 | 252.892 | 63.3795 | 2.9232 | 252.892 | 59.313 | 0.015258 | 229.835 | 57.1178 | 0.011497 | 278.355 | 278.353 | 625109 | 43.3099 | 582420 | 532805 | 521069 | 0 | 0 | 518446 | 638.184 | 0 | 0 | 0 | 7591.43 | 510855 | 660 | 503986 | 493906.1875
5850 | 2006-09-01 17:00 | 98 | 203 | 68 | 34.71 | 0.89 | 0 | 8.4836 | 273.934 | 83.9711 | 0 | 98 | 21.3583 | 62.5021 | 0.91818 | 21.3583 | 58.4918 | 0.0047926 | 12.2586 | 56.3271 | 0.0036113 | 66.5316 | 66.5295 | 149409 | 36.6794 | 123454 | 115862 | 113230 | 0 | 0 | 113088 | 598.546 | 0 | 0 | 0 | 19517.2 | 93571.2 | 659.999 | 90540.9 | 88730.0703
5851 | 2006-09-01 18:00 | 2 | 25 | 1 | 34.35 | 3.23 | 0 | -3.7468 | 282.39 | 90 | 0 | 2 | 0 | 0.70108 | 0.018738 | 0 | 0.65609 | 0 | 0 | 0.63181 | 0 | 0.61286 | 0.61281 | 1376.21 | 34.3655 | 91.8563 | 92.8675 | 92.2693 | 0 | 0 | 92.2656 | 94.8798 | 0 | 0 | 0 | 92.2656 | 0 | 660 | 0 | 0
5852 | 2006-09-01 19:00 | 0 | 0 | 0 | 33.99 | 3.23 | 0
5853 | 2006-09-01 20:00 | 0 | 0 | 0 | 33.17 | 3.23 | 0
5854 | 2006-09-01 21:00 | 0 | 0 | 0 | 32.35 | 3.36 | 0
5855 | 2006-09-01 22:00 | 0 | 0 | 0 | 31.54 | 3.36 | 0
5856 | 2006-09-01 23:00 | 0 | 0 | 0 | 30.63 | 3.36 | 0
5857 | 2006-09-02 | 0 | 0 | 0 | 29.73 | 3.58 | 0
5858 | 2006-09-02 01:00 | 0 | 0 | 0 | 28.83 | 3.58 | 0
5859 | 2006-09-02 02:00 | 0 | 0 | 0 | 28.04 | 3.58 | 0
5860 | 2006-09-02 03:00 | 0 | 0 | 0 | 27.24 | 0.8 | 0
5861 | 2006-09-02 04:00 | 0 | 0 | 0 | 26.45 | 0.8 | 0
5862 | 2006-09-02 05:00 | 7 | 206 | 0 | 26.11 | 0.8 | 0 | 0.54142 | 80.8452 | 90 | 0 | 7 | 0 | 0 | 0.065585 | 0 | 0 | 0.00034233 | 0 | 0 | 0.00025795 | 0.00025021 | 0.00024747 | 0.55624 | 26.11 | 0.0028761 | 0.0028791 | 0.0028622 | 0 | 0 | 0.0028621 | 6.6931 | 0 | 0 | 0 | 0.0028621 | 0 | 660 | 0 | 0
5863 | 2006-09-02 06:00 | 193 | 643 | 49 | 25.76 | 0.92 | 0 | 12.8332 | 89.2746 | 78.6918 | 0 | 193 | 127.126 | 50.9743 | 1.8083 | 98.9466 | 47.7037 | 0.0094385 | 78.6637 | 45.9382 | 0.0071121 | 120.871 | 120.859 | 271402 | 29.3305 | 238459 | 232871 | 210270 | 0 | 0 | 209830 | 648.705 | 0 | 0 | 0 | 862.149 | 208967 | 660 | 203837 | 199760.4688
5864 | 2006-09-02 07:00 | 397 | 762 | 73 | 25.42 | 0.92 | 0 | 25.1453 | 98.1044 | 63.9575 | 0 | 397 | 334.768 | 80.5184 | 3.7196 | 330.003 | 75.3522 | 0.019415 | 308.921 | 72.5635 | 0.01463 | 370.054 | 370.038 | 831020 | 36.3519 | 789396 | 748676 | 712007 | 0 | 0 | 707431 | 659.887 | 0 | 0 | 0 | 6405.77 | 701026 | 670.874 | 691531 | 677700.5
5865 | 2006-09-02 08:00 | 594 | 848 | 82 | 27.81 | 0.92 | 0 | 37.158 | 108.377 | 49.1857 | 0 | 594 | 554.039 | 91.1683 | 5.5653 | 554.039 | 85.3187 | 0.029049 | 539.358 | 82.1611 | 0.021889 | 602.895 | 602.892 | 1353940 | 45.6211 | 1325430 | 1206390 | 1177850 | 0 | 0 | 1165530 | 661.561 | 0 | 0 | 0 | 4.5587 | 1165530 | 661.662 | 1149140 | 1126153.5
5866 | 2006-09-02 09:00 | 739 | 804 | 139 | 30.21 | 2.22 | 0 | 48.3474 | 121.794 | 34.3946 | 0 | 739 | 662.617 | 156.604 | 6.9238 | 662.617 | 146.556 | 0.03614 | 655.598 | 141.133 | 0.027232 | 772.855 | 772.849 | 1735620 | 51.1364 | 1723520 | 1530240 | 1495000 | 0 | 0 | 1474580 | 650.735 | 0 | 0 | 0 | 4467.4 | 1470120 | 660 | 1446860 | 1417922
5867 | 2006-09-02 10:00 | 900 | 850 | 183 | 32.6 | 2.22 | 0 | 57.6355 | 141.27 | 19.6091 | 0 | 900 | 799.633 | 204.344 | 8.4323 | 799.633 | 191.233 | 0.044014 | 797.171 | 184.156 | 0.033165 | 951.919 | 951.902 | 2137730 | 58.3746 | 2146130 | 1841640 | 1800440 | 0 | 0 | 1769290 | 631.205 | 0 | 0 | 0 | 44761 | 1724530 | 660 | 1693060 | 1659199.375
5868 | 2006-09-02 11:00 | 757 | 445 | 362 | 33.37 | 2.22 | 0 | 62.844 | 169.639 | 5.0312 | 0 | 757 | 442.226 | 393.46 | 7.0925 | 442.226 | 368.215 | 0.03702 | 442.141 | 354.587 | 0.027896 | 772.853 | 772.847 | 1735620 | 54.2964 | 1723540 | 1506270 | 1471740 | 0 | 0 | 1451340 | 639.899 | 0 | 0 | 0 | 19085.7 | 1432250 | 660 | 1409920 | 1381721.625
5869 | 2006-09-02 12:00 | 943 | 848 | 199 | 34.13 | 3.74 | 0 | 61.5727 | 201.745 | 10.2966 | 0 | 943 | 832.386 | 221.633 | 8.8352 | 832.386 | 207.412 | 0.046117 | 831.705 | 199.736 | 0.03475 | 1000.53 | 1000.52 | 2246910 | 58.6255 | 2261210 | 1939110 | 1896780 | 0 | 0 | 1862180 | 630.867 | 0 | 0 | 0 | 46329.1 | 1815850 | 660 | 1781060 | 1745436
5870 | 2006-09-02 13:00 | 843 | 885 | 123 | 34.9 | 3.74 | 0 | 54.5196 | 226.755 | 25.0312 | 0 | 843 | 801.135 | 134.949 | 7.8982 | 801.135 | 126.29 | 0.041226 | 796.983 | 121.616 | 0.031065 | 891.072 | 891.067 | 2001110 | 56.7159 | 2002290 | 1731510 | 1695420 | 0 | 0 | 1667920 | 633.75 | 0 | 0 | 0 | 33354.8 | 1634560 | 660 | 1606210 | 1574086.125
5871 | 2006-09-02 14:00 | 728 | 892 | 105 | 35.04 | 3.74 | 0 | 44.3365 | 243.558 | 39.8261 | 0 | 728 | 684.617 | 115.84 | 6.8208 | 684.617 | 108.407 | 0.035602 | 674.276 | 104.395 | 0.026827 | 755.337 | 755.33 | 1696280 | 53.5326 | 1682330 | 1475660 | 1443840 | 0 | 0 | 1424150 | 639.856 | 0 | 0 | 0 | 16538.2 | 1407610 | 660 | 1385870 | 1358152.375
5872 | 2006-09-02 15:00 | 544 | 887 | 64 | 35.18 | 3.31 | 0 | 32.7484 | 255.536 | 54.6164 | 0 | 544 | 513.805 | 71.7398 | 5.0969 | 513.805 | 67.1369 | 0.026604 | 495.129 | 64.6522 | 0.020047 | 543.007 | 543.004 | 1219450 | 48.8566 | 1186260 | 1061650 | 1037180 | 0 | 0 | 1027120 | 645.063 | 0 | 0 | 0 | 5994.7 | 1021120 | 660 | 1007720 | 987565.4375
5873 | 2006-09-02 16:00 | 319 | 758 | 52 | 35.33 | 3.31 | 0 | 20.5673 | 265.11 | 69.3828 | 0 | 319 | 267.62 | 57.3052 | 2.9888 | 267.62 | 53.6284 | 0.0156 | 243 | 51.6437 | 0.011755 | 285.816 | 285.811 | 641857 | 42.5287 | 599106 | 550409 | 537719 | 0 | 0 | 534966 | 642.915 | 0 | 0 | 0 | 4960.16 | 530006 | 660 | 522930 | 512471.4062
5874 | 2006-09-02 17:00 | 69 | 0 | 69 | 34.81 | 3.31 | 0 | 8.2135 | 273.672 | 84.1062 | 0 | 69 | 0 | 62.1227 | 0.64648 | 0 | 58.1368 | 0.0033744 | 0 | 55.9852 | 0.0025427 | 54.3081 | 54.3065 | 121958 | 36.1778 | 98565.2 | 92677.4 | 90501.3 | 0 | 0 | 90408 | 589.509 | 0 | 0 | 0 | 21223.1 | 69184.9 | 659.999 | 66843.2 | 65506.3281
5875 | 2006-09-02 18:00 | 1 | 0 | 1 | 34.29 | 5.41 | 0 | -4.0247 | 282.139 | 90 | 0 | 1 | 0 | 1.0019 | 0.0093692 | 0 | 0.93761 | 0 | 0 | 0.90291 | 0 | 0.87582 | 0.87579 | 1966.79 | 34.3092 | 187.413 | 189.429 | 188.536 | 0 | 0 | 188.527 | 131.07 | 0 | 0 | 0 | 188.527 | 0 | 660 | 0 | 0
5876 | 2006-09-02 19:00 | 0 | 0 | 0 | 33.78 | 5.41 | 0
5877 | 2006-09-02 20:00 | 0 | 0 | 0 | 32.91 | 5.41 | 0
5878 | 2006-09-02 21:00 | 0 | 0 | 0 | 32.04 | 5.71 | 0
5879 | 2006-09-02 22:00 | 0 | 0 | 0 | 31.17 | 5.71 | 0
5880 | 2006-09-02 23:00 | 0 | 0 | 0 | 30.51 | 5.71 | 0
5881 | 2006-09-03 | 0 | 0 | 0 | 29.84 | 6.31 | 0
5882 | 2006-09-03 01:00 | 0 | 0 | 0 | 29.17 | 6.31 | 0
5883 | 2006-09-03 02:00 | 0 | 0 | 0 | 28.5 | 6.31 | 0
5884 | 2006-09-03 03:00 | 0 | 0 | 0 | 27.84 | 3.45 | 0
5885 | 2006-09-03 04:00 | 0 | 0 | 0 | 27.17 | 3.45 | 0
5886 | 2006-09-03 05:00 | 5 | 112 | 0 | 26.94 | 3.45 | 0 | 0.39827 | 81.1917 | 90 | 0 | 5 | 0 | 0 | 0.046846 | 0 | 0 | 0.00024452 | 0 | 0 | 0.00018425 | 0.00017872 | 0.00017918 | 0.40276 | 26.94 | 0.0015074 | 0.0015103 | 0.0015027 | 0 | 0 | 0.0015027 | 4.8465 | 0 | 0 | 0 | 0.0015027 | 0 | 660 | 0 | 0
5887 | 2006-09-03 06:00 | 190 | 601 | 57 | 26.71 | 2.81 | 0 | 12.6963 | 89.6326 | 78.6648 | 0 | 190 | 118.939 | 58.196 | 1.7801 | 91.6891 | 54.462 | 0.0092918 | 72.9487 | 52.4464 | 0.0070016 | 121.64 | 121.646 | 273169 | 29.877 | 239986 | 233814 | 212434 | 0 | 0 | 211989 | 647.241 | 0 | 0 | 0 | 876.307 | 211113 | 660 | 205932 | 201813.1406
5888 | 2006-09-03 07:00 | 397 | 767 | 73 | 26.48 | 2.81 | 0 | 25.003 | 98.4876 | 63.9219 | 0 | 397 | 336.978 | 80.7201 | 3.7196 | 331.49 | 75.5409 | 0.019415 | 310.36 | 72.7452 | 0.01463 | 371.626 | 371.639 | 834615 | 36.1555 | 793089 | 752904 | 714062 | 0 | 0 | 709454 | 660.272 | 0 | 0 | 0 | 13265 | 696190 | 672.332 | 686703 | 672969.25
5889 | 2006-09-03 08:00 | 613 | 905 | 69 | 28.13 | 2.81 | 0 | 36.9957 | 108.801 | 49.1443 | 0 | 613 | 591.372 | 77.5482 | 5.7433 | 591.372 | 72.5726 | 0.029978 | 575.74 | 69.8867 | 0.022589 | 626.279 | 626.274 | 1406450 | 44.4349 | 1379940 | 1263640 | 1236170 | 0 | 0 | 1222680 | 663.522 | 0 | 0 | 0 | 0 | 1222680 | 663.522 | 1204980 | 1180885.125
5890 | 2006-09-03 09:00 | 777 | 940 | 78 | 29.79 | 1.98 | 0 | 48.144 | 122.268 | 34.3516 | 0 | 777 | 774.797 | 87.6998 | 7.2799 | 774.797 | 82.0729 | 0.037998 | 766.613 | 79.0354 | 0.028633 | 820.307 | 820.3 | 1842190 | 52.36 | 1835290 | 1620580 | 1584320 | 0 | 0 | 1561240 | 647.407 | 0 | 0 | 0 | 7570.41 | 1553670 | 659.999 | 1527970 | 1497413.125
5891 | 2006-09-03 10:00 | 895 | 746 | 268 | 31.44 | 1.98 | 0 | 57.3633 | 141.752 | 19.575 | 0 | 895 | 701.528 | 296.546 | 8.3855 | 701.528 | 277.519 | 0.043769 | 699.376 | 267.249 | 0.032981 | 937.658 | 937.643 | 2105700 | 57.2385 | 2112390 | 1822820 | 1781040 | 0 | 0 | 1750950 | 635.683 | 0 | 0 | 0 | 33570.7 | 1717380 | 660 | 1686160 | 1652441.625
5892 | 2006-09-03 11:00 | 168 | 10 | 159 | 32.28 | 1.98 | 0 | 62.4931 | 169.931 | 5.1028 | 0 | 168 | 10.1069 | 148.546 | 1.574 | 10.1069 | 139.015 | 0.0082159 | 10.1048 | 133.87 | 0.0061909 | 139.662 | 139.654 | 313626 | 36.1225 | 277555 | 262316 | 255830 | 0 | 0 | 255187 | 634.501 | 0 | 0 | 0 | 5701.71 | 249486 | 660 | 243740 | 238865.4219
5893 | 2006-09-03 12:00 | 513 | 125 | 404 | 33.12 | 3.43 | 0 | 61.1988 | 201.67 | 10.451 | 0 | 513 | 122.324 | 414.829 | 4.8064 | 122.324 | 388.213 | 0.025088 | 122.22 | 373.845 | 0.018904 | 481.202 | 481.182 | 1080620 | 45.1439 | 1043420 | 950155 | 928208 | 0 | 0 | 920316 | 652.713 | 0 | 0 | 0 | 884.027 | 919432 | 660 | 907480 | 889330.125
5894 | 2006-09-03 13:00 | 161 | 0 | 161 | 33.96 | 3.43 | 0 | 54.1783 | 226.485 | 25.1526 | 0 | 161 | 0 | 150.208 | 1.5084 | 0 | 140.57 | 0.0078736 | 0 | 135.368 | 0.0059329 | 131.313 | 131.309 | 294887 | 37.2412 | 259646 | 243857 | 237881 | 0 | 0 | 237312 | 626.588 | 0 | 0 | 0 | 8849.74 | 228462 | 660 | 222913 | 218454.6719
5895 | 2006-09-03 14:00 | 364 | 83 | 306 | 34.16 | 3.43 | 0 | 44.0308 | 243.254 | 39.9443 | 0 | 364 | 63.9769 | 319.323 | 3.4104 | 63.9769 | 298.835 | 0.017801 | 63.0034 | 287.775 | 0.013414 | 340.268 | 340.252 | 764117 | 42.6623 | 721623 | 663428 | 647136 | 0 | 0 | 643245 | 649.954 | 0 | 0 | 0 | 1969.96 | 641275 | 660 | 632939 | 620279.8125
5896 | 2006-09-03 15:00 | 111 | 0 | 111 | 34.36 | 2.45 | 0 | 32.465 | 255.243 | 54.7378 | 0 | 111 | 0 | 102.734 | 1.04 | 0 | 96.1428 | 0.0054284 | 0 | 92.5846 | 0.0040904 | 89.8111 | 89.8047 | 201678 | 36.7547 | 171693 | 161326 | 157528 | 0 | 0 | 157265 | 611.282 | 0 | 0 | 0 | 14636.3 | 142629 | 660 | 138430 | 135661.1719
5897 | 2006-09-03 16:00 | 164 | 77 | 137 | 34.55 | 2.45 | 0 | 20.2942 | 264.834 | 69.5105 | 0 | 164 | 27.2487 | 138.766 | 1.5366 | 27.2487 | 129.862 | 0.0080203 | 24.7188 | 125.056 | 0.0060434 | 145.288 | 145.284 | 326270 | 38.424 | 289673 | 270517 | 263905 | 0 | 0 | 263208 | 628.333 | 0 | 0 | 0 | 9449.72 | 253759 | 660 | 247980 | 243020.2344
5898 | 2006-09-03 17:00 | 87 | 0 | 87 | 34.2 | 2.45 | 0 | 7.941 | 273.411 | 84.243 | 0 | 87 | 0 | 77.4762 | 0.81512 | 0 | 72.5052 | 0.0042547 | 0 | 69.8218 | 0.003206 | 67.7303 | 67.7297 | 152104 | 36.006 | 125920 | 118638 | 115857 | 0 | 0 | 115710 | 601.19 | 0 | 0 | 0 | 17479.1 | 98230.5 | 660 | 95076.8 | 93175.2969
5899 | 2006-09-03 18:00 | 1 | 0 | 1 | 33.84 | 3.42 | 0 | -4.3046 | 281.887 | 90 | 0 | 1 | 0 | 1.0022 | 0.0093692 | 0 | 0.93785 | 0 | 0 | 0.90314 | 0 | 0.87604 | 0.87601 | 1967.28 | 33.8619 | 187.488 | 189.409 | 188.534 | 0 | 0 | 188.526 | 131.028 | 0 | 0 | 0 | 188.526 | 0 | 660 | 0 | 0
5900 | 2006-09-03 19:00 | 0 | 0 | 0 | 33.48 | 3.42 | 0
5901 | 2006-09-03 20:00 | 0 | 0 | 0 | 32.99 | 3.42 | 0
5902 | 2006-09-03 21:00 | 0 | 0 | 0 | 32.5 | 3.02 | 0
5903 | 2006-09-03 22:00 | 0 | 0 | 0 | 32 | 3.02 | 0
5904 | 2006-09-03 23:00 | 0 | 0 | 0 | 31.33 | 3.02 | 0
5905 | 2006-09-04 | 0 | 0 | 0 | 30.66 | 2.53 | 0
5906 | 2006-09-04 01:00 | 0 | 0 | 0 | 29.98 | 2.53 | 0
5907 | 2006-09-04 02:00 | 0 | 0 | 0 | 29.23 | 2.53 | 0
5908 | 2006-09-04 03:00 | 0 | 0 | 0 | 28.47 | 3.06 | 0
5909 | 2006-09-04 04:00 | 0 | 0 | 0 | 27.72 | 3.06 | 0
5910 | 2006-09-04 05:00 | 4 | 108 | 0 | 27.39 | 3.06 | 0 | 0.25494 | 81.5406 | 90 | 0 | 4 | 0 | 0 | 0.037477 | 0 | 0 | 0.00019562 | 0 | 0 | 0.0001474 | 0.00014298 | 0.00014349 | 0.32252 | 27.39 | 0.00096601 | 0.00096856 | 0.00096349 | 0 | 0 | 0.00096346 | 3.8846 | 0 | 0 | 0 | 0.00096346 | 0 | 660 | 0 | 0
5911 | 2006-09-04 06:00 | 187 | 597 | 56 | 27.06 | 2.24 | 0 | 12.5588 | 89.9926 | 78.6375 | 0 | 187 | 118.694 | 57.4311 | 1.752 | 90.5452 | 53.7462 | 0.0091451 | 72.0933 | 51.7571 | 0.006891 | 120.142 | 120.156 | 269824 | 30.3091 | 236844 | 230213 | 208444 | 0 | 0 | 208015 | 648.238 | 0 | 0 | 0 | 1027.46 | 206988 | 660 | 201852 | 197815.4531
5912 | 2006-09-04 07:00 | 404 | 824 | 57 | 26.73 | 2.24 | 0 | 24.8596 | 98.8725 | 63.8865 | 0 | 404 | 363.306 | 63.5729 | 3.7852 | 356.669 | 59.4939 | 0.019757 | 333.986 | 57.2921 | 0.014887 | 379.554 | 379.525 | 852331 | 36.9927 | 811133 | 766925 | 724628 | 0 | 0 | 719839 | 657.774 | 0 | 0 | 0 | 19232.3 | 700606 | 669.965 | 691127 | 677304.5625
5913 | 2006-09-04 08:00 | 610 | 904 | 68 | 28.4 | 2.24 | 0 | 36.8315 | 109.226 | 49.1041 | 0 | 610 | 591.93 | 76.6226 | 5.7152 | 591.93 | 71.7064 | 0.029832 | 576.319 | 69.0526 | 0.022479 | 626.032 | 626.029 | 1405900 | 45.3284 | 1379380 | 1257670 | 1227870 | 0 | 0 | 1214530 | 662.521 | 0 | 0 | 0 | 0 | 1214530 | 662.521 | 1197060 | 1173118.375
5914 | 2006-09-04 09:00 | 779 | 948 | 76 | 30.06 | 0.87 | 0 | 47.9381 | 122.741 | 34.3112 | 0 | 779 | 782.129 | 85.7026 | 7.2986 | 782.129 | 80.2037 | 0.038096 | 773.891 | 77.2355 | 0.028706 | 825.62 | 825.615 | 1854130 | 54.5332 | 1847820 | 1614130 | 1577020 | 0 | 0 | 1553730 | 641.6 | 0 | 0 | 0 | 18061.7 | 1535670 | 660 | 1510550 | 1480336.375
5915 | 2006-09-04 10:00 | 896 | 972 | 81 | 31.73 | 0.87 | 0 | 57.0883 | 142.23 | 19.5469 | 0 | 896 | 914.856 | 91.1189 | 8.3948 | 914.856 | 85.2726 | 0.043818 | 912.059 | 82.1167 | 0.033018 | 964.382 | 964.377 | 2165750 | 60.3165 | 2175650 | 1848770 | 1809160 | 0 | 0 | 1777010 | 624.679 | 0 | 0 | 0 | 68092.8 | 1708910 | 660 | 1678000 | 1644440.125
5916 | 2006-09-04 11:00 | 949 | 981 | 84 | 32.33 | 0.87 | 0 | 62.1399 | 170.219 | 5.2005 | 0 | 949 | 974.378 | 94.2554 | 8.8914 | 974.378 | 88.2078 | 0.04641 | 974.177 | 84.9433 | 0.034971 | 1027.38 | 1027.38 | 2307240 | 62.784 | 2324840 | 1952030 | 1909370 | 0 | 0 | 1872930 | 618.091 | 0 | 0 | 0 | 101519 | 1771410 | 660 | 1738260 | 1703492.25
5917 | 2006-09-04 12:00 | 936 | 978 | 84 | 32.93 | 1.08 | 0 | 60.8226 | 201.598 | 10.6179 | 0 | 936 | 959.109 | 94.2967 | 8.7696 | 959.109 | 88.2465 | 0.045774 | 958.274 | 84.9805 | 0.034492 | 1011.99 | 1011.99 | 2272670 | 62.5064 | 2288380 | 1923820 | 1881880 | 0 | 0 | 1846540 | 618.706 | 0 | 0 | 0 | 97667.1 | 1748880 | 660 | 1716540 | 1682210.625
5918 | 2006-09-04 13:00 | 858 | 965 | 80 | 33.53 | 1.08 | 0 | 53.8342 | 226.22 | 25.2802 | 0 | 858 | 871.398 | 90.0873 | 8.0388 | 871.398 | 84.3071 | 0.04196 | 866.784 | 81.187 | 0.031618 | 919.562 | 919.557 | 2065100 | 60.4051 | 2069630 | 1756850 | 1719850 | 0 | 0 | 1690660 | 623.292 | 0 | 0 | 0 | 71667.6 | 1618990 | 660 | 1591160 | 1559333.75
5919 | 2006-09-04 14:00 | 718 | 738 | 208 | 33.71 | 1.08 | 0 | 43.722 | 242.951 | 40.0666 | 0 | 718 | 564.705 | 228.193 | 6.7271 | 564.705 | 213.551 | 0.035113 | 556.046 | 205.648 | 0.026458 | 738.868 | 738.86 | 1659290 | 55.304 | 1643620 | 1428410 | 1397020 | 0 | 0 | 1378230 | 633.463 | 0 | 0 | 0 | 28448.5 | 1349780 | 660 | 1329400 | 1302809.375
5920 | 2006-09-04 15:00 | 252 | 144 | 175 | 33.9 | 2.6 | 0 | 32.1788 | 254.95 | 54.8622 | 0 | 252 | 83.2145 | 172.809 | 2.361 | 83.2145 | 161.721 | 0.012324 | 80.146 | 155.736 | 0.0092863 | 228.815 | 228.81 | 513847 | 39.9407 | 472244 | 438894 | 428456 | 0 | 0 | 426707 | 642.989 | 0 | 0 | 0 | 4089.93 | 422617 | 660 | 416748 | 408412.9062
5921 | 2006-09-04 16:00 | 50 | 0 | 50 | 34.08 | 2.6 | 0 | 20.0186 | 264.558 | 69.6406 | 0 | 50 | 0 | 45.9206 | 0.46846 | 0 | 42.9743 | 0.0024452 | 0 | 41.3838 | 0.0018425 | 40.1441 | 40.1413 | 90147 | 35.1397 | 70234 | 66355.6 | 64822.4 | 0 | 0 | 64772.4 | 576.915 | 0 | 0 | 0 | 22598.6 | 42173.8 | 659.999 | 40678 | 39864.4219
5922 | 2006-09-04 17:00 | 13 | 0 | 13 | 33.82 | 2.6 | 0 | 7.6663 | 273.148 | 84.3816 | 0 | 13 | 0 | 12.0765 | 0.1218 | 0 | 11.3016 | 0.00063575 | 0 | 10.8834 | 0.00047905 | 10.5573 | 10.557 | 23708.5 | 34.0987 | 14286 | 13593.2 | 13328.9 | 0 | 0 | 13326.1 | 502.54 | 0 | 0 | 0 | 13326.1 | 0 | 660 | 0 | 0
5923 | 2006-09-04 18:00 | 0 | 0 | 0 | 33.56 | 2.14 | 0
5924 | 2006-09-04 19:00 | 0 | 0 | 0 | 33.31 | 2.14 | 0
5925 | 2006-09-04 20:00 | 0 | 0 | 0 | 32.97 | 2.14 | 0
5926 | 2006-09-04 21:00 | 0 | 0 | 0 | 32.63 | 3.37 | 0
5927 | 2006-09-04 22:00 | 0 | 0 | 0 | 32.29 | 3.37 | 0
5928 | 2006-09-04 23:00 | 0 | 0 | 0 | 31.65 | 3.37 | 0
5929 | 2006-09-05 | 0 | 0 | 0 | 31.02 | 1.28 | 0
5930 | 2006-09-05 01:00 | 0 | 0 | 0 | 30.39 | 1.28 | 0
5931 | 2006-09-05 02:00 | 0 | 0 | 0 | 29.89 | 1.28 | 0
5932 | 2006-09-05 03:00 | 0 | 0 | 0 | 29.38 | 3.45 | 0
5933 | 2006-09-05 04:00 | 0 | 0 | 0 | 28.88 | 3.45 | 0
5934 | 2006-09-05 05:00 | 3 | 183 | 0 | 28.37 | 3.45 | 0 | 0.11145 | 81.8917 | 90 | 0 | 3 | 0 | 0 | 0.028108 | 0 | 0 | 0.00014671 | 0 | 0 | 0.00011055 | 0.00010723 | 0.00010811 | 0.24298 | 28.37 | 0.00054906 | 0.00055118 | 0.00054663 | 0 | 0 | 0.00054662 | 2.9327 | 0 | 0 | 0 | 0.00054662 | 0 | 660 | 0 | 0
5935 | 2006-09-05 06:00 | 186 | 656 | 44 | 27.86 | 1.77 | 0 | 12.4207 | 90.3545 | 78.6098 | 0 | 186 | 130.382 | 46.5151 | 1.7427 | 98.4211 | 43.5306 | 0.0090962 | 78.4241 | 41.9196 | 0.0068542 | 116.74 | 116.744 | 262161 | 31.1176 | 229905 | 222413 | 199267 | 0 | 0 | 198862 | 643.828 | 0 | 0 | 0 | 1856.98 | 197005 | 660 | 192038 | 188197.625
5936 | 2006-09-05 07:00 | 404 | 830 | 57 | 27.34 | 1.77 | 0 | 24.715 | 99.2589 | 63.8514 | 0 | 404 | 365.753 | 63.7125 | 3.7852 | 358.32 | 59.6246 | 0.019757 | 335.582 | 57.4179 | 0.014887 | 381.225 | 381.205 | 856107 | 37.9769 | 815015 | 766893 | 717747 | 0 | 0 | 713025 | 657.368 | 0 | 0 | 0 | 16809.5 | 696215 | 668.827 | 686821 | 673084.8125
5937 | 2006-09-05 08:00 | 609 | 908 | 67 | 28.91 | 1.77 | 0 | 36.6655 | 109.652 | 49.0651 | 0 | 609 | 594.697 | 75.693 | 5.7059 | 594.697 | 70.8364 | 0.029783 | 579.049 | 68.2148 | 0.022442 | 627.868 | 627.866 | 1410030 | 46.4296 | 1383670 | 1254880 | 1225070 | 0 | 0 | 1211590 | 657.895 | 0 | 0 | 0 | -24.2747 | 1211620 | 660.045 | 1194330 | 1170439.125
5938 | 2006-09-05 09:00 | 778 | 950 | 76 | 30.47 | 4.05 | 0 | 47.7297 | 123.213 | 34.2736 | 0 | 778 | 783.945 | 85.8594 | 7.2893 | 783.945 | 80.3505 | 0.038047 | 775.709 | 77.3768 | 0.02867 | 827.521 | 827.516 | 1858390 | 50.3214 | 1852290 | 1652260 | 1612830 | 0 | 0 | 1589500 | 655.769 | 0 | 0 | 0 | 1158.04 | 1588340 | 660 | 1561520 | 1530291.125
5939 | 2006-09-05 10:00 | 893 | 972 | 81 | 32.04 | 4.05 | 0 | 56.8104 | 142.704 | 19.525 | 0 | 893 | 914.494 | 91.2871 | 8.3667 | 914.494 | 85.4299 | 0.043671 | 911.704 | 82.2682 | 0.032907 | 964.185 | 964.181 | 2165310 | 55.1699 | 2175180 | 1897280 | 1856010 | 0 | 0 | 1823990 | 642.218 | 0 | 0 | 0 | 17918.6 | 1806070 | 660 | 1771650 | 1736215.125
5940 | 2006-09-05 11:00 | 946 | 981 | 84 | 32.66 | 4.05 | 0 | 61.7843 | 170.503 | 5.3234 | 0 | 946 | 974.021 | 94.4342 | 8.8633 | 974.021 | 88.3751 | 0.046263 | 973.81 | 85.1044 | 0.03486 | 1027.18 | 1027.18 | 2306780 | 57.3011 | 2324360 | 2007250 | 1962950 | 0 | 0 | 1926720 | 637.443 | 0 | 0 | 0 | 31780.4 | 1894940 | 660 | 1857140 | 1819994.125
5941 | 2006-09-05 12:00 | 934 | 978 | 85 | 33.29 | 3.07 | 0 | 60.4442 | 201.528 | 10.797 | 0 | 934 | 958.723 | 95.5534 | 8.7508 | 958.723 | 89.4225 | 0.045677 | 957.859 | 86.113 | 0.034418 | 1012.69 | 1012.68 | 2274230 | 59.2045 | 2290020 | 1958300 | 1914670 | 0 | 0 | 1879410 | 630.54 | 0 | 0 | 0 | 51728.8 | 1827680 | 660 | 1792440 | 1756595.5
5942 | 2006-09-05 13:00 | 854 | 965 | 80 | 33.91 | 3.07 | 0 | 53.4873 | 225.958 | 25.4138 | 0 | 854 | 869.827 | 90.2524 | 8.0013 | 869.827 | 84.4617 | 0.041764 | 865.167 | 81.3358 | 0.03147 | 918.139 | 918.133 | 2061900 | 57.405 | 2066260 | 1781180 | 1742270 | 0 | 0 | 1713140 | 632.787 | 0 | 0 | 0 | 37077.9 | 1676060 | 660 | 1646290 | 1613368
5943 | 2006-09-05 14:00 | 716 | 935 | 74 | 34.36 | 3.07 | 0 | 43.4104 | 242.651 | 40.1928 | 0 | 716 | 713.613 | 83.6193 | 6.7084 | 713.613 | 78.2542 | 0.035015 | 702.584 | 75.358 | 0.026385 | 754.629 | 754.627 | 1694710 | 53.6709 | 1680680 | 1473150 | 1439010 | 0 | 0 | 1419580 | 641.606 | 0 | 0 | 0 | 15926.9 | 1403660 | 660 | 1382010 | 1354368.375
5944 | 2006-09-05 15:00 | 530 | 842 | 85 | 34.81 | 2.72 | 0 | 31.89 | 254.659 | 54.9894 | 0 | 530 | 483.274 | 96.1667 | 4.9657 | 483.274 | 89.9965 | 0.025919 | 465.321 | 86.6658 | 0.019531 | 535.446 | 535.443 | 1202470 | 48.8337 | 1168730 | 1045940 | 1021380 | 0 | 0 | 1011630 | 645.462 | 0 | 0 | 0 | 6038.12 | 1005590 | 660 | 992482 | 972632.625
5945 | 2006-09-05 16:00 | 289 | 650 | 69 | 35.25 | 2.72 | 0 | 19.7406 | 264.282 | 69.7727 | 0 | 289 | 225.2 | 74.7091 | 2.7077 | 225.2 | 69.9157 | 0.014133 | 203.892 | 67.3281 | 0.01065 | 263.094 | 263.09 | 590835 | 42.1405 | 548352 | 504441 | 493192 | 0 | 0 | 490864 | 641.088 | 0 | 0 | 0 | 5917.07 | 484947 | 660 | 478363 | 468796.0625
5946 | 2006-09-05 17:00 | 75 | 433 | 18 | 34.55 | 2.72 | 0 | 7.3895 | 272.885 | 84.5217 | 0 | 75 | 42.3105 | 18.9838 | 0.70269 | 42.3105 | 17.7658 | 0.0036678 | 22.2666 | 17.1083 | 0.0027638 | 38.1964 | 38.1956 | 85777.5 | 35.5504 | 66391.3 | 62564.8 | 61287.6 | 0 | 0 | 61242.2 | 573.026 | 0 | 0 | 0 | 24412.8 | 36829.4 | 659.998 | 35511.3 | 34801.0742
5947 | 2006-09-05 18:00 | 1 | 33 | 1 | 33.84 | 2.48 | 0 | -4.8705 | 281.38 | 90 | 0 | 1 | 0 | 1.0027 | 0.0093692 | 0 | 0.93832 | 0 | 0 | 0.9036 | 0 | 0.87649 | 0.87646 | 1968.3 | 33.8633 | 187.69 | 189.614 | 188.732 | 0 | 0 | 188.724 | 131.11 | 0 | 0 | 0 | 188.724 | 0 | 660 | 0 | 0
5948 | 2006-09-05 19:00 | 0 | 0 | 0 | 33.13 | 2.48 | 0
5949 | 2006-09-05 20:00 | 0 | 0 | 0 | 32.84 | 2.48 | 0
5950 | 2006-09-05 21:00 | 0 | 0 | 0 | 32.54 | 2.69 | 0
5951 | 2006-09-05 22:00 | 0 | 0 | 0 | 32.24 | 2.69 | 0
5952 | 2006-09-05 23:00 | 0 | 0 | 0 | 31.44 | 2.69 | 0
5953 | 2006-09-06 | 0 | 0 | 0 | 30.64 | 2.24 | 0
5954 | 2006-09-06 01:00 | 0 | 0 | 0 | 29.84 | 2.24 | 0
5955 | 2006-09-06 02:00 | 0 | 0 | 0 | 29.57 | 2.24 | 0
5956 | 2006-09-06 03:00 | 0 | 0 | 0 | 29.3 | 0.93 | 0
5957 | 2006-09-06 04:00 | 0 | 0 | 0 | 29.04 | 0.93 | 0
5958 | 2006-09-06 05:00 | 2 | 112 | 0 | 28.4 | 0.93 | 0 | -0.032217 | 82.2449 | 90 | 0 | 2 | 0 | 0 | 0.018738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.4 | 0 | 0 | 0 | 0 | 0 | 0 | 660 | 0 | 0 | 0 | 0 | 0 | 660 | 0 | 0
5959 | 2006-09-06 06:00 | 180 | 586 | 55 | 27.76 | 1.52 | 0 | 12.2819 | 90.7182 | 78.5819 | 0 | 180 | 116.33 | 56.872 | 1.6865 | 86.8581 | 53.223 | 0.0088027 | 69.2635 | 51.2533 | 0.0066331 | 116.908 | 116.933 | 262588 | 31.0779 | 230015 | 222643 | 202027 | 0 | 0 | 201619 | 644.276 | 0 | 0 | 0 | 1644.24 | 199975 | 660 | 194923 | 191024.3906
5960 | 2006-09-06 07:00 | 402 | 829 | 57 | 27.12 | 1.52 | 0 | 24.5692 | 99.6467 | 63.8168 | 0 | 402 | 366.117 | 63.8535 | 3.7664 | 357.828 | 59.7566 | 0.019659 | 335.171 | 57.545 | 0.014814 | 380.949 | 380.961 | 855560 | 37.9297 | 814523 | 766531 | 715017 | 0 | 0 | 710280 | 653.517 | 0 | 0 | 0 | 14481.9 | 695798 | 667.143 | 686465 | 672735.625
5961 | 2006-09-06 08:00 | 607 | 907 | 68 | 28.9 | 1.52 | 0 | 36.4977 | 110.079 | 49.0275 | 0 | 607 | 594.193 | 76.918 | 5.6871 | 594.193 | 71.9828 | 0.029685 | 578.593 | 69.3188 | 0.022368 | 628.496 | 628.493 | 1411440 | 46.7333 | 1385130 | 1254340 | 1224770 | 0 | 0 | 1211340 | 658.55 | 0 | 0 | 0 | 61.5938 | 1211280 | 660 | 1193990 | 1170113
5962 | 2006-09-06 09:00 | 775 | 950 | 75 | 30.67 | 0.94 | 0 | 47.5187 | 123.685 | 34.2388 | 0 | 775 | 784.667 | 84.9334 | 7.2611 | 784.667 | 79.4839 | 0.037901 | 776.442 | 76.5423 | 0.028559 | 827.422 | 827.418 | 1858170 | 55.0813 | 1852060 | 1613430 | 1578340 | 0 | 0 | 1554710 | 637.203 | 0 | 0 | 0 | 22591.9 | 1532120 | 660 | 1507120 | 1476973
5963 | 2006-09-06 10:00 | 890 | 972 | 81 | 32.45 | 0.94 | 0 | 56.5297 | 143.175 | 19.5095 | 0 | 890 | 914.143 | 91.4562 | 8.3386 | 914.143 | 85.5882 | 0.043525 | 911.359 | 82.4206 | 0.032797 | 963.998 | 963.997 | 2164890 | 60.8907 | 2174750 | 1842540 | 1802440 | 0 | 0 | 1770320 | 622.529 | 0 | 0 | 0 | 75439 | 1694880 | 660 | 1664460 | 1631171
5964 | 2006-09-06 11:00 | 943 | 981 | 84 | 33.05 | 0.94 | 0 | 61.4266 | 170.783 | 5.47 | 0 | 943 | 973.677 | 94.6138 | 8.8352 | 973.677 | 88.5432 | 0.046117 | 973.455 | 85.2663 | 0.03475 | 1026.99 | 1026.99 | 2306350 | 63.3491 | 2323900 | 1945490 | 1903240 | 0 | 0 | 1866810 | 616.292 | 0 | 0 | 0 | 111339 | 1755480 | 660 | 1722900 | 1688443.5
5965 | 2006-09-06 12:00 | 930 | 978 | 84 | 33.65 | 4.13 | 0 | 60.0638 | 201.461 | 10.9877 | 0 | 930 | 958.353 | 94.654 | 8.7134 | 958.353 | 88.5808 | 0.045481 | 957.458 | 85.3025 | 0.034271 | 1011.51 | 1011.51 | 2271590 | 57.7882 | 2287230 | 1970040 | 1928170 | 0 | 0 | 1892730 | 633.358 | 0 | 0 | 0 | 37902.8 | 1854830 | 660 | 1818570 | 1782197.875
5966 | 2006-09-06 13:00 | 834 | 763 | 224 | 34.25 | 4.13 | 0 | 53.1378 | 225.7 | 25.5533 | 0 | 834 | 687.846 | 251.881 | 7.8139 | 687.846 | 235.72 | 0.040786 | 684.117 | 226.996 | 0.030733 | 883.81 | 883.801 | 1984800 | 55.3407 | 1985140 | 1728440 | 1689780 | 0 | 0 | 1663010 | 640.278 | 0 | 0 | 0 | 21175.1 | 1641830 | 660 | 1613230 | 1580969.625
5967 | 2006-09-06 14:00 | 185 | 0 | 185 | 34.43 | 4.13 | 0 | 43.096 | 242.353 | 40.323 | 0 | 185 | 0 | 173.142 | 1.7333 | 0 | 162.033 | 0.0090473 | 0 | 156.036 | 0.0068173 | 151.361 | 151.349 | 339892 | 38.0417 | 302767 | 283394 | 276457 | 0 | 0 | 275702 | 631.89 | 0 | 0 | 0 | 7897.14 | 267805 | 660 | 261932 | 256693.4688
5968 | 2006-09-06 15:00 | 467 | 485 | 213 | 34.6 | 5.71 | 0 | 31.5986 | 254.368 | 55.1195 | 0 | 467 | 277.221 | 222.339 | 4.3754 | 277.221 | 208.074 | 0.022838 | 266.844 | 200.373 | 0.017209 | 453.217 | 453.205 | 1017780 | 44.3585 | 979045 | 894625 | 873820 | 0 | 0 | 866859 | 654.759 | 0 | 0 | 0 | 600.914 | 866258 | 660 | 854997 | 837896.625
5969 | 2006-09-06 16:00 | 304 | 616 | 98 | 34.78 | 5.71 | 0 | 19.4603 | 264.007 | 69.907 | 0 | 304 | 212.426 | 103.562 | 2.8482 | 212.426 | 96.9169 | 0.014867 | 192.13 | 93.33 | 0.011203 | 276.907 | 276.902 | 621852 | 40.7423 | 579181 | 536840 | 524679 | 0 | 0 | 522081 | 645.689 | 0 | 0 | 0 | 2446.37 | 519635 | 660 | 512671 | 502417.375
5970 | 2006-09-06 17:00 | 77 | 411 | 25 | 34.14 | 5.71 | 0 | 7.1107 | 272.621 | 84.6633 | 0 | 77 | 39.0705 | 25.3514 | 0.72143 | 39.0705 | 23.7248 | 0.0037656 | 20.0201 | 22.8468 | 0.0028375 | 41.5837 | 41.5823 | 93383.3 | 35.0354 | 73081.2 | 69096.4 | 67659.1 | 0 | 0 | 67605 | 579.314 | 0 | 0 | 0 | 22023.7 | 45581.3 | 659.999 | 43973.9 | 43094.4414
5971 | 2006-09-06 18:00 | 0 | 26 | 0 | 33.51 | 7.11 | 0
5972 | 2006-09-06 19:00 | 0 | 0 | 0 | 32.87 | 7.11 | 0
5973 | 2006-09-06 20:00 | 0 | 0 | 0 | 32.33 | 7.11 | 0
5974 | 2006-09-06 21:00 | 0 | 0 | 0 | 31.78 | 8.34 | 0
5975 | 2006-09-06 22:00 | 0 | 0 | 0 | 31.23 | 8.34 | 0
5976 | 2006-09-06 23:00 | 0 | 0 | 0 | 30.37 | 8.34 | 0
5977 | 2006-09-07 | 0 | 0 | 0 | 29.51 | 8.23 | 0
5978 | 2006-09-07 01:00 | 0 | 0 | 0 | 28.64 | 8.23 | 0
5979 | 2006-09-07 02:00 | 0 | 0 | 0 | 27.8 | 8.23 | 0
5980 | 2006-09-07 03:00 | 0 | 0 | 0 | 26.96 | 3.48 | 0
5981 | 2006-09-07 04:00 | 0 | 0 | 0 | 26.12 | 3.48 | 0
5982 | 2006-09-07 05:00 | 2 | 191 | 0 | 25.48 | 3.48 | 0 | -0.17607 | 82.6 | 90 | 0 | 2 | 0 | 0 | 0.018738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.48 | 0 | 0 | 0 | 0 | 0 | 0 | 660 | 0 | 0 | 0 | 0 | 0 | 660 | 0 | 0
5983 | 2006-09-07 06:00 | 181 | 651 | 43 | 24.84 | 3.19 | 0 | 12.1425 | 91.0834 | 78.5537 | 0 | 181 | 130.196 | 45.8433 | 1.6958 | 96.1005 | 42.9019 | 0.0088517 | 76.6927 | 41.3141 | 0.0066699 | 114.473 | 114.461 | 257038 | 27.7459 | 225133 | 221573 | 199411 | 0 | 0 | 199016 | 654.833 | 0 | 0 | 0 | 432.196 | 198584 | 660.654 | 193578 | 189706.7969
5984 | 2006-09-07 07:00 | 400 | 829 | 57 | 24.2 | 3.19 | 0 | 24.4223 | 100.036 | 63.7826 | 0 | 400 | 366.493 | 63.996 | 3.7477 | 357.345 | 59.8899 | 0.019562 | 334.768 | 57.6734 | 0.01474 | 380.682 | 380.652 | 854865 | 33.8638 | 813884 | 780903 | 714035 | 0 | 0 | 709584 | 677.887 | 0 | 0 | 0 | 521.063 | 709063 | 680.027 | 699103 | 685120.6875
5985 | 2006-09-07 08:00 | 605 | 907 | 68 | 26.09 | 3.19 | 0 | 36.328 | 110.506 | 48.9913 | 0 | 605 | 594.802 | 77.0675 | 5.6684 | 594.802 | 72.1227 | 0.029587 | 579.219 | 69.4535 | 0.022294 | 629.234 | 629.232 | 1413100 | 42.0647 | 1386850 | 1284450 | 1253090 | 0 | 0 | 1239670 | 674.092 | 0 | 0 | 0 | 0 | 1239670 | 674.092 | 1221110 | 1196686
5986 | 2006-09-07 09:00 | 772 | 950 | 75 | 27.99 | 1.81 | 0 | 47.3053 | 124.156 | 34.207 | 0 | 772 | 784.28 | 85.0905 | 7.233 | 784.28 | 79.6309 | 0.037754 | 776.077 | 76.6838 | 0.028448 | 827.206 | 827.2 | 1857680 | 51.01 | 1851550 | 1645970 | 1607970 | 0 | 0 | 1584520 | 652.505 | 0 | 0 | 0 | 2723.19 | 1581800 | 660 | 1555190 | 1524089.5
5987 | 2006-09-07 10:00 | 885 | 967 | 82 | 29.88 | 1.81 | 0 | 56.2462 | 143.642 | 19.5006 | 0 | 885 | 910.403 | 92.7105 | 8.2918 | 910.403 | 86.7621 | 0.04328 | 907.633 | 83.5511 | 0.032613 | 961.48 | 961.477 | 2159230 | 56.6368 | 2168780 | 1877740 | 1838360 | 0 | 0 | 1806330 | 635.952 | 0 | 0 | 0 | 29651 | 1776680 | 660 | 1743330 | 1708468
5988 | 2006-09-07 11:00 | 941 | 981 | 85 | 30.6 | 1.81 | 0 | 61.0667 | 171.06 | 5.6391 | 0 | 941 | 973.347 | 95.8764 | 8.8164 | 973.347 | 89.7248 | 0.046019 | 973.111 | 86.4042 | 0.034676 | 1027.76 | 1027.76 | 2308080 | 59.2013 | 2325730 | 1989170 | 1947580 | 0 | 0 | 1910920 | 628.895 | 0 | 0 | 0 | 52948.5 | 1857970 | 660 | 1821590 | 1785161
5989 | 2006-09-07 12:00 | 926 | 978 | 84 | 31.31 | 5 | 0 | 59.6814 | 201.397 | 11.1896 | 0 | 926 | 956.862 | 94.8337 | 8.6759 | 956.862 | 88.749 | 0.045285 | 955.935 | 85.4645 | 0.034123 | 1010.19 | 1010.19 | 2268630 | 54.0853 | 2284120 | 2003960 | 1958110 | 0 | 0 | 1923040 | 646.852 | 0 | 0 | 0 | 9484.99 | 1913550 | 660 | 1875020 | 1837522.875
5990 | 2006-09-07 13:00 | 846 | 660 | 321 | 32.03 | 5 | 0 | 52.7858 | 225.446 | 25.6986 | 0 | 846 | 594.026 | 347.827 | 7.9264 | 594.026 | 325.51 | 0.041373 | 590.766 | 313.463 | 0.031175 | 877.133 | 877.102 | 1969740 | 51.8049 | 1969310 | 1744850 | 1704320 | 0 | 0 | 1677980 | 651.465 | 0 | 0 | 0 | 3801.14 | 1674170 | 659.999 | 1644470 | 1611581.625
5991 | 2006-09-07 14:00 | 129 | 0 | 129 | 32.63 | 5 | 0 | 42.7791 | 242.057 | 40.4569 | 0 | 129 | 0 | 119.756 | 1.2086 | 0 | 112.072 | 0.0063086 | 0 | 107.925 | 0.0047537 | 104.691 | 104.688 | 235103 | 34.9903 | 202990 | 192727 | 187869 | 0 | 0 | 187511 | 624.76 | 0 | 0 | 0 | 8155.21 | 179356 | 660 | 174471 | 170981.2031
5992 | 2006-09-07 15:00 | 519 | 596 | 209 | 33.24 | 6.34 | 0 | 31.3048 | 254.078 | 55.2523 | 0 | 519 | 340.054 | 218.73 | 4.8626 | 340.054 | 204.696 | 0.025381 | 327.225 | 197.12 | 0.019125 | 508.634 | 508.626 | 1142240 | 43.7568 | 1106700 | 1015200 | 990783 | 0 | 0 | 982056 | 662.62 | 0 | 0 | 0 | -7.5865 | 982063 | 662.814 | 969158 | 949775.125
5993 | 2006-09-07 16:00 | 283 | 696 | 54 | 33.85 | 6.34 | 0 | 19.1778 | 263.731 | 70.0432 | 0 | 283 | 237.93 | 60.0492 | 2.6515 | 237.93 | 56.1963 | 0.01384 | 214.971 | 54.1165 | 0.010429 | 261.025 | 261.023 | 586189 | 39.2471 | 543743 | 507618 | 495816 | 0 | 0 | 493526 | 650.449 | 0 | 0 | 0 | 1299.35 | 492227 | 660 | 485563 | 475851.7188
5994 | 2006-09-07 17:00 | 70 | 464 | 14 | 32.68 | 6.34 | 0 | 6.83 | 272.357 | 84.8064 | 0 | 70 | 42.6258 | 14.9806 | 0.65585 | 42.6258 | 14.0194 | 0.0034233 | 21.2127 | 13.5006 | 0.0025795 | 33.6744 | 33.6732 | 75621.5 | 33.3763 | 57531.4 | 54888.3 | 53768.7 | 0 | 0 | 53733.9 | 574.671 | 0 | 0 | 0 | 20480.2 | 33253.7 | 660 | 32056.4 | 31415.3047
5995 | 2006-09-07 18:00 | 0 | 24 | 0 | 31.52 | 8.17 | 0
5996 | 2006-09-07 19:00 | 0 | 0 | 0 | 30.36 | 8.17 | 0
5997 | 2006-09-07 20:00 | 0 | 0 | 0 | 29.28 | 8.17 | 0
5998 | 2006-09-07 21:00 | 0 | 0 | 0 | 28.2 | 6.49 | 0
5999 | 2006-09-07 22:00 | 0 | 0 | 0 | 27.13 | 6.49 | 0
6000 | 2006-09-07 23:00 | 0 | 0 | 0 | 26.15 | 6.49 | 0
6001 | 2006-09-08 | 0 | 0 | 0 | 25.18 | 7.76 | 0
6002 | 2006-09-08 01:00 | 0 | 0 | 0 | 24.2 | 7.76 | 0
6003 | 2006-09-08 02:00 | 0 | 0 | 0 | 23.83 | 7.76 | 0
6004 | 2006-09-08 03:00 | 0 | 0 | 0 | 23.45 | 6.51 | 0
6005 | 2006-09-08 04:00 | 0 | 0 | 0 | 23.07 | 6.51 | 0
6006 | 2006-09-08 05:00 | 1 | 193 | 0 | 22.63 | 6.51 | 0 | -0.32012 | 82.957 | 90 | 0 | 1 | 0 | 0 | 0.0093692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.63 | 0 | 0 | 0 | 0 | 0 | 0 | 660 | 0 | 0 | 0 | 0 | 0 | 660 | 0 | 0
6007 | 2006-09-08 06:00 | 174 | 628 | 43 | 22.18 | 7.27 | 0 | 12.0025 | 91.4502 | 78.5254 | 0 | 174 | 125.317 | 46.0066 | 1.6302 | 91.3697 | 43.0547 | 0.0085093 | 72.9732 | 41.4613 | 0.0064119 | 111.008 | 111.024 | 249324 | 24.3434 | 217804 | 218139 | 197030 | 0 | 0 | 196656 | 665.191 | 0 | 0 | 0 | 220.35 | 196436 | 667.49 | 191336 | 187508.8906
6008 | 2006-09-08 07:00 | 397 | 827 | 57 | 21.74 | 7.27 | 0 | 24.2741 | 100.426 | 63.7491 | 0 | 397 | 365.804 | 64.14 | 3.7196 | 355.904 | 60.0246 | 0.019415 | 333.466 | 57.8032 | 0.01463 | 379.545 | 379.53 | 852343 | 29.1355 | 811394 | 795860 | 726633 | 0 | 0 | 722300 | 700.903 | 0 | 0 | 0 | 0 | 722300 | 700.903 | 711376 | 697148
6009 | 2006-09-08 08:00 | 603 | 907 | 68 | 23.78 | 7.27 | 0 | 36.1565 | 110.933 | 48.9567 | 0 | 603 | 595.425 | 77.2182 | 5.6496 | 595.425 | 72.2637 | 0.029489 | 579.857 | 69.5893 | 0.022221 | 629.985 | 629.981 | 1414770 | 36.0557 | 1388590 | 1322510 | 1288070 | 0 | 0 | 1274690 | 694.177 | 0 | 0 | 0 | 0 | 1274690 | 694.177 | 1254440 | 1229348.875
6010 | 2006-09-08 09:00 | 770 | 950 | 75 | 25.83 | 6.32 | 0 | 47.0893 | 124.626 | 34.1783 | 0 | 770 | 785.031 | 85.2486 | 7.2143 | 785.031 | 79.7789 | 0.037656 | 776.836 | 76.8263 | 0.028375 | 828.08 | 828.075 | 1859650 | 42.974 | 1853610 | 1712410 | 1670710 | 0 | 0 | 1647350 | 679.308 | 0 | 0 | 0 | 0 | 1647350 | 679.308 | 1618010 | 1585645.375
6011 | 2006-09-08 10:00 | 885 | 972 | 81 | 27.87 | 6.32 | 0 | 55.96 | 144.104 | 19.4984 | 0 | 885 | 914.613 | 91.7971 | 8.2918 | 914.613 | 85.9072 | 0.04328 | 911.831 | 82.7278 | 0.032613 | 964.754 | 964.749 | 2166580 | 47.8436 | 2176520 | 1967280 | 1919170 | 0 | 0 | 1887380 | 666.936 | 0 | 0 | 0 | 0 | 1887380 | 666.936 | 1849800 | 1812802.75
6012 | 2006-09-08 11:00 | 937 | 981 | 84 | 28.53 | 6.32 | 0 | 60.7047 | 171.332 | 5.829 | 0 | 937 | 973.031 | 94.9751 | 8.779 | 973.031 | 88.8813 | 0.045823 | 972.778 | 85.5919 | 0.034529 | 1026.65 | 1026.65 | 2305590 | 49.785 | 2323100 | 2081450 | 2032870 | 0 | 0 | 1996670 | 661.307 | 0 | 0 | 0 | -64.3149 | 1996730 | 661.686 | 1954870 | 1915769.375
6013 | 2006-09-08 12:00 | 922 | 978 | 83 | 29.18 | 9.01 | 0 | 59.2973 | 201.334 | 11.4021 | 0 | 922 | 956.519 | 93.929 | 8.6384 | 956.519 | 87.9023 | 0.04509 | 955.556 | 84.6491 | 0.033976 | 1009.03 | 1009.03 | 2266020 | 46.8066 | 2281360 | 2072910 | 2026190 | 0 | 0 | 1991100 | 669.554 | 0 | 0 | 0 | 0 | 1991100 | 669.554 | 1949450 | 1910462.875
6014 | 2006-09-08 13:00 | 841 | 961 | 80 | 29.83 | 9.01 | 0 | 52.4315 | 225.196 | 25.8496 | 0 | 841 | 864.035 | 90.7533 | 7.8795 | 864.035 | 84.9304 | 0.041128 | 859.231 | 81.7872 | 0.030991 | 912.818 | 912.816 | 2049950 | 45.7759 | 2053690 | 1873790 | 1829390 | 0 | 0 | 1800940 | 672.518 | 0 | 0 | 0 | 0 | 1800940 | 672.518 | 1766480 | 1731153.25
6015 | 2006-09-08 14:00 | 703 | 934 | 73 | 29.64 | 9.01 | 0 | 42.4596 | 241.763 | 40.5946 | 0 | 703 | 708.637 | 82.991 | 6.5866 | 708.637 | 77.6661 | 0.03438 | 697.407 | 74.7918 | 0.025906 | 749.057 | 749.053 | 1682180 | 42.7252 | 1667560 | 1541420 | 1503440 | 0 | 0 | 1484420 | 678.383 | 0 | 0 | 0 | 0 | 1484420 | 678.383 | 1460110 | 1430906
6016 | 2006-09-08 15:00 | 517 | 880 | 64 | 29.45 | 10.23 | 0 | 31.0087 | 253.79 | 55.3877 | 0 | 517 | 499.474 | 72.5317 | 4.8439 | 499.474 | 67.878 | 0.025283 | 480.482 | 65.3658 | 0.019052 | 529.491 | 529.486 | 1189090 | 38.0297 | 1154930 | 1089170 | 1062750 | 0 | 0 | 1053220 | 680.358 | 0 | 0 | 0 | 0 | 1053220 | 680.358 | 1038180 | 1017417.6875
6017 | 2006-09-08 16:00 | 289 | 729 | 52 | 29.26 | 10.23 | 0 | 18.8934 | 263.455 | 70.1814 | 0 | 289 | 248.151 | 58.1019 | 2.7077 | 248.151 | 54.374 | 0.014133 | 223.963 | 52.3616 | 0.01065 | 268.045 | 268.044 | 601958 | 33.6033 | 559397 | 537120 | 523729 | 0 | 0 | 521332 | 671.191 | 0 | 0 | 0 | 0 | 521332 | 671.191 | 514001 | 503720.625
6018 | 2006-09-08 17:00 | 69 | 486 | 12 | 28.41 | 10.23 | 0 | 6.5476 | 272.093 | 84.9507 | 0 | 69 | 43.9957 | 12.9433 | 0.64648 | 43.9957 | 12.1128 | 0.0033744 | 21.2017 | 11.6645 | 0.0025427 | 31.8827 | 31.8826 | 71600.4 | 28.9266 | 54048.8 | 52887.8 | 51764.5 | 0 | 0 | 51733.7 | 586.962 | 0 | 0 | 0 | 12503.4 | 39230.3 | 660 | 37831.9 | 37075.2578
6019 | 2006-09-08 18:00 | 0 | 20 | 0 | 27.57 | 8.09 | 0
6020 | 2006-09-08 19:00 | 0 | 0 | 0 | 26.72 | 8.09 | 0
6021 | 2006-09-08 20:00 | 0 | 0 | 0 | 25.62 | 8.09 | 0
6022 | 2006-09-08 21:00 | 0 | 0 | 0 | 24.52 | 10.14 | 0
6023 | 2006-09-08 22:00 | 0 | 0 | 0 | 23.42 | 10.14 | 0
6024 | 2006-09-08 23:00 | 0 | 0 | 0 | 22.51 | 10.14 | 0
6025 | 2006-09-09 | 0 | 0 | 0 | 21.59 | 10.11 | 0
6026 | 2006-09-09 01:00 | 0 | 0 | 0 | 20.68 | 10.11 | 0
6027 | 2006-09-09 02:00 | 0 | 0 | 0 | 20.1 | 10.11 | 0
6028 | 2006-09-09 03:00 | 0 | 0 | 0 | 19.52 | 9.3 | 0
6029 | 2006-09-09 04:00 | 0 | 0 | 0 | 18.94 | 9.3 | 0
6030 | 2006-09-09 05:00 | 1 | 187 | 0 | 18.58 | 9.3 | 0 | -0.46438 | 83.3158 | 90 | 0 | 1 | 0 | 0 | 0.0093692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.58 | 0 | 0 | 0 | 0 | 0 | 0 | 660 | 0 | 0 | 0 | 0 | 0 | 660 | 0 | 0
6031 | 2006-09-09 06:00 | 167 | 595 | 44 | 18.22 | 6.53 | 0 | 11.8618 | 91.8184 | 78.4971 | 0 | 167 | 119.329 | 47.1662 | 1.5647 | 85.9516 | 44.1399 | 0.008167 | 68.6984 | 42.5063 | 0.006154 | 107.875 | 107.882 | 242269 | 20.4237 | 211070 | 215457 | 194915 | 0 | 0 | 194564 | 677.552 | 0 | 0 | 0 | 20.8221 | 194543 | 678.169 | 189277 | 185491.5625
6032 | 2006-09-09 07:00 | 390 | 813 | 57 | 17.85 | 6.53 | 0 | 24.1246 | 100.817 | 63.7163 | 0 | 390 | 360.777 | 64.2853 | 3.654 | 350.254 | 60.1606 | 0.019073 | 328.218 | 57.9341 | 0.014372 | 374.582 | 374.578 | 841214 | 25.5014 | 800178 | 797738 | 728305 | 0 | 0 | 724084 | 712.302 | 0 | 0 | 0 | 0 | 724084 | 712.302 | 712709 | 698454.625
6033 | 2006-09-09 08:00 | 598 | 903 | 68 | 19.96 | 6.53 | 0 | 35.9831 | 111.361 | 48.9238 | 0 | 598 | 592.708 | 77.3699 | 5.6028 | 592.708 | 72.4057 | 0.029245 | 577.241 | 69.726 | 0.022037 | 627.579 | 627.575 | 1409370 | 32.7793 | 1382980 | 1336740 | 1302090 | 0 | 0 | 1288830 | 705.582 | 0 | 0 | 0 | 0 | 1288830 | 705.582 | 1267760 | 1242401.875
6034 | 2006-09-09 09:00 | 766 | 949 | 74 | 22.06 | 3.69 | 0 | 46.8708 | 125.094 | 34.153 | 0 | 766 | 784.664 | 84.3169 | 7.1768 | 784.664 | 78.907 | 0.037461 | 776.488 | 75.9867 | 0.028227 | 826.928 | 826.927 | 1857070 | 42.3723 | 1850910 | 1714620 | 1670650 | 0 | 0 | 1647430 | 681.021 | 0 | 0 | 0 | 0 | 1647430 | 681.021 | 1618030 | 1585673.375
6035 | 2006-09-09 10:00 | 882 | 971 | 82 | 24.17 | 3.69 | 0 | 55.6711 | 144.563 | 19.5032 | 0 | 882 | 913.158 | 93.057 | 8.2637 | 913.158 | 87.0863 | 0.043133 | 910.379 | 83.8632 | 0.032502 | 964.446 | 964.442 | 2165900 | 47.8601 | 2175810 | 1966390 | 1918120 | 0 | 0 | 1886450 | 667.798 | 0 | 0 | 0 | 0 | 1886450 | 667.798 | 1848890 | 1811916.375
6036 | 2006-09-09 11:00 | 912 | 899 | 133 | 25.33 | 3.69 | 0 | 60.3408 | 171.6 | 6.0381 | 0 | 912 | 891.475 | 147.09 | 8.5447 | 891.475 | 137.652 | 0.044601 | 891.227 | 132.558 | 0.033607 | 993.104 | 993.092 | 2230230 | 49.7239 | 2243630 | 2010200 | 1964180 | 0 | 0 | 1930450 | 661.879 | 0 | 0 | 0 | 9.3827 | 1930440 | 661.958 | 1891230 | 1853402
6037 | 2006-09-09 12:00 | 918 | 977 | 83 | 26.5 | 4.75 | 0 | 58.9113 | 201.274 | 11.6247 | 0 | 918 | 955.047 | 94.1082 | 8.6009 | 955.047 | 88.07 | 0.044894 | 954.047 | 84.8106 | 0.033829 | 1007.72 | 1007.72 | 2263090 | 49.5926 | 2278270 | 2042810 | 1995090 | 0 | 0 | 1960310 | 662.122 | 0 | 0 | 0 | -33.6083 | 1960350 | 662.389 | 1919950 | 1881546.625
6038 | 2006-09-09 13:00 | 838 | 963 | 80 | 27.66 | 4.75 | 0 | 52.0749 | 224.949 | 26.0062 | 0 | 838 | 863.637 | 90.922 | 7.8514 | 863.637 | 85.0882 | 0.040982 | 858.772 | 81.9392 | 0.030881 | 912.519 | 912.514 | 2049280 | 48.5708 | 2052990 | 1848370 | 1803920 | 0 | 0 | 1775540 | 664.066 | 0 | 0 | 0 | 0 | 1775540 | 664.066 | 1742160 | 1707316.625
6039 | 2006-09-09 14:00 | 698 | 933 | 73 | 28.05 | 4.75 | 0 | 42.1378 | 241.472 | 40.7359 | 0 | 698 | 705.868 | 83.1436 | 6.5397 | 705.868 | 77.809 | 0.034135 | 694.584 | 74.9293 | 0.025722 | 746.452 | 746.448 | 1676330 | 45.1553 | 1661450 | 1518150 | 1482030 | 0 | 0 | 1463000 | 668.98 | 0 | 0 | 0 | 0 | 1463000 | 668.98 | 1439560 | 1410770.125
6040 | 2006-09-09 15:00 | 512 | 839 | 84 | 28.43 | 5.07 | 0 | 30.7104 | 253.502 | 55.5257 | 0 | 512 | 474.377 | 95.84 | 4.797 | 474.377 | 89.6907 | 0.025039 | 456.192 | 86.3713 | 0.018867 | 526.305 | 526.302 | 1181940 | 40.242 | 1147570 | 1070910 | 1044200 | 0 | 0 | 1034850 | 674.63 | 0 | 0 | 0 | 0 | 1034850 | 674.63 | 1020450 | 1000039.5625
6041 | 2006-09-09 16:00 | 271 | 670 | 57 | 28.81 | 5.07 | 0 | 18.607 | 263.18 | 70.3213 | 0 | 271 | 225.851 | 63.4172 | 2.5391 | 225.851 | 59.3483 | 0.013253 | 203.609 | 57.1518 | 0.0099864 | 252.948 | 252.946 | 568054 | 34.487 | 525769 | 502528 | 490059 | 0 | 0 | 487925 | 665.61 | 0 | 0 | 0 | 0 | 487925 | 665.61 | 481133 | 471510.3125
6042 | 2006-09-09 17:00 | 63 | 447 | 13 | 28.06 | 5.07 | 0 | 6.2635 | 271.827 | 85.0962 | 0 | 63 | 39.1759 | 14.0128 | 0.59026 | 39.1759 | 13.1137 | 0.003081 | 18.2203 | 12.6283 | 0.0023216 | 29.9254 | 29.9246 | 67203.3 | 28.7316 | 50258.9 | 49230.4 | 48218.3 | 0 | 0 | 48191.3 | 584.541 | 0 | 0 | 0 | 12769.8 | 35421.5 | 660 | 34150.7 | 33467.7305
6043 | 2006-09-09 18:00 | 0 | 13 | 0 | 27.31 | 7.02 | 0
6044 | 2006-09-09 19:00 | 0 | 0 | 0 | 26.56 | 7.02 | 0
6045 | 2006-09-09 20:00 | 0 | 0 | 0 | 25.41 | 7.02 | 0
6046 | 2006-09-09 21:00 | 0 | 0 | 0 | 24.26 | 6.58 | 0
6047 | 2006-09-09 22:00 | 0 | 0 | 0 | 23.11 | 6.58 | 0
6048 | 2006-09-09 23:00 | 0 | 0 | 0 | 22.2 | 6.58 | 0
6049 | 2006-09-10 | 0 | 0 | 0 | 21.29 | 5.37 | 0
6050 | 2006-09-10 01:00 | 0 | 0 | 0 | 20.39 | 5.37 | 0
6051 | 2006-09-10 02:00 | 0 | 0 | 0 | 19.74 | 5.37 | 0
6052 | 2006-09-10 03:00 | 0 | 0 | 0 | 19.1 | 3.66 | 0
6053 | 2006-09-10 04:00 | 0 | 0 | 0 | 18.45 | 3.66 | 0
6054 | 2006-09-10 05:00 | 10 | 147 | 3 | 18.18 | 3.66 | 0 | -0.60886 | 83.6762 | 90 | 0 | 10 | 0 | 2.6826 | 0.093692 | 0 | 2.5105 | 0 | 0 | 2.4175 | 0 | 2.345 | 2.3449 | 5266.08 | 18.2377 | 1324.17 | 1318.71 | 1310.42 | 0 | 0 | 1310.36 | 345.494 | 0 | 0 | 0 | 1310.36 | 0 | 660 | 0 | 0
6055 | 2006-09-10 06:00 | 168 | 605 | 44 | 17.91 | 0.36 | 0 | 11.7203 | 92.1879 | 78.4689 | 0 | 168 | 122.026 | 47.3299 | 1.574 | 86.7644 | 44.2931 | 0.0082159 | 69.4007 | 42.6538 | 0.0061909 | 108.699 | 108.719 | 244149 | 21.2456 | 212915 | 216263 | 195588 | 0 | 0 | 195229 | 673.322 | 0 | 0 | 0 | 108.021 | 195121 | 675.331 | 189898 | 186100.2344
6056 | 2006-09-10 07:00 | 366 | 672 | 93 | 17.64 | 0.36 | 0 | 23.9739 | 101.209 | 63.6842 | 0 | 366 | 297.857 | 102.811 | 3.4291 | 288.508 | 96.2143 | 0.017899 | 270.393 | 92.6535 | 0.013487 | 352.169 | 352.157 | 790859 | 28.4446 | 749096 | 736792 | 679849 | 0 | 0 | 676058 | 698.558 | 0 | 0 | 0 | 0 | 676058 | 698.558 | 665891 | 652573
6057 | 2006-09-10 08:00 | 586 | 842 | 94 | 19.78 | 0.36 | 0 | 35.8077 | 111.789 | 48.8926 | 0 | 586 | 552.888 | 108.209 | 5.4904 | 552.888 | 101.266 | 0.028658 | 538.486 | 97.5183 | 0.021594 | 616.945 | 616.942 | 1385500 | 38.7086 | 1358190 | 1277650 | 1244250 | 0 | 0 | 1231470 | 686.321 | 0 | 0 | 0 | 0 | 1231470 | 686.321 | 1212500 | 1188250.875
6058 | 2006-09-10 09:00 | 752 | 925 | 80 | 21.93 | 3.1 | 0 | 46.6499 | 125.56 | 34.1309 | 0 | 752 | 764.953 | 91.0111 | 7.0457 | 764.953 | 85.1716 | 0.036776 | 756.995 | 82.0195 | 0.027711 | 813.871 | 813.87 | 1827750 | 42.7156 | 1820130 | 1683240 | 1644010 | 0 | 0 | 1621520 | 681.255 | 0 | 0 | 0 | 0 | 1621520 | 681.255 | 1592950 | 1561094.875
6059 | 2006-09-10 10:00 | 861 | 934 | 94 | 24.07 | 3.1 | 0 | 55.3795 | 145.017 | 19.515 | 0 | 861 | 878.49 | 106.222 | 8.0669 | 878.49 | 99.4064 | 0.042106 | 875.813 | 95.7274 | 0.031728 | 942.425 | 942.421 | 2116440 | 48.1386 | 2123700 | 1916400 | 1870800 | 0 | 0 | 1840420 | 665.061 | 0 | 0 | 0 | 0 | 1840420 | 665.061 | 1804630 | 1768540.25
6060 | 2006-09-10 11:00 | 915 | 953 | 92 | 25.62 | 3.1 | 0 | 59.975 | 171.864 | 6.2648 | 0 | 915 | 944.881 | 104.013 | 8.5728 | 944.881 | 97.3396 | 0.044747 | 944.597 | 93.7371 | 0.033718 | 1007.22 | 1007.21 | 2261940 | 51.3434 | 2277060 | 2024540 | 1978890 | 0 | 0 | 1943900 | 654.596 | 0 | 0 | 0 | 924.694 | 1942970 | 660 | 1903280 | 1865210.25
6061 | 2006-09-10 12:00 | 894 | 937 | 97 | 27.18 | 2.99 | 0 | 58.5238 | 201.215 | 11.8569 | 0 | 894 | 914.567 | 109.432 | 8.3761 | 914.567 | 102.411 | 0.04372 | 913.57 | 98.6206 | 0.032944 | 981.857 | 981.855 | 2205000 | 52.4391 | 2217020 | 1960260 | 1914700 | 0 | 0 | 1881460 | 650.582 | 0 | 0 | 0 | 3585.88 | 1877880 | 660 | 1840730 | 1803918.75
6062 | 2006-09-10 13:00 | 827 | 950 | 82 | 28.73 | 2.99 | 0 | 51.7163 | 224.706 | 26.1683 | 0 | 827 | 851.821 | 93.2692 | 7.7484 | 851.821 | 87.2849 | 0.040444 | 846.957 | 84.0546 | 0.030475 | 903.111 | 903.106 | 2028140 | 51.9632 | 2030740 | 1798340 | 1755770 | 0 | 0 | 1727900 | 652.32 | 0 | 0 | 0 | 3387.91 | 1724510 | 660 | 1693050 | 1659186.25
6063 | 2006-09-10 14:00 | 693 | 933 | 71 | 29.25 | 2.99 | 0 | 41.8138 | 241.183 | 40.8808 | 0 | 693 | 705.368 | 81.116 | 6.4929 | 705.368 | 75.9115 | 0.033891 | 693.99 | 73.1021 | 0.025537 | 744.104 | 744.101 | 1671060 | 48.3927 | 1655930 | 1489650 | 1455990 | 0 | 0 | 1437010 | 657.542 | 0 | 0 | 0 | 335.701 | 1436680 | 660.052 | 1414240 | 1385950.5
6064 | 2006-09-10 15:00 | 507 | 839 | 82 | 29.77 | 3.21 | 0 | 30.41 | 253.215 | 55.6662 | 0 | 507 | 473.554 | 93.9104 | 4.7502 | 473.554 | 87.885 | 0.024794 | 455.251 | 84.6324 | 0.018683 | 523.705 | 523.702 | 1176110 | 43.048 | 1141550 | 1051000 | 1026020 | 0 | 0 | 1016720 | 664.624 | 0 | 0 | 0 | 0 | 1016720 | 664.624 | 1003170 | 983104.6875
6065 | 2006-09-10 16:00 | 269 | 674 | 57 | 30.29 | 3.21 | 0 | 18.3189 | 262.904 | 70.4629 | 0 | 269 | 225.565 | 63.5497 | 2.5203 | 225.565 | 59.4722 | 0.013155 | 203.118 | 57.2712 | 0.0099127 | 252.588 | 252.583 | 567238 | 36.694 | 524960 | 496297 | 484694 | 0 | 0 | 482558 | 657.783 | 0 | 0 | 0 | 29.8433 | 482529 | 660 | 475972 | 466452.8438
6066 | 2006-09-10 17:00 | 61 | 449 | 13 | 29.91 | 3.21 | 0 | 5.978 | 271.562 | 85.2428 | 0 | 61 | 38.2231 | 14.0466 | 0.57152 | 38.2231 | 13.1454 | 0.0029831 | 17.0898 | 12.6589 | 0.0022479 | 28.8584 | 28.8576 | 64806.8 | 30.6417 | 48201.9 | 46705.2 | 45741 | 0 | 0 | 45716 | 576.149 | 0 | 0 | 0 | 16339.8 | 29376.2 | 660 | 28311.7 | 27745.4629
6067 | 2006-09-10 18:00 | 0 | 8 | 0 | 29.53 | 2.65 | 0
6068 | 2006-09-10 19:00 | 0 | 0 | 0 | 29.15 | 2.65 | 0
6069 | 2006-09-10 20:00 | 0 | 0 | 0 | 28.57 | 2.65 | 0
6070 | 2006-09-10 21:00 | 0 | 0 | 0 | 27.98 | 4.49 | 0
6071 | 2006-09-10 22:00 | 0 | 0 | 0 | 27.4 | 4.49 | 0
6072 | 2006-09-10 23:00 | 0 | 0 | 0 | 26.68 | 4.49 | 0
6073 | 2006-09-11 | 0 | 0 | 0 | 25.96 | 1.15 | 0
6074 | 2006-09-11 01:00 | 0 | 0 | 0 | 25.24 | 1.15 | 0
6075 | 2006-09-11 02:00 | 0 | 0 | 0 | 24.69 | 1.15 | 0
6076 | 2006-09-11 03:00 | 0 | 0 | 0 | 24.13 | 0.92 | 0
6077 | 2006-09-11 04:00 | 0 | 0 | 0 | 23.58 | 0.92 | 0
6078 | 2006-09-11 05:00 | 10 | 127 | 4 | 23.46 | 0.92 | 0 | -0.75356 | 84.0381 | 90 | 0 | 10 | 0 | 3.0026 | 0.093692 | 0 | 2.81 | 0 | 0 | 2.706 | 0 | 2.6248 | 2.6246 | 5894.23 | 23.5375 | 1645.25 | 1645.11 | 1631.88 | 0 | 0 | 1631.8 | 374.37 | 0 | 0 | 0 | 1631.8 | 0 | 660 | 0 | 0
6079 | 2006-09-11 06:00 | 172 | 536 | 64 | 23.34 | 2.76 | 0 | 11.5782 | 92.5585 | 78.4407 | 0 | 172 | 107.826 | 66.5612 | 1.6115 | 75.618 | 62.2905 | 0.0084115 | 60.5304 | 59.9851 | 0.0063383 | 116.906 | 116.892 | 262502 | 26.3934 | 229839 | 227861 | 209830 | 0 | 0 | 209413 | 658.321 | 0 | 0 | 0 | 558.149 | 208855 | 663.109 | 203612 | 199539.8594
6080 | 2006-09-11 07:00 | 390 | 824 | 57 | 23.23 | 2.76 | 0 | 23.822 | 101.602 | 63.653 | 0 | 390 | 365.904 | 64.5802 | 3.654 | 353.552 | 60.4366 | 0.019073 | 331.398 | 58.1999 | 0.014372 | 377.924 | 377.936 | 848753 | 33.1022 | 807933 | 777716 | 713402 | 0 | 0 | 709024 | 684.645 | 0 | 0 | 0 | 0 | 709024 | 684.645 | 698876 | 684898.8125
6081 | 2006-09-11 08:00 | 582 | 837 | 95 | 25.11 | 2.76 | 0 | 35.6305 | 112.217 | 48.8633 | 0 | 582 | 549.95 | 109.512 | 5.4529 | 549.95 | 102.486 | 0.028462 | 535.649 | 98.6929 | 0.021447 | 615.333 | 615.329 | 1381870 | 41.1832 | 1354410 | 1259450 | 1228800 | 0 | 0 | 1215910 | 675.003 | 0 | 0 | 0 | 0 | 1215910 | 675.003 | 1197810 | 1173853.5
6082 | 2006-09-11 09:00 | 758 | 897 | 109 | 26.99 | 3.13 | 0 | 46.4264 | 126.025 | 34.1124 | 0 | 758 | 741.669 | 122.16 | 7.1019 | 741.669 | 114.322 | 0.037069 | 733.963 | 110.091 | 0.027932 | 818.759 | 818.749 | 1838700 | 47.8587 | 1831630 | 1653240 | 1613500 | 0 | 0 | 1590650 | 662.68 | 0 | 0 | 0 | 0 | 1590650 | 662.68 | 1563670 | 1532393
6083 | 2006-09-11 10:00 | 846 | 873 | 132 | 28.88 | 3.13 | 0 | 55.0855 | 145.466 | 19.5341 | 0 | 846 | 820.608 | 146.52 | 7.9264 | 820.608 | 137.119 | 0.041373 | 818.102 | 132.045 | 0.031175 | 921.673 | 921.67 | 2069840 | 52.372 | 2074630 | 1833880 | 1791640 | 0 | 0 | 1762560 | 650.756 | 0 | 0 | 0 | 4507.68 | 1758050 | 660 | 1725380 | 1690875.25
6084 | 2006-09-11 11:00 | 907 | 943 | 96 | 29.44 | 3.13 | 0 | 59.6075 | 172.124 | 6.5074 | 0 | 907 | 934.146 | 108.53 | 8.4979 | 934.146 | 101.566 | 0.044356 | 933.843 | 97.8073 | 0.033423 | 1000.73 | 1000.73 | 2247380 | 54.947 | 2261700 | 1975620 | 1931180 | 0 | 0 | 1896650 | 643.373 | 0 | 0 | 0 | 14651.4 | 1882000 | 660 | 1844700 | 1807803.25
6085 | 2006-09-11 12:00 | 912 | 978 | 83 | 30 | 4.21 | 0 | 58.1348 | 201.158 | 12.0981 | 0 | 912 | 954.427 | 94.4683 | 8.5447 | 954.427 | 88.4071 | 0.044601 | 953.344 | 85.1352 | 0.033607 | 1007.36 | 1007.35 | 2262260 | 53.9134 | 2277400 | 1999700 | 1956850 | 0 | 0 | 1921700 | 645.794 | 0 | 0 | 0 | 9737.26 | 1911960 | 660 | 1873490 | 1836021.625
6086 | 2006-09-11 13:00 | 830 | 963 | 79 | 30.56 | 4.21 | 0 | 51.3557 | 224.466 | 26.3357 | 0 | 830 | 861.743 | 90.1691 | 7.7764 | 861.743 | 84.3837 | 0.040591 | 856.753 | 81.2607 | 0.030586 | 909.903 | 909.897 | 2043400 | 52.1598 | 2046800 | 1810990 | 1771170 | 0 | 0 | 1742580 | 649.627 | 0 | 0 | 0 | 4816.04 | 1737770 | 660 | 1705830 | 1671711.75
6087 | 2006-09-11 14:00 | 667 | 853 | 102 | 30.98 | 4.21 | 0 | 41.4877 | 240.896 | 41.0291 | 0 | 667 | 643.395 | 118.732 | 6.2493 | 643.395 | 111.114 | 0.032619 | 632.921 | 107.002 | 0.024579 | 717.749 | 717.743 | 1611870 | 48.0183 | 1594040 | 1436160 | 1402320 | 0 | 0 | 1384780 | 658.998 | 0 | 0 | 0 | 143.499 | 1384640 | 660.375 | 1363430 | 1336160
6088 | 2006-09-11 15:00 | 502 | 837 | 82 | 31.4 | 4.18 | 0 | 30.1077 | 252.929 | 55.809 | 0 | 502 | 470.51 | 94.0912 | 4.7034 | 470.51 | 88.0542 | 0.02455 | 452.171 | 84.7953 | 0.018499 | 520.876 | 520.867 | 1169730 | 43.7891 | 1134990 | 1041170 | 1016330 | 0 | 0 | 1007170 | 663.581 | 0 | 0 | 0 | 0 | 1007170 | 663.581 | 993851 | 973974.4375
6089 | 2006-09-11 16:00 | 281 | 741 | 51 | 31.83 | 4.18 | 0 | 18.0291 | 262.629 | 70.6062 | 0 | 281 | 246.765 | 57.4612 | 2.6328 | 246.765 | 53.7743 | 0.013742 | 221.947 | 51.7842 | 0.010355 | 265.529 | 265.527 | 596305 | 38.1457 | 553782 | 519915 | 507235 | 0 | 0 | 504876 | 655.295 | 0 | 0 | 0 | 230.41 | 504646 | 660 | 497845 | 487887.8438
6090 | 2006-09-11 17:00 | 62 | 494 | 11 | 31.46 | 4.18 | 0 | 5.6911 | 271.296 | 85.3904 | 0 | 62 | 41.3318 | 11.9966 | 0.58089 | 41.3318 | 11.2269 | 0.0030321 | 17.6836 | 10.8114 | 0.0022847 | 27.6423 | 27.6418 | 62076.3 | 32.1175 | 45865.8 | 44063.8 | 43152.6 | 0 | 0 | 43129.6 | 567.358 | 0 | 0 | 0 | 19650.7 | 23479 | 660 | 22619.8 | 22167.4473
6091 | 2006-09-11 18:00 | 0 | 3 | 0 | 31.09 | 4.6 | 0
6092 | 2006-09-11 19:00 | 0 | 0 | 0 | 30.72 | 4.6 | 0
6093 | 2006-09-11 20:00 | 0 | 0 | 0 | 30.38 | 4.6 | 0
6094 | 2006-09-11 21:00 | 0 | 0 | 0 | 30.04 | 1.71 | 0
6095 | 2006-09-11 22:00 | 0 | 0 | 0 | 29.7 | 1.71 | 0
6096 | 2006-09-11 23:00 | 0 | 0 | 0 | 29.07 | 1.71 | 0
6097 | 2006-09-12 | 0 | 0 | 0 | 28.44 | 0.21 | 0
6098 | 2006-09-12 01:00 | 0 | 0 | 0 | 27.81 | 0.21 | 0
6099 | 2006-09-12 02:00 | 0 | 0 | 0 | 27.23 | 0.21 | 0
6100 | 2006-09-12 03:00 | 0 | 0 | 0 | 26.65 | 0.64 | 0
6101 | 2006-09-12 04:00 | 0 | 0 | 0 | 26.07 | 0.64 | 0
6102 | 2006-09-12 05:00 | 9 | 131 | 3 | 25.56 | 0.64 | 0 | -0.89851 | 84.4015 | 90 | 0 | 9 | 0 | 2.3255 | 0.084323 | 0 | 2.1763 | 0 | 0 | 2.0957 | 0 | 2.0329 | 2.0328 | 4565.09 | 25.6212 | 1000.91 | 1001.37 | 995.752 | 0 | 0 | 995.708 | 300.463 | 0 | 0 | 0 | 995.708 | 0 | 660 | 0 | 0
6103 | 2006-09-12 06:00 | 166 | 568 | 53 | 25.05 | 2.33 | 0 | 11.4353 | 92.9301 | 78.4128 | 0 | 166 | 114.481 | 56.1789 | 1.5553 | 79.1593 | 52.5744 | 0.0081181 | 63.4121 | 50.6286 | 0.0061172 | 110.625 | 110.635 | 248450 | 28.0238 | 216789 | 213078 | 194908 | 0 | 0 | 194530 | 649.129 | 0 | 0 | 0 | 1372.18 | 193158 | 660 | 188210 | 184445.7812
6104 | 2006-09-12 07:00 | 388 | 824 | 57 | 24.54 | 2.33 | 0 | 23.6687 | 101.995 | 63.6228 | 0 | 388 | 366.315 | 64.7296 | 3.6353 | 353.028 | 60.5764 | 0.018975 | 330.949 | 58.3345 | 0.014298 | 377.619 | 377.664 | 848140 | 34.6913 | 807391 | 771306 | 708599 | 0 | 0 | 704230 | 680.802 | 0 | 0 | 0 | 0 | 704230 | 680.802 | 694287 | 680400.875
6105 | 2006-09-12 08:00 | 592 | 905 | 67 | 26.46 | 2.33 | 0 | 35.4514 | 112.645 | 48.8359 | 0 | 592 | 595.788 | 76.7416 | 5.5466 | 595.788 | 71.8177 | 0.028951 | 580.32 | 69.1598 | 0.021815 | 630.016 | 630.011 | 1414840 | 43.3942 | 1388660 | 1278030 | 1249940 | 0 | 0 | 1236330 | 668.383 | 0 | 0 | 0 | 0 | 1236330 | 668.383 | 1218110 | 1193749.25
6106 | 2006-09-12 09:00 | 743 | 875 | 112 | 28.38 | 2.11 | 0 | 46.2006 | 126.488 | 34.0976 | 0 | 743 | 723.947 | 125.528 | 6.9613 | 723.947 | 117.474 | 0.036336 | 716.432 | 113.126 | 0.02738 | 804.698 | 804.689 | 1807130 | 50.329 | 1798500 | 1603760 | 1567420 | 0 | 0 | 1545140 | 652.342 | 0 | 0 | 0 | 1782.75 | 1543350 | 660 | 1517990 | 1487630.625
6107 | 2006-09-12 10:00 | 841 | 901 | 106 | 30.3 | 2.11 | 0 | 54.7889 | 145.911 | 19.5604 | 0 | 841 | 847.68 | 119.484 | 7.8795 | 847.68 | 111.818 | 0.041128 | 845.084 | 107.68 | 0.030991 | 924.211 | 924.204 | 2075520 | 55.509 | 2080610 | 1810830 | 1768920 | 0 | 0 | 1739660 | 640.69 | 0 | 0 | 0 | 19983.5 | 1719680 | 660 | 1688380 | 1654616.875
6108 | 2006-09-12 11:00 | 902 | 936 | 100 | 31 | 2.11 | 0 | 59.2382 | 172.379 | 6.7645 | 0 | 902 | 926.82 | 113.044 | 8.451 | 926.82 | 105.791 | 0.044111 | 926.495 | 101.876 | 0.033239 | 997.551 | 997.545 | 2240230 | 58.2094 | 2254170 | 1937030 | 1894700 | 0 | 0 | 1860270 | 631.891 | 0 | 0 | 0 | 41826.3 | 1818450 | 660 | 1783560 | 1747889
6109 | 2006-09-12 12:00 | 907 | 927 | 125 | 31.69 | 2.52 | 0 | 57.7444 | 201.102 | 12.3479 | 0 | 907 | 903.313 | 139.574 | 8.4979 | 903.313 | 130.618 | 0.044356 | 902.244 | 125.784 | 0.033423 | 997.22 | 997.213 | 2239490 | 58.1573 | 2253380 | 1936890 | 1896790 | 0 | 0 | 1862300 | 631.736 | 0 | 0 | 0 | 42777.7 | 1819520 | 660 | 1784600 | 1748905.625
6110 | 2006-09-12 13:00 | 790 | 815 | 158 | 32.39 | 2.52 | 0 | 50.9933 | 224.229 | 26.5082 | 0 | 790 | 727.806 | 180.928 | 7.4017 | 727.806 | 169.32 | 0.038634 | 723.531 | 163.053 | 0.029112 | 860.015 | 860.01 | 1931360 | 55.2158 | 1928960 | 1680030 | 1642960 | 0 | 0 | 1617480 | 638.464 | 0 | 0 | 0 | 21738.5 | 1595740 | 660 | 1568680 | 1537306.25
6111 | 2006-09-12 14:00 | 685 | 780 | 172 | 32.97 | 2.52 | 0 | 41.1596 | 240.611 | 41.1807 | 0 | 685 | 586.64 | 194.574 | 6.4179 | 586.64 | 182.09 | 0.033499 | 577 | 175.351 | 0.025243 | 729.805 | 729.795 | 1638930 | 52.3397 | 1622320 | 1431010 | 1398170 | 0 | 0 | 1379900 | 643.281 | 0 | 0 | 0 | 10364.6 | 1369540 | 660 | 1348700 | 1321721.125
6112 | 2006-09-12 15:00 | 420 | 525 | 159 | 33.56 | 2.08 | 0 | 29.8037 | 252.644 | 55.9541 | 0 | 420 | 293.992 | 170.524 | 3.9351 | 293.992 | 159.583 | 0.02054 | 282.436 | 153.677 | 0.015477 | 423.044 | 423.034 | 950022 | 45.122 | 909888 | 827775 | 808882 | 0 | 0 | 802822 | 650.19 | 0 | 0 | 0 | 2552.74 | 800269 | 660 | 789865 | 774068.0625
6113 | 2006-09-12 16:00 | 276 | 583 | 98 | 34.14 | 2.08 | 0 | 17.7378 | 262.354 | 70.7509 | 0 | 276 | 192.615 | 104.312 | 2.5859 | 192.615 | 97.6196 | 0.013498 | 173.033 | 94.0068 | 0.010171 | 259.038 | 259.035 | 581727 | 41.2197 | 539321 | 498420 | 486628 | 0 | 0 | 484377 | 643.395 | 0 | 0 | 0 | 4071.94 | 480305 | 660 | 473774 | 464298.5
6114 | 2006-09-12 17:00 | 45 | 288 | 16 | 33.6 | 2.08 | 0 | 5.4029 | 271.029 | 85.5389 | 0 | 45 | 23.9561 | 16.7662 | 0.42162 | 23.9561 | 15.6905 | 0.0022007 | 9.7544 | 15.1098 | 0.0016583 | 24.1199 | 24.1197 | 54166.9 | 34.2592 | 39150 | 37136.5 | 36388.9 | 0 | 0 | 36371.7 | 552.754 | 0 | 0 | 0 | 25887.1 | 10484.6 | 659.999 | 10092.8 | 9890.9492
6115 | 2006-09-12 18:00 | 0 | 0 | 0 | 33.07 | 0.47 | 0
6116 | 2006-09-12 19:00 | 0 | 0 | 0 | 32.54 | 0.47 | 0
6117 | 2006-09-12 20:00 | 0 | 0 | 0 | 32.04 | 0.47 | 0
6118 | 2006-09-12 21:00 | 0 | 0 | 0 | 31.54 | 2.65 | 0
6119 | 2006-09-12 22:00 | 0 | 0 | 0 | 31.04 | 2.65 | 0
6120 | 2006-09-12 23:00 | 0 | 0 | 0 | 30.13 | 2.65 | 0
6121 | 2006-09-13 | 0 | 0 | 0 | 29.22 | 5.66 | 0
6122 | 2006-09-13 01:00 | 0 | 0 | 0 | 28.31 | 5.66 | 0
6123 | 2006-09-13 02:00 | 0 | 0 | 0 | 27.65 | 5.66 | 0
6124 | 2006-09-13 03:00 | 0 | 0 | 0 | 26.99 | 5.69 | 0
6125 | 2006-09-13 04:00 | 0 | 0 | 0 | 26.34 | 5.69 | 0
6126 | 2006-09-13 05:00 | 8 | 104 | 3 | 25.87 | 5.69 | 0 | -1.0437 | 84.766 | 90 | 0 | 8 | 0 | 2.3284 | 0.074954 | 0 | 2.179 | 0 | 0 | 2.0983 | 0 | 2.0354 | 2.0353 | 4570.72 | 25.9139 | 1003.32 | 1004.01 | 998.35 | 0 | 0 | 998.306 | 300.837 | 0 | 0 | 0 | 998.306 | 0 | 660 | 0 | 0
6127 | 2006-09-13 06:00 | 154 | 462 | 63 | 25.4 | 4.83 | 0 | 11.2916 | 93.3026 | 78.3851 | 0 | 154 | 93.5703 | 66.0086 | 1.4429 | 63.7708 | 61.7734 | 0.0075312 | 51.1222 | 59.4872 | 0.0056749 | 107.297 | 107.282 | 240921 | 27.8456 | 209299 | 206051 | 190485 | 0 | 0 | 190133 | 648.522 | 0 | 0 | 0 | 1004.53 | 189128 | 660 | 184194 | 180510.1875
6128 | 2006-09-13 07:00 | 380 | 772 | 72 | 24.93 | 4.83 | 0 | 23.5141 | 102.389 | 63.5936 | 0 | 380 | 343.326 | 81.7598 | 3.5603 | 330.093 | 76.514 | 0.018584 | 309.487 | 73.6822 | 0.014003 | 371.687 | 371.674 | 834691 | 33.4029 | 793708 | 762990 | 703456 | 0 | 0 | 699207 | 684.402 | 0 | 0 | 0 | 0 | 699207 | 684.402 | 689207 | 675423.1875
6129 | 2006-09-13 08:00 | 589 | 905 | 67 | 26.75 | 4.83 | 0 | 35.2704 | 113.072 | 48.8106 | 0 | 589 | 595.327 | 76.8956 | 5.5185 | 595.327 | 71.9619 | 0.028805 | 579.894 | 69.2986 | 0.021705 | 629.738 | 629.734 | 1414220 | 41.1057 | 1388020 | 1291400 | 1259750 | 0 | 0 | 1246250 | 675.997 | 0 | 0 | 0 | 0 | 1246250 | 675.997 | 1227450 | 1202903.625
6130 | 2006-09-13 09:00 | 749 | 892 | 108 | 28.57 | 0.94 | 0 | 45.9723 | 126.948 | 34.0864 | 0 | 749 | 738.344 | 121.551 | 7.0175 | 738.344 | 113.752 | 0.036629 | 730.685 | 109.542 | 0.027601 | 815.048 | 815.047 | 1830390 | 52.6163 | 1822900 | 1607460 | 1569060 | 0 | 0 | 1546440 | 647.712 | 0 | 0 | 0 | 7651.87 | 1538790 | 660 | 1513570 | 1483298
6131 | 2006-09-13 10:00 | 829 | 845 | 143 | 30.38 | 0.94 | 0 | 54.4899 | 146.35 | 19.5942 | 0 | 829 | 793.937 | 166.731 | 7.7671 | 793.937 | 156.033 | 0.040542 | 791.496 | 150.259 | 0.030549 | 913.532 | 913.524 | 2051550 | 57.3316 | 2055370 | 1772240 | 1731890 | 0 | 0 | 1703140 | 632.882 | 0 | 0 | 0 | 35342.3 | 1667790 | 660 | 1638310 | 1605544.875
6132 | 2006-09-13 11:00 | 887 | 874 | 141 | 31.14 | 0.94 | 0 | 58.8673 | 172.63 | 7.0347 | 0 | 887 | 864.963 | 156.457 | 8.3105 | 864.963 | 146.418 | 0.043378 | 864.635 | 141 | 0.032686 | 975.497 | 975.49 | 2190700 | 59.9198 | 2201950 | 1875190 | 1834760 | 0 | 0 | 1801920 | 626.25 | 0 | 0 | 0 | 62431.9 | 1739490 | 660 | 1707490 | 1673343.5
6133 | 2006-09-13 12:00 | 899 | 923 | 124 | 31.9 | 1.05 | 0 | 57.3527 | 201.048 | 12.6058 | 0 | 899 | 898.232 | 138.782 | 8.4229 | 898.232 | 129.877 | 0.043965 | 897.123 | 125.071 | 0.033128 | 991.56 | 991.552 | 2226780 | 60.9378 | 2239990 | 1898000 | 1856400 | 0 | 0 | 1822430 | 622.938 | 0 | 0 | 0 | 74821.9 | 1747610 | 660 | 1715320 | 1681013.25
6134 | 2006-09-13 13:00 | 821 | 913 | 116 | 32.66 | 1.05 | 0 | 50.6293 | 223.996 | 26.6857 | 0 | 821 | 814.824 | 130.243 | 7.6921 | 814.824 | 121.886 | 0.04015 | 809.967 | 117.375 | 0.030254 | 899.551 | 899.544 | 2020150 | 59.0033 | 2022330 | 1728650 | 1691350 | 0 | 0 | 1663400 | 627.145 | 0 | 0 | 0 | 54789.2 | 1608610 | 660 | 1581120 | 1549498.875
6135 | 2006-09-13 14:00 | 650 | 742 | 165 | 33.05 | 1.05 | 0 | 40.8297 | 240.329 | 41.3356 | 0 | 650 | 556.985 | 187.692 | 6.09 | 556.985 | 175.649 | 0.031788 | 547.744 | 169.148 | 0.023953 | 695.409 | 695.403 | 1561700 | 53.415 | 1541650 | 1351790 | 1320530 | 0 | 0 | 1304050 | 639.833 | 0 | 0 | 0 | 17525.6 | 1286520 | 659.999 | 1267580 | 1242231.25
6136 | 2006-09-13 15:00 | 398 | 457 | 173 | 33.44 | 3.46 | 0 | 29.4979 | 252.36 | 56.1013 | 0 | 398 | 254.855 | 184.858 | 3.729 | 254.855 | 172.997 | 0.019464 | 244.75 | 166.594 | 0.014666 | 399.018 | 399.012 | 896082 | 43.3909 | 855032 | 784248 | 765168 | 0 | 0 | 759838 | 655.675 | 0 | 0 | 0 | 767.665 | 759071 | 660 | 749203 | 734218.625
6137 | 2006-09-13 16:00 | 237 | 435 | 106 | 33.83 | 3.46 | 0 | 17.4451 | 262.079 | 70.8971 | 0 | 237 | 143.006 | 110.472 | 2.2205 | 143.006 | 103.384 | 0.01159 | 128.308 | 99.558 | 0.0087335 | 221.038 | 221.032 | 496383 | 39.3423 | 455052 | 424128 | 414520 | 0 | 0 | 412878 | 642.251 | 0 | 0 | 0 | 3769.47 | 409109 | 660 | 403400 | 395331.9375
6138 | 2006-09-13 17:00 | 38 | 210 | 17 | 33.12 | 3.46 | 0 | 5.1136 | 270.762 | 85.6882 | 0 | 38 | 17.714 | 17.4376 | 0.35603 | 17.714 | 16.3188 | 0.0018584 | 6.8193 | 15.7149 | 0.0014003 | 21.8595 | 21.8588 | 49089.2 | 33.6651 | 34882.3 | 33202.6 | 32540.8 | 0 | 0 | 32526.8 | 549.546 | 0 | 0 | 0 | 25276 | 7250.79 | 659.999 | 6978.43 | 6838.8623
6139 | 2006-09-13 18:00 | 0 | 0 | 0 | 32.42 | 7.2 | 0
6140 | 2006-09-13 19:00 | 0 | 0 | 0 | 31.72 | 7.2 | 0
6141 | 2006-09-13 20:00 | 0 | 0 | 0 | 31.03 | 7.2 | 0
6142 | 2006-09-13 21:00 | 0 | 0 | 0 | 30.34 | 7.5 | 0
6143 | 2006-09-13 22:00 | 0 | 0 | 0 | 29.65 | 7.5 | 0
6144 | 2006-09-13 23:00 | 0 | 0 | 0 | 28.57 | 7.5 | 0
6145 | 2006-09-14 | 0 | 0 | 0 | 27.49 | 9 | 0
6146 | 2006-09-14 01:00 | 0 | 0 | 0 | 26.4 | 9 | 0
6147 | 2006-09-14 02:00 | 0 | 0 | 0 | 26.02 | 9 | 0
6148 | 2006-09-14 03:00 | 0 | 0 | 0 | 25.64 | 6.64 | 0
6149 | 2006-09-14 04:00 | 0 | 0 | 0 | 25.27 | 6.64 | 0
6150 | 2006-09-14 05:00 | 8 | 86 | 4 | 24.9 | 6.64 | 0 | -1.1892 | 85.1318 | 90 | 0 | 8 | 0 | 3.0146 | 0.074954 | 0 | 2.8212 | 0 | 0 | 2.7168 | 0 | 2.6353 | 2.6352 | 5918 | 24.9535 | 1658 | 1657.92 | 1644.16 | 0 | 0 | 1644.08 | 373.434 | 0 | 0 | 0 | 1644.08 | 0 | 660 | 0 | 0
6151 | 2006-09-14 06:00 | 159 | 390 | 83 | 24.54 | 8.16 | 0 | 11.1472 | 93.6759 | 78.3577 | 0 | 159 | 79.3298 | 83.9917 | 1.4897 | 53.222 | 78.6026 | 0.0077758 | 42.6964 | 75.6936 | 0.0058592 | 114.844 | 114.833 | 257880 | 26.6554 | 225033 | 223014 | 208546 | 0 | 0 | 208146 | 659.687 | 0 | 0 | 0 | 250.138 | 207895 | 663.004 | 202613 | 198560.9688
6152 | 2006-09-14 07:00 | 379 | 814 | 56 | 24.18 | 8.16 | 0 | 23.3582 | 102.783 | 63.5655 | 0 | 379 | 362.671 | 63.9576 | 3.5509 | 347.93 | 59.854 | 0.018535 | 326.249 | 57.6388 | 0.013966 | 372.385 | 372.422 | 836381 | 31.0405 | 795611 | 773361 | 710184 | 0 | 0 | 705954 | 693.976 | 0 | 0 | 0 | 0 | 705954 | 693.976 | 695510 | 681599.375
6153 | 2006-09-14 08:00 | 587 | 904 | 68 | 25.51 | 8.16 | 0 | 35.0874 | 113.498 | 48.7875 | 0 | 587 | 594.868 | 78.1444 | 5.4997 | 594.868 | 73.1305 | 0.028707 | 579.467 | 70.424 | 0.021631 | 630.415 | 630.415 | 1415750 | 37.1231 | 1389610 | 1317060 | 1285730 | 0 | 0 | 1272220 | 689.587 | 0 | 0 | 0 | 0 | 1272220 | 689.587 | 1252230 | 1227185.625
6154 | 2006-09-14 09:00 | 727 | 855 | 115 | 26.84 | 7.31 | 0 | 45.7415 | 127.406 | 34.0792 | 0 | 727 | 707.761 | 134.751 | 6.8114 | 707.761 | 126.105 | 0.035553 | 700.424 | 121.438 | 0.02679 | 797.232 | 797.226 | 1790370 | 42.3353 | 1780920 | 1649780 | 1609110 | 0 | 0 | 1587480 | 680.054 | 0 | 0 | 0 | 0 | 1587480 | 680.054 | 1560040 | 1528837.125
6155 | 2006-09-14 10:00 | 851 | 900 | 123 | 28.17 | 7.31 | 0 | 54.1885 | 146.785 | 19.6355 | 0 | 851 | 845.514 | 137.924 | 7.9732 | 845.514 | 129.074 | 0.041617 | 842.904 | 124.297 | 0.03136 | 938.215 | 938.209 | 2106980 | 46.4055 | 2113730 | 1923200 | 1878300 | 0 | 0 | 1848220 | 671.24 | 0 | 0 | 0 | 0 | 1848220 | 671.24 | 1812060 | 1775814.375
6156 | 2006-09-14 11:00 | 871 | 873 | 129 | 28.52 | 7.31 | 0 | 58.4949 | 172.877 | 7.3167 | 0 | 871 | 863.199 | 144.274 | 8.1606 | 863.199 | 135.017 | 0.042596 | 862.845 | 130.02 | 0.032097 | 963.11 | 963.108 | 2162900 | 47.2395 | 2172650 | 1969420 | 1921950 | 0 | 0 | 1890190 | 668.48 | 0 | 0 | 0 | 0 | 1890190 | 668.48 | 1852480 | 1815430
6157 | 2006-09-14 12:00 | 853 | 840 | 150 | 28.87 | 11.46 | 0 | 56.9599 | 200.995 | 12.8712 | 0 | 853 | 817.541 | 175.264 | 7.992 | 817.541 | 164.019 | 0.041715 | 816.488 | 157.949 | 0.031433 | 945.234 | 945.226 | 2122740 | 43.0864 | 2130340 | 1968680 | 1920620 | 0 | 0 | 1890100 | 681.476 | 0 | 0 | 0 | 0 | 1890100 | 681.476 | 1852260 | 1815213.75
6158 | 2006-09-14 13:00 | 802 | 893 | 116 | 29.22 | 11.46 | 0 | 50.2637 | 223.766 | 26.8681 | 0 | 802 | 795.774 | 130.475 | 7.5141 | 795.774 | 122.104 | 0.039221 | 790.959 | 117.585 | 0.029554 | 881.316 | 881.308 | 1979200 | 42.4751 | 1979250 | 1833480 | 1787770 | 0 | 0 | 1761320 | 682.442 | 0 | 0 | 0 | 0 | 1761320 | 682.442 | 1728060 | 1693499.875
6159 | 2006-09-14 14:00 | 642 | 828 | 105 | 29.01 | 11.46 | 0 | 40.4981 | 240.048 | 41.4936 | 0 | 642 | 619.363 | 122.617 | 6.015 | 619.363 | 114.75 | 0.031397 | 608.987 | 110.503 | 0.023658 | 697.928 | 697.921 | 1567360 | 39.5069 | 1547540 | 1451490 | 1415840 | 0 | 0 | 1399270 | 685.51 | 0 | 0 | 0 | 0 | 1399270 | 685.51 | 1376650 | 1349120.625
6160 | 2006-09-14 15:00 | 466 | 821 | 66 | 28.81 | 12.18 | 0 | 29.1907 | 252.077 | 56.2506 | 0 | 466 | 455.642 | 75.5328 | 4.3661 | 455.642 | 70.6864 | 0.022789 | 437.416 | 68.0704 | 0.017172 | 490.339 | 490.337 | 1101170 | 35.8744 | 1064490 | 1013670 | 987784 | 0 | 0 | 979702 | 686.813 | 0 | 0 | 0 | 0 | 979702 | 686.813 | 965652 | 946339.4375
6161 | 2006-09-14 16:00 | 243 | 619 | 60 | 28.61 | 12.18 | 0 | 17.1511 | 261.804 | 71.0445 | 0 | 243 | 201.58 | 66.9795 | 2.2767 | 201.58 | 62.682 | 0.011884 | 180.631 | 60.3621 | 0.0089546 | 233.772 | 233.77 | 524989 | 31.978 | 483213 | 467425 | 455644 | 0 | 0 | 453832 | 672.123 | 0 | 0 | 0 | 0 | 453832 | 672.123 | 447225 | 438280.25
6162 | 2006-09-14 17:00 | 37 | 291 | 9 | 27.5 | 12.18 | 0 | 4.8233 | 270.494 | 85.8382 | 0 | 37 | 23.3572 | 9.9176 | 0.34666 | 23.3572 | 9.2812 | 0.0018094 | 8.4331 | 8.9378 | 0.0013635 | 16.851 | 16.8504 | 37841.9 | 27.7428 | 25575.9 | 25191 | 24703.2 | 0 | 0 | 24695.3 | 556.05 | 0 | 0 | 0 | 15448.4 | 9246.9 | 660 | 8900.65 | 8722.6416
6163 | 2006-09-14 18:00 | 0 | 0 | 0 | 26.39 | 10.06 | 0
6164 | 2006-09-14 19:00 | 0 | 0 | 0 | 25.29 | 10.06 | 0
6165 | 2006-09-14 20:00 | 0 | 0 | 0 | 24.19 | 10.06 | 0
6166 | 2006-09-14 21:00 | 0 | 0 | 0 | 23.08 | 10.72 | 0
6167 | 2006-09-14 22:00 | 0 | 0 | 0 | 21.98 | 10.72 | 0
6168 | 2006-09-14 23:00 | 0 | 0 | 0 | 20.93 | 10.72 | 0
6169 | 2006-09-15 | 0 | 0 | 0 | 19.88 | 10.45 | 0
6170 | 2006-09-15 01:00 | 0 | 0 | 0 | 18.82 | 10.45 | 0
6171 | 2006-09-15 02:00 | 0 | 0 | 0 | 17.94 | 10.45 | 0
6172 | 2006-09-15 03:00 | 0 | 0 | 0 | 17.05 | 12.24 | 0
6173 | 2006-09-15 04:00 | 0 | 0 | 0 | 16.16 | 12.24 | 0
6174 | 2006-09-15 05:00 | 7 | 128 | 1 | 15.97 | 12.24 | 0 | -1.335 | 85.4986 | 90 | 0 | 7 | 0 | 0.91407 | 0.065585 | 0 | 0.85542 | 0 | 0 | 0.82376 | 0 | 0.79905 | 0.79902 | 1794.38 | 15.9815 | 156.042 | 154.378 | 153.625 | 0 | 0 | 153.619 | 119.374 | 0 | 0 | 0 | 153.619 | 0 | 660 | 0 | 0
6175 | 2006-09-15 06:00 | 156 | 599 | 41 | 15.77 | 12.48 | 0 | 11.002 | 94.0498 | 78.3308 | 0 | 156 | 121.88 | 45.1598 | 1.4616 | 80.3994 | 42.2623 | 0.0076291 | 64.5442 | 40.6982 | 0.0057487 | 102.091 | 102.084 | 229244 | 17.2148 | 199088 | 206407 | 185261 | 0 | 0 | 184940 | 677.886 | 0 | 0 | 0 | 68.5576 | 184871 | 684.345 | 179695 | 176100.8281
6176 | 2006-09-15 07:00 | 379 | 818 | 56 | 15.58 | 12.48 | 0 | 23.2009 | 103.177 | 63.5387 | 0 | 379 | 365.337 | 64.109 | 3.5509 | 349.605 | 59.9956 | 0.018535 | 327.856 | 57.7752 | 0.013966 | 374.075 | 374.065 | 840074 | 20.8743 | 799406 | 813322 | 746219 | 0 | 0 | 741973 | 728.504 | 0 | 0 | 0 | 0 | 741973 | 728.504 | 729722 | 715127.625
6177 | 2006-09-15 08:00 | 580 | 894 | 69 | 17.66 | 12.48 | 0 | 34.9025 | 113.924 | 48.7667 | 0 | 580 | 588.649 | 79.3964 | 5.4341 | 588.649 | 74.3022 | 0.028364 | 573.428 | 71.5523 | 0.021373 | 625.651 | 625.649 | 1405060 | 26.5151 | 1378500 | 1369470 | 1330670 | 0 | 0 | 1317680 | 728.62 | 0 | 0 | 0 | 0 | 1317680 | 728.62 | 1294960 | 1269057.25
6178 | 2006-09-15 09:00 | 741 | 929 | 79 | 19.75 | 11.24 | 0 | 45.5084 | 127.862 | 34.0758 | 0 | 741 | 768.669 | 90.7756 | 6.9426 | 768.669 | 84.9513 | 0.036238 | 760.702 | 81.8073 | 0.027306 | 817.26 | 817.26 | 1835360 | 32.2055 | 1828120 | 1772680 | 1728800 | 0 | 0 | 1706130 | 714.029 | 0 | 0 | 0 | 0 | 1706130 | 714.029 | 1673960 | 1640479.125
6179 | 2006-09-15 10:00 | 853 | 953 | 85 | 21.84 | 11.24 | 0 | 53.8848 | 147.215 | 19.6844 | 0 | 853 | 895.135 | 97.4062 | 7.992 | 895.135 | 91.1564 | 0.041715 | 892.357 | 87.7828 | 0.031433 | 950.766 | 950.762 | 2135170 | 36.3302 | 2143430 | 2042090 | 1989480 | 0 | 0 | 1958860 | 705.033 | 0 | 0 | 0 | 0 | 1958860 | 705.033 | 1918350 | 1879980.25
6180 | 2006-09-15 11:00 | 913 | 980 | 83 | 22.62 | 11.24 | 0 | 58.1211 | 173.119 | 7.6093 | 0 | 913 | 968.822 | 95.1598 | 8.5541 | 968.822 | 89.0542 | 0.04465 | 968.392 | 85.7584 | 0.033644 | 1022.56 | 1022.55 | 2296390 | 38.2043 | 2313400 | 2186410 | 2132330 | 0 | 0 | 2096610 | 698.909 | 50974.3 | 0 | 0 | 0 | 2043480 | 727.927 | 1999980 | 1959976.125
6181 | 2006-09-15 12:00 | 896 | 977 | 83 | 23.41 | 13.28 | 0 | 56.566 | 200.943 | 13.1437 | 0 | 896 | 948.69 | 95.195 | 8.3948 | 948.69 | 89.0871 | 0.043818 | 947.414 | 85.7901 | 0.033018 | 1002.24 | 1002.24 | 2250770 | 36.9442 | 2265280 | 2152800 | 2097000 | 0 | 0 | 2062910 | 704.292 | 18591.9 | 0 | 0 | 0 | 2043520 | 720.33 | 1999990 | 1959987.375
6182 | 2006-09-15 13:00 | 812 | 913 | 115 | 24.2 | 13.28 | 0 | 49.8967 | 223.538 | 27.0551 | 0 | 812 | 811.531 | 129.653 | 7.6078 | 811.531 | 121.334 | 0.03971 | 806.545 | 116.844 | 0.029922 | 895.716 | 895.709 | 2011530 | 36.2956 | 2013260 | 1918000 | 1867550 | 0 | 0 | 1840410 | 703.925 | 0 | 0 | 0 | 0 | 1840410 | 703.925 | 1804050 | 1767970.125
6183 | 2006-09-15 14:00 | 643 | 839 | 102 | 23.76 | 13.28 | 0 | 40.165 | 239.77 | 41.6546 | 0 | 643 | 626.7 | 119.61 | 6.0244 | 626.7 | 111.936 | 0.031445 | 616.096 | 107.793 | 0.023695 | 702.196 | 702.191 | 1576940 | 33.2424 | 1557550 | 1502910 | 1465250 | 0 | 0 | 1448600 | 707.422 | 0 | 0 | 0 | 0 | 1448600 | 707.422 | 1423980 | 1395499.75
6184 | 2006-09-15 15:00 | 458 | 811 | 66 | 23.32 | 11.94 | 0 | 28.882 | 251.795 | 56.4019 | 0 | 458 | 449.1 | 75.6793 | 4.2911 | 449.1 | 70.8236 | 0.022398 | 430.976 | 68.2025 | 0.016877 | 484.219 | 484.217 | 1087430 | 30.3966 | 1050380 | 1025550 | 999087 | 0 | 0 | 991219 | 704.38 | 0 | 0 | 0 | 0 | 991219 | 704.38 | 976134 | 956611.25
6185 | 2006-09-15 16:00 | 240 | 623 | 59 | 22.89 | 11.94 | 0 | 16.856 | 261.529 | 71.1932 | 0 | 240 | 201.231 | 66.1114 | 2.2486 | 201.231 | 61.8696 | 0.011737 | 180.083 | 59.5798 | 0.0088441 | 232.481 | 232.476 | 522083 | 26.2875 | 480347 | 477447 | 465484 | 0 | 0 | 463690 | 689.711 | 0 | 0 | 0 | 0 | 463690 | 689.711 | 456423 | 447294.2188
6186 | 2006-09-15 17:00 | 35 | 286 | 9 | 21.91 | 11.94 | 0 | 4.5322 | 270.226 | 85.9887 | 0 | 35 | 20.9056 | 9.8299 | 0.32792 | 20.9056 | 9.1992 | 0.0017117 | 7.0084 | 8.8588 | 0.0012898 | 15.3924 | 15.3918 | 34566.1 | 22.1349 | 22912.1 | 23265.8 | 22789.8 | 0 | 0 | 22783.5 | 570.872 | 0 | 0 | 0 | 8818.44 | 13965 | 660 | 13446.1 | 13177.1436
6187 | 2006-09-15 18:00 | 0 | 0 | 0 | 20.94 | 10.84 | 0
6188 | 2006-09-15 19:00 | 0 | 0 | 0 | 19.96 | 10.84 | 0
6189 | 2006-09-15 20:00 | 0 | 0 | 0 | 19 | 10.84 | 0
6190 | 2006-09-15 21:00 | 0 | 0 | 0 | 18.03 | 9.42 | 0
6191 | 2006-09-15 22:00 | 0 | 0 | 0 | 17.07 | 9.42 | 0
6192 | 2006-09-15 23:00 | 0 | 0 | 0 | 16.32 | 9.42 | 0
6193 | 2006-09-16 | 0 | 0 | 0 | 15.57 | 9.94 | 0
6194 | 2006-09-16 01:00 | 0 | 0 | 0 | 14.82 | 9.94 | 0
6195 | 2006-09-16 02:00 | 0 | 0 | 0 | 13.89 | 9.94 | 0
6196 | 2006-09-16 03:00 | 0 | 0 | 0 | 12.97 | 9.63 | 0
6197 | 2006-09-16 04:00 | 0 | 0 | 0 | 12.05 | 9.63 | 0
6198 | 2006-09-16 05:00 | 7 | 121 | 2 | 11.86 | 9.63 | 0 | -1.481 | 85.8663 | 90 | 0 | 7 | 0 | 1.8145 | 0.065585 | 0 | 1.698 | 0 | 0 | 1.6352 | 0 | 1.5861 | 1.586 | 3561.87 | 11.8867 | 612.111 | 603.134 | 600.364 | 0 | 0 | 600.338 | 233.296 | 0 | 0 | 0 | 600.338 | 0 | 660 | 0 | 0
6199 | 2006-09-16 06:00 | 152 | 582 | 42 | 11.67 | 7.94 | 0 | 10.8559 | 94.4243 | 78.3044 | 0 | 152 | 118.394 | 46.3222 | 1.4241 | 76.7921 | 43.3501 | 0.0074334 | 61.6905 | 41.7458 | 0.0056013 | 100.339 | 100.298 | 225235 | 13.5434 | 195266 | 205877 | 184295 | 0 | 0 | 183993 | 695.235 | 0 | 0 | 0 | 9.2461 | 183984 | 695.766 | 178633 | 175060.5938
6200 | 2006-09-16 07:00 | 364 | 775 | 60 | 11.48 | 7.94 | 0 | 23.0422 | 103.571 | 63.5131 | 0 | 364 | 346.393 | 69.7051 | 3.4104 | 330.565 | 65.2327 | 0.017801 | 310.033 | 62.8185 | 0.013414 | 361.679 | 361.706 | 812323 | 18.2359 | 771316 | 793553 | 730462 | 0 | 0 | 726469 | 735.33 | 0 | 0 | 0 | 0 | 726469 | 735.33 | 714203 | 699918.6875
6201 | 2006-09-16 08:00 | 558 | 840 | 80 | 13.53 | 7.94 | 0 | 34.7156 | 114.349 | 48.7482 | 0 | 558 | 553.427 | 91.5027 | 5.228 | 553.427 | 85.6317 | 0.027289 | 539.132 | 82.4626 | 0.020563 | 602.967 | 602.963 | 1354100 | 24.7921 | 1325590 | 1326590 | 1290580 | 0 | 0 | 1278380 | 729.948 | 0 | 0 | 0 | 0 | 1278380 | 729.948 | 1256400 | 1231274.625
6202 | 2006-09-16 09:00 | 713 | 833 | 122 | 15.57 | 7.76 | 0 | 45.2729 | 128.315 | 34.0765 | 0 | 713 | 689.011 | 142.805 | 6.6803 | 689.011 | 133.643 | 0.034869 | 681.869 | 128.697 | 0.026274 | 786.274 | 786.262 | 1765740 | 30.4233 | 1755100 | 1714880 | 1668350 | 0 | 0 | 1647610 | 720.64 | 0 | 0 | 0 | 0 | 1647610 | 720.64 | 1617050 | 1584712.625
6203 | 2006-09-16 10:00 | 848 | 906 | 120 | 17.61 | 7.76 | 0 | 53.5788 | 147.639 | 19.7409 | 0 | 848 | 851.543 | 135.265 | 7.9451 | 851.543 | 126.586 | 0.041471 | 848.884 | 121.901 | 0.031249 | 941.692 | 941.69 | 2114800 | 35.3995 | 2121970 | 2029800 | 1977200 | 0 | 0 | 1947100 | 706.8 | 0 | 0 | 0 | 0 | 1947100 | 706.8 | 1907000 | 1868860.75
6204 | 2006-09-16 11:00 | 909 | 979 | 83 | 18.92 | 7.76 | 0 | 57.746 | 173.357 | 7.9115 | 0 | 909 | 967.42 | 95.3432 | 8.5166 | 967.42 | 89.2258 | 0.044454 | 966.955 | 85.9236 | 0.033497 | 1021.33 | 1021.32 | 2293620 | 38.2138 | 2310480 | 2183450 | 2127920 | 0 | 0 | 2092410 | 699.919 | 46940.9 | 0 | 0 | 0 | 2043480 | 727.032 | 1999970 | 1959975.375
6205 | 2006-09-16 12:00 | 892 | 976 | 83 | 20.23 | 7.15 | 0 | 56.1712 | 200.892 | 13.4229 | 0 | 892 | 947.269 | 95.3778 | 8.3574 | 947.269 | 89.2582 | 0.043623 | 945.939 | 85.9548 | 0.03287 | 1000.97 | 1000.97 | 2247910 | 39.8839 | 2262270 | 2121830 | 2071230 | 0 | 0 | 2036920 | 693.066 | 1617.4 | 0 | 0 | 0 | 2035230 | 696.178 | 1991900 | 1952061.375
6206 | 2006-09-16 13:00 | 797 | 897 | 116 | 21.54 | 7.15 | 0 | 49.5284 | 223.314 | 27.2467 | 0 | 797 | 795.867 | 130.941 | 7.4673 | 795.867 | 122.54 | 0.038977 | 790.901 | 118.005 | 0.02937 | 881.667 | 881.659 | 1979980 | 38.8513 | 1980070 | 1864730 | 1819660 | 0 | 0 | 1793170 | 694.288 | 0 | 0 | 0 | 0 | 1793170 | 694.288 | 1758590 | 1723414.625
6207 | 2006-09-16 14:00 | 618 | 789 | 113 | 22 | 7.15 | 0 | 39.8305 | 239.493 | 41.8185 | 0 | 618 | 587.581 | 131.591 | 5.7902 | 587.581 | 123.148 | 0.030223 | 577.538 | 118.59 | 0.022773 | 675.267 | 675.261 | 1516470 | 35.2587 | 1494460 | 1428850 | 1392260 | 0 | 0 | 1376850 | 699.017 | 0 | 0 | 0 | 0 | 1376850 | 699.017 | 1354170 | 1327083.25
6208 | 2006-09-16 15:00 | 449 | 786 | 73 | 22.47 | 6.5 | 0 | 28.5721 | 251.514 | 56.555 | 0 | 449 | 433.29 | 85.3695 | 4.2068 | 433.29 | 79.892 | 0.021958 | 415.645 | 76.9353 | 0.016546 | 477.819 | 477.812 | 1073040 | 32.2489 | 1035620 | 1002640 | 976961 | 0 | 0 | 969297 | 698.022 | 0 | 0 | 0 | 0 | 969297 | 698.022 | 954854 | 935756.625
6209 | 2006-09-16 16:00 | 248 | 621 | 71 | 22.93 | 6.5 | 0 | 16.5598 | 261.255 | 71.343 | 0 | 248 | 198.665 | 78.5508 | 2.3236 | 198.665 | 73.5109 | 0.012128 | 177.547 | 70.7903 | 0.0091389 | 240.896 | 240.894 | 540985 | 27.8601 | 498999 | 492336 | 479495 | 0 | 0 | 477571 | 686.254 | 0 | 0 | 0 | 0 | 477571 | 686.254 | 470251 | 460846.2812
6210 | 2006-09-16 17:00 | 35 | 278 | 10 | 22.43 | 6.5 | 0 | 4.2404 | 269.958 | 86.1397 | 0 | 35 | 19.3461 | 10.7785 | 0.32792 | 19.3461 | 10.0869 | 0.0017117 | 5.9456 | 9.7136 | 0.0012898 | 15.1907 | 15.1903 | 34113.3 | 22.7409 | 22546.1 | 22820.6 | 22344.4 | 0 | 0 | 22338.2 | 567.856 | 0 | 0 | 0 | 9500.61 | 12837.6 | 660 | 12359.7 | 12112.5049
6211 | 2006-09-16 18:00 | 0 | 0 | 0 | 21.93 | 7.92 | 0
6212 | 2006-09-16 19:00 | 0 | 0 | 0 | 21.43 | 7.92 | 0
6213 | 2006-09-16 20:00 | 0 | 0 | 0 | 20.65 | 7.92 | 0
6214 | 2006-09-16 21:00 | 0 | 0 | 0 | 19.87 | 8.18 | 0
6215 | 2006-09-16 22:00 | 0 | 0 | 0 | 19.08 | 8.18 | 0
6216 | 2006-09-16 23:00 | 0 | 0 | 0 | 18.34 | 8.18 | 0
6217 | 2006-09-17 | 0 | 0 | 0 | 17.6 | 8.62 | 0
6218 | 2006-09-17 01:00 | 0 | 0 | 0 | 16.86 | 8.62 | 0
6219 | 2006-09-17 02:00 | 0 | 0 | 0 | 16.3 | 8.62 | 0
6220 | 2006-09-17 03:00 | 0 | 0 | 0 | 15.74 | 8.73 | 0
6221 | 2006-09-17 04:00 | 0 | 0 | 0 | 15.19 | 8.73 | 0
6222 | 2006-09-17 05:00 | 7 | 117 | 2 | 14.81 | 8.73 | 0 | -1.6274 | 86.2347 | 90 | 0 | 7 | 0 | 1.8162 | 0.065585 | 0 | 1.6997 | 0 | 0 | 1.6368 | 0 | 1.5877 | 1.5876 | 3565.41 | 14.8382 | 613.357 | 606.444 | 603.635 | 0 | 0 | 603.608 | 233.93 | 0 | 0 | 0 | 603.608 | 0 | 660 | 0 | 0
6223 | 2006-09-17 06:00 | 149 | 578 | 41 | 14.43 | 7.66 | 0 | 10.7091 | 94.7991 | 78.2786 | 0 | 149 | 118.073 | 45.4884 | 1.396 | 75.2001 | 42.5698 | 0.0072867 | 60.4519 | 40.9943 | 0.0054907 | 98.4081 | 98.4123 | 220999 | 16.3009 | 191341 | 199170 | 177408 | 0 | 0 | 177115 | 681.556 | 0 | 0 | 0 | 199.859 | 176915 | 683.926 | 171877 | 168439.0625
6224 | 2006-09-17 07:00 | 370 | 806 | 56 | 14.05 | 7.66 | 0 | 22.8822 | 103.965 | 63.489 | 0 | 370 | 360.459 | 64.4154 | 3.4666 | 343.073 | 60.2824 | 0.018094 | 321.797 | 58.0514 | 0.013635 | 368.466 | 368.518 | 827621 | 21.0558 | 786940 | 799737 | 736330 | 0 | 0 | 732176 | 727.282 | 0 | 0 | 0 | 0 | 732176 | 727.282 | 720112 | 705709.6875
6225 | 2006-09-17 08:00 | 577 | 902 | 66 | 16.39 | 7.66 | 0 | 34.5268 | 114.772 | 48.7321 | 0 | 577 | 594.654 | 76.4198 | 5.406 | 594.654 | 71.5165 | 0.028218 | 579.309 | 68.8697 | 0.021263 | 628.754 | 628.75 | 1412010 | 28.343 | 1385720 | 1365800 | 1329070 | 0 | 0 | 1315810 | 720.111 | 0 | 0 | 0 | 0 | 1315810 | 720.111 | 1293500 | 1267632.875
6226 | 2006-09-17 09:00 | 734 | 927 | 79 | 18.73 | 7.24 | 0 | 45.0351 | 128.765 | 34.0814 | 0 | 734 | 766.74 | 91.1214 | 6.877 | 766.74 | 85.2749 | 0.035896 | 758.789 | 82.1189 | 0.027048 | 815.707 | 815.702 | 1831850 | 34.655 | 1824430 | 1750150 | 1705510 | 0 | 0 | 1682960 | 706.619 | 0 | 0 | 0 | 0 | 1682960 | 706.619 | 1651710 | 1618676.25
6227 | 2006-09-17 10:00 | 839 | 936 | 90 | 21.06 | 7.24 | 0 | 53.2707 | 148.058 | 19.8051 | 0 | 839 | 879.255 | 103.256 | 7.8608 | 879.255 | 96.6312 | 0.041031 | 876.491 | 93.055 | 0.030917 | 940.49 | 940.487 | 2112090 | 39.4212 | 2119120 | 1991140 | 1939830 | 0 | 0 | 1909780 | 694.121 | 0 | 0 | 0 | 0 | 1909780 | 694.121 | 1871110 | 1833684.875
6228 | 2006-09-17 11:00 | 906 | 979 | 84 | 22.37 | 7.24 | 0 | 57.3696 | 173.59 | 8.2223 | 0 | 906 | 966.021 | 96.6298 | 8.4885 | 966.021 | 90.4299 | 0.044307 | 965.519 | 87.0831 | 0.033386 | 1021.06 | 1021.06 | 2293030 | 42.3041 | 2309860 | 2143060 | 2089750 | 0 | 0 | 2054340 | 687.624 | 10664.2 | 0 | 0 | 0 | 2043190 | 698.095 | 1999570 | 1959577.875
6229 | 2006-09-17 12:00 | 887 | 927 | 122 | 23.67 | 5.11 | 0 | 55.7756 | 200.841 | 13.7081 | 0 | 887 | 898.854 | 137.69 | 8.3105 | 898.854 | 128.856 | 0.043378 | 897.536 | 124.087 | 0.032686 | 991.006 | 991.001 | 2225530 | 45.8537 | 2238660 | 2042850 | 1994220 | 0 | 0 | 1960410 | 672.234 | 0 | 0 | 0 | 0 | 1960410 | 672.234 | 1919970 | 1881572.625
6230 | 2006-09-17 13:00 | 772 | 860 | 122 | 24.97 | 5.11 | 0 | 49.159 | 223.092 | 27.4427 | 0 | 772 | 762.507 | 144.293 | 7.233 | 762.507 | 135.035 | 0.037754 | 757.673 | 130.037 | 0.028448 | 861.106 | 861.101 | 1933820 | 44.2458 | 1931530 | 1774240 | 1732390 | 0 | 0 | 1707100 | 676.254 | 0 | 0 | 0 | 0 | 1707100 | 676.254 | 1675850 | 1642329.625
6231 | 2006-09-17 14:00 | 661 | 881 | 101 | 25.63 | 5.11 | 0 | 39.4948 | 239.219 | 41.9852 | 0 | 661 | 654.486 | 118.967 | 6.1931 | 654.486 | 111.334 | 0.032326 | 643.185 | 107.214 | 0.024358 | 727.911 | 727.909 | 1634700 | 41.9243 | 1617900 | 1500780 | 1463870 | 0 | 0 | 1445910 | 679.782 | 0 | 0 | 0 | 0 | 1445910 | 679.782 | 1422450 | 1393998.75
6232 | 2006-09-17 15:00 | 471 | 831 | 78 | 26.29 | 4.99 | 0 | 28.2611 | 251.234 | 56.7099 | 0 | 471 | 455.573 | 90.9201 | 4.4129 | 455.573 | 85.0865 | 0.023034 | 436.851 | 81.9375 | 0.017357 | 503.242 | 503.238 | 1130140 | 37.6432 | 1094250 | 1033510 | 1007860 | 0 | 0 | 999323 | 682.04 | 0 | 0 | 0 | 0 | 999323 | 682.04 | 985223 | 965519
6233 | 2006-09-17 16:00 | 230 | 604 | 60 | 26.95 | 4.99 | 0 | 16.2629 | 260.981 | 71.4937 | 0 | 230 | 192.682 | 67.4908 | 2.1549 | 192.682 | 63.1605 | 0.011248 | 171.964 | 60.8229 | 0.0084756 | 225.811 | 225.808 | 507108 | 32.0443 | 465599 | 450178 | 439117 | 0 | 0 | 437430 | 671.104 | 0 | 0 | 0 | 0 | 437430 | 671.104 | 431046 | 422425
6234 | 2006-09-17 17:00 | 31 | 263 | 8 | 26.44 | 4.99 | 0 | 3.948 | 269.689 | 86.291 | 0 | 31 | 17.1016 | 8.6178 | 0.29045 | 17.1016 | 8.0648 | 0.001516 | 4.7383 | 7.7664 | 0.0011424 | 12.1307 | 12.1301 | 27241.3 | 26.7137 | 17052.3 | 16896.1 | 16563.7 | 0 | 0 | 16559.9 | 537.613 | 0 | 0 | 0 | 15651 | 908.863 | 660 | 874.377 | 856.8896
6235 | 2006-09-17 18:00 | 0 | 0 | 0 | 25.92 | 3.71 | 0
6236 | 2006-09-17 19:00 | 0 | 0 | 0 | 25.41 | 3.71 | 0
6237 | 2006-09-17 20:00 | 0 | 0 | 0 | 24.77 | 3.71 | 0
6238 | 2006-09-17 21:00 | 0 | 0 | 0 | 24.13 | 3.85 | 0
6239 | 2006-09-17 22:00 | 0 | 0 | 0 | 23.49 | 3.85 | 0
6240 | 2006-09-17 23:00 | 0 | 0 | 0 | 22.96 | 3.85 | 0
6241 | 2006-09-18 | 0 | 0 | 0 | 22.43 | 3.71 | 0
6242 | 2006-09-18 01:00 | 0 | 0 | 0 | 21.9 | 3.71 | 0
6243 | 2006-09-18 02:00 | 0 | 0 | 0 | 21.16 | 3.71 | 0
6244 | 2006-09-18 03:00 | 0 | 0 | 0 | 20.41 | 4.51 | 0
6245 | 2006-09-18 04:00 | 0 | 0 | 0 | 19.67 | 4.51 | 0
6246 | 2006-09-18 05:00 | 6 | 93 | 2 | 19.14 | 4.51 | 0 | -1.7742 | 86.6039 | 90 | 0 | 6 | 0 | 1.502 | 0.056215 | 0 | 1.4057 | 0 | 0 | 1.3536 | 0 | 1.313 | 1.3129 | 2948.52 | 19.1706 | 420.212 | 417.411 | 415.497 | 0 | 0 | 415.479 | 194.018 | 0 | 0 | 0 | 415.479 | 0 | 660 | 0 | 0
6247 | 2006-09-18 06:00 | 134 | 476 | 46 | 18.61 | 4.29 | 0 | 10.5613 | 95.1742 | 78.2534 | 0 | 134 | 97.7439 | 50.5328 | 1.2555 | 61.0457 | 47.2905 | 0.0065532 | 49.1051 | 45.5403 | 0.0049379 | 91.8108 | 91.7866 | 206117 | 20.7775 | 176992 | 180396 | 161582 | 0 | 0 | 161332 | 664.191 | 0 | 0 | 0 | 348.403 | 160983 | 669.265 | 156405 | 153276.8594
6248 | 2006-09-18 07:00 | 347 | 669 | 88 | 18.07 | 4.29 | 0 | 22.7208 | 104.358 | 63.4663 | 0 | 347 | 299.558 | 99.8423 | 3.2511 | 284.443 | 93.4362 | 0.01697 | 266.829 | 89.9782 | 0.012787 | 346.115 | 346.117 | 777316 | 26.2434 | 735813 | 730828 | 678403 | 0 | 0 | 674697 | 706.402 | 0 | 0 | 0 | 0 | 674697 | 706.402 | 664265 | 650979.25
6249 | 2006-09-18 08:00 | 569 | 849 | 90 | 20.42 | 4.29 | 0 | 34.3361 | 115.195 | 48.7186 | 0 | 569 | 560.279 | 105.847 | 5.3311 | 560.279 | 99.0558 | 0.027827 | 545.832 | 95.3898 | 0.020968 | 622.006 | 621.999 | 1396860 | 35.1083 | 1369980 | 1310310 | 1277700 | 0 | 0 | 1264640 | 697.346 | 0 | 0 | 0 | 0 | 1264640 | 697.346 | 1244450 | 1219564
6250 | 2006-09-18 09:00 | 740 | 947 | 74 | 22.78 | 2.04 | 0 | 44.795 | 129.211 | 34.0905 | 0 | 740 | 782.816 | 85.77 | 6.9332 | 782.816 | 80.2669 | 0.036189 | 774.694 | 77.2962 | 0.027269 | 826.457 | 826.454 | 1856000 | 45.4283 | 1849790 | 1689190 | 1648850 | 0 | 0 | 1625580 | 671.529 | 0 | 0 | 0 | 0 | 1625580 | 671.529 | 1597170 | 1565230.5
6251 | 2006-09-18 10:00 | 853 | 970 | 80 | 25.13 | 2.04 | 0 | 52.9605 | 148.472 | 19.877 | 0 | 853 | 910.711 | 92.4399 | 7.992 | 910.711 | 86.5088 | 0.041715 | 907.826 | 83.3072 | 0.031433 | 961.43 | 961.427 | 2159120 | 51.4771 | 2168660 | 1926090 | 1881660 | 0 | 0 | 1849890 | 654.301 | 0 | 0 | 0 | 1581.16 | 1848310 | 660 | 1812300 | 1776051.125
6252 | 2006-09-18 11:00 | 902 | 979 | 83 | 26.33 | 2.04 | 0 | 56.9921 | 173.818 | 8.5409 | 0 | 902 | 965.802 | 95.7111 | 8.451 | 965.802 | 89.5701 | 0.044111 | 965.261 | 86.2551 | 0.033239 | 1020 | 1020 | 2290650 | 54.2822 | 2307340 | 2022440 | 1974900 | 0 | 0 | 1939320 | 647.469 | 0 | 0 | 0 | 9733.68 | 1929580 | 660 | 1890420 | 1852610
6253 | 2006-09-18 12:00 | 883 | 976 | 82 | 27.54 | 1.72 | 0 | 55.3793 | 200.792 | 13.9991 | 0 | 883 | 944.441 | 94.6392 | 8.273 | 944.441 | 88.5669 | 0.043182 | 942.996 | 85.2891 | 0.032539 | 997.468 | 997.465 | 2240060 | 55.466 | 2253990 | 1963690 | 1917350 | 0 | 0 | 1883210 | 642.365 | 0 | 0 | 0 | 16690.7 | 1866520 | 660 | 1829820 | 1793221.5
6254 | 2006-09-18 13:00 | 799 | 959 | 79 | 28.74 | 1.72 | 0 | 48.7886 | 222.873 | 27.6428 | 0 | 799 | 847.841 | 91.3672 | 7.486 | 847.841 | 85.5049 | 0.039074 | 842.379 | 82.3405 | 0.029443 | 897.007 | 897.006 | 2014450 | 53.8535 | 2016330 | 1768870 | 1731180 | 0 | 0 | 1703330 | 643.074 | 0 | 0 | 0 | 12773.4 | 1690560 | 660 | 1660280 | 1627079.25
6255 | 2006-09-18 14:00 | 656 | 926 | 72 | 29.17 | 1.72 | 0 | 39.1579 | 238.946 | 42.1545 | 0 | 656 | 685.62 | 83.4571 | 6.1462 | 685.62 | 78.1023 | 0.032081 | 673.659 | 75.2118 | 0.024174 | 726.428 | 726.425 | 1631370 | 49.5077 | 1614410 | 1444070 | 1410460 | 0 | 0 | 1392490 | 654.294 | 0 | 0 | 0 | 1621.99 | 1390870 | 660 | 1369530 | 1342135.625
6256 | 2006-09-18 15:00 | 455 | 842 | 60 | 29.61 | 0.39 | 0 | 27.9491 | 250.955 | 56.8664 | 0 | 455 | 460.658 | 69.5729 | 4.263 | 460.658 | 65.109 | 0.022251 | 441.552 | 62.6994 | 0.016767 | 489.14 | 489.137 | 1098480 | 44.5869 | 1061710 | 969637 | 947429 | 0 | 0 | 939294 | 656.324 | 0 | 0 | 0 | 226.023 | 939068 | 660 | 926860 | 908322.4375
6257 | 2006-09-18 16:00 | 237 | 671 | 52 | 30.04 | 0.39 | 0 | 15.9651 | 260.707 | 71.6453 | 0 | 237 | 211.8 | 59.4345 | 2.2205 | 211.8 | 55.6211 | 0.01159 | 188.76 | 53.5626 | 0.0087335 | 235.062 | 235.061 | 527887 | 37.2373 | 486071 | 458094 | 447205 | 0 | 0 | 445354 | 652.846 | 0 | 0 | 0 | 605.297 | 444749 | 660 | 438622 | 429849.5625
6258 | 2006-09-18 17:00 | 31 | 284 | 6 | 29.56 | 0.39 | 0 | 3.6551 | 269.42 | 86.4426 | 0 | 31 | 17.8301 | 6.4633 | 0.29045 | 17.8301 | 6.0486 | 0.001516 | 4.3537 | 5.8248 | 0.0011424 | 9.8742 | 9.8739 | 22174.2 | 29.8623 | 13097 | 12765.5 | 12529.7 | 0 | 0 | 12527.4 | 515.021 | 0 | 0 | 0 | 12527.4 | 0 | 660 | 0 | 0
6259 | 2006-09-18 18:00 | 0 | 0 | 0 | 29.08 | 2.92 | 0
6260 | 2006-09-18 19:00 | 0 | 0 | 0 | 28.6 | 2.92 | 0
6261 | 2006-09-18 20:00 | 0 | 0 | 0 | 27.81 | 2.92 | 0
6262 | 2006-09-18 21:00 | 0 | 0 | 0 | 27.01 | 5.52 | 0
6263 | 2006-09-18 22:00 | 0 | 0 | 0 | 26.22 | 5.52 | 0
6264 | 2006-09-18 23:00 | 0 | 0 | 0 | 25.29 | 5.52 | 0
6265 | 2006-09-19 | 0 | 0 | 0 | 24.35 | 8.66 | 0
6266 | 2006-09-19 01:00 | 0 | 0 | 0 | 23.42 | 8.66 | 0
6267 | 2006-09-19 02:00 | 0 | 0 | 0 | 23.29 | 8.66 | 0
6268 | 2006-09-19 03:00 | 0 | 0 | 0 | 23.17 | 9.21 | 0
6269 | 2006-09-19 04:00 | 0 | 0 | 0 | 23.04 | 9.21 | 0
6270 | 2006-09-19 05:00 | 6 | 114 | 2 | 22.67 | 9.21 | 0 | -1.9212 | 86.9736 | 90 | 0 | 6 | 0 | 1.504 | 0.056215 | 0 | 1.4075 | 0 | 0 | 1.3554 | 0 | 1.3147 | 1.3147 | 2952.45 | 22.6927 | 421.325 | 420.224 | 418.302 | 0 | 0 | 418.284 | 194.643 | 0 | 0 | 0 | 418.284 | 0 | 660 | 0 | 0
6271 | 2006-09-19 06:00 | 149 | 598 | 40 | 22.3 | 5.04 | 0 | 10.4127 | 95.5494 | 78.2291 | 0 | 149 | 123.029 | 44.8148 | 1.396 | 75.3597 | 41.9394 | 0.0072867 | 60.6571 | 40.3873 | 0.0054907 | 98.0183 | 98.035 | 220144 | 24.5045 | 190712 | 190683 | 167425 | 0 | 0 | 167139 | 655.914 | 0 | 0 | 0 | 1478.25 | 165660 | 662.202 | 161161 | 157937.9531
6272 | 2006-09-19 07:00 | 369 | 816 | 56 | 21.93 | 5.04 | 0 | 22.5579 | 104.752 | 63.4452 | 0 | 369 | 364.759 | 64.7267 | 3.4572 | 345.473 | 60.5737 | 0.018046 | 324.107 | 58.3319 | 0.013598 | 370.979 | 370.95 | 833092 | 30.2716 | 792604 | 772732 | 713178 | 0 | 0 | 708925 | 696.118 | 0 | 0 | 0 | 0 | 708925 | 696.118 | 698342 | 684375.375
6273 | 2006-09-19 08:00 | 563 | 843 | 90 | 23.51 | 5.04 | 0 | 34.1435 | 115.616 | 48.7077 | 0 | 563 | 556.121 | 106.086 | 5.2749 | 556.121 | 99.2797 | 0.027533 | 541.791 | 95.6054 | 0.020747 | 618.294 | 618.288 | 1388520 | 37.4135 | 1361320 | 1288380 | 1256310 | 0 | 0 | 1243360 | 688.689 | 0 | 0 | 0 | 0 | 1243360 | 688.689 | 1224030 | 1199547.5
6274 | 2006-09-19 09:00 | 716 | 899 | 86 | 25.1 | 4.35 | 0 | 44.5526 | 129.655 | 34.1039 | 0 | 716 | 743.56 | 99.161 | 6.7084 | 743.56 | 92.7987 | 0.035015 | 735.838 | 89.3643 | 0.026385 | 800.472 | 800.469 | 1797650 | 43.9288 | 1788560 | 1644560 | 1603570 | 0 | 0 | 1581780 | 675.12 | 0 | 0 | 0 | 0 | 1581780 | 675.12 | 1554670 | 1523580.5
6275 | 2006-09-19 10:00 | 825 | 918 | 97 | 26.68 | 4.35 | 0 | 52.6483 | 148.879 | 19.9566 | 0 | 825 | 860.815 | 111.295 | 7.7296 | 860.815 | 104.154 | 0.040346 | 858.065 | 100.299 | 0.030402 | 929.643 | 929.64 | 2087740 | 48.5471 | 2093480 | 1885300 | 1839340 | 0 | 0 | 1810020 | 665.783 | 0 | 0 | 0 | 0 | 1810020 | 665.783 | 1775350 | 1739838.875
6276 | 2006-09-19 11:00 | 882 | 948 | 93 | 27.26 | 4.35 | 0 | 56.6136 | 174.042 | 8.8663 | 0 | 882 | 933.643 | 106.911 | 8.2637 | 933.643 | 100.051 | 0.043133 | 933.079 | 96.3483 | 0.032502 | 998.576 | 998.569 | 2242540 | 50.7485 | 2256600 | 2012040 | 1966170 | 0 | 0 | 1931920 | 657.41 | 0 | 0 | 0 | 190.352 | 1931730 | 660 | 1892480 | 1854629.5
6277 | 2006-09-19 12:00 | 862 | 944 | 91 | 27.83 | 8.84 | 0 | 54.9824 | 200.742 | 14.2954 | 0 | 862 | 912.269 | 104.745 | 8.0763 | 912.269 | 98.0243 | 0.042155 | 910.812 | 94.3965 | 0.031765 | 975.083 | 975.079 | 2189770 | 45.0446 | 2200970 | 2015930 | 1967590 | 0 | 0 | 1935110 | 676.593 | 0 | 0 | 0 | 0 | 1935110 | 676.593 | 1895620 | 1857709.625
6278 | 2006-09-19 13:00 | 794 | 959 | 78 | 28.4 | 8.84 | 0 | 48.4173 | 222.657 | 27.8469 | 0 | 794 | 846.374 | 90.4324 | 7.4392 | 846.374 | 84.6301 | 0.03883 | 840.831 | 81.498 | 0.029259 | 894.688 | 894.685 | 2009230 | 44.1953 | 2010840 | 1848060 | 1803600 | 0 | 0 | 1776190 | 676.217 | 0 | 0 | 0 | 0 | 1776190 | 676.217 | 1742550 | 1707696
6279 | 2006-09-19 14:00 | 650 | 926 | 70 | 28.39 | 8.84 | 0 | 38.82 | 238.676 | 42.3263 | 0 | 650 | 684.038 | 81.4022 | 6.09 | 684.038 | 76.1793 | 0.031788 | 671.979 | 73.36 | 0.023953 | 723.002 | 722.997 | 1623660 | 41.1542 | 1606360 | 1495450 | 1457550 | 0 | 0 | 1439880 | 682.298 | 0 | 0 | 0 | 0 | 1439880 | 682.298 | 1416460 | 1388127.375
6280 | 2006-09-19 15:00 | 462 | 829 | 77 | 28.38 | 7.21 | 0 | 27.6362 | 250.677 | 57.0244 | 0 | 462 | 451.754 | 90.2087 | 4.3286 | 451.754 | 84.4208 | 0.022594 | 432.841 | 81.2964 | 0.017025 | 498.73 | 498.728 | 1120020 | 38.1352 | 1083850 | 1021290 | 994904 | 0 | 0 | 986550 | 680.448 | 0 | 0 | 0 | 0 | 986550 | 680.448 | 972717 | 953262.25
6281 | 2006-09-19 16:00 | 212 | 511 | 74 | 28.36 | 7.21 | 0 | 15.6668 | 260.433 | 71.7977 | 0 | 212 | 159.632 | 81.987 | 1.9863 | 159.632 | 76.7266 | 0.010368 | 142.062 | 73.887 | 0.0078123 | 209.478 | 209.477 | 470433 | 32.4574 | 429581 | 414412 | 404834 | 0 | 0 | 403371 | 664.646 | 0 | 0 | 0 | 0 | 403371 | 664.646 | 397591 | 389638.7188
6282 | 2006-09-19 17:00 | 27 | 210 | 10 | 27.48 | 7.21 | 0 | 3.3619 | 269.15 | 86.5943 | 0 | 27 | 11.608 | 10.0411 | 0.25297 | 11.608 | 9.3968 | 0.0013204 | 2.4183 | 9.049 | 0.00099496 | 11.1243 | 11.1239 | 24981.5 | 27.6976 | 15277.3 | 15059.4 | 14764.6 | 0 | 0 | 14761.5 | 528.615 | 0 | 0 | 0 | 14761.5 | 0 | 660 | 0 | 0
6283 | 2006-09-19 18:00 | 0 | 0 | 0 | 26.6 | 8.95 | 0
6284 | 2006-09-19 19:00 | 0 | 0 | 0 | 25.71 | 8.95 | 0
6285 | 2006-09-19 20:00 | 0 | 0 | 0 | 25.07 | 8.95 | 0
6286 | 2006-09-19 21:00 | 0 | 0 | 0 | 24.43 | 9.55 | 0
6287 | 2006-09-19 22:00 | 0 | 0 | 0 | 23.79 | 9.55 | 0
6288 | 2006-09-19 23:00 | 0 | 0 | 0 | 22.88 | 9.55 | 0
6289 | 2006-09-20 | 0 | 0 | 0 | 21.97 | 11.38 | 0
6290 | 2006-09-20 01:00 | 0 | 0 | 0 | 21.06 | 11.38 | 0
6291 | 2006-09-20 02:00 | 0 | 0 | 0 | 20.13 | 11.38 | 0
6292 | 2006-09-20 03:00 | 0 | 0 | 0 | 19.2 | 9.58 | 0
6293 | 2006-09-20 04:00 | 0 | 0 | 0 | 18.28 | 9.58 | 0
6294 | 2006-09-20 05:00 | 5 | 95 | 1 | 17.79 | 9.58 | 0 | -2.0687 | 87.3437 | 90 | 0 | 5 | 0 | 0.9185 | 0.046846 | 0 | 0.85957 | 0 | 0 | 0.82776 | 0 | 0.80292 | 0.80288 | 1803.07 | 17.8035 | 157.546 | 156.207 | 155.45 | 0 | 0 | 155.443 | 120.019 | 0 | 0 | 0 | 155.443 | 0 | 660 | 0 | 0
6295 | 2006-09-20 06:00 | 136 | 516 | 43 | 17.3 | 9.2 | 0 | 10.2632 | 95.9246 | 78.2055 | 0 | 136 | 106.692 | 47.9418 | 1.2742 | 63.9759 | 44.8657 | 0.006651 | 51.5252 | 43.2053 | 0.0050116 | 91.8934 | 91.8561 | 206273 | 18.8858 | 177384 | 182474 | 161089 | 0 | 0 | 160841 | 672.737 | 0 | 0 | 0 | 367.748 | 160473 | 675.932 | 155834 | 152717.7812
6296 | 2006-09-20 07:00 | 346 | 738 | 65 | 16.81 | 9.2 | 0 | 22.3936 | 105.144 | 63.4258 | 0 | 346 | 329.968 | 75.8713 | 3.2418 | 311.613 | 71.0033 | 0.016921 | 292.365 | 68.3755 | 0.01275 | 349.931 | 349.91 | 785835 | 22.8509 | 744714 | 751010 | 694878 | 0 | 0 | 691103 | 719.089 | 0 | 0 | 0 | 0 | 691103 | 719.089 | 679965 | 666365.5625
6297 | 2006-09-20 08:00 | 541 | 794 | 98 | 18.67 | 9.2 | 0 | 33.9489 | 116.035 | 48.6996 | 0 | 541 | 523.559 | 114.909 | 5.0687 | 523.559 | 107.537 | 0.026457 | 510.074 | 103.557 | 0.019936 | 595.241 | 595.236 | 1336750 | 28.9463 | 1307600 | 1285340 | 1252480 | 0 | 0 | 1240560 | 716.119 | 0 | 0 | 0 | 0 | 1240560 | 716.119 | 1220000 | 1195598.625
6298 | 2006-09-20 09:00 | 730 | 892 | 108 | 20.53 | 4.71 | 0 | 44.3079 | 130.095 | 34.1217 | 0 | 730 | 737.167 | 123.12 | 6.8395 | 737.167 | 115.221 | 0.0357 | 729.502 | 110.957 | 0.026901 | 815.271 | 815.267 | 1830890 | 39.2611 | 1823420 | 1713370 | 1670350 | 0 | 0 | 1647880 | 692.401 | 0 | 0 | 0 | 0 | 1647880 | 692.401 | 1618130 | 1585771.5
6299 | 2006-09-20 10:00 | 828 | 933 | 91 | 22.39 | 4.71 | 0 | 52.3341 | 149.282 | 20.0438 | 0 | 828 | 874.648 | 104.94 | 7.7577 | 874.648 | 98.2069 | 0.040493 | 871.828 | 94.5723 | 0.030512 | 937.438 | 937.43 | 2105230 | 43.9279 | 2111900 | 1943810 | 1897010 | 0 | 0 | 1867030 | 679.067 | 0 | 0 | 0 | 0 | 1867030 | 679.067 | 1830070 | 1793466.25
6300 | 2006-09-20 11:00 | 885 | 917 | 125 | 23.53 | 4.71 | 0 | 56.2341 | 174.261 | 9.198 | 0 | 885 | 902.459 | 141.642 | 8.2918 | 902.459 | 132.554 | 0.04328 | 901.871 | 127.648 | 0.032613 | 998.665 | 998.657 | 2242730 | 46.4746 | 2256800 | 2053500 | 2004740 | 0 | 0 | 1970700 | 673.158 | 0 | 0 | 0 | 0 | 1970700 | 673.158 | 1929850 | 1891253
6301 | 2006-09-20 12:00 | 836 | 860 | 137 | 24.68 | 6.33 | 0 | 54.5851 | 200.693 | 14.5966 | 0 | 836 | 830.011 | 163.046 | 7.8327 | 830.011 | 152.585 | 0.040884 | 828.626 | 146.938 | 0.030807 | 946.327 | 946.318 | 2125200 | 44.2594 | 2132920 | 1960300 | 1914270 | 0 | 0 | 1883610 | 677.95 | 0 | 0 | 0 | 0 | 1883610 | 677.95 | 1846050 | 1809125.125
6302 | 2006-09-20 13:00 | 762 | 901 | 93 | 25.82 | 6.33 | 0 | 48.0453 | 222.442 | 28.0548 | 0 | 762 | 793.884 | 107.121 | 7.1394 | 793.884 | 100.248 | 0.037265 | 788.599 | 96.538 | 0.02808 | 858.61 | 858.604 | 1928210 | 43.5846 | 1925640 | 1774290 | 1731590 | 0 | 0 | 1706430 | 677.49 | 0 | 0 | 0 | 0 | 1706430 | 677.49 | 1675170 | 1641664.875
6303 | 2006-09-20 14:00 | 631 | 897 | 73 | 26.46 | 6.33 | 0 | 38.4813 | 238.408 | 42.5005 | 0 | 631 | 661.136 | 84.8853 | 5.912 | 661.136 | 79.4389 | 0.030859 | 649.356 | 76.4989 | 0.023252 | 704.102 | 704.099 | 1581230 | 41.0279 | 1562030 | 1454780 | 1418860 | 0 | 0 | 1402050 | 681.064 | 0 | 0 | 0 | 0 | 1402050 | 681.064 | 1379560 | 1351966.875
6304 | 2006-09-20 15:00 | 440 | 827 | 60 | 27.09 | 2.2 | 0 | 27.3226 | 250.4 | 57.1839 | 0 | 440 | 448.669 | 69.8594 | 4.1225 | 448.669 | 65.3771 | 0.021518 | 429.709 | 62.9575 | 0.016214 | 477.902 | 477.899 | 1073240 | 40.0473 | 1035820 | 966931 | 943620 | 0 | 0 | 935897 | 671.444 | 0 | 0 | 0 | 0 | 935897 | 671.444 | 923194 | 904730.625
6305 | 2006-09-20 16:00 | 224 | 620 | 59 | 27.72 | 2.2 | 0 | 15.368 | 260.159 | 71.9508 | 0 | 224 | 192.902 | 66.9643 | 2.0987 | 192.902 | 62.6677 | 0.010955 | 171.418 | 60.3484 | 0.0082545 | 224.821 | 224.816 | 504878 | 33.8154 | 463405 | 444159 | 433175 | 0 | 0 | 431493 | 662.861 | 0 | 0 | 0 | 0 | 431493 | 662.861 | 425432 | 416923.4375
6306 | 2006-09-20 17:00 | 28 | 248 | 8 | 27.07 | 2.2 | 0 | 3.0685 | 268.88 | 86.746 | 0 | 28 | 13.0488 | 8.3797 | 0.26234 | 13.0488 | 7.8421 | 0.0013693 | 2.2069 | 7.5519 | 0.0010318 | 9.4671 | 9.4669 | 21260.3 | 27.3267 | 12395.1 | 12247.3 | 12016.3 | 0 | 0 | 12014.2 | 522.435 | 0 | 0 | 0 | 12014.2 | 0 | 660 | 0 | 0
6307 | 2006-09-20 18:00 | 0 | 0 | 0 | 26.41 | 3.9 | 0
6308 | 2006-09-20 19:00 | 0 | 0 | 0 | 25.76 | 3.9 | 0
6309 | 2006-09-20 20:00 | 0 | 0 | 0 | 24.85 | 3.9 | 0
6310 | 2006-09-20 21:00 | 0 | 0 | 0 | 23.95 | 2.2 | 0
6311 | 2006-09-20 22:00 | 0 | 0 | 0 | 23.05 | 2.2 | 0
6312 | 2006-09-20 23:00 | 0 | 0 | 0 | 22.27 | 2.2 | 0
6313 | 2006-09-21 | 0 | 0 | 0 | 21.5 | 4.7 | 0
6314 | 2006-09-21 01:00 | 0 | 0 | 0 | 20.73 | 4.7 | 0
6315 | 2006-09-21 02:00 | 0 | 0 | 0 | 19.75 | 4.7 | 0
6316 | 2006-09-21 03:00 | 0 | 0 | 0 | 18.78 | 3.51 | 0
6317 | 2006-09-21 04:00 | 0 | 0 | 0 | 17.81 | 3.51 | 0
6318 | 2006-09-21 05:00 | 5 | 105 | 1 | 17.52 | 3.51 | 0 | -2.2165 | 87.7142 | 90 | 0 | 5 | 0 | 0.91939 | 0.046846 | 0 | 0.8604 | 0 | 0 | 0.82856 | 0 | 0.80371 | 0.80364 | 1804.78 | 17.54 | 157.854 | 156.462 | 155.695 | 0 | 0 | 155.688 | 120.125 | 0 | 0 | 0 | 155.688 | 0 | 660 | 0 | 0
6319 | 2006-09-21 06:00 | 143 | 587 | 39 | 17.24 | 1.64 | 0 | 10.1128 | 96.2996 | 78.1829 | 0 | 143 | 121.296 | 44.1378 | 1.3398 | 71.1121 | 41.3058 | 0.0069933 | 57.3054 | 39.7771 | 0.0052696 | 94.1752 | 94.1887 | 211513 | 19.8912 | 182676 | 186684 | 162726 | 0 | 0 | 162464 | 668.898 | 0 | 0 | 0 | 308.53 | 162155 | 672.296 | 157571 | 154419.9688
6320 | 2006-09-21 07:00 | 364 | 814 | 56 | 16.96 | 1.64 | 0 | 22.2279 | 105.536 | 63.408 | 0 | 364 | 364.457 | 65.0427 | 3.4104 | 343.197 | 60.8694 | 0.017801 | 322.022 | 58.6167 | 0.013414 | 369.233 | 369.248 | 829268 | 27.3534 | 788882 | 778911 | 722546 | 0 | 0 | 718262 | 702.568 | 0 | 0 | 0 | 0 | 718262 | 702.568 | 707323 | 693176.3125
6321 | 2006-09-21 08:00 | 561 | 848 | 90 | 19.24 | 1.64 | 0 | 33.7524 | 116.453 | 48.6942 | 0 | 561 | 559.564 | 106.565 | 5.2561 | 559.564 | 99.7276 | 0.027435 | 545.156 | 96.0368 | 0.020673 | 621.977 | 621.971 | 1396800 | 36.7469 | 1369920 | 1300460 | 1267510 | 0 | 0 | 1254430 | 690.923 | 0 | 0 | 0 | 0 | 1254430 | 690.923 | 1234760 | 1210062
6322 | 2006-09-21 09:00 | 709 | 893 | 89 | 21.53 | 3.55 | 0 | 44.0611 | 130.532 | 34.1439 | 0 | 709 | 737.866 | 102.824 | 6.6428 | 737.866 | 96.227 | 0.034673 | 730.182 | 92.6657 | 0.026127 | 798.188 | 798.179 | 1792500 | 41.3178 | 1783150 | 1659590 | 1618500 | 0 | 0 | 1596820 | 683.588 | 0 | 0 | 0 | 0 | 1596820 | 683.588 | 1568970 | 1537588.625
6323 | 2006-09-21 10:00 | 808 | 860 | 132 | 23.82 | 3.55 | 0 | 52.0181 | 149.678 | 20.1387 | 0 | 808 | 805.21 | 157.294 | 7.5703 | 805.21 | 147.201 | 0.039515 | 802.588 | 141.754 | 0.029775 | 916.04 | 916.036 | 2057180 | 46.5296 | 2061300 | 1873960 | 1827240 | 0 | 0 | 1798660 | 670.348 | 0 | 0 | 0 | 0 | 1798660 | 670.348 | 1764320 | 1729034.25
6324 | 2006-09-21 11:00 | 886 | 925 | 122 | 25.21 | 3.55 | 0 | 55.8538 | 174.475 | 9.5352 | 0 | 886 | 910.388 | 138.711 | 8.3011 | 910.388 | 129.811 | 0.043329 | 909.751 | 125.007 | 0.032649 | 1003.75 | 1003.74 | 2254140 | 50.0939 | 2268830 | 2029350 | 1981480 | 0 | 0 | 1947000 | 660.462 | 0 | 0 | 0 | 41.319 | 1946950 | 660.999 | 1907090 | 1868952.125
6325 | 2006-09-21 12:00 | 839 | 874 | 132 | 26.61 | 8.44 | 0 | 54.1873 | 200.645 | 14.9023 | 0 | 839 | 842.51 | 149.28 | 7.8608 | 842.51 | 139.702 | 0.041031 | 841.044 | 134.532 | 0.030917 | 946.339 | 946.333 | 2125220 | 43.7395 | 2132950 | 1965110 | 1917370 | 0 | 0 | 1886830 | 680.341 | 0 | 0 | 0 | 0 | 1886830 | 680.341 | 1849120 | 1812137.25
6326 | 2006-09-21 13:00 | 785 | 910 | 113 | 28 | 8.44 | 0 | 47.6728 | 222.231 | 28.2664 | 0 | 785 | 800.567 | 128.919 | 7.3548 | 800.567 | 120.647 | 0.03839 | 795.147 | 116.182 | 0.028927 | 884.017 | 884.007 | 1985260 | 44.0013 | 1985620 | 1826400 | 1782740 | 0 | 0 | 1756070 | 677.744 | 0 | 0 | 0 | 0 | 1756070 | 677.744 | 1723100 | 1688637.25
6327 | 2006-09-21 14:00 | 623 | 855 | 95 | 28.51 | 8.44 | 0 | 38.1419 | 238.141 | 42.6769 | 0 | 623 | 628.518 | 113.298 | 5.837 | 628.518 | 106.029 | 0.030467 | 617.198 | 102.105 | 0.022958 | 697.746 | 697.748 | 1566960 | 41.1399 | 1547130 | 1440110 | 1403230 | 0 | 0 | 1386750 | 681.077 | 0 | 0 | 0 | 0 | 1386750 | 681.077 | 1364610 | 1337318.25
6328 | 2006-09-21 15:00 | 449 | 825 | 74 | 29.01 | 9.1 | 0 | 27.0084 | 250.124 | 57.3446 | 0 | 449 | 445.574 | 87.3417 | 4.2068 | 445.574 | 81.7377 | 0.021958 | 426.564 | 78.7126 | 0.016546 | 490.135 | 490.129 | 1100700 | 37.5243 | 1064000 | 1005400 | 982829 | 0 | 0 | 974656 | 679.483 | 0 | 0 | 0 | 0 | 974656 | 679.483 | 961036 | 941815.8125
6329 | 2006-09-21 16:00 | 213 | 575 | 63 | 29.52 | 9.1 | 0 | 15.0689 | 259.886 | 72.1044 | 0 | 213 | 177.293 | 71.2412 | 1.9956 | 177.293 | 66.6702 | 0.010417 | 157.309 | 64.2028 | 0.0078491 | 214.874 | 214.869 | 482543 | 33.2526 | 441457 | 424239 | 414143 | 0 | 0 | 412610 | 664.323 | 0 | 0 | 0 | 0 | 412610 | 664.323 | 406729 | 398593.9375
6330 | 2006-09-21 17:00 | 25 | 223 | 8 | 28.54 | 9.1 | 0 | 2.775 | 268.61 | 86.8976 | 0 | 25 | 10.5751 | 8.2984 | 0.23423 | 10.5751 | 7.766 | 0.0012226 | 1.3338 | 7.4786 | 0.00092126 | 8.5489 | 8.5485 | 19197.6 | 28.6885 | 10823.9 | 10623.9 | 10422.9 | 0 | 0 | 10421.2 | 511.771 | 0 | 0 | 0 | 10421.2 | 0 | 660 | 0 | 0
6331 | 2006-09-21 18:00 | 0 | 0 | 0 | 27.55 | 10.23 | 0
6332 | 2006-09-21 19:00 | 0 | 0 | 0 | 26.56 | 10.23 | 0
6333 | 2006-09-21 20:00 | 0 | 0 | 0 | 25.41 | 10.23 | 0
6334 | 2006-09-21 21:00 | 0 | 0 | 0 | 24.26 | 12.2 | 0
6335 | 2006-09-21 22:00 | 0 | 0 | 0 | 23.11 | 12.2 | 0
6336 | 2006-09-21 23:00 | 0 | 0 | 0 | 21.9 | 12.2 | 0
6337 | 2006-09-22 | 0 | 0 | 0 | 20.69 | 10.97 | 0
6338 | 2006-09-22 01:00 | 0 | 0 | 0 | 19.49 | 10.97 | 0
6339 | 2006-09-22 02:00 | 0 | 0 | 0 | 18.85 | 10.97 | 0
6340 | 2006-09-22 03:00 | 0 | 0 | 0 | 18.21 | 10.58 | 0
6341 | 2006-09-22 04:00 | 0 | 0 | 0 | 17.57 | 10.58 | 0
6342 | 2006-09-22 05:00 | 5 | 98 | 2 | 17.09 | 10.58 | 0 | -2.3648 | 88.0848 | 90 | 0 | 5 | 0 | 1.4289 | 0.046846 | 0 | 1.3372 | 0 | 0 | 1.2877 | 0 | 1.2491 | 1.249 | 2804.96 | 17.1098 | 380.435 | 376.97 | 375.243 | 0 | 0 | 375.227 | 184.442 | 0 | 0 | 0 | 375.227 | 0 | 660 | 0 | 0
6343 | 2006-09-22 06:00 | 140 | 568 | 41 | 16.61 | 9.02 | 0 | 9.9615 | 96.6744 | 78.1612 | 0 | 140 | 117.412 | 46.2838 | 1.3117 | 67.2064 | 43.3142 | 0.0068466 | 54.1876 | 41.7112 | 0.005159 | 93.0268 | 93.0227 | 208897 | 18.234 | 180131 | 185794 | 162138 | 0 | 0 | 161880 | 671.547 | 0 | 0 | 0 | 308.774 | 161571 | 674.751 | 156952 | 153813.2812
6344 | 2006-09-22 07:00 | 352 | 785 | 57 | 16.12 | 9.02 | 0 | 22.0608 | 105.927 | 63.3921 | 0 | 352 | 351.781 | 67.6589 | 3.298 | 330.401 | 63.3178 | 0.017214 | 310.036 | 60.9744 | 0.012971 | 359.893 | 359.947 | 808376 | 22.404 | 767769 | 775600 | 718868 | 0 | 0 | 714837 | 720.144 | 0 | 0 | 0 | 0 | 714837 | 720.144 | 703298 | 689231.875
6345 | 2006-09-22 08:00 | 557 | 884 | 69 | 18.33 | 9.02 | 0 | 33.554 | 116.869 | 48.6917 | 0 | 557 | 582.813 | 80.5391 | 5.2187 | 582.813 | 75.3715 | 0.02724 | 567.808 | 72.5821 | 0.020526 | 621.198 | 621.194 | 1395040 | 29.1749 | 1368090 | 1343540 | 1307710 | 0 | 0 | 1294730 | 716.242 | 0 | 0 | 0 | 0 | 1294730 | 716.242 | 1273040 | 1247575.875
6346 | 2006-09-22 09:00 | 728 | 946 | 74 | 20.53 | 2.36 | 0 | 43.8121 | 130.965 | 34.1707 | 0 | 728 | 781.6 | 86.4341 | 6.8208 | 781.6 | 80.8883 | 0.035602 | 773.446 | 77.8947 | 0.026827 | 825.826 | 825.821 | 1854580 | 42.683 | 1848290 | 1709680 | 1668330 | 0 | 0 | 1645010 | 679.17 | 0 | 0 | 0 | 0 | 1645010 | 679.17 | 1615750 | 1583430.25
6347 | 2006-09-22 10:00 | 837 | 967 | 80 | 22.73 | 2.36 | 0 | 51.7003 | 150.068 | 20.2412 | 0 | 837 | 905.032 | 93.1476 | 7.842 | 905.032 | 87.171 | 0.040933 | 902.054 | 83.9449 | 0.030844 | 956.449 | 956.446 | 2147930 | 48.3871 | 2156880 | 1944240 | 1897000 | 0 | 0 | 1865830 | 665.995 | 0 | 0 | 0 | 0 | 1865830 | 665.995 | 1829070 | 1792490.375
6348 | 2006-09-22 11:00 | 887 | 978 | 83 | 23.5 | 2.36 | 0 | 55.4728 | 174.685 | 9.8774 | 0 | 887 | 961.432 | 96.4503 | 8.3105 | 961.432 | 90.2619 | 0.043378 | 960.709 | 86.9213 | 0.032686 | 1016.23 | 1016.23 | 2282200 | 50.7609 | 2298430 | 2049410 | 2001510 | 0 | 0 | 1966180 | 658.824 | 0 | 0 | 0 | 206.052 | 1965970 | 660.589 | 1925350 | 1886845.75
6349 | 2006-09-22 12:00 | 866 | 974 | 82 | 24.27 | 4.37 | 0 | 53.7894 | 200.596 | 15.2121 | 0 | 866 | 937.632 | 95.3688 | 8.1137 | 937.632 | 89.2497 | 0.042351 | 935.93 | 85.9467 | 0.031912 | 991.251 | 991.247 | 2226080 | 47.5558 | 2239250 | 2027090 | 1979500 | 0 | 0 | 1945730 | 667.575 | 0 | 0 | 0 | 0 | 1945730 | 667.575 | 1905880 | 1867765.375
6350 | 2006-09-22 13:00 | 756 | 870 | 118 | 25.05 | 4.37 | 0 | 47.2997 | 222.021 | 28.4813 | 0 | 756 | 763.064 | 141.19 | 7.0831 | 763.064 | 132.131 | 0.036971 | 757.811 | 127.241 | 0.027859 | 858.527 | 858.522 | 1928030 | 45.2179 | 1925450 | 1760540 | 1719460 | 0 | 0 | 1694250 | 672.34 | 0 | 0 | 0 | 0 | 1694250 | 672.34 | 1663530 | 1630260.875
6351 | 2006-09-22 14:00 | 631 | 871 | 98 | 25.17 | 4.37 | 0 | 37.8019 | 237.876 | 42.8555 | 0 | 631 | 637.471 | 116.792 | 5.912 | 637.471 | 109.299 | 0.030859 | 625.866 | 105.254 | 0.023252 | 709.208 | 709.206 | 1592700 | 41.8302 | 1574000 | 1460470 | 1424500 | 0 | 0 | 1407510 | 680.416 | 0 | 0 | 0 | 0 | 1407510 | 680.416 | 1384920 | 1357225.125
6352 | 2006-09-22 15:00 | 446 | 856 | 61 | 25.29 | 4.5 | 0 | 26.6938 | 249.849 | 57.5065 | 0 | 446 | 460.404 | 71.2545 | 4.1787 | 460.404 | 66.6827 | 0.021811 | 440.573 | 64.2148 | 0.016435 | 489.66 | 489.657 | 1099640 | 36.6954 | 1062910 | 1008240 | 983105 | 0 | 0 | 975055 | 684.953 | 0 | 0 | 0 | 0 | 975055 | 684.953 | 961162 | 941939.125
6353 | 2006-09-22 16:00 | 222 | 657 | 54 | 25.41 | 4.5 | 0 | 14.7696 | 259.613 | 72.2584 | 0 | 222 | 200.813 | 61.9698 | 2.08 | 200.813 | 57.9937 | 0.010857 | 177.904 | 55.8474 | 0.0081808 | 226.747 | 226.746 | 509216 | 30.6915 | 467674 | 455173 | 443487 | 0 | 0 | 441788 | 675.421 | 0 | 0 | 0 | 0 | 441788 | 675.421 | 435220 | 426515.2188
6354 | 2006-09-22 17:00 | 24 | 247 | 6 | 24.58 | 4.5 | 0 | 2.4817 | 268.339 | 87.0491 | 0 | 24 | 10.6512 | 6.2325 | 0.22486 | 10.6512 | 5.8326 | 0.0011737 | 0.83895 | 5.6167 | 0.00088441 | 6.2629 | 6.2626 | 14064.3 | 24.7259 | 7021.95 | 7029.87 | 6897.17 | 0 | 0 | 6896.42 | 505.015 | 0 | 0 | 0 | 6896.42 | 0 | 660 | 0 | 0
6355 | 2006-09-22 18:00 | 0 | 0 | 0 | 23.75 | 8.04 | 0
6356 | 2006-09-22 19:00 | 0 | 0 | 0 | 22.92 | 8.04 | 0
6357 | 2006-09-22 20:00 | 0 | 0 | 0 | 22 | 8.04 | 0
6358 | 2006-09-22 21:00 | 0 | 0 | 0 | 21.08 | 9.29 | 0
6359 | 2006-09-22 22:00 | 0 | 0 | 0 | 20.16 | 9.29 | 0
6360 | 2006-09-22 23:00 | 0 | 0 | 0 | 19.22 | 9.29 | 0
6361 | 2006-09-23 | 0 | 0 | 0 | 18.29 | 9.86 | 0
6362 | 2006-09-23 01:00 | 0 | 0 | 0 | 17.35 | 9.86 | 0
6363 | 2006-09-23 02:00 | 0 | 0 | 0 | 16.39 | 9.86 | 0
6364 | 2006-09-23 03:00 | 0 | 0 | 0 | 15.43 | 10.92 | 0
6365 | 2006-09-23 04:00 | 0 | 0 | 0 | 14.46 | 10.92 | 0
6366 | 2006-09-23 05:00 | 4 | 86 | 1 | 14.16 | 10.92 | 0 | -2.5134 | 88.4554 | 90 | 0 | 4 | 0 | 0.92119 | 0.037477 | 0 | 0.86208 | 0 | 0 | 0.83018 | 0 | 0.80527 | 0.8052 | 1808.28 | 14.1725 | 158.457 | 156.429 | 155.664 | 0 | 0 | 155.658 | 120.211 | 0 | 0 | 0 | 155.658 | 0 | 660 | 0 | 0
6367 | 2006-09-23 06:00 | 130 | 518 | 41 | 13.85 | 11.66 | 0 | 9.8093 | 97.0489 | 78.1406 | 0 | 130 | 107.358 | 46.5554 | 1.218 | 59.926 | 43.5683 | 0.0063575 | 48.3425 | 41.9559 | 0.0047905 | 87.5941 | 87.5715 | 196653 | 15.1514 | 168527 | 176498 | 154561 | 0 | 0 | 154341 | 689.459 | 0 | 0 | 0 | 8.1392 | 154333 | 690.049 | 149623 | 146630.1406
6368 | 2006-09-23 07:00 | 344 | 761 | 60 | 13.54 | 11.66 | 0 | 21.8922 | 106.317 | 63.378 | 0 | 344 | 341.309 | 71.123 | 3.223 | 319.725 | 66.5596 | 0.016823 | 300.035 | 64.0963 | 0.012677 | 353.22 | 353.178 | 793176 | 18.7886 | 752388 | 772217 | 715733 | 0 | 0 | 711879 | 733.148 | 0 | 0 | 0 | 0 | 711879 | 733.148 | 699909 | 685911
6369 | 2006-09-23 08:00 | 546 | 829 | 91 | 15.42 | 11.66 | 0 | 33.3537 | 117.282 | 48.6921 | 0 | 546 | 546.279 | 108.127 | 5.1156 | 546.279 | 101.189 | 0.026702 | 532.215 | 97.4441 | 0.02012 | 610.789 | 610.782 | 1371670 | 24.4968 | 1343820 | 1346560 | 1309080 | 0 | 0 | 1296680 | 733.792 | 0 | 0 | 0 | 0 | 1296680 | 733.792 | 1274150 | 1248667.75
6370 | 2006-09-23 09:00 | 685 | 836 | 110 | 17.29 | 11.01 | 0 | 43.561 | 131.394 | 34.2021 | 0 | 685 | 690.09 | 131.729 | 6.4179 | 690.09 | 123.277 | 0.033499 | 682.875 | 118.714 | 0.025243 | 777.566 | 777.559 | 1746200 | 29.306 | 1734610 | 1703070 | 1657830 | 0 | 0 | 1637470 | 723.783 | 0 | 0 | 0 | 0 | 1637470 | 723.783 | 1607130 | 1574984
6371 | 2006-09-23 10:00 | 786 | 845 | 127 | 19.17 | 11.01 | 0 | 51.3808 | 150.453 | 20.3512 | 0 | 786 | 790.804 | 152.408 | 7.3642 | 790.804 | 142.629 | 0.038439 | 788.172 | 137.351 | 0.028964 | 897.785 | 897.78 | 2016190 | 33.0439 | 2018160 | 1950270 | 1897630 | 0 | 0 | 1870500 | 715.432 | 0 | 0 | 0 | 0 | 1870500 | 715.432 | 1832970 | 1796312.25
6372 | 2006-09-23 11:00 | 818 | 789 | 173 | 19.88 | 11.01 | 0 | 55.0911 | 174.89 | 10.2241 | 0 | 818 | 774.036 | 202.631 | 7.664 | 774.036 | 189.63 | 0.040004 | 773.412 | 182.612 | 0.030144 | 927.372 | 927.366 | 2082630 | 34.2111 | 2088100 | 2007800 | 1954070 | 0 | 0 | 1925030 | 711.611 | 0 | 0 | 0 | 0 | 1925030 | 711.611 | 1885670 | 1847959.25
6373 | 2006-09-23 12:00 | 837 | 888 | 126 | 20.59 | 6.86 | 0 | 53.3913 | 200.548 | 15.5257 | 0 | 837 | 853.411 | 143.465 | 7.842 | 853.411 | 134.26 | 0.040933 | 851.795 | 129.291 | 0.030844 | 951.683 | 951.674 | 2137230 | 39.6242 | 2145600 | 2014280 | 1964510 | 0 | 0 | 1933650 | 693.501 | 0 | 0 | 0 | 0 | 1933650 | 693.501 | 1894110 | 1856225.75
6374 | 2006-09-23 13:00 | 733 | 831 | 127 | 21.31 | 6.86 | 0 | 46.9264 | 221.814 | 28.6996 | 0 | 733 | 727.679 | 151.223 | 6.8676 | 727.679 | 141.521 | 0.035847 | 722.583 | 136.283 | 0.027011 | 833.127 | 833.121 | 1870970 | 37.973 | 1865510 | 1763370 | 1719130 | 0 | 0 | 1695570 | 696.028 | 0 | 0 | 0 | 0 | 1695570 | 696.028 | 1664190 | 1630910.375
6375 | 2006-09-23 14:00 | 629 | 875 | 97 | 21.67 | 6.86 | 0 | 37.4614 | 237.613 | 43.036 | 0 | 629 | 639.32 | 115.915 | 5.8932 | 639.32 | 108.478 | 0.030761 | 627.552 | 104.463 | 0.023179 | 710.077 | 710.074 | 1594640 | 35.872 | 1576040 | 1502960 | 1464990 | 0 | 0 | 1447870 | 697.531 | 0 | 0 | 0 | 0 | 1447870 | 697.531 | 1423660 | 1395183.625
6376 | 2006-09-23 15:00 | 439 | 853 | 60 | 22.04 | 7.42 | 0 | 26.3789 | 249.575 | 57.6694 | 0 | 439 | 456.198 | 70.2987 | 4.1131 | 456.198 | 65.7882 | 0.021469 | 436.357 | 63.3534 | 0.016177 | 484.734 | 484.732 | 1088580 | 31.396 | 1051560 | 1022060 | 995926 | 0 | 0 | 988034 | 701.288 | 0 | 0 | 0 | 0 | 988034 | 701.288 | 973150 | 953686.875
6377 | 2006-09-23 16:00 | 211 | 608 | 59 | 22.41 | 7.42 | 0 | 14.4702 | 259.34 | 72.4127 | 0 | 211 | 183.803 | 67.4647 | 1.9769 | 183.803 | 63.136 | 0.010319 | 162.578 | 60.7994 | 0.0077754 | 216.684 | 216.678 | 486604 | 26.5922 | 445444 | 442093 | 430645 | 0 | 0 | 429097 | 687.362 | 0 | 0 | 0 | 0 | 429097 | 687.362 | 422314 | 413868.0625
6378 | 2006-09-23 17:00 | 23 | 221 | 7 | 21.89 | 7.42 | 0 | 2.1885 | 268.068 | 87.2001 | 0 | 23 | 8.9834 | 7.1586 | 0.21549 | 8.9834 | 6.6993 | 0.0011248 | 0.23716 | 6.4513 | 0.00084756 | 6.4886 | 6.4885 | 14571.6 | 22.0152 | 7389.63 | 7484.37 | 7341.7 | 0 | 0 | 7340.9 | 515.361 | 0 | 0 | 0 | 7340.9 | 0 | 660 | 0 | 0
6379 | 2006-09-23 18:00 | 0 | 0 | 0 | 21.37 | 7.97 | 0
6380 | 2006-09-23 19:00 | 0 | 0 | 0 | 20.84 | 7.97 | 0
6381 | 2006-09-23 20:00 | 0 | 0 | 0 | 20.23 | 7.97 | 0
6382 | 2006-09-23 21:00 | 0 | 0 | 0 | 19.62 | 6.3 | 0
6383 | 2006-09-23 22:00 | 0 | 0 | 0 | 19.01 | 6.3 | 0
6384 | 2006-09-23 23:00 | 0 | 0 | 0 | 18.29 | 6.3 | 0
6385 | 2006-09-24 | 0 | 0 | 0 | 17.57 | 7.48 | 0
6386 | 2006-09-24 01:00 | 0 | 0 | 0 | 16.86 | 7.48 | 0
6387 | 2006-09-24 02:00 | 0 | 0 | 0 | 16.44 | 7.48 | 0
6388 | 2006-09-24 03:00 | 0 | 0 | 0 | 16.02 | 8.58 | 0
6389 | 2006-09-24 04:00 | 0 | 0 | 0 | 15.6 | 8.58 | 0
6390 | 2006-09-24 05:00 | 4 | 90 | 1 | 15.12 | 8.58 | 0 | -2.6625 | 88.826 | 90 | 0 | 4 | 0 | 0.92209 | 0.037477 | 0 | 0.86293 | 0 | 0 | 0.83099 | 0 | 0.80606 | 0.806 | 1810.07 | 15.1345 | 158.778 | 156.927 | 156.153 | 0 | 0 | 156.146 | 120.382 | 0 | 0 | 0 | 156.146 | 0 | 660 | 0 | 0
6391 | 2006-09-24 06:00 | 134 | 564 | 38 | 14.63 | 5.25 | 0 | 9.6561 | 97.4228 | 78.1212 | 0 | 134 | 117.811 | 43.6162 | 1.2555 | 64.0273 | 40.8177 | 0.0065532 | 51.6762 | 39.307 | 0.0049379 | 88.2585 | 88.2885 | 198265 | 16.5885 | 170336 | 176971 | 154068 | 0 | 0 | 153835 | 676.179 | 0 | 0 | 0 | 144.508 | 153691 | 677.929 | 149182 | 146198.2812
6392 | 2006-09-24 07:00 | 353 | 803 | 56 | 14.15 | 5.25 | 0 | 21.7222 | 106.706 | 63.3659 | 0 | 353 | 359.741 | 66.9639 | 3.3073 | 335.939 | 62.6674 | 0.017263 | 315.267 | 60.3481 | 0.013008 | 364.359 | 364.37 | 818312 | 22.2327 | 777952 | 786033 | 729147 | 0 | 0 | 725002 | 720.936 | 0 | 0 | 0 | 0 | 725002 | 720.936 | 713274 | 699008.9375
6393 | 2006-09-24 08:00 | 557 | 900 | 65 | 16.7 | 5.25 | 0 | 33.1516 | 117.694 | 48.6956 | 0 | 557 | 593.849 | 76.4156 | 5.2187 | 593.849 | 71.5126 | 0.02724 | 578.557 | 68.866 | 0.020526 | 628.02 | 628.016 | 1410370 | 30.631 | 1384020 | 1350520 | 1314870 | 0 | 0 | 1301620 | 712.755 | 0 | 0 | 0 | 0 | 1301620 | 712.755 | 1279950 | 1254351
6394 | 2006-09-24 09:00 | 721 | 945 | 74 | 19.26 | 7.53 | 0 | 43.3079 | 131.819 | 34.2381 | 0 | 721 | 779.8 | 86.7693 | 6.7552 | 779.8 | 81.2021 | 0.03526 | 771.627 | 78.1968 | 0.026569 | 824.354 | 824.347 | 1851270 | 35.0607 | 1844820 | 1766580 | 1720900 | 0 | 0 | 1697890 | 705.312 | 0 | 0 | 0 | 0 | 1697890 | 705.312 | 1666200 | 1632875
6395 | 2006-09-24 10:00 | 826 | 958 | 83 | 21.81 | 7.53 | 0 | 51.0597 | 150.831 | 20.4687 | 0 | 826 | 894.945 | 96.854 | 7.739 | 894.945 | 90.6397 | 0.040395 | 891.93 | 87.2852 | 0.030438 | 949.868 | 949.866 | 2133150 | 40.0166 | 2141300 | 2006680 | 1954310 | 0 | 0 | 1923650 | 692.038 | 0 | 0 | 0 | 0 | 1923650 | 692.038 | 1884480 | 1846793.25
6396 | 2006-09-24 11:00 | 874 | 970 | 84 | 22.82 | 7.53 | 0 | 54.7089 | 175.089 | 10.5747 | 0 | 874 | 951.43 | 97.9375 | 8.1887 | 951.43 | 91.6537 | 0.042742 | 950.608 | 88.2616 | 0.032207 | 1007.74 | 1007.73 | 2263100 | 42.1357 | 2278280 | 2115240 | 2062470 | 0 | 0 | 2027870 | 686.793 | 0 | 0 | 0 | 0 | 2027870 | 686.793 | 1984800 | 1945099.375
6397 | 2006-09-24 12:00 | 851 | 964 | 83 | 23.84 | 8.03 | 0 | 52.9933 | 200.499 | 15.8427 | 0 | 851 | 925.194 | 96.8519 | 7.9732 | 925.194 | 90.6377 | 0.041617 | 923.367 | 87.2832 | 0.03136 | 980.362 | 980.358 | 2201630 | 42.0477 | 2213470 | 2055610 | 2004940 | 0 | 0 | 1972170 | 686.362 | 0 | 0 | 0 | 0 | 1972170 | 686.362 | 1931230 | 1892609
6398 | 2006-09-24 13:00 | 770 | 956 | 77 | 24.85 | 8.03 | 0 | 46.5529 | 221.609 | 28.9209 | 0 | 770 | 835.492 | 90.1796 | 7.2143 | 835.492 | 84.3935 | 0.037656 | 829.54 | 81.2702 | 0.028375 | 883.514 | 883.507 | 1984130 | 41.2589 | 1984440 | 1848550 | 1803490 | 0 | 0 | 1776890 | 686.6 | 0 | 0 | 0 | 0 | 1776890 | 686.6 | 1743010 | 1708154.125
6399 | 2006-09-24 14:00 | 617 | 867 | 94 | 25.48 | 8.03 | 0 | 37.1207 | 237.352 | 43.2184 | 0 | 617 | 631.545 | 112.839 | 5.7808 | 631.545 | 105.599 | 0.030174 | 619.792 | 101.691 | 0.022737 | 699.861 | 699.862 | 1571710 | 38.4782 | 1552090 | 1462620 | 1424350 | 0 | 0 | 1407750 | 688.956 | 0 | 0 | 0 | 0 | 1407750 | 688.956 | 1384800 | 1357100.25
6400 | 2006-09-24 15:00 | 404 | 760 | 70 | 26.11 | 6.54 | 0 | 26.0638 | 249.302 | 57.8332 | 0 | 404 | 404.707 | 83.5383 | 3.7852 | 404.707 | 78.1783 | 0.019757 | 386.934 | 75.285 | 0.014887 | 448.366 | 448.361 | 1006900 | 35.2627 | 967916 | 923962 | 902904 | 0 | 0 | 896100 | 684.633 | 0 | 0 | 0 | 0 | 896100 | 684.633 | 883347 | 865679.875
6401 | 2006-09-24 16:00 | 191 | 523 | 62 | 26.74 | 6.54 | 0 | 14.1709 | 259.068 | 72.5673 | 0 | 191 | 157.861 | 70.6915 | 1.7895 | 157.861 | 66.1558 | 0.0093407 | 139.407 | 63.7075 | 0.0070384 | 197.028 | 197.023 | 442465 | 30.762 | 402217 | 391191 | 381731 | 0 | 0 | 380445 | 668.916 | 0 | 0 | 0 | 0 | 380445 | 668.916 | 374415 | 366926.2812
6402 | 2006-09-24 17:00 | 19 | 184 | 6 | 26.07 | 6.54 | 0 | 1.8957 | 267.797 | 87.3508 | 0 | 19 | 6.9066 | 6.113 | 0.17802 | 6.9066 | 5.7207 | 0.00092918 | 0 | 5.509 | 0.00070016 | 5.3444 | 5.3441 | 12001.5 | 26.1791 | 5554.27 | 5528.91 | 5429.58 | 0 | 0 | 5429.08 | 484.223 | 0 | 0 | 0 | 5429.08 | 0 | 660 | 0 | 0
6403 | 2006-09-24 18:00 | 0 | 0 | 0 | 25.41 | 4.51 | 0
6404 | 2006-09-24 19:00 | 0 | 0 | 0 | 24.75 | 4.51 | 0
6405 | 2006-09-24 20:00 | 0 | 0 | 0 | 23.96 | 4.51 | 0
6406 | 2006-09-24 21:00 | 0 | 0 | 0 | 23.17 | 3.79 | 0
6407 | 2006-09-24 22:00 | 0 | 0 | 0 | 22.38 | 3.79 | 0
6408 | 2006-09-24 23:00 | 0 | 0 | 0 | 21.67 | 3.79 | 0
6409 | 2006-09-25 | 0 | 0 | 0 | 20.95 | 4.33 | 0
6410 | 2006-09-25 01:00 | 0 | 0 | 0 | 20.24 | 4.33 | 0
6411 | 2006-09-25 02:00 | 0 | 0 | 0 | 19.97 | 4.33 | 0
6412 | 2006-09-25 03:00 | 0 | 0 | 0 | 19.71 | 5.21 | 0
6413 | 2006-09-25 04:00 | 0 | 0 | 0 | 19.44 | 5.21 | 0
6414 | 2006-09-25 05:00 | 4 | 86 | 1 | 18.92 | 5.21 | 0 | -2.8121 | 89.1964 | 90 | 0 | 4 | 0 | 0.92299 | 0.037477 | 0 | 0.86377 | 0 | 0 | 0.8318 | 0 | 0.80685 | 0.8068 | 1811.87 | 18.9379 | 159.089 | 157.951 | 157.187 | 0 | 0 | 157.181 | 120.607 | 0 | 0 | 0 | 157.181 | 0 | 660 | 0 | 0
6415 | 2006-09-25 06:00 | 131 | 557 | 38 | 18.39 | 3.04 | 0 | 9.5019 | 97.7961 | 78.103 | 0 | 131 | 116.14 | 43.7728 | 1.2274 | 61.3394 | 40.9643 | 0.0064064 | 49.5292 | 39.4482 | 0.0048274 | 86.3128 | 86.3308 | 193874 | 20.6036 | 166233 | 169331 | 146905 | 0 | 0 | 146681 | 659.111 | 0 | 0 | 0 | 411.3 | 146270 | 664.881 | 142073 | 139231.7188
6416 | 2006-09-25 07:00 | 346 | 791 | 55 | 17.86 | 3.04 | 0 | 21.5507 | 107.094 | 63.3559 | 0 | 346 | 355.268 | 66.063 | 3.2418 | 330.74 | 61.8243 | 0.016921 | 310.401 | 59.5362 | 0.01275 | 358.851 | 358.899 | 806019 | 27.0625 | 765611 | 756875 | 702331 | 0 | 0 | 698266 | 700.804 | 0 | 0 | 0 | 0 | 698266 | 700.804 | 687681 | 673927.5625
6417 | 2006-09-25 08:00 | 547 | 884 | 67 | 20.35 | 3.04 | 0 | 32.9475 | 118.103 | 48.7021 | 0 | 547 | 582.469 | 78.8114 | 5.125 | 582.469 | 73.7547 | 0.026751 | 567.464 | 71.0251 | 0.020157 | 619.354 | 619.35 | 1390900 | 36.2306 | 1363790 | 1297710 | 1264590 | 0 | 0 | 1251610 | 692.473 | 0 | 0 | 0 | 0 | 1251610 | 692.473 | 1231930 | 1207287.75
6418 | 2006-09-25 09:00 | 706 | 919 | 80 | 22.83 | 4.32 | 0 | 43.0527 | 132.239 | 34.2788 | 0 | 706 | 757.712 | 93.6437 | 6.6147 | 757.712 | 87.6353 | 0.034526 | 749.748 | 84.392 | 0.026016 | 809.141 | 809.135 | 1817100 | 41.9 | 1808960 | 1679240 | 1638480 | 0 | 0 | 1616080 | 680.798 | 0 | 0 | 0 | 0 | 1616080 | 680.798 | 1587700 | 1555950.125
6419 | 2006-09-25 10:00 | 826 | 966 | 80 | 25.31 | 4.32 | 0 | 50.737 | 151.204 | 20.5935 | 0 | 826 | 901.945 | 93.682 | 7.739 | 901.945 | 87.6712 | 0.040395 | 898.866 | 84.4265 | 0.030438 | 953.823 | 953.82 | 2142040 | 47.79 | 2150670 | 1944180 | 1896870 | 0 | 0 | 1865840 | 667.582 | 0 | 0 | 0 | 0 | 1865840 | 667.582 | 1829070 | 1792487.5
6420 | 2006-09-25 11:00 | 867 | 965 | 85 | 26.76 | 4.32 | 0 | 54.3262 | 175.284 | 10.9288 | 0 | 867 | 945.18 | 99.2422 | 8.1231 | 945.18 | 92.8746 | 0.0424 | 944.307 | 89.4374 | 0.031949 | 1002.76 | 1002.76 | 2251950 | 50.3935 | 2266530 | 2024400 | 1977070 | 0 | 0 | 1942670 | 659.653 | 0 | 0 | 0 | 71.3264 | 1942600 | 660.991 | 1902910 | 1864854.625
6421 | 2006-09-25 12:00 | 843 | 958 | 84 | 28.21 | 6 | 0 | 52.5953 | 200.451 | 16.1628 | 0 | 843 | 917.714 | 98.1547 | 7.8982 | 917.714 | 91.8569 | 0.041226 | 915.826 | 88.4573 | 0.031065 | 974.185 | 974.181 | 2187760 | 48.7978 | 2198840 | 1978620 | 1932440 | 0 | 0 | 1899940 | 664.666 | 0 | 0 | 0 | -23.1844 | 1899960 | 664.858 | 1861920 | 1824677.875
6422 | 2006-09-25 13:00 | 765 | 955 | 77 | 29.66 | 6 | 0 | 46.1793 | 221.406 | 29.145 | 0 | 765 | 832.826 | 90.3523 | 7.1674 | 832.826 | 84.5551 | 0.037412 | 826.79 | 81.4258 | 0.028191 | 880.996 | 880.993 | 1978490 | 48.2784 | 1978500 | 1783340 | 1742580 | 0 | 0 | 1716010 | 663.509 | 0 | 0 | 0 | 0 | 1716010 | 663.509 | 1684770 | 1651070.75
6423 | 2006-09-25 14:00 | 620 | 919 | 70 | 29.79 | 6 | 0 | 36.7799 | 237.092 | 43.4025 | 0 | 620 | 667.398 | 82.3596 | 5.8089 | 667.398 | 77.0752 | 0.030321 | 654.838 | 74.2227 | 0.022847 | 707.211 | 707.21 | 1588210 | 44.7357 | 1569320 | 1436280 | 1401770 | 0 | 0 | 1384760 | 668.905 | 0 | 0 | 0 | 0 | 1384760 | 668.905 | 1363180 | 1335920.5
6424 | 2006-09-25 15:00 | 430 | 850 | 61 | 29.91 | 5.37 | 0 | 25.7487 | 249.03 | 57.9979 | 0 | 430 | 450.14 | 71.706 | 4.0288 | 450.14 | 67.1053 | 0.021029 | 430.177 | 64.6217 | 0.015846 | 479.97 | 479.967 | 1077880 | 40.4744 | 1040580 | 969449 | 945969 | 0 | 0 | 938206 | 670.981 | 0 | 0 | 0 | 0 | 938206 | 670.981 | 925494 | 906984.375
6425 | 2006-09-25 16:00 | 199 | 591 | 57 | 30.04 | 5.37 | 0 | 13.8718 | 258.796 | 72.7219 | 0 | 199 | 175.914 | 65.729 | 1.8645 | 175.914 | 61.5118 | 0.0097319 | 155.096 | 59.2352 | 0.0073332 | 207.908 | 207.905 | 466903 | 34.6162 | 426121 | 406670 | 396937 | 0 | 0 | 395497 | 656.86 | 0 | 0 | 0 | 67.7904 | 395430 | 660 | 389785 | 381989.75
6426 | 2006-09-25 17:00 | 19 | 201 | 5 | 29.45 | 5.37 | 0 | 1.6035 | 267.525 | 87.5009 | 0 | 19 | 7.0167 | 5.078 | 0.17802 | 6.9387 | 4.7522 | 0.00092918 | 0 | 4.5763 | 0.00070016 | 4.4397 | 4.4394 | 9969.75 | 29.5477 | 4158.68 | 4098.01 | 4032.1 | 0 | 0 | 4031.79 | 452.871 | 0 | 0 | 0 | 4031.79 | 0 | 660 | 0 | 0
6427 | 2006-09-25 18:00 | 0 | 0 | 0 | 28.85 | 4.96 | 0
6428 | 2006-09-25 19:00 | 0 | 0 | 0 | 28.25 | 4.96 | 0
6429 | 2006-09-25 20:00 | 0 | 0 | 0 | 27.5 | 4.96 | 0
6430 | 2006-09-25 21:00 | 0 | 0 | 0 | 26.76 | 2.83 | 0
6431 | 2006-09-25 22:00 | 0 | 0 | 0 | 26.01 | 2.83 | 0
6432 | 2006-09-25 23:00 | 0 | 0 | 0 | 25.08 | 2.83 | 0
6433 | 2006-09-26 | 0 | 0 | 0 | 24.15 | 3.88 | 0
6434 | 2006-09-26 01:00 | 0 | 0 | 0 | 23.23 | 3.88 | 0
6435 | 2006-09-26 02:00 | 0 | 0 | 0 | 22.74 | 3.88 | 0
6436 | 2006-09-26 03:00 | 0 | 0 | 0 | 22.26 | 4.55 | 0
6437 | 2006-09-26 04:00 | 0 | 0 | 0 | 21.78 | 4.55 | 0
6438 | 2006-09-26 05:00 | 3 | 81 | 1 | 21.89 | 4.55 | 0 | -2.9621 | 89.5665 | 90 | 0 | 3 | 0 | 0.72919 | 0.028108 | 0 | 0.68241 | 0 | 0 | 0.65715 | 0 | 0.63743 | 0.6374 | 1431.43 | 21.9048 | 99.3688 | 99.0041 | 98.332 | 0 | 0 | 98.328 | 98.2826 | 0 | 0 | 0 | 98.328 | 0 | 660 | 0 | 0
6439 | 2006-09-26 06:00 | 128 | 550 | 38 | 22.01 | 3.66 | 0 | 9.3467 | 98.1686 | 78.0861 | 0 | 128 | 114.402 | 43.9263 | 1.1993 | 58.6248 | 41.1079 | 0.0062597 | 47.3572 | 39.5865 | 0.0047168 | 84.34 | 84.3481 | 189427 | 24.086 | 162080 | 162327 | 140360 | 0 | 0 | 140145 | 644.344 | 0 | 0 | 0 | 888.152 | 139257 | 660 | 135257 | 132551.5312
6440 | 2006-09-26 07:00 | 340 | 748 | 67 | 22.12 | 3.66 | 0 | 21.3777 | 107.48 | 63.3479 | 0 | 340 | 335.954 | 79.2413 | 3.1855 | 311.907 | 74.1571 | 0.016627 | 292.736 | 71.4126 | 0.012529 | 353.236 | 353.219 | 793255 | 30.8135 | 752591 | 731420 | 681361 | 0 | 0 | 677403 | 688.049 | 0 | 0 | 0 | 0 | 677403 | 688.049 | 667575 | 654223.8125
6441 | 2006-09-26 08:00 | 520 | 782 | 97 | 24.13 | 3.66 | 0 | 32.7416 | 118.51 | 48.7118 | 0 | 520 | 516.066 | 115.309 | 4.872 | 516.066 | 107.911 | 0.02543 | 502.765 | 103.917 | 0.019162 | 588.5 | 588.494 | 1321600 | 38.6141 | 1291900 | 1215600 | 1185330 | 0 | 0 | 1173660 | 684.826 | 0 | 0 | 0 | 0 | 1173660 | 684.826 | 1155980 | 1132857.625
6442 | 2006-09-26 09:00 | 665 | 801 | 122 | 26.14 | 4 | 0 | 42.7956 | 132.656 | 34.3242 | 0 | 665 | 660.07 | 145.557 | 6.2305 | 660.07 | 136.218 | 0.032521 | 653.111 | 131.177 | 0.024505 | 760.783 | 760.782 | 1708530 | 44.4505 | 1695150 | 1554310 | 1515180 | 0 | 0 | 1495510 | 671.792 | 0 | 0 | 0 | 0 | 1495510 | 671.792 | 1471170 | 1441747.125
6443 | 2006-09-26 10:00 | 756 | 775 | 160 | 28.16 | 4 | 0 | 50.413 | 151.57 | 20.7256 | 0 | 756 | 723.318 | 188.587 | 7.0831 | 723.318 | 176.487 | 0.036971 | 720.816 | 169.955 | 0.027859 | 864.075 | 864.066 | 1940480 | 48.9563 | 1938540 | 1741300 | 1699100 | 0 | 0 | 1673620 | 660.859 | 0 | 0 | 0 | -83.9586 | 1673700 | 662.152 | 1643950 | 1611074
6444 | 2006-09-26 11:00 | 808 | 797 | 165 | 29.1 | 4 | 0 | 53.9432 | 175.475 | 11.2861 | 0 | 808 | 779.984 | 195.186 | 7.5703 | 779.984 | 182.663 | 0.039515 | 779.215 | 175.903 | 0.029775 | 926.493 | 926.478 | 2080630 | 51.3985 | 2085990 | 1852830 | 1811010 | 0 | 0 | 1781560 | 653.693 | 0 | 0 | 0 | 1988.44 | 1779570 | 660 | 1746120 | 1711195.75
6445 | 2006-09-26 12:00 | 816 | 871 | 129 | 30.04 | 4.61 | 0 | 52.1976 | 200.402 | 16.4856 | 0 | 816 | 833.734 | 155.939 | 7.6453 | 833.734 | 145.934 | 0.039906 | 831.947 | 140.533 | 0.03007 | 943.335 | 943.328 | 2118480 | 51.8553 | 2125850 | 1884370 | 1841040 | 0 | 0 | 1810570 | 653.278 | 0 | 0 | 0 | 2471.48 | 1808100 | 660 | 1773600 | 1738128.5
6446 | 2006-09-26 13:00 | 728 | 881 | 97 | 30.98 | 4.61 | 0 | 45.8058 | 221.204 | 29.3718 | 0 | 728 | 766.949 | 112.716 | 6.8208 | 766.949 | 105.483 | 0.035602 | 761.293 | 101.58 | 0.026827 | 837.012 | 837.005 | 1879710 | 50.3365 | 1874680 | 1672280 | 1632740 | 0 | 0 | 1608820 | 655.41 | 0 | 0 | 0 | 1172.86 | 1607650 | 660 | 1580200 | 1548594.25
6447 | 2006-09-26 14:00 | 594 | 842 | 94 | 31.04 | 4.61 | 0 | 36.439 | 236.834 | 43.5882 | 0 | 594 | 609.726 | 113.262 | 5.5653 | 609.726 | 105.995 | 0.029049 | 598.122 | 102.073 | 0.021889 | 679.21 | 679.204 | 1525320 | 46.7472 | 1503690 | 1362550 | 1330720 | 0 | 0 | 1314980 | 660.731 | 0 | 0 | 0 | 4.9869 | 1314970 | 661.614 | 1295320 | 1269411.125
6448 | 2006-09-26 15:00 | 423 | 848 | 59 | 31.11 | 6.36 | 0 | 25.4337 | 248.759 | 58.1632 | 0 | 423 | 447.091 | 69.6378 | 3.9632 | 447.091 | 65.1697 | 0.020687 | 427.067 | 62.7578 | 0.015588 | 475.145 | 475.143 | 1067050 | 40.9219 | 1029480 | 956992 | 933390 | 0 | 0 | 925758 | 668.03 | 0 | 0 | 0 | 0 | 925758 | 668.03 | 913351 | 895084.4375
6449 | 2006-09-26 16:00 | 197 | 612 | 53 | 31.17 | 6.36 | 0 | 13.573 | 258.524 | 72.8765 | 0 | 197 | 180.661 | 61.7359 | 1.8457 | 180.661 | 57.7748 | 0.0096341 | 159.014 | 55.6366 | 0.0072595 | 208.218 | 208.217 | 467603 | 35.4697 | 426807 | 405587 | 395682 | 0 | 0 | 394240 | 654.618 | 0 | 0 | 0 | 307.581 | 393933 | 660 | 388275 | 380509.1562
6450 | 2006-09-26 17:00 | 18 | 201 | 5 | 30.29 | 6.36 | 0 | 1.3118 | 267.253 | 87.6503 | 0 | 18 | 6.1261 | 5.028 | 0.16865 | 5.7777 | 4.7054 | 0.00088028 | 0 | 4.5312 | 0.00066331 | 4.396 | 4.3956 | 9871.54 | 30.3808 | 4092.75 | 4022.5 | 3959.97 | 0 | 0 | 3959.66 | 449.453 | 0 | 0 | 0 | 3959.66 | 0 | 660 | 0 | 0
6451 | 2006-09-26 18:00 | 0 | 0 | 0 | 29.41 | 5.36 | 0
6452 | 2006-09-26 19:00 | 0 | 0 | 0 | 28.53 | 5.36 | 0
6453 | 2006-09-26 20:00 | 0 | 0 | 0 | 27.47 | 5.36 | 0
6454 | 2006-09-26 21:00 | 0 | 0 | 0 | 26.4 | 4.58 | 0
6455 | 2006-09-26 22:00 | 0 | 0 | 0 | 25.34 | 4.58 | 0
6456 | 2006-09-26 23:00 | 0 | 0 | 0 | 24.48 | 4.58 | 0
6457 | 2006-09-27 | 0 | 0 | 0 | 23.63 | 3.68 | 0
6458 | 2006-09-27 01:00 | 0 | 0 | 0 | 22.78 | 3.68 | 0
6459 | 2006-09-27 02:00 | 0 | 0 | 0 | 22.27 | 3.68 | 0
6460 | 2006-09-27 03:00 | 0 | 0 | 0 | 21.76 | 2.2 | 0
6461 | 2006-09-27 04:00 | 0 | 0 | 0 | 21.24 | 2.2 | 0
6462 | 2006-09-27 05:00 | 3 | 80 | 1 | 20.72 | 2.2 | 0 | -3.1127 | 89.9361 | 90 | 0 | 3 | 0 | 0.73022 | 0.028108 | 0 | 0.68337 | 0 | 0 | 0.65807 | 0 | 0.63833 | 0.63831 | 1433.49 | 20.7373 | 99.6658 | 99.1621 | 98.48 | 0 | 0 | 98.476 | 98.3471 | 0 | 0 | 0 | 98.476 | 0 | 660 | 0 | 0
6463 | 2006-09-27 06:00 | 128 | 562 | 37 | 20.19 | 1.69 | 0 | 9.1905 | 98.5401 | 78.0705 | 0 | 128 | 117.773 | 43.0834 | 1.1993 | 58.4594 | 40.3191 | 0.0062597 | 47.2418 | 38.8269 | 0.0047168 | 83.4912 | 83.5126 | 187551 | 22.5328 | 160450 | 161821 | 138973 | 0 | 0 | 138756 | 636.789 | 0 | 0 | 0 | 872.393 | 137883 | 660 | 133911 | 131232.9219
6464 | 2006-09-27 07:00 | 342 | 758 | 68 | 19.66 | 1.69 | 0 | 21.2033 | 107.865 | 63.3422 | 0 | 342 | 339.897 | 80.5052 | 3.2043 | 314.624 | 75.3399 | 0.016725 | 295.292 | 72.5516 | 0.012603 | 356.821 | 356.802 | 801293 | 29.6695 | 760754 | 743032 | 692054 | 0 | 0 | 688000 | 690.687 | 0 | 0 | 0 | 0 | 688000 | 690.687 | 677932 | 664372.875
6465 | 2006-09-27 08:00 | 516 | 737 | 120 | 21.9 | 1.69 | 0 | 32.5339 | 118.914 | 48.7247 | 0 | 516 | 485.744 | 141.998 | 4.8345 | 485.744 | 132.887 | 0.025234 | 473.214 | 127.969 | 0.019015 | 583.167 | 583.162 | 1309630 | 38.2596 | 1279500 | 1205830 | 1176060 | 0 | 0 | 1164560 | 684.285 | 0 | 0 | 0 | 0 | 1164560 | 684.285 | 1147090 | 1124146
6466 | 2006-09-27 09:00 | 711 | 897 | 106 | 24.14 | 4.25 | 0 | 42.5366 | 133.068 | 34.3744 | 0 | 711 | 738.611 | 122.559 | 6.6615 | 738.611 | 114.695 | 0.034771 | 730.797 | 110.451 | 0.026201 | 816.036 | 816.029 | 1832590 | 43.4608 | 1825210 | 1682140 | 1639760 | 0 | 0 | 1617230 | 678.553 | 0 | 0 | 0 | 0 | 1617230 | 678.553 | 1588880 | 1557103.625
6467 | 2006-09-27 10:00 | 820 | 968 | 79 | 26.37 | 4.25 | 0 | 50.0875 | 151.93 | 20.8648 | 0 | 820 | 902.718 | 92.9144 | 7.6828 | 902.718 | 86.9528 | 0.040101 | 899.551 | 83.7348 | 0.030217 | 953.816 | 953.814 | 2142030 | 48.9531 | 2150660 | 1933430 | 1885570 | 0 | 0 | 1854520 | 663.358 | 0 | 0 | 0 | -16.9211 | 1854540 | 663.44 | 1818240 | 1781878.125
6468 | 2006-09-27 11:00 | 866 | 976 | 83 | 27.74 | 4.25 | 0 | 53.5601 | 175.66 | 11.646 | 0 | 866 | 953.263 | 97.3782 | 8.1137 | 953.263 | 91.1302 | 0.042351 | 952.261 | 87.7575 | 0.031912 | 1008.85 | 1008.85 | 2265620 | 51.6261 | 2280940 | 2025290 | 1981290 | 0 | 0 | 1946040 | 653.007 | 0 | 0 | 0 | 1667.74 | 1944370 | 660 | 1904620 | 1866528.5
6469 | 2006-09-27 12:00 | 837 | 962 | 83 | 29.11 | 3.14 | 0 | 51.8003 | 200.352 | 16.8109 | 0 | 837 | 918.456 | 97.4079 | 7.842 | 918.456 | 91.1581 | 0.040933 | 916.406 | 87.7844 | 0.030844 | 974.094 | 974.09 | 2187560 | 53.9217 | 2198640 | 1929770 | 1885750 | 0 | 0 | 1853140 | 646.522 | 0 | 0 | 0 | 9448.33 | 1843700 | 660 | 1807860 | 1771701.5
6470 | 2006-09-27 13:00 | 737 | 880 | 111 | 30.47 | 3.14 | 0 | 45.4325 | 221.005 | 29.6012 | 0 | 737 | 764.007 | 128.153 | 6.9051 | 764.007 | 119.93 | 0.036042 | 758.273 | 115.492 | 0.027159 | 847.578 | 847.572 | 1903430 | 52.0591 | 1899600 | 1680420 | 1642960 | 0 | 0 | 1618240 | 648.26 | 0 | 0 | 0 | 5646.04 | 1612590 | 660 | 1584970 | 1553272.5
6471 | 2006-09-27 14:00 | 609 | 917 | 69 | 30.83 | 3.14 | 0 | 36.0983 | 236.578 | 43.7752 | 0 | 609 | 661.796 | 81.561 | 5.7059 | 661.796 | 76.3279 | 0.029783 | 649.059 | 73.503 | 0.022442 | 700.907 | 700.905 | 1574060 | 48.6832 | 1554540 | 1395750 | 1362960 | 0 | 0 | 1346160 | 654.757 | 0 | 0 | 0 | 919.408 | 1345240 | 660 | 1324970 | 1298466.375
6472 | 2006-09-27 15:00 | 409 | 828 | 57 | 31.18 | 4.31 | 0 | 25.1189 | 248.489 | 58.3292 | 0 | 409 | 435.369 | 67.5555 | 3.832 | 435.369 | 63.2211 | 0.020002 | 415.677 | 60.8813 | 0.015072 | 462.276 | 462.273 | 1038140 | 42.0822 | 999869 | 924068 | 901418 | 0 | 0 | 894212 | 664.042 | 0 | 0 | 0 | 0 | 894212 | 664.042 | 882407 | 864758.8125
6473 | 2006-09-27 16:00 | 195 | 623 | 51 | 31.54 | 4.31 | 0 | 13.2747 | 258.252 | 73.031 | 0 | 195 | 183.028 | 59.4518 | 1.827 | 183.028 | 55.6372 | 0.0095363 | 160.824 | 53.5781 | 0.0071858 | 207.977 | 207.974 | 467057 | 36.4448 | 426272 | 403080 | 393566 | 0 | 0 | 392127 | 651.491 | 0 | 0 | 0 | 969.872 | 391157 | 660 | 385474 | 377764.2812
6474 | 2006-09-27 17:00 | 17 | 197 | 4 | 30.8 | 4.31 | 0 | 1.0209 | 266.981 | 87.799 | 0 | 17 | 5.7388 | 4.0137 | 0.15928 | 5.0196 | 3.7561 | 0.00083137 | 0 | 3.6171 | 0.00062646 | 3.5092 | 3.509 | 7880.28 | 30.8828 | 2802.36 | 2769.11 | 2733.88 | 0 | 0 | 2733.7 | 415.803 | 0 | 0 | 0 | 2733.7 | 0 | 660 | 0 | 0
6475 | 2006-09-27 18:00 | 0 | 0 | 0 | 30.05 | 2.49 | 0
6476 | 2006-09-27 19:00 | 0 | 0 | 0 | 29.31 | 2.49 | 0
6477 | 2006-09-27 20:00 | 0 | 0 | 0 | 28.61 | 2.49 | 0
6478 | 2006-09-27 21:00 | 0 | 0 | 0 | 27.92 | 6.38 | 0
6479 | 2006-09-27 22:00 | 0 | 0 | 0 | 27.23 | 6.38 | 0
6480 | 2006-09-27 23:00 | 0 | 0 | 0 | 26.26 | 6.38 | 0
6481 | 2006-09-28 | 0 | 0 | 0 | 25.28 | 3.25 | 0
6482 | 2006-09-28 01:00 | 0 | 0 | 0 | 24.31 | 3.25 | 0
6483 | 2006-09-28 02:00 | 0 | 0 | 0 | 23.94 | 3.25 | 0
6484 | 2006-09-28 03:00 | 0 | 0 | 0 | 23.56 | 2.94 | 0
6485 | 2006-09-28 04:00 | 0 | 0 | 0 | 23.18 | 2.94 | 0
6486 | 2006-09-28 05:00 | 3 | 66 | 1 | 22.59 | 2.94 | 0 | -3.2637 | 90.3052 | 90 | 0 | 3 | 0 | 0.73125 | 0.028108 | 0 | 0.68433 | 0 | 0 | 0.659 | 0 | 0.63923 | 0.63919 | 1435.47 | 22.6065 | 99.9299 | 99.6463 | 98.9779 | 0 | 0 | 98.9738 | 98.5194 | 0 | 0 | 0 | 98.9738 | 0 | 660 | 0 | 0
6487 | 2006-09-28 06:00 | 119 | 483 | 42 | 22 | 1.12 | 0 | 9.0334 | 98.9107 | 78.0564 | 0 | 119 | 101.491 | 48.6441 | 1.1149 | 48.6436 | 45.523 | 0.0058196 | 39.3232 | 43.8382 | 0.0043852 | 80.6709 | 80.6898 | 181210 | 24.3519 | 154113 | 154153 | 134372 | 0 | 0 | 134184 | 651.278 | 0 | 0 | 0 | 861.42 | 133322 | 660 | 129410 | 126821.6641
6488 | 2006-09-28 07:00 | 344 | 714 | 88 | 21.41 | 1.12 | 0 | 21.0274 | 108.248 | 63.3386 | 0 | 344 | 320.142 | 102.513 | 3.223 | 295.293 | 95.9351 | 0.016823 | 277.153 | 92.3846 | 0.012677 | 358.464 | 358.453 | 805001 | 31.858 | 764299 | 739027 | 689310 | 0 | 0 | 685226 | 683.237 | 0 | 0 | 0 | 0 | 685226 | 683.237 | 675467 | 661958.0625
6489 | 2006-09-28 08:00 | 511 | 731 | 120 | 23.51 | 1.12 | 0 | 32.3244 | 119.315 | 48.7409 | 0 | 511 | 482.224 | 142.303 | 4.7877 | 482.224 | 133.172 | 0.02499 | 469.774 | 128.244 | 0.018831 | 580.095 | 580.086 | 1302730 | 40.4181 | 1272350 | 1187000 | 1158630 | 0 | 0 | 1147230 | 677.304 | 0 | 0 | 0 | 0 | 1147230 | 677.304 | 1130460 | 1107847.75
6490 | 2006-09-28 09:00 | 680 | 841 | 115 | 25.6 | 1.31 | 0 | 42.2757 | 133.475 | 34.4294 | 0 | 680 | 692.77 | 138.511 | 6.3711 | 692.77 | 129.624 | 0.033255 | 685.413 | 124.827 | 0.025058 | 785.957 | 785.951 | 1765040 | 48.2178 | 1754360 | 1580200 | 1543380 | 0 | 0 | 1522200 | 659.361 | 0 | 0 | 0 | -98.315 | 1522300 | 661.088 | 1497560 | 1467609.25
6491 | 2006-09-28 10:00 | 802 | 939 | 87 | 27.7 | 1.31 | 0 | 49.7609 | 152.283 | 21.0109 | 0 | 802 | 874.378 | 102.071 | 7.5141 | 874.378 | 95.5224 | 0.039221 | 871.265 | 91.9872 | 0.029554 | 934.383 | 934.38 | 2098380 | 54.5892 | 2104680 | 1840380 | 1799000 | 0 | 0 | 1768980 | 643.188 | 0 | 0 | 0 | 14743.8 | 1754230 | 660 | 1721700 | 1687270.75
6492 | 2006-09-28 11:00 | 846 | 872 | 150 | 28.95 | 1.31 | 0 | 53.1768 | 175.84 | 12.0084 | 0 | 846 | 850.443 | 179.837 | 7.9264 | 850.443 | 168.298 | 0.041373 | 849.492 | 162.069 | 0.031175 | 981.244 | 981.234 | 2203600 | 57.1875 | 2215540 | 1913280 | 1869420 | 0 | 0 | 1836250 | 634.946 | 0 | 0 | 0 | 31363.7 | 1804890 | 660 | 1770510 | 1735097
6493 | 2006-09-28 12:00 | 750 | 668 | 229 | 30.19 | 3.2 | 0 | 51.4034 | 200.303 | 17.1384 | 0 | 750 | 637.017 | 269.093 | 7.0269 | 637.017 | 251.827 | 0.036678 | 635.537 | 242.507 | 0.027638 | 851.73 | 851.723 | 1912760 | 51.7989 | 1909410 | 1691320 | 1650370 | 0 | 0 | 1625730 | 652.432 | 0 | 0 | 0 | 3665.78 | 1622060 | 659.999 | 1594130 | 1562245.875
6494 | 2006-09-28 13:00 | 662 | 645 | 206 | 31.44 | 3.2 | 0 | 45.0596 | 220.807 | 29.8328 | 0 | 662 | 558.841 | 240.608 | 6.2024 | 558.841 | 225.17 | 0.032375 | 554.573 | 216.837 | 0.024395 | 748.291 | 748.289 | 1680470 | 50.4247 | 1665780 | 1483740 | 1451370 | 0 | 0 | 1432050 | 649.095 | 0 | 0 | 0 | 3593.8 | 1428450 | 659.999 | 1406210 | 1378086.125
6495 | 2006-09-28 14:00 | 439 | 299 | 264 | 31.69 | 3.2 | 0 | 35.7579 | 236.323 | 43.9636 | 0 | 439 | 215.555 | 282.492 | 4.1131 | 215.555 | 264.366 | 0.021469 | 211.359 | 254.582 | 0.016177 | 451.979 | 451.968 | 1015010 | 43.1568 | 976215 | 897291 | 875631 | 0 | 0 | 868761 | 660.155 | 0 | 0 | 0 | 9.8038 | 868751 | 660.574 | 857433 | 840283.9375
6496 | 2006-09-28 15:00 | 187 | 48 | 167 | 31.95 | 4.25 | 0 | 24.8046 | 248.219 | 58.4955 | 0 | 187 | 24.9123 | 170.932 | 1.752 | 24.9123 | 159.965 | 0.0091451 | 23.7743 | 154.045 | 0.006891 | 172.491 | 172.483 | 387353 | 36.0338 | 348601 | 329986 | 321884 | 0 | 0 | 320897 | 643.275 | 0 | 0 | 0 | 2572.24 | 318325 | 660 | 312309 | 306062.5625
6497 | 2006-09-28 16:00 | 141 | 217 | 92 | 32.21 | 4.25 | 0 | 12.9771 | 257.981 | 73.1851 | 0 | 141 | 63.1217 | 96.4377 | 1.3211 | 63.1217 | 90.2501 | 0.0068955 | 55.3676 | 86.91 | 0.0051959 | 138.014 | 138.012 | 309941 | 35.4777 | 274019 | 259847 | 253599 | 0 | 0 | 252968 | 634.61 | 0 | 0 | 0 | 4861.29 | 248107 | 660 | 242372 | 237524.6562
6498 | 2006-09-28 17:00 | 12 | 66 | 8 | 31.49 | 4.25 | 0 | 0.73091 | 266.708 | 87.9467 | 0 | 12 | 1.6473 | 7.0797 | 0.11243 | 1.3389 | 6.6254 | 0.00058685 | 0 | 6.3802 | 0.0004422 | 6.1892 | 6.1889 | 13898.5 | 31.6365 | 6902.9 | 6699.65 | 6570.29 | 0 | 0 | 6569.55 | 481.657 | 0 | 0 | 0 | 6569.55 | 0 | 660 | 0 | 0
6499 | 2006-09-28 18:00 | 0 | 0 | 0 | 30.77 | 5.71 | 0
6500 | 2006-09-28 19:00 | 0 | 0 | 0 | 30.06 | 5.71 | 0
6501 | 2006-09-28 20:00 | 0 | 0 | 0 | 28.92 | 5.71 | 0
6502 | 2006-09-28 21:00 | 0 | 0 | 0 | 27.78 | 5.23 | 0
6503 | 2006-09-28 22:00 | 0 | 0 | 0 | 26.64 | 5.23 | 0
6504 | 2006-09-28 23:00 | 0 | 0 | 0 | 25.81 | 5.23 | 0
6505 | 2006-09-29 | 0 | 0 | 0 | 24.97 | 3.95 | 0
6506 | 2006-09-29 01:00 | 0 | 0 | 0 | 24.14 | 3.95 | 0
6507 | 2006-09-29 02:00 | 0 | 0 | 0 | 23.67 | 3.95 | 0
6508 | 2006-09-29 03:00 | 0 | 0 | 0 | 23.2 | 5.83 | 0
6509 | 2006-09-29 04:00 | 0 | 0 | 0 | 22.73 | 5.83 | 0
6510 | 2006-09-29 05:00 | 3 | 71 | 1 | 22.67 | 5.83 | 0 | -3.4153 | 90.6735 | 90 | 0 | 3 | 0 | 0.73228 | 0.028108 | 0 | 0.6853 | 0 | 0 | 0.65994 | 0 | 0.64014 | 0.64011 | 1437.53 | 22.6837 | 100.215 | 99.9408 | 99.286 | 0 | 0 | 99.282 | 98.5329 | 0 | 0 | 0 | 99.282 | 0 | 660 | 0 | 0
6511 | 2006-09-29 06:00 | 122 | 547 | 37 | 22.61 | 5 | 0 | 8.8751 | 99.2801 | 78.0439 | 0 | 122 | 114.134 | 43.3803 | 1.143 | 52.6652 | 40.5969 | 0.0059663 | 42.5874 | 39.0945 | 0.0044957 | 79.2358 | 79.2825 | 178051 | 24.3975 | 151588 | 151592 | 130706 | 0 | 0 | 130515 | 641.487 | 0 | 0 | 0 | 1395.43 | 129119 | 660 | 125317 | 122810.1875
6512 | 2006-09-29 07:00 | 340 | 762 | 69 | 22.56 | 5 | 0 | 20.8501 | 108.629 | 63.3374 | 0 | 340 | 341.667 | 81.9679 | 3.1855 | 314.123 | 76.7086 | 0.016627 | 294.829 | 73.8697 | 0.012529 | 357.649 | 357.623 | 803135 | 30.6229 | 762766 | 741925 | 691387 | 0 | 0 | 687284 | 685.758 | 0 | 0 | 0 | 0 | 687284 | 685.758 | 677400 | 663852.25
6513 | 2006-09-29 08:00 | 517 | 756 | 115 | 24.84 | 5 | 0 | 32.1131 | 119.713 | 48.7603 | 0 | 517 | 498.507 | 137.218 | 4.8439 | 498.507 | 128.414 | 0.025283 | 485.621 | 123.662 | 0.019052 | 591.023 | 591.015 | 1327270 | 38.1648 | 1297770 | 1223710 | 1193700 | 0 | 0 | 1181830 | 683.814 | 0 | 0 | 0 | 0 | 1181830 | 683.814 | 1164030 | 1140747.875
6514 | 2006-09-29 09:00 | 696 | 885 | 105 | 27.11 | 1.65 | 0 | 42.0131 | 133.878 | 34.4891 | 0 | 696 | 727.808 | 121.927 | 6.521 | 727.808 | 114.104 | 0.034037 | 720.048 | 109.881 | 0.025648 | 805.056 | 805.049 | 1807940 | 49.7549 | 1799350 | 1609010 | 1572850 | 0 | 0 | 1550580 | 654.909 | 0 | 0 | 0 | 1008.87 | 1549570 | 660 | 1524010 | 1493530.5
6515 | 2006-09-29 10:00 | 789 | 882 | 121 | 29.39 | 1.65 | 0 | 49.433 | 152.63 | 21.164 | 0 | 789 | 820.045 | 139.569 | 7.3923 | 820.045 | 130.614 | 0.038585 | 817.079 | 125.78 | 0.029075 | 914.602 | 914.594 | 2053950 | 55.1162 | 2057900 | 1794380 | 1754600 | 0 | 0 | 1725790 | 640.416 | 0 | 0 | 0 | 18712 | 1707080 | 660 | 1676230 | 1642707.75
6516 | 2006-09-29 11:00 | 805 | 822 | 152 | 30.36 | 1.65 | 0 | 52.7934 | 176.016 | 12.3728 | 0 | 805 | 800.835 | 182.267 | 7.5422 | 800.835 | 170.573 | 0.039368 | 799.883 | 164.26 | 0.029664 | 935.247 | 935.241 | 2100320 | 56.667 | 2106720 | 1823140 | 1782590 | 0 | 0 | 1752420 | 635.512 | 0 | 0 | 0 | 29406.1 | 1723010 | 660 | 1691600 | 1657765.75
6517 | 2006-09-29 12:00 | 742 | 657 | 233 | 31.32 | 3.35 | 0 | 51.007 | 200.252 | 17.4678 | 0 | 742 | 624.695 | 273.51 | 6.952 | 624.695 | 255.961 | 0.036287 | 623.185 | 246.488 | 0.027343 | 843.61 | 843.599 | 1894510 | 52.5116 | 1890230 | 1668300 | 1630130 | 0 | 0 | 1605650 | 646.999 | 0 | 0 | 0 | 7128.38 | 1598530 | 660 | 1571370 | 1539946.5
6518 | 2006-09-29 13:00 | 691 | 793 | 134 | 32.29 | 3.35 | 0 | 44.6872 | 220.611 | 30.0664 | 0 | 691 | 685.478 | 160.224 | 6.4741 | 685.478 | 149.944 | 0.033793 | 680.149 | 144.395 | 0.025464 | 799.832 | 799.819 | 1796190 | 52.3819 | 1787020 | 1577420 | 1540790 | 0 | 0 | 1518830 | 645.645 | 0 | 0 | 0 | 7764.28 | 1511060 | 660 | 1486720 | 1456982.125
6519 | 2006-09-29 14:00 | 559 | 795 | 99 | 32.41 | 3.35 | 0 | 35.4179 | 236.07 | 44.153 | 0 | 559 | 569.494 | 119.369 | 5.2374 | 569.494 | 111.71 | 0.027337 | 558.281 | 107.576 | 0.020599 | 645.901 | 645.899 | 1450530 | 48.6353 | 1425780 | 1279500 | 1249710 | 0 | 0 | 1235480 | 652.129 | 0 | 0 | 0 | 1783.03 | 1233690 | 659.999 | 1215930 | 1191607.75
6520 | 2006-09-29 15:00 | 355 | 650 | 86 | 32.54 | 3.21 | 0 | 24.4907 | 247.951 | 58.6621 | 0 | 355 | 337.483 | 102.539 | 3.3261 | 337.483 | 95.9598 | 0.017361 | 321.913 | 92.4084 | 0.013082 | 401.904 | 401.897 | 902559 | 42.7297 | 861604 | 792927 | 774366 | 0 | 0 | 768894 | 655.332 | 0 | 0 | 0 | 332.896 | 768562 | 660 | 758570 | 743398.875
6521 | 2006-09-29 16:00 | 159 | 443 | 61 | 32.66 | 3.21 | 0 | 12.6802 | 257.71 | 73.339 | 0 | 159 | 128.001 | 70.3843 | 1.4897 | 128.001 | 65.8683 | 0.0077758 | 112.079 | 63.4305 | 0.0058592 | 170.25 | 170.247 | 382333 | 36.9765 | 343723 | 323772 | 316643 | 0 | 0 | 315672 | 638.443 | 0 | 0 | 0 | 4317.23 | 311354 | 660 | 305340 | 299233
6522 | 2006-09-29 17:00 | 12 | 130 | 5 | 31.91 | 3.21 | 0 | 0.44196 | 266.435 | 88.0935 | 0 | 12 | 2.6768 | 4.3791 | 0.11243 | 1.9865 | 4.0981 | 0.00058685 | 0 | 3.9464 | 0.0004422 | 3.8285 | 3.8282 | 8597.18 | 32.0071 | 3255.9 | 3197.48 | 3153.42 | 0 | 0 | 3153.2 | 425.975 | 0 | 0 | 0 | 3153.2 | 0 | 660 | 0 | 0
6523 | 2006-09-29 18:00 | 0 | 0 | 0 | 31.16 | 4.61 | 0
6524 | 2006-09-29 19:00 | 0 | 0 | 0 | 30.41 | 4.61 | 0
6525 | 2006-09-29 20:00 | 0 | 0 | 0 | 29.31 | 4.61 | 0
6526 | 2006-09-29 21:00 | 0 | 0 | 0 | 28.22 | 4.71 | 0
6527 | 2006-09-29 22:00 | 0 | 0 | 0 | 27.12 | 4.71 | 0
6528 | 2006-09-29 23:00 | 0 | 0 | 0 | 26.31 | 4.71 | 0
6529 | 2006-09-30 | 0 | 0 | 0 | 25.5 | 3.6 | 0
6530 | 2006-09-30 01:00 | 0 | 0 | 0 | 24.68 | 3.6 | 0
6531 | 2006-09-30 02:00 | 0 | 0 | 0 | 23.78 | 3.6 | 0
6532 | 2006-09-30 03:00 | 0 | 0 | 0 | 22.88 | 6.31 | 0
6533 | 2006-09-30 04:00 | 0 | 0 | 0 | 21.97 | 6.31 | 0
6534 | 2006-09-30 05:00 | 2 | 63 | 0 | 21.64 | 6.31 | 0 | -3.5674 | 91.041 | 90 | 0 | 2 | 0 | 0 | 0.018738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.64 | 0 | 0 | 0 | 0 | 0 | 0 | 660 | 0 | 0 | 0 | 0 | 0 | 660 | 0 | 0
6535 | 2006-09-30 06:00 | 117 | 514 | 38 | 21.3 | 5.83 | 0 | 8.7159 | 99.6482 | 78.0329 | 0 | 117 | 108.098 | 44.9922 | 1.0962 | 47.871 | 42.1054 | 0.0057218 | 38.7211 | 40.5471 | 0.0043115 | 76.8943 | 76.8652 | 172622 | 22.9423 | 146395 | 147528 | 127604 | 0 | 0 | 127428 | 647.763 | 0 | 0 | 0 | 878.091 | 126550 | 661.71 | 122770 | 120314.5547
6536 | 2006-09-30 07:00 | 334 | 756 | 67 | 20.96 | 5.83 | 0 | 20.6713 | 109.008 | 63.3386 | 0 | 334 | 339.392 | 80.0597 | 3.1293 | 311.114 | 74.923 | 0.016334 | 292.002 | 72.1501 | 0.012308 | 353.24 | 353.25 | 793312 | 28.5076 | 752916 | 739570 | 688151 | 0 | 0 | 684177 | 694.155 | 0 | 0 | 0 | 0 | 684177 | 694.155 | 674042 | 660560.75
6537 | 2006-09-30 08:00 | 526 | 785 | 112 | 23.4 | 5.83 | 0 | 31.9001 | 120.108 | 48.7832 | 0 | 526 | 516.216 | 134.259 | 4.9282 | 516.216 | 125.644 | 0.025724 | 502.855 | 120.994 | 0.019383 | 605.152 | 605.147 | 1359000 | 36.3296 | 1330680 | 1265550 | 1233460 | 0 | 0 | 1221100 | 692.098 | 0 | 0 | 0 | 0 | 1221100 | 692.098 | 1202070 | 1178033.25
6538 | 2006-09-30 09:00 | 596 | 584 | 208 | 25.83 | 5.98 | 0 | 41.7487 | 134.276 | 34.5537 | 0 | 596 | 479.91 | 237.183 | 5.5841 | 479.91 | 221.965 | 0.029147 | 474.77 | 213.75 | 0.021963 | 667.886 | 667.878 | 1499880 | 39.9627 | 1477170 | 1382170 | 1348090 | 0 | 0 | 1332940 | 682.432 | 0 | 0 | 0 | 0 | 1332940 | 682.432 | 1311950 | 1285714.875
6539 | 2006-09-30 10:00 | 724 | 696 | 199 | 28.26 | 5.98 | 0 | 49.1041 | 152.971 | 21.3237 | 0 | 724 | 646.988 | 237.281 | 6.7833 | 646.988 | 222.056 | 0.035407 | 644.611 | 213.838 | 0.02668 | 832.722 | 832.704 | 1870040 | 45.8805 | 1864530 | 1699200 | 1659080 | 0 | 0 | 1635460 | 670.423 | 0 | 0 | 0 | 0 | 1635460 | 670.423 | 1606770 | 1574633
6540 | 2006-09-30 11:00 | 762 | 640 | 256 | 29.05 | 5.98 | 0 | 52.4102 | 176.186 | 12.739 | 0 | 762 | 622.849 | 298.624 | 7.1394 | 622.849 | 279.464 | 0.037265 | 622.063 | 269.121 | 0.02808 | 864.476 | 864.48 | 1941400 | 47.3429 | 1939510 | 1755730 | 1712020 | 0 | 0 | 1686500 | 665.296 | 0 | 0 | 0 | 0 | 1686500 | 665.296 | 1656230 | 1623108.375
6541 | 2006-09-30 12:00 | 447 | 108 | 364 | 29.83 | 5.51 | 0 | 50.6114 | 200.201 | 17.7988 | 0 | 447 | 102.253 | 390.544 | 4.188 | 102.253 | 365.486 | 0.02186 | 101.996 | 351.96 | 0.016472 | 440.353 | 440.328 | 988863 | 39.4345 | 949520 | 888535 | 867638 | 0 | 0 | 861112 | 671.631 | 0 | 0 | 0 | 0 | 861112 | 671.631 | 849416 | 832428.125
6542 | 2006-09-30 13:00 | 625 | 531 | 255 | 30.62 | 5.51 | 0 | 44.3154 | 220.416 | 30.302 | 0 | 625 | 457.266 | 288.812 | 5.8558 | 457.266 | 270.281 | 0.030565 | 453.648 | 260.278 | 0.023031 | 692.531 | 692.51 | 1555210 | 45.7252 | 1534870 | 1397880 | 1364980 | 0 | 0 | 1348690 | 665.912 | 0 | 0 | 0 | 0 | 1348690 | 665.912 | 1328080 | 1301519
6543 | 2006-09-30 14:00 | 328 | 105 | 268 | 30.76 | 5.51 | 0 | 35.0784 | 235.818 | 44.3435 | 0 | 328 | 74.665 | 283.441 | 3.0731 | 74.665 | 265.255 | 0.016041 | 73.1781 | 255.438 | 0.012087 | 318.769 | 318.754 | 715839 | 37.7127 | 673111 | 633967 | 617673 | 0 | 0 | 614277 | 664.018 | 0 | 0 | 0 | 0 | 614277 | 664.018 | 606168 | 594044.5625
6544 | 2006-09-30 15:00 | 220 | 103 | 178 | 30.9 | 7.19 | 0 | 24.1776 | 247.683 | 58.8289 | 0 | 220 | 53.078 | 184.49 | 2.0612 | 53.078 | 172.653 | 0.010759 | 50.6046 | 166.263 | 0.0081071 | 210.369 | 210.359 | 472414 | 35.0199 | 431534 | 411020 | 400758 | 0 | 0 | 399284 | 655.689 | 0 | 0 | 0 | 135.725 | 399149 | 660 | 393509 | 385638.625
6545 | 2006-09-30 16:00 | 62 | 0 | 62 | 31.04 | 7.19 | 0 | 12.3843 | 257.439 | 73.4923 | 0 | 62 | 0 | 57.8174 | 0.58089 | 0 | 54.1077 | 0.0030321 | 0 | 52.1052 | 0.0022847 | 50.5443 | 50.5415 | 113504 | 32.0299 | 90974.9 | 87553.1 | 85580.9 | 0 | 0 | 85500.4 | 600.172 | 0 | 0 | 0 | 13031.5 | 72468.8 | 660 | 70030.2 | 68629.5938
6546 | 2006-09-30 17:00 | 2 | 0 | 2 | 30.21 | 7.19 | 0 | 0.15419 | 266.162 | 88.2391 | 0 | 2 | 0 | 1.9185 | 0.018738 | 0 | 1.7954 | 9.7808e-05 | 0 | 1.729 | 7.3701e-05 | 1.6772 | 1.6771 | 3766.43 | 30.2428 | 684.028 | 687.502 | 683.955 | 0 | 0 | 683.925 | 249.445 | 0 | 0 | 0 | 683.925 | 0 | 660 | 0 | 0
6547 | 2006-09-30 18:00 | 0 | 0 | 0 | 29.38 | 8.83 | 0
6548 | 2006-09-30 19:00 | 0 | 0 | 0 | 28.56 | 8.83 | 0
6549 | 2006-09-30 20:00 | 0 | 0 | 0 | 27.61 | 8.83 | 0
6550 | 2006-09-30 21:00 | 0 | 0 | 0 | 27.96 | 8.17 | 0
6551 | 2006-09-30 22:00 | 0 | 0 | 0 | 27.81 | 7 | 0
6552 | 2006-09-30 23:00 | 0 | 0 | 0 | 27.66 | 5.84 | 0
6553 | 2008-10-01 | 0 | 0 | 0 | 27.5 | 4.68 | 0
6554 | 2008-10-01 01:00 | 0 | 0 | 0 | 27.35 | 3.52 | 0
6555 | 2008-10-01 02:00 | 0 | 0 | 0 | 27.2 | 2.35 | 0
6556 | 2008-10-01 03:00 | 0 | 0 | 0 | 26.55 | 0.69 | 0
6557 | 2008-10-01 04:00 | 0 | 0 | 0 | 26.28 | 0.69 | 0
6558 | 2008-10-01 05:00 | 2 | 60 | 1 | 25.81 | 0.69 | 0 | -3.7996 | 91.5958 | 90 | 0 | 2 | 0 | 0.70107 | 0.018738 | 0 | 0.65609 | 0 | 0 | 0.63181 | 0 | 0.61285 | 0.61281 | 1376.22 | 25.8284 | 91.8643 | 91.9542 | 91.1671 | 0 | 0 | 91.1636 | 96.1204 | 0 | 0 | 0 | 91.1636 | 0 | 660 | 0 | 0
6559 | 2008-10-01 06:00 | 116 | 531 | 37 | 25.34 | 1.6 | 0 | 8.4721 | 100.203 | 78.0201 | 0 | 116 | 111.302 | 43.7262 | 1.0868 | 45.947 | 40.9207 | 0.0056729 | 37.1765 | 39.4062 | 0.0042746 | 74.2893 | 74.273 | 166801 | 27.4362 | 141127 | 138863 | 120463 | 0 | 0 | 120296 | 629.312 | 0 | 0 | 0 | 3779.01 | 116517 | 660 | 112992 | 110731.6953
6560 | 2008-10-01 07:00 | 339 | 806 | 58 | 24.87 | 1.6 | 0 | 20.397 | 109.578 | 63.3457 | 0 | 339 | 361.693 | 70.6688 | 3.1762 | 329.747 | 66.1346 | 0.016578 | 309.482 | 63.687 | 0.012492 | 361.986 | 361.905 | 812750 | 35.084 | 772852 | 735474 | 683706 | 0 | 0 | 679514 | 672.104 | 0 | 0 | 0 | 712.51 | 678802 | 676.072 | 669359 | 655972.125
6561 | 2008-10-01 08:00 | 542 | 904 | 69 | 26.79 | 1.6 | 0 | 31.5734 | 120.7 | 48.8251 | 0 | 542 | 594.748 | 82.1484 | 5.0781 | 594.748 | 76.8776 | 0.026506 | 579.317 | 74.0324 | 0.019973 | 633.768 | 633.767 | 1423280 | 44.6768 | 1397440 | 1278260 | 1247620 | 0 | 0 | 1234060 | 667.482 | 0 | 0 | 0 | 0 | 1234060 | 667.482 | 1215930 | 1191607.75
6562 | 2008-10-01 09:00 | 706 | 953 | 77 | 28.7 | 3.22 | 0 | 41.3444 | 134.868 | 34.6613 | 0 | 706 | 783.201 | 91.4411 | 6.6147 | 783.201 | 85.5741 | 0.034526 | 774.752 | 82.4071 | 0.026016 | 831.47 | 831.466 | 1867250 | 49.7671 | 1861600 | 1665110 | 1626860 | 0 | 0 | 1603130 | 656.452 | 0 | 0 | 0 | 629.496 | 1602500 | 660.198 | 1575210 | 1543706
6563 | 2008-10-01 10:00 | 816 | 977 | 85 | 30.62 | 3.22 | 0 | 48.6035 | 153.474 | 21.5787 | 0 | 816 | 906.172 | 100.499 | 7.6453 | 906.172 | 94.0504 | 0.039906 | 902.757 | 90.5697 | 0.03007 | 963.556 | 963.553 | 2163900 | 55.0338 | 2173700 | 1897210 | 1855980 | 0 | 0 | 1823940 | 642.223 | 0 | 0 | 0 | 16909.3 | 1807030 | 660 | 1772570 | 1737114.125
6564 | 2008-10-01 11:00 | 860 | 986 | 87 | 30.99 | 3.22 | 0 | 51.8298 | 176.434 | 13.2968 | 0 | 860 | 956.879 | 102.733 | 8.0575 | 956.879 | 96.1416 | 0.042058 | 955.561 | 92.5835 | 0.031691 | 1016.73 | 1016.73 | 2283310 | 56.7511 | 2299600 | 1991070 | 1946770 | 0 | 0 | 1911160 | 638.116 | 0 | 0 | 0 | 27267.5 | 1883890 | 660 | 1846510 | 1809583.875
6565 | 2008-10-01 12:00 | 835 | 981 | 85 | 31.36 | 3.59 | 0 | 50.0135 | 200.121 | 18.3025 | 0 | 835 | 929.343 | 100.505 | 7.8233 | 929.343 | 94.0563 | 0.040835 | 926.867 | 90.5754 | 0.03077 | 986.949 | 986.944 | 2216420 | 55.7631 | 2229060 | 1938980 | 1895550 | 0 | 0 | 1862030 | 640.597 | 0 | 0 | 0 | 20496.2 | 1841530 | 660 | 1805780 | 1769662.5
6566 | 2008-10-01 13:00 | 744 | 761 | 219 | 31.73 | 3.59 | 0 | 43.7537 | 220.122 | 30.6617 | 0 | 744 | 653.018 | 254.679 | 6.9707 | 653.018 | 238.339 | 0.036385 | 647.712 | 229.518 | 0.027417 | 850.939 | 850.937 | 1910990 | 52.7702 | 1907550 | 1681600 | 1641420 | 0 | 0 | 1616760 | 648.338 | 0 | 0 | 0 | 7177.6 | 1609580 | 660 | 1582060 | 1550421.75
6567 | 2008-10-01 14:00 | 284 | 170 | 188 | 32.01 | 3.59 | 0 | 34.5657 | 235.439 | 44.6331 | 0 | 284 | 120.412 | 193.572 | 2.6609 | 120.412 | 181.152 | 0.013889 | 117.972 | 174.448 | 0.010466 | 283.657 | 283.648 | 637004 | 39.0235 | 594279 | 555705 | 542002 | 0 | 0 | 539314 | 655.588 | 0 | 0 | 0 | 330.678 | 538984 | 660 | 531812 | 521176.2188
6568 | 2008-10-01 15:00 | 349 | 498 | 149 | 32.28 | 4.49 | 0 | 23.705 | 247.279 | 59.0812 | 0 | 349 | 255.615 | 165.368 | 3.2699 | 255.615 | 154.757 | 0.017067 | 243.522 | 149.03 | 0.012861 | 380.788 | 380.775 | 855125 | 41.155 | 813494 | 754202 | 736623 | 0 | 0 | 731733 | 659.381 | 0 | 0 | 0 | 19.6951 | 731713 | 660.577 | 722180 | 707736.5
6569 | 2008-10-01 16:00 | 177 | 452 | 83 | 32.55 | 4.49 | 0 | 11.9382 | 257.029 | 73.7228 | 0 | 177 | 127.368 | 91.366 | 1.6583 | 127.368 | 85.5038 | 0.008656 | 111.015 | 82.3393 | 0.0065225 | 187.56 | 187.556 | 421203 | 36.9215 | 381481 | 359640 | 351110 | 0 | 0 | 349945 | 646.129 | 0 | 0 | 0 | 2581.41 | 347364 | 660 | 341404 | 334576.125
6570 | 2008-10-01 17:00 | 1 | 171 | 0 | 31.69 | 4.49 | 0 | -0.27889 | 265.747 | 88.4568 | 0 | 1 | 0.30954 | 0 | 0.0093692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.69 | 0 | 0 | 0 | 0 | 0 | 0 | 660 | 0 | 0 | 0 | 0 | 0 | 660 | 0 | 0
6571 | 2008-10-01 18:00 | 0 | 0 | 0 | 30.82 | 4.87 | 0
6572 | 2008-10-01 19:00 | 0 | 0 | 0 | 29.95 | 4.87 | 0
6573 | 2008-10-01 20:00 | 0 | 0 | 0 | 29.23 | 4.87 | 0
6574 | 2008-10-01 21:00 | 0 | 0 | 0 | 28.5 | 4.89 | 0
6575 | 2008-10-01 22:00 | 0 | 0 | 0 | 27.78 | 4.89 | 0
6576 | 2008-10-01 23:00 | 0 | 0 | 0 | 26.95 | 4.89 | 0
6577 | 2008-10-02 | 0 | 0 | 0 | 26.12 | 4.77 | 0
6578 | 2008-10-02 01:00 | 0 | 0 | 0 | 25.3 | 4.77 | 0
6579 | 2008-10-02 02:00 | 0 | 0 | 0 | 24.96 | 4.77 | 0
6580 | 2008-10-02 03:00 | 0 | 0 | 0 | 24.62 | 4.69 | 0
6581 | 2008-10-02 04:00 | 0 | 0 | 0 | 24.28 | 4.69 | 0
6582 | 2008-10-02 05:00 | 2 | 53 | 1 | 23.73 | 4.69 | 0 | -3.9531 | 91.9607 | 90 | 0 | 2 | 0 | 0.70217 | 0.018738 | 0 | 0.65712 | 0 | 0 | 0.6328 | 0 | 0.61381 | 0.61378 | 1378.39 | 23.7441 | 92.151 | 92.0135 | 91.3408 | 0 | 0 | 91.3372 | 95.22 | 0 | 0 | 0 | 91.3372 | 0 | 660 | 0 | 0
6583 | 2008-10-02 06:00 | 109 | 495 | 37 | 23.17 | 5.24 | 0 | 8.3103 | 100.567 | 78.0134 | 0 | 109 | 103.458 | 44.5034 | 1.0212 | 40.4711 | 41.648 | 0.0053305 | 32.7511 | 40.1066 | 0.0040167 | 70.6759 | 70.6533 | 158680 | 24.7383 | 133461 | 133288 | 115712 | 0 | 0 | 115567 | 642.003 | 0 | 0 | 0 | 1772.39 | 113795 | 660 | 110317 | 108110.6719
6584 | 2008-10-02 07:00 | 321 | 766 | 56 | 22.62 | 5.24 | 0 | 20.2146 | 109.952 | 63.3532 | 0 | 321 | 343.957 | 68.6664 | 3.0075 | 312.48 | 64.2606 | 0.015698 | 293.267 | 61.8824 | 0.011829 | 344.507 | 344.472 | 773606 | 30.2663 | 733365 | 714249 | 662222 | 0 | 0 | 658422 | 684.012 | 0 | 0 | 0 | 456.196 | 657966 | 686.363 | 648465 | 635496
6585 | 2008-10-02 08:00 | 538 | 903 | 69 | 24.03 | 5.24 | 0 | 31.3561 | 121.087 | 48.8566 | 0 | 538 | 593.011 | 82.3201 | 5.0406 | 593.011 | 77.0383 | 0.02631 | 577.596 | 74.1872 | 0.019825 | 632.249 | 632.244 | 1419860 | 38.0639 | 1393890 | 1315390 | 1283220 | 0 | 0 | 1269670 | 687.301 | 0 | 0 | 0 | 0 | 1269670 | 687.301 | 1249840 | 1224842.5
6586 | 2008-10-02 09:00 | 702 | 901 | 111 | 25.45 | 4.64 | 0 | 41.076 | 135.253 | 34.7379 | 0 | 702 | 739.148 | 135.296 | 6.5772 | 739.148 | 126.615 | 0.034331 | 731.132 | 121.929 | 0.025869 | 827.494 | 827.489 | 1858330 | 44.549 | 1852230 | 1698530 | 1657800 | 0 | 0 | 1634460 | 674.152 | 0 | 0 | 0 | 0 | 1634460 | 674.152 | 1605690 | 1573575.375
6587 | 2008-10-02 10:00 | 754 | 748 | 197 | 26.86 | 4.64 | 0 | 48.2724 | 153.799 | 21.7544 | 0 | 754 | 693.177 | 236.029 | 7.0644 | 693.177 | 220.885 | 0.036874 | 690.52 | 212.71 | 0.027785 | 876.16 | 876.153 | 1967610 | 47.0822 | 1967070 | 1783060 | 1740790 | 0 | 0 | 1714550 | 666.777 | 0 | 0 | 0 | 0 | 1714550 | 666.777 | 1683270 | 1649605.875
6588 | 2008-10-02 11:00 | 631 | 367 | 345 | 27.39 | 4.64 | 0 | 51.4473 | 176.592 | 13.6661 | 0 | 631 | 355.359 | 379.12 | 5.912 | 355.359 | 354.795 | 0.030859 | 354.841 | 341.664 | 0.023252 | 675.632 | 675.61 | 1517240 | 42.9835 | 1495280 | 1379470 | 1344310 | 0 | 0 | 1328910 | 674.198 | 0 | 0 | 0 | 0 | 1328910 | 674.198 | 1308380 | 1282209.375
6589 | 2008-10-02 12:00 | 576 | 295 | 352 | 27.92 | 5.82 | 0 | 49.6202 | 200.068 | 18.6364 | 0 | 576 | 278.635 | 385.94 | 5.3967 | 278.635 | 361.178 | 0.028169 | 277.864 | 347.811 | 0.021226 | 606.925 | 606.915 | 1362980 | 40.8958 | 1334830 | 1242830 | 1210080 | 0 | 0 | 1197700 | 678.229 | 0 | 0 | 0 | 0 | 1197700 | 678.229 | 1179830 | 1156234.625
6590 | 2008-10-02 13:00 | 549 | 401 | 274 | 28.46 | 5.82 | 0 | 43.3841 | 219.931 | 30.9012 | 0 | 549 | 343.528 | 298.364 | 5.1437 | 343.528 | 279.221 | 0.026848 | 340.687 | 268.887 | 0.020231 | 591.306 | 591.303 | 1327920 | 41.102 | 1298460 | 1207620 | 1179350 | 0 | 0 | 1167490 | 675.5 | 0 | 0 | 0 | 0 | 1167490 | 675.5 | 1150390 | 1127382.125
6591 | 2008-10-02 14:00 | 440 | 424 | 202 | 28.66 | 5.82 | 0 | 34.2283 | 235.19 | 44.8254 | 0 | 440 | 300.1 | 227.59 | 4.1225 | 300.1 | 212.987 | 0.021518 | 293.949 | 205.105 | 0.016214 | 484.098 | 484.089 | 1087140 | 39.0098 | 1050090 | 985213 | 960772 | 0 | 0 | 952904 | 676.846 | 0 | 0 | 0 | 0 | 952904 | 676.846 | 939714 | 920919.5625
6592 | 2008-10-02 15:00 | 304 | 480 | 113 | 28.86 | 7.85 | 0 | 23.3942 | 247.014 | 59.2479 | 0 | 304 | 245.968 | 128.033 | 2.8482 | 245.968 | 119.818 | 0.014867 | 234.214 | 115.383 | 0.011203 | 339.121 | 339.115 | 761565 | 35.23 | 719030 | 685660 | 669093 | 0 | 0 | 665240 | 675.386 | 0 | 0 | 0 | 0 | 665240 | 675.386 | 656081 | 642959
6593 | 2008-10-02 16:00 | 132 | 309 | 69 | 29.06 | 7.85 | 0 | 11.6451 | 256.759 | 73.8743 | 0 | 132 | 86.6884 | 77.3557 | 1.2367 | 86.6884 | 72.3924 | 0.0064554 | 75.4171 | 69.7132 | 0.0048642 | 140.781 | 140.78 | 316156 | 31.7044 | 279966 | 270748 | 264154 | 0 | 0 | 263502 | 651.1 | 0 | 0 | 0 | 743.126 | 262759 | 660 | 256917 | 251778.6719
6594 | 2008-10-02 17:00 | 8 | 78 | 4 | 27.76 | 7.85 | 0 | -0.56308 | 265.473 | 88.5992 | 0 | 8 | 1.124 | 3.3753 | 0.074954 | 0 | 3.1587 | 0 | 0 | 3.0418 | 0 | 2.9506 | 2.9504 | 6625.8 | 27.8154 | 2050.29 | 2045.54 | 2024.8 | 0 | 0 | 2024.7 | 393.731 | 0 | 0 | 0 | 2024.7 | 0 | 660 | 0 | 0
6595 | 2008-10-02 18:00 | 0 | 0 | 0 | 26.45 | 7.38 | 0
6596 | 2008-10-02 19:00 | 0 | 0 | 0 | 25.14 | 7.38 | 0
6597 | 2008-10-02 20:00 | 0 | 0 | 0 | 24.14 | 7.38 | 0
6598 | 2008-10-02 21:00 | 0 | 0 | 0 | 23.15 | 11.25 | 0
6599 | 2008-10-02 22:00 | 0 | 0 | 0 | 22.15 | 11.25 | 0
6600 | 2008-10-02 23:00 | 0 | 0 | 0 | 21.35 | 11.25 | 0
6601 | 2008-10-03 | 0 | 0 | 0 | 20.55 | 8.73 | 0
6602 | 2008-10-03 01:00 | 0 | 0 | 0 | 19.75 | 8.73 | 0
6603 | 2008-10-03 02:00 | 0 | 0 | 0 | 19.49 | 8.73 | 0
6604 | 2008-10-03 03:00 | 0 | 0 | 0 | 19.23 | 10.43 | 0
6605 | 2008-10-03 04:00 | 0 | 0 | 0 | 18.96 | 10.43 | 0
6606 | 2008-10-03 05:00 | 2 | 54 | 1 | 18.44 | 10.43 | 0 | -4.1072 | 92.3243 | 90 | 0 | 2 | 0 | 0.70328 | 0.018738 | 0 | 0.65815 | 0 | 0 | 0.6338 | 0 | 0.61478 | 0.61475 | 1380.56 | 18.4498 | 92.4433 | 91.725 | 91.0215 | 0 | 0 | 91.0179 | 95.3389 | 0 | 0 | 0 | 91.0179 | 0 | 660 | 0 | 0
6607 | 2008-10-03 06:00 | 113 | 534 | 36 | 17.91 | 7.06 | 0 | 8.1474 | 100.93 | 78.0086 | 0 | 113 | 112.883 | 43.0097 | 1.0587 | 41.6841 | 40.2502 | 0.0055262 | 33.7368 | 38.7605 | 0.0041641 | 70.3264 | 70.2958 | 157878 | 19.2982 | 132950 | 136415 | 117299 | 0 | 0 | 117148 | 646.072 | 0 | 0 | 0 | 599.592 | 116549 | 660 | 113007 | 110746.4219
6608 | 2008-10-03 07:00 | 331 | 799 | 57 | 17.39 | 7.06 | 0 | 20.0308 | 110.323 | 63.3632 | 0 | 331 | 358.641 | 69.9686 | 3.1012 | 324.728 | 65.4792 | 0.016187 | 304.75 | 63.0559 | 0.012198 | 356.783 | 356.685 | 801026 | 24.4337 | 761180 | 761309 | 702435 | 0 | 0 | 698358 | 700.882 | 0 | 0 | 0 | -45.0799 | 698403 | 703.724 | 687727 | 673972.4375
6609 | 2008-10-03 08:00 | 512 | 818 | 89 | 19.13 | 7.06 | 0 | 31.1372 | 121.47 | 48.8916 | 0 | 512 | 537.849 | 108.422 | 4.797 | 537.849 | 101.465 | 0.025039 | 523.84 | 97.7102 | 0.018867 | 602.922 | 602.921 | 1354010 | 31.0362 | 1325500 | 1291020 | 1257280 | 0 | 0 | 1245090 | 710.596 | 0 | 0 | 0 | 0 | 1245090 | 710.596 | 1224700 | 1200202.625
6610 | 2008-10-03 09:00 | 662 | 838 | 115 | 20.88 | 6.02 | 0 | 40.8062 | 135.633 | 34.8193 | 0 | 662 | 687.165 | 139.94 | 6.2024 | 687.165 | 130.961 | 0.032375 | 679.671 | 126.114 | 0.024395 | 781.636 | 781.63 | 1755340 | 37.3773 | 1744190 | 1652680 | 1611320 | 0 | 0 | 1590490 | 695.203 | 0 | 0 | 0 | 0 | 1590490 | 695.203 | 1562460 | 1531210.5
6611 | 2008-10-03 10:00 | 807 | 922 | 124 | 22.62 | 6.02 | 0 | 47.9406 | 154.116 | 21.9363 | 0 | 807 | 853.323 | 143.937 | 7.561 | 853.323 | 134.701 | 0.039466 | 849.993 | 129.716 | 0.029738 | 950.347 | 950.342 | 2134230 | 42.6781 | 2142440 | 1983520 | 1936240 | 0 | 0 | 1905390 | 683.723 | 0 | 0 | 0 | 0 | 1905390 | 683.723 | 1866960 | 1829623.875
6612 | 2008-10-03 11:00 | 850 | 985 | 86 | 23.23 | 6.02 | 0 | 51.0653 | 176.745 | 14.0362 | 0 | 850 | 952.853 | 101.988 | 7.9638 | 952.853 | 95.4443 | 0.041569 | 951.387 | 91.9119 | 0.031323 | 1012.03 | 1012.03 | 2272760 | 44.5901 | 2288470 | 2100880 | 2049810 | 0 | 0 | 2014750 | 677.925 | 0 | 0 | 0 | 0 | 2014750 | 677.925 | 1972170 | 1932724.625
6613 | 2008-10-03 12:00 | 805 | 903 | 123 | 23.85 | 9.51 | 0 | 49.228 | 200.014 | 18.971 | 0 | 805 | 851.636 | 142.93 | 7.5422 | 851.636 | 133.759 | 0.039368 | 849.19 | 128.809 | 0.029664 | 948.688 | 948.681 | 2130500 | 39.9173 | 2138510 | 2005000 | 1954870 | 0 | 0 | 1924240 | 692.366 | 0 | 0 | 0 | 0 | 1924240 | 692.366 | 1885050 | 1847347.5
6614 | 2008-10-03 13:00 | 733 | 960 | 79 | 24.47 | 9.51 | 0 | 43.0156 | 219.741 | 31.1419 | 0 | 733 | 820.512 | 94.1067 | 6.8676 | 820.512 | 88.0686 | 0.035847 | 813.604 | 84.8093 | 0.027011 | 871.487 | 871.481 | 1957130 | 39.2298 | 1956040 | 1838900 | 1791970 | 0 | 0 | 1766190 | 693.128 | 0 | 0 | 0 | 0 | 1766190 | 693.128 | 1732550 | 1697895.75
6615 | 2008-10-03 14:00 | 578 | 811 | 126 | 24.32 | 9.51 | 0 | 33.8919 | 234.943 | 45.0181 | 0 | 578 | 572.983 | 151.953 | 5.4154 | 572.983 | 142.204 | 0.028267 | 561.103 | 136.941 | 0.021299 | 677.124 | 677.115 | 1520630 | 35.7879 | 1498800 | 1429630 | 1393540 | 0 | 0 | 1377980 | 696.7 | 0 | 0 | 0 | 0 | 1377980 | 696.7 | 1355370 | 1328259.625
6616 | 2008-10-03 15:00 | 327 | 490 | 135 | 24.17 | 9.42 | 0 | 23.0845 | 246.749 | 59.4144 | 0 | 327 | 249.164 | 151.442 | 3.0637 | 249.164 | 141.725 | 0.015992 | 237.138 | 136.48 | 0.01205 | 362.421 | 362.416 | 813897 | 30.3422 | 771795 | 753263 | 733500 | 0 | 0 | 729120 | 694.167 | 0 | 0 | 0 | 0 | 729120 | 694.167 | 718395 | 704027.5625
6617 | 2008-10-03 16:00 | 161 | 404 | 81 | 24.03 | 9.42 | 0 | 11.3534 | 256.489 | 74.0249 | 0 | 161 | 111.844 | 89.7761 | 1.5084 | 111.844 | 84.0159 | 0.0078736 | 97.1168 | 80.9066 | 0.0059329 | 172.688 | 172.686 | 387809 | 26.971 | 349033 | 345722 | 336732 | 0 | 0 | 335750 | 675.346 | 0 | 0 | 0 | 0 | 335750 | 675.346 | 329348 | 322761.3125
6618 | 2008-10-03 17:00 | 9 | 97 | 4 | 22.82 | 9.42 | 0 | -0.84562 | 265.199 | 88.74 | 0 | 9 | 1.2638 | 3.3428 | 0.084323 | 0 | 3.1283 | 0 | 0 | 3.0126 | 0 | 2.9222 | 2.922 | 6562.07 | 22.8698 | 2013.77 | 2015.89 | 1996.77 | 0 | 0 | 1996.67 | 401.825 | 0 | 0 | 0 | 1996.67 | 0 | 660 | 0 | 0
6619 | 2008-10-03 18:00 | 0 | 0 | 0 | 21.61 | 8.69 | 0
6620 | 2008-10-03 19:00 | 0 | 0 | 0 | 20.4 | 8.69 | 0
6621 | 2008-10-03 20:00 | 0 | 0 | 0 | 19.86 | 8.69 | 0
6622 | 2008-10-03 21:00 | 0 | 0 | 0 | 19.32 | 10.5 | 0
6623 | 2008-10-03 22:00 | 0 | 0 | 0 | 18.78 | 10.5 | 0
6624 | 2008-10-03 23:00 | 0 | 0 | 0 | 18.21 | 10.5 | 0
6625 | 2008-10-04 | 0 | 0 | 0 | 17.64 | 9.82 | 0
6626 | 2008-10-04 01:00 | 0 | 0 | 0 | 17.07 | 9.82 | 0
6627 | 2008-10-04 02:00 | 0 | 0 | 0 | 16.51 | 9.82 | 0
6628 | 2008-10-04 03:00 | 0 | 0 | 0 | 15.94 | 11.78 | 0
6629 | 2008-10-04 04:00 | 0 | 0 | 0 | 15.38 | 11.78 | 0
6630 | 2008-10-04 05:00 | 1 | 32 | 0 | 15.19 | 11.78 | 0 | -4.2619 | 92.6865 | 90 | 0 | 1 | 0 | 0 | 0.0093692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.19 | 0 | 0 | 0 | 0 | 0 | 0 | 660 | 0 | 0 | 0 | 0 | 0 | 660 | 0 | 0
6631 | 2008-10-04 06:00 | 113 | 333 | 66 | 15 | 11.63 | 0 | 7.9835 | 101.29 | 78.0057 | 0 | 113 | 70.3251 | 73.0646 | 1.0587 | 24.2982 | 68.3767 | 0.0055262 | 19.667 | 65.8461 | 0.0041641 | 82.9517 | 82.9341 | 186254 | 16.2347 | 157919 | 164774 | 150645 | 0 | 0 | 150444 | 673.735 | 0 | 0 | 0 | 0 | 150444 | 673.735 | 145925 | 143006.8125
6632 | 2008-10-04 07:00 | 177 | 102 | 142 | 14.81 | 11.63 | 0 | 19.8456 | 110.691 | 63.3758 | 0 | 177 | 46.2015 | 146.348 | 1.6583 | 41.6731 | 136.958 | 0.008656 | 39.1072 | 131.889 | 0.0065225 | 165.873 | 165.86 | 372478 | 17.2793 | 334279 | 346525 | 332594 | 0 | 0 | 331727 | 708.816 | 0 | 0 | 0 | 0 | 331727 | 708.816 | 324464 | 317974.2188
6633 | 2008-10-04 08:00 | 532 | 704 | 171 | 16.02 | 11.63 | 0 | 30.9167 | 121.849 | 48.9302 | 0 | 532 | 461.605 | 196.285 | 4.9844 | 461.605 | 183.691 | 0.026017 | 449.554 | 176.893 | 0.019604 | 607.673 | 607.668 | 1364670 | 25.0668 | 1336570 | 1336040 | 1297590 | 0 | 0 | 1285390 | 733.186 | 0 | 0 | 0 | 0 | 1285390 | 733.186 | 1263110 | 1237851.25
6634 | 2008-10-04 09:00 | 695 | 951 | 78 | 17.23 | 8.22 | 0 | 40.5349 | 136.008 | 34.9055 | 0 | 695 | 778.569 | 93.1053 | 6.5116 | 778.569 | 87.1315 | 0.033988 | 770.029 | 83.9068 | 0.025611 | 828.343 | 828.342 | 1860250 | 32.4319 | 1854240 | 1796250 | 1751760 | 0 | 0 | 1728470 | 713.673 | 0 | 0 | 0 | 0 | 1728470 | 713.673 | 1695610 | 1661693.125
6635 | 2008-10-04 10:00 | 802 | 677 | 303 | 18.44 | 8.22 | 0 | 47.6082 | 154.427 | 22.1239 | 0 | 802 | 625.9 | 344.686 | 7.5141 | 625.9 | 322.57 | 0.039221 | 623.412 | 310.632 | 0.029554 | 906.052 | 906.039 | 2034730 | 35.0678 | 2037680 | 1951760 | 1900890 | 0 | 0 | 1873130 | 707.932 | 0 | 0 | 0 | 0 | 1873130 | 707.932 | 1835600 | 1798888.625
6636 | 2008-10-04 11:00 | 160 | 3 | 158 | 18.75 | 8.22 | 0 | 50.6839 | 176.894 | 14.4069 | 0 | 160 | 2.5038 | 148.044 | 1.4991 | 2.5038 | 138.545 | 0.0078247 | 2.4998 | 133.418 | 0.005896 | 131.846 | 131.839 | 296076 | 21.1695 | 260780 | 265644 | 258427 | 0 | 0 | 257863 | 683.867 | 0 | 0 | 0 | 0 | 257863 | 683.867 | 251538 | 246506.8281
6637 | 2008-10-04 12:00 | 597 | 315 | 360 | 19.06 | 12 | 0 | 48.837 | 199.959 | 19.3061 | 0 | 597 | 297.105 | 395.691 | 5.5934 | 297.105 | 370.303 | 0.029196 | 296.22 | 356.598 | 0.022 | 633.255 | 633.247 | 1422110 | 28.2816 | 1396240 | 1376560 | 1338590 | 0 | 0 | 1325180 | 721.353 | 0 | 0 | 0 | 0 | 1325180 | 721.353 | 1302620 | 1276572.5
6638 | 2008-10-04 13:00 | 648 | 662 | 200 | 19.37 | 12 | 0 | 42.6484 | 219.552 | 31.3836 | 0 | 648 | 564.515 | 236.19 | 6.0713 | 564.515 | 221.036 | 0.03169 | 559.678 | 212.856 | 0.023879 | 749.381 | 749.368 | 1682880 | 30.2826 | 1668310 | 1631000 | 1586360 | 0 | 0 | 1567550 | 720.155 | 0 | 0 | 0 | 0 | 1567550 | 720.155 | 1539370 | 1508583.5
6639 | 2008-10-04 14:00 | 551 | 784 | 118 | 18.93 | 12 | 0 | 33.5567 | 234.698 | 45.2112 | 0 | 551 | 551.859 | 143.462 | 5.1624 | 551.859 | 134.257 | 0.026946 | 540.285 | 129.288 | 0.020304 | 649.506 | 649.5 | 1458610 | 28.3883 | 1434190 | 1413380 | 1376870 | 0 | 0 | 1362720 | 722.104 | 0 | 0 | 0 | 0 | 1362720 | 722.104 | 1339340 | 1312557.75
6640 | 2008-10-04 15:00 | 345 | 529 | 140 | 18.49 | 10.55 | 0 | 22.7762 | 246.486 | 59.5804 | 0 | 345 | 268.119 | 156.877 | 3.2324 | 268.119 | 146.811 | 0.016872 | 255.048 | 141.378 | 0.012713 | 384.545 | 384.54 | 863581 | 24.6006 | 822059 | 823454 | 801473 | 0 | 0 | 796569 | 716.764 | 0 | 0 | 0 | 0 | 796569 | 716.764 | 783953 | 768273.5
6641 | 2008-10-04 16:00 | 88 | 48 | 79 | 18.04 | 10.55 | 0 | 11.0632 | 256.22 | 74.1745 | 0 | 88 | 12.7904 | 79.9474 | 0.82449 | 12.7904 | 74.8178 | 0.0043036 | 11.0848 | 72.0489 | 0.0032428 | 80.6429 | 80.637 | 181091 | 19.3214 | 152577 | 156984 | 152890 | 0 | 0 | 152682 | 667.854 | 0 | 0 | 0 | 0 | 152682 | 667.854 | 148171 | 145207.3438
6642 | 2008-10-04 17:00 | 5 | 11 | 5 | 17.33 | 10.55 | 0 | -1.1264 | 264.925 | 88.8792 | 0 | 5 | 0 | 4.6723 | 0.046846 | 0 | 4.3726 | 0 | 0 | 4.2107 | 0 | 4.0844 | 4.0842 | 9171.94 | 17.3949 | 3629.07 | 3692.03 | 3639.33 | 0 | 0 | 3639.1 | 475.918 | 0 | 0 | 0 | 3639.1 | 0 | 660 | 0 | 0
6643 | 2008-10-04 18:00 | 0 | 0 | 0 | 16.62 | 12.75 | 0
6644 | 2008-10-04 19:00 | 0 | 0 | 0 | 15.91 | 12.75 | 0
6645 | 2008-10-04 20:00 | 0 | 0 | 0 | 15.58 | 12.75 | 0
6646 | 2008-10-04 21:00 | 0 | 0 | 0 | 15.26 | 10.39 | 0
6647 | 2008-10-04 22:00 | 0 | 0 | 0 | 14.94 | 10.39 | 0
6648 | 2008-10-04 23:00 | 0 | 0 | 0 | 14.49 | 10.39 | 0
6649 | 2008-10-05 | 0 | 0 | 0 | 14.03 | 9.71 | 0
6650 | 2008-10-05 01:00 | 0 | 0 | 0 | 13.58 | 9.71 | 0
6651 | 2008-10-05 02:00 | 0 | 0 | 0 | 13.2 | 9.71 | 0
6652 | 2008-10-05 03:00 | 0 | 0 | 0 | 12.82 | 9.64 | 0
6653 | 2008-10-05 04:00 | 0 | 0 | 0 | 12.43 | 9.64 | 0
6654 | 2008-10-05 05:00 | 1 | 44 | 0 | 12.18 | 9.64 | 0 | -4.4173 | 93.0471 | 90 | 0 | 1 | 0 | 0 | 0.0093692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.18 | 0 | 0 | 0 | 0 | 0 | 0 | 660 | 0 | 0 | 0 | 0 | 0 | 660 | 0 | 0
6655 | 2008-10-05 06:00 | 105 | 499 | 36 | 11.93 | 4.79 | 0 | 7.8185 | 101.649 | 78.0047 | 0 | 105 | 105.416 | 44.1096 | 0.98377 | 33.865 | 41.2795 | 0.0051349 | 27.411 | 39.7517 | 0.0038693 | 65.1516 | 65.1222 | 146251 | 13.4184 | 122055 | 128857 | 109879 | 0 | 0 | 109751 | 652.317 | 0 | 0 | 0 | 347.496 | 109404 | 668.348 | 105927 | 103808.9375
6656 | 2008-10-05 07:00 | 309 | 729 | 64 | 11.68 | 4.79 | 0 | 19.659 | 111.057 | 63.3911 | 0 | 309 | 326.183 | 77.964 | 2.8951 | 293.078 | 72.9617 | 0.015111 | 275.014 | 70.2614 | 0.011387 | 334.929 | 334.927 | 752159 | 19.3351 | 711748 | 727856 | 671256 | 0 | 0 | 667653 | 712.873 | 0 | 0 | 0 | 690.961 | 666962 | 716.843 | 656313 | 643186.3125
6657 | 2008-10-05 08:00 | 504 | 845 | 73 | 13.84 | 4.79 | 0 | 30.6947 | 122.225 | 48.9724 | 0 | 504 | 554.238 | 87.3529 | 4.7221 | 554.238 | 81.7481 | 0.024648 | 539.733 | 78.7227 | 0.018573 | 599.92 | 599.917 | 1347260 | 27.5517 | 1318500 | 1303910 | 1269110 | 0 | 0 | 1257060 | 722.13 | 0 | 0 | 0 | 0 | 1257060 | 722.13 | 1235880 | 1211165.375
6658 | 2008-10-05 09:00 | 644 | 809 | 122 | 16 | 2.04 | 0 | 40.2623 | 136.377 | 34.9963 | 0 | 644 | 661.651 | 148.05 | 6.0338 | 661.651 | 138.551 | 0.031494 | 654.349 | 133.423 | 0.023732 | 764.162 | 764.15 | 1716080 | 36.9409 | 1703060 | 1616640 | 1574720 | 0 | 0 | 1554990 | 697.393 | 0 | 0 | 0 | 0 | 1554990 | 697.393 | 1527960 | 1497404.75
6659 | 2008-10-05 10:00 | 772 | 888 | 121 | 18.16 | 2.04 | 0 | 47.2753 | 154.732 | 22.3173 | 0 | 772 | 819.792 | 149.155 | 7.233 | 819.792 | 139.585 | 0.037754 | 816.473 | 134.419 | 0.028448 | 922.393 | 922.391 | 2071460 | 43.4374 | 2076330 | 1915130 | 1867720 | 0 | 0 | 1838900 | 682.035 | 0 | 0 | 0 | 0 | 1838900 | 682.035 | 1802910 | 1766855.125
6660 | 2008-10-05 11:00 | 801 | 874 | 130 | 19.63 | 2.04 | 0 | 50.3033 | 177.037 | 14.778 | 0 | 801 | 843.221 | 160.024 | 7.5047 | 843.221 | 149.756 | 0.039172 | 841.778 | 144.214 | 0.029517 | 956.441 | 956.43 | 2147900 | 45.8402 | 2156850 | 1967710 | 1920260 | 0 | 0 | 1889020 | 673.67 | 0 | 0 | 0 | 0 | 1889020 | 673.67 | 1851310 | 1814280.25
6661 | 2008-10-05 12:00 | 815 | 926 | 124 | 21.1 | 2.29 | 0 | 48.4474 | 199.903 | 19.6415 | 0 | 815 | 869.641 | 144.512 | 7.6359 | 869.641 | 135.24 | 0.039857 | 866.955 | 130.235 | 0.030033 | 967.303 | 967.299 | 2172310 | 47.1696 | 2182560 | 1978960 | 1934270 | 0 | 0 | 1902130 | 668.632 | 0 | 0 | 0 | 0 | 1902130 | 668.632 | 1863960 | 1826683.875
6662 | 2008-10-05 13:00 | 723 | 959 | 79 | 22.57 | 2.29 | 0 | 42.2825 | 219.364 | 31.6262 | 0 | 723 | 815.055 | 94.464 | 6.774 | 815.055 | 88.403 | 0.035358 | 807.947 | 85.1313 | 0.026643 | 866.312 | 866.306 | 1945510 | 45.9177 | 1943820 | 1771540 | 1730770 | 0 | 0 | 1705070 | 670.293 | 0 | 0 | 0 | 0 | 1705070 | 670.293 | 1674030 | 1640547.75
6663 | 2008-10-05 14:00 | 551 | 843 | 90 | 22.83 | 2.29 | 0 | 33.2229 | 234.453 | 45.4044 | 0 | 551 | 590.745 | 110.806 | 5.1624 | 590.745 | 103.697 | 0.026946 | 578.212 | 99.8588 | 0.020304 | 657.748 | 657.743 | 1477130 | 40.5568 | 1453470 | 1356060 | 1322450 | 0 | 0 | 1307780 | 680.37 | 0 | 0 | 0 | 0 | 1307780 | 680.37 | 1287440 | 1261691
6664 | 2008-10-05 15:00 | 362 | 779 | 64 | 23.08 | 3.17 | 0 | 22.4692 | 246.223 | 59.746 | 0 | 362 | 392.851 | 78.9688 | 3.3917 | 392.851 | 73.902 | 0.017703 | 373.508 | 71.167 | 0.01334 | 431.347 | 431.341 | 968678 | 34.0452 | 928899 | 891603 | 869128 | 0 | 0 | 862858 | 687.083 | 0 | 0 | 0 | 0 | 862858 | 687.083 | 850472 | 833462.75
6665 | 2008-10-05 16:00 | 145 | 485 | 54 | 23.33 | 3.17 | 0 | 10.7746 | 255.951 | 74.323 | 0 | 145 | 131.532 | 64.1776 | 1.3585 | 131.532 | 60.0599 | 0.0070911 | 113.77 | 57.8371 | 0.0053433 | 166.464 | 166.462 | 373831 | 27.5617 | 335494 | 331339 | 322852 | 0 | 0 | 321944 | 673.523 | 0 | 0 | 0 | 0 | 321944 | 673.523 | 315581 | 309269.6562
6666 | 2008-10-05 17:00 | 7 | 106 | 3 | 22.71 | 3.17 | 0 | -1.4052 | 264.651 | 89.0166 | 0 | 7 | 0.78907 | 2.4106 | 0.065585 | 0 | 2.2559 | 0 | 0 | 2.1724 | 0 | 2.1072 | 2.1071 | 4732.09 | 22.7636 | 1074.32 | 1072.45 | 1066.25 | 0 | 0 | 1066.2 | 311.46 | 0 | 0 | 0 | 1066.2 | 0 | 660 | 0 | 0
6667 | 2008-10-05 18:00 | 0 | 0 | 0 | 22.08 | 5.52 | 0
6668 | 2008-10-05 19:00 | 0 | 0 | 0 | 21.46 | 5.52 | 0
6669 | 2008-10-05 20:00 | 0 | 0 | 0 | 20.61 | 5.52 | 0
6670 | 2008-10-05 21:00 | 0 | 0 | 0 | 19.76 | 5.17 | 0
6671 | 2008-10-05 22:00 | 0 | 0 | 0 | 18.91 | 5.17 | 0
6672 | 2008-10-05 23:00 | 0 | 0 | 0 | 18.17 | 5.17 | 0
6673 | 2008-10-06 | 0 | 0 | 0 | 17.43 | 3.93 | 0
6674 | 2008-10-06 01:00 | 0 | 0 | 0 | 16.69 | 3.93 | 0
6675 | 2008-10-06 02:00 | 0 | 0 | 0 | 16.19 | 3.93 | 0
6676 | 2008-10-06 03:00 | 0 | 0 | 0 | 15.7 | 4.26 | 0
6677 | 2008-10-06 04:00 | 0 | 0 | 0 | 15.2 | 4.26 | 0
6678 | 2008-10-06 05:00 | 1 | 44 | 0 | 14.97 | 4.26 | 0 | -4.5732 | 93.4061 | 90 | 0 | 1 | 0 | 0 | 0.0093692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.97 | 0 | 0 | 0 | 0 | 0 | 0 | 660 | 0 | 0 | 0 | 0 | 0 | 660 | 0 | 0
6679 | 2008-10-06 06:00 | 108 | 530 | 36 | 14.75 | 5.54 | 0 | 7.6525 | 102.006 | 78.0057 | 0 | 108 | 112.361 | 43.3328 | 1.0119 | 33.2995 | 40.5525 | 0.0052816 | 26.9526 | 39.0517 | 0.0039798 | 64.0281 | 64.0486 | 143846 | 16.1443 | 119993 | 125017 | 105114 | 0 | 0 | 104988 | 636.688 | 0 | 0 | 0 | 635.507 | 104353 | 665.659 | 101032 | 99011.2891
6680 | 2008-10-06 07:00 | 323 | 796 | 57 | 14.53 | 5.54 | 0 | 19.471 | 111.42 | 63.4092 | 0 | 323 | 357.201 | 70.56 | 3.0263 | 319.739 | 66.0327 | 0.015796 | 300.01 | 63.5889 | 0.011903 | 352.703 | 352.711 | 792098 | 22.2085 | 752402 | 759587 | 698678 | 0 | 0 | 694695 | 706.826 | 0 | 0 | 0 | 1573.49 | 693122 | 711.311 | 682251 | 668606.25
6681 | 2008-10-06 08:00 | 524 | 900 | 68 | 16.77 | 5.54 | 0 | 30.4712 | 122.596 | 49.0181 | 0 | 524 | 589.728 | 81.8755 | 4.9095 | 589.728 | 76.6222 | 0.025626 | 574.254 | 73.7864 | 0.01931 | 628.618 | 628.615 | 1411700 | 30.4549 | 1385410 | 1352930 | 1317500 | 0 | 0 | 1304230 | 713.613 | 0 | 0 | 0 | 0 | 1304230 | 713.613 | 1282460 | 1256808.75
6682 | 2008-10-06 09:00 | 687 | 950 | 78 | 19.02 | 4.5 | 0 | 39.9884 | 136.74 | 35.0919 | 0 | 687 | 775.409 | 93.4625 | 6.4367 | 775.409 | 87.4657 | 0.033597 | 766.796 | 84.2287 | 0.025316 | 825.519 | 825.511 | 1853890 | 38.2483 | 1847570 | 1744130 | 1700780 | 0 | 0 | 1677560 | 693.821 | 0 | 0 | 0 | 0 | 1677560 | 693.821 | 1646830 | 1613892.875
6683 | 2008-10-06 10:00 | 793 | 975 | 82 | 21.26 | 4.5 | 0 | 46.9419 | 155.03 | 22.516 | 0 | 793 | 898.914 | 98.0278 | 7.4298 | 898.914 | 91.7381 | 0.038781 | 895.205 | 88.3429 | 0.029222 | 954.07 | 954.071 | 2142600 | 43.4828 | 2151260 | 1984300 | 1933390 | 0 | 0 | 1902480 | 682.015 | 0 | 0 | 0 | 0 | 1902480 | 682.015 | 1864170 | 1826889.625
6684 | 2008-10-06 11:00 | 835 | 983 | 85 | 22.7 | 4.5 | 0 | 49.9234 | 177.175 | 15.1493 | 0 | 835 | 946.094 | 101.422 | 7.8233 | 946.094 | 94.9142 | 0.040835 | 944.391 | 91.4014 | 0.03077 | 1004.75 | 1004.74 | 2256390 | 46.103 | 2271210 | 2070310 | 2024980 | 0 | 0 | 1990030 | 670.808 | 0 | 0 | 0 | 0 | 1990030 | 670.808 | 1948430 | 1909459.5
6685 | 2008-10-06 12:00 | 809 | 978 | 83 | 24.14 | 2.74 | 0 | 48.0593 | 199.846 | 19.9769 | 0 | 809 | 917.294 | 99.1724 | 7.5797 | 917.294 | 92.8093 | 0.039564 | 914.358 | 89.3745 | 0.029812 | 973.649 | 973.642 | 2186560 | 49.6066 | 2197580 | 1969710 | 1924460 | 0 | 0 | 1891930 | 661.093 | 0 | 0 | 0 | -26.622 | 1891950 | 661.971 | 1854250 | 1817161.25
6686 | 2008-10-06 13:00 | 718 | 958 | 79 | 25.58 | 2.74 | 0 | 41.9181 | 219.177 | 31.8695 | 0 | 718 | 812.303 | 94.6428 | 6.7271 | 812.303 | 88.5703 | 0.035113 | 805.093 | 85.2924 | 0.026458 | 863.7 | 863.695 | 1939630 | 48.1708 | 1937650 | 1747050 | 1704500 | 0 | 0 | 1679070 | 663.439 | 0 | 0 | 0 | 0 | 1679070 | 663.439 | 1649110 | 1616124.625
6687 | 2008-10-06 14:00 | 566 | 914 | 70 | 26.21 | 2.74 | 0 | 32.8905 | 234.21 | 45.5976 | 0 | 566 | 639.089 | 84.2686 | 5.303 | 639.089 | 78.8618 | 0.02768 | 625.374 | 75.9432 | 0.020857 | 680.298 | 680.293 | 1527770 | 44.0038 | 1506240 | 1382940 | 1349900 | 0 | 0 | 1334150 | 670.051 | 0 | 0 | 0 | 0 | 1334150 | 670.051 | 1313680 | 1287407.875
6688 | 2008-10-06 15:00 | 369 | 824 | 58 | 26.83 | 3.89 | 0 | 22.1639 | 245.961 | 59.9108 | 0 | 369 | 413.296 | 70.1679 | 3.4572 | 413.296 | 65.6658 | 0.018046 | 392.743 | 63.2355 | 0.013598 | 442.312 | 442.309 | 993314 | 37.5527 | 954034 | 900870 | 880034 | 0 | 0 | 873432 | 677.351 | 0 | 0 | 0 | 0 | 873432 | 677.351 | 861319 | 844093
6689 | 2008-10-06 16:00 | 148 | 553 | 47 | 27.46 | 3.89 | 0 | 10.4879 | 255.682 | 74.4702 | 0 | 148 | 148.558 | 57.2095 | 1.3866 | 148.558 | 53.5389 | 0.0072378 | 128.243 | 51.5574 | 0.0054538 | 174.411 | 174.41 | 391681 | 31.6881 | 352784 | 341421 | 333273 | 0 | 0 | 332265 | 659.755 | 0 | 0 | 0 | -7.1561 | 332272 | 660.664 | 326253 | 319727.7812
6690 | 2008-10-06 17:00 | 7 | 114 | 2 | 26.8 | 3.89 | 0 | -1.6819 | 264.376 | 89.1523 | 0 | 7 | 0.8503 | 1.9055 | 0.065585 | 0 | 1.7833 | 0 | 0 | 1.7173 | 0 | 1.6658 | 1.6657 | 3740.61 | 26.8404 | 674.693 | 675.941 | 672.572 | 0 | 0 | 672.543 | 247.497 | 0 | 0 | 0 | 672.543 | 0 | 660 | 0 | 0
6691 | 2008-10-06 18:00 | 0 | 0 | 0 | 26.14 | 5.89 | 0
6692 | 2008-10-06 19:00 | 0 | 0 | 0 | 25.48 | 5.89 | 0
6693 | 2008-10-06 20:00 | 0 | 0 | 0 | 24.5 | 5.89 | 0
6694 | 2008-10-06 21:00 | 0 | 0 | 0 | 23.51 | 4.86 | 0
6695 | 2008-10-06 22:00 | 0 | 0 | 0 | 22.52 | 4.86 | 0
6696 | 2008-10-06 23:00 | 0 | 0 | 0 | 21.86 | 4.86 | 0
6697 | 2008-10-07 | 0 | 0 | 0 | 21.2 | 7.76 | 0
6698 | 2008-10-07 01:00 | 0 | 0 | 0 | 20.54 | 7.76 | 0
6699 | 2008-10-07 02:00 | 0 | 0 | 0 | 19.93 | 7.76 | 0
6700 | 2008-10-07 03:00 | 0 | 0 | 0 | 19.33 | 5.8 | 0
6701 | 2008-10-07 04:00 | 0 | 0 | 0 | 18.72 | 5.8 | 0
6702 | 2008-10-07 05:00 | 1 | 38 | 0 | 18.07 | 5.8 | 0 | -4.7298 | 93.7634 | 90 | 0 | 1 | 0 | 0 | 0.0093692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.07 | 0 | 0 | 0 | 0 | 0 | 0 | 660 | 0 | 0 | 0 | 0 | 0 | 660 | 0 | 0
6703 | 2008-10-07 06:00 | 102 | 501 | 36 | 17.43 | 9.35 | 0 | 7.4855 | 102.36 | 78.0089 | 0 | 102 | 105.256 | 44.5224 | 0.95566 | 28.5969 | 41.6657 | 0.0049882 | 23.1445 | 40.1237 | 0.0037587 | 61.3738 | 61.329 | 137736 | 18.479 | 114194 | 117753 | 100408 | 0 | 0 | 100299 | 650.396 | 0 | 0 | 0 | 411.74 | 99887.5 | 660.622 | 96722 | 94787.5625
6704 | 2008-10-07 07:00 | 301 | 720 | 63 | 16.78 | 9.35 | 0 | 19.2817 | 111.78 | 63.43 | 0 | 301 | 322.383 | 77.2786 | 2.8201 | 287.397 | 72.3203 | 0.01472 | 269.64 | 69.6438 | 0.011092 | 329.116 | 329.087 | 739042 | 22.4089 | 698640 | 705331 | 648268 | 0 | 0 | 644802 | 702.813 | 0 | 0 | 0 | 915.324 | 643887 | 708.469 | 633864 | 621186.5
6705 | 2008-10-07 08:00 | 488 | 787 | 92 | 19.25 | 9.35 | 0 | 30.2462 | 122.964 | 49.0675 | 0 | 488 | 515.066 | 112.598 | 4.5722 | 515.016 | 105.373 | 0.023865 | 501.463 | 101.474 | 0.017983 | 584.866 | 584.862 | 1313450 | 29.2539 | 1283450 | 1259890 | 1226470 | 0 | 0 | 1214970 | 714.591 | 0 | 0 | 0 | 0 | 1214970 | 714.591 | 1195010 | 1171106.125
6706 | 2008-10-07 09:00 | 682 | 899 | 109 | 21.72 | 4.85 | 0 | 39.7133 | 137.098 | 35.1921 | 0 | 682 | 732.877 | 134.326 | 6.3898 | 732.877 | 125.707 | 0.033353 | 724.682 | 121.055 | 0.025132 | 820.389 | 820.385 | 1842380 | 40.3976 | 1835490 | 1715820 | 1674240 | 0 | 0 | 1651400 | 688.584 | 0 | 0 | 0 | 0 | 1651400 | 688.584 | 1621650 | 1589220.375
6707 | 2008-10-07 10:00 | 790 | 974 | 84 | 24.19 | 4.85 | 0 | 46.6083 | 155.321 | 22.72 | 0 | 790 | 896.16 | 100.49 | 7.4017 | 896.16 | 94.0427 | 0.038634 | 892.391 | 90.5623 | 0.029112 | 953.493 | 953.491 | 2141300 | 45.898 | 2149890 | 1960880 | 1913560 | 0 | 0 | 1882590 | 673.831 | 0 | 0 | 0 | 0 | 1882590 | 673.831 | 1845110 | 1808207.5
6708 | 2008-10-07 11:00 | 831 | 983 | 85 | 25.49 | 4.85 | 0 | 49.5444 | 177.308 | 15.5205 | 0 | 831 | 944.655 | 101.609 | 7.7858 | 944.655 | 95.09 | 0.040639 | 942.868 | 91.5708 | 0.030623 | 1003.43 | 1003.43 | 2253440 | 48.3349 | 2268100 | 2045840 | 1997340 | 0 | 0 | 1962820 | 665.786 | 0 | 0 | 0 | 0 | 1962820 | 665.786 | 1922310 | 1883862.875
6709 | 2008-10-07 12:00 | 804 | 977 | 84 | 26.8 | 6.18 | 0 | 47.6727 | 199.788 | 20.3121 | 0 | 804 | 913.32 | 100.497 | 7.5328 | 913.32 | 94.0493 | 0.039319 | 910.292 | 90.5686 | 0.029628 | 970.864 | 970.859 | 2180310 | 47.0815 | 2190990 | 1987600 | 1940290 | 0 | 0 | 1908030 | 669.1 | 0 | 0 | 0 | 0 | 1908030 | 669.1 | 1869630 | 1832241.375
6710 | 2008-10-07 13:00 | 712 | 957 | 78 | 28.1 | 6.18 | 0 | 41.5553 | 218.99 | 32.1131 | 0 | 712 | 809.534 | 93.6801 | 6.6709 | 809.534 | 87.6694 | 0.03482 | 802.222 | 84.4248 | 0.026237 | 860.073 | 860.067 | 1931500 | 46.067 | 1929100 | 1756900 | 1714060 | 0 | 0 | 1688820 | 669.652 | 0 | 0 | 0 | 0 | 1688820 | 669.652 | 1658360 | 1625190.125
6711 | 2008-10-07 14:00 | 562 | 913 | 71 | 28.49 | 6.18 | 0 | 32.5597 | 233.968 | 45.7908 | 0 | 562 | 636.155 | 85.5777 | 5.2655 | 636.155 | 80.0869 | 0.027484 | 622.346 | 77.1229 | 0.02071 | 678.505 | 678.5 | 1523740 | 42.664 | 1502040 | 1387920 | 1354490 | 0 | 0 | 1338860 | 675.248 | 0 | 0 | 0 | 0 | 1338860 | 675.248 | 1318060 | 1291694.125
6712 | 2008-10-07 15:00 | 356 | 809 | 55 | 28.87 | 3.8 | 0 | 21.8602 | 245.7 | 60.075 | 0 | 356 | 403.281 | 66.9211 | 3.3354 | 403.281 | 62.6273 | 0.01741 | 383.025 | 60.3096 | 0.013119 | 430.047 | 430.045 | 965775 | 39.3573 | 925938 | 866694 | 845238 | 0 | 0 | 839010 | 669.981 | 0 | 0 | 0 | 0 | 839010 | 669.981 | 827684 | 811130.1875
6713 | 2008-10-07 16:00 | 140 | 516 | 48 | 29.26 | 3.8 | 0 | 10.2031 | 255.414 | 74.6161 | 0 | 140 | 137.782 | 58.3846 | 1.3117 | 137.782 | 54.6385 | 0.0068466 | 118.702 | 52.6164 | 0.005159 | 166.184 | 166.182 | 373204 | 33.3126 | 334888 | 321405 | 313523 | 0 | 0 | 312609 | 652.079 | 0 | 0 | 0 | 529.727 | 312080 | 660 | 306064 | 299943.1562
6714 | 2008-10-07 17:00 | 6 | 101 | 2 | 28.53 | 3.8 | 0 | -1.9565 | 264.102 | 89.2859 | 0 | 6 | 0.57298 | 1.6159 | 0.056215 | 0 | 1.5122 | 0 | 0 | 1.4563 | 0 | 1.4126 | 1.4125 | 3172.06 | 28.5644 | 486.035 | 487.916 | 485.673 | 0 | 0 | 485.651 | 209.529 | 0 | 0 | 0 | 485.651 | 0 | 660 | 0 | 0
6715 | 2008-10-07 18:00 | 0 | 0 | 0 | 27.81 | 4.87 | 0
6716 | 2008-10-07 19:00 | 0 | 0 | 0 | 27.09 | 4.87 | 0
6717 | 2008-10-07 20:00 | 0 | 0 | 0 | 26.37 | 4.87 | 0
6718 | 2008-10-07 21:00 | 0 | 0 | 0 | 25.66 | 4.31 | 0
6719 | 2008-10-07 22:00 | 0 | 0 | 0 | 24.94 | 4.31 | 0
6720 | 2008-10-07 23:00 | 0 | 0 | 0 | 24.26 | 4.31 | 0
6721 | 2008-10-08 | 0 | 0 | 0 | 23.58 | 5.45 | 0
6722 | 2008-10-08 01:00 | 0 | 0 | 0 | 22.9 | 5.45 | 0
6723 | 2008-10-08 02:00 | 0 | 0 | 0 | 22.32 | 5.45 | 0
6724 | 2008-10-08 03:00 | 0 | 0 | 0 | 21.74 | 1.64 | 0
6725 | 2008-10-08 04:00 | 0 | 0 | 0 | 21.16 | 1.64 | 0
6726 | 2008-10-08 05:00 | 1 | 36 | 0 | 20.41 | 1.64 | 0 | -4.8871 | 94.1187 | 90 | 0 | 1 | 0 | 0 | 0.0093692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.41 | 0 | 0 | 0 | 0 | 0 | 0 | 660 | 0 | 0 | 0 | 0 | 0 | 660 | 0 | 0
6727 | 2008-10-08 06:00 | 101 | 515 | 34 | 19.66 | 3.01 | 0 | 7.3173 | 102.712 | 78.0141 | 0 | 101 | 109.245 | 41.6461 | 0.94629 | 27.0248 | 38.974 | 0.0049393 | 21.8694 | 37.5316 | 0.0037219 | 57.6226 | 57.6348 | 129443 | 21.1407 | 106761 | 108516 | 92571 | 0 | 0 | 92470.7 | 632.943 | 0 | 0 | 0 | 1771.12 | 90699.6 | 660 | 87782.3 | 86026.6094
6728 | 2008-10-08 07:00 | 316 | 792 | 57 | 18.91 | 3.01 | 0 | 19.091 | 112.137 | 63.4537 | 0 | 316 | 353.908 | 70.9486 | 2.9607 | 314.191 | 66.3964 | 0.015454 | 294.75 | 63.9391 | 0.011645 | 347.94 | 347.906 | 781299 | 27.8484 | 741640 | 729589 | 669121 | 0 | 0 | 665246 | 687.724 | 0 | 0 | 0 | 1109.18 | 664136 | 694.183 | 654276 | 641190.4375
6729 | 2008-10-08 08:00 | 517 | 897 | 69 | 21.31 | 3.01 | 0 | 30.0198 | 123.327 | 49.1204 | 0 | 517 | 586.056 | 83.3583 | 4.8439 | 585.957 | 78.0099 | 0.025283 | 570.489 | 75.1228 | 0.019052 | 626.262 | 626.261 | 1406430 | 37.3998 | 1379930 | 1306100 | 1271110 | 0 | 0 | 1257920 | 690.22 | 0 | 0 | 0 | 0 | 1257920 | 690.22 | 1238210 | 1213445.75
6730 | 2008-10-08 09:00 | 678 | 898 | 109 | 23.71 | 1.86 | 0 | 39.4372 | 137.45 | 35.2969 | 0 | 678 | 731.072 | 134.568 | 6.3523 | 731.072 | 125.933 | 0.033157 | 722.839 | 121.273 | 0.024984 | 818.812 | 818.811 | 1838840 | 46.4205 | 1831770 | 1664760 | 1627320 | 0 | 0 | 1604340 | 666.947 | 0 | 0 | 0 | 0 | 1604340 | 666.947 | 1576780 | 1545240
6731 | 2008-10-08 10:00 | 733 | 790 | 164 | 26.11 | 1.86 | 0 | 46.2745 | 155.605 | 22.9291 | 0 | 733 | 725.158 | 202.159 | 6.8676 | 725.158 | 189.188 | 0.035847 | 722.047 | 182.186 | 0.027011 | 877.133 | 877.125 | 1969800 | 50.4378 | 1969360 | 1756500 | 1715540 | 0 | 0 | 1689280 | 656.507 | 0 | 0 | 0 | 843.323 | 1688440 | 660 | 1658240 | 1625077.25
6732 | 2008-10-08 11:00 | 809 | 909 | 123 | 27.29 | 1.86 | 0 | 49.1665 | 177.437 | 15.8914 | 0 | 809 | 872.021 | 144.226 | 7.5797 | 872.021 | 134.972 | 0.039564 | 870.288 | 129.977 | 0.029812 | 970.286 | 970.279 | 2179000 | 54.2016 | 2189620 | 1919080 | 1876800 | 0 | 0 | 1844260 | 644.119 | 0 | 0 | 0 | 11647.6 | 1832610 | 660 | 1797200 | 1761253.125
6733 | 2008-10-08 12:00 | 800 | 977 | 84 | 28.47 | 0.89 | 0 | 47.2879 | 199.728 | 20.6469 | 0 | 800 | 911.865 | 100.683 | 7.4954 | 911.865 | 94.2233 | 0.039123 | 908.736 | 90.7362 | 0.02948 | 969.517 | 969.515 | 2177290 | 57.1701 | 2187810 | 1889260 | 1846890 | 0 | 0 | 1814410 | 634.546 | 0 | 0 | 0 | 32327 | 1782080 | 660 | 1748540 | 1713571.5
6734 | 2008-10-08 13:00 | 707 | 955 | 79 | 29.65 | 0.89 | 0 | 41.1943 | 218.805 | 32.3571 | 0 | 707 | 805.464 | 95.0004 | 6.624 | 805.464 | 88.905 | 0.034575 | 798.061 | 85.6146 | 0.026053 | 857.19 | 857.185 | 1925020 | 55.0248 | 1922280 | 1675710 | 1637040 | 0 | 0 | 1611740 | 638.509 | 0 | 0 | 0 | 19486.7 | 1592250 | 660 | 1565300 | 1533998
6735 | 2008-10-08 14:00 | 555 | 911 | 70 | 30.05 | 0.89 | 0 | 32.2306 | 233.727 | 45.9836 | 0 | 555 | 631.898 | 84.6077 | 5.1999 | 631.898 | 79.1791 | 0.027142 | 618.023 | 76.2487 | 0.020452 | 673.464 | 673.46 | 1512420 | 49.9861 | 1490240 | 1328920 | 1299330 | 0 | 0 | 1283800 | 649.033 | 0 | 0 | 0 | 4500.33 | 1279300 | 660 | 1260520 | 1235312.5
6736 | 2008-10-08 15:00 | 344 | 782 | 57 | 30.45 | 4.08 | 0 | 21.5584 | 245.44 | 60.2382 | 0 | 344 | 387.715 | 71.6587 | 3.223 | 387.715 | 67.0609 | 0.016823 | 368.048 | 64.579 | 0.012677 | 419.66 | 419.658 | 942448 | 40.4974 | 902168 | 839676 | 819626 | 0 | 0 | 813692 | 665.945 | 0 | 0 | 0 | 0 | 813692 | 665.945 | 802872 | 786814.875
6737 | 2008-10-08 16:00 | 141 | 547 | 46 | 30.85 | 4.08 | 0 | 9.9203 | 255.146 | 74.7604 | 0 | 141 | 144.948 | 56.4758 | 1.3211 | 144.948 | 52.8522 | 0.0068955 | 124.623 | 50.8962 | 0.0051959 | 170.259 | 170.255 | 382350 | 34.9262 | 343739 | 327230 | 319630 | 0 | 0 | 318662 | 645.313 | 0 | 0 | 0 | 1620.71 | 317041 | 660 | 311025 | 304804.125
6738 | 2008-10-08 17:00 | 5 | 101 | 1 | 29.8 | 4.08 | 0 | -2.2287 | 263.827 | 89.4176 | 0 | 5 | 0.46735 | 0.95067 | 0.046846 | 0 | 0.88967 | 0 | 0 | 0.85675 | 0 | 0.83105 | 0.83099 | 1866.2 | 29.8199 | 168.751 | 169.701 | 168.906 | 0 | 0 | 168.899 | 124.36 | 0 | 0 | 0 | 168.899 | 0 | 660 | 0 | 0
6739 | 2008-10-08 18:00 | 0 | 0 | 0 | 28.75 | 6.48 | 0
6740 | 2008-10-08 19:00 | 0 | 0 | 0 | 27.7 | 6.48 | 0
6741 | 2008-10-08 20:00 | 0 | 0 | 0 | 26.77 | 6.48 | 0
6742 | 2008-10-08 21:00 | 0 | 0 | 0 | 25.84 | 6.99 | 0
6743 | 2008-10-08 22:00 | 0 | 0 | 0 | 24.91 | 6.99 | 0
6744 | 2008-10-08 23:00 | 0 | 0 | 0 | 23.94 | 6.99 | 0
6745 | 2008-10-09 | 0 | 0 | 0 | 22.97 | 8.43 | 0
6746 | 2008-10-09 01:00 | 0 | 0 | 0 | 21.99 | 8.43 | 0
6747 | 2008-10-09 02:00 | 0 | 0 | 0 | 21.41 | 8.43 | 0
6748 | 2008-10-09 03:00 | 0 | 0 | 0 | 20.83 | 7.93 | 0
6749 | 2008-10-09 04:00 | 0 | 0 | 0 | 20.24 | 7.93 | 0
6750 | 2008-10-09 05:00 | 1 | 30 | 1 | 19.79 | 7.93 | 0 | -5.045 | 94.472 | 90 | 0 | 1 | 0 | 1.0031 | 0.0093692 | 0 | 0.93873 | 0 | 0 | 0.90399 | 0 | 0.87687 | 0.87682 | 1969.11 | 19.8064 | 187.831 | 186.683 | 185.799 | 0 | 0 | 185.791 | 130.806 | 0 | 0 | 0 | 185.791 | 0 | 660 | 0 | 0
6751 | 2008-10-09 06:00 | 93 | 473 | 33 | 19.33 | 9.08 | 0 | 7.1482 | 103.061 | 78.0216 | 0 | 93 | 100.073 | 40.7994 | 0.87134 | 22.427 | 38.1817 | 0.0045481 | 18.1454 | 36.7686 | 0.0034271 | 53.2699 | 53.2861 | 119679 | 20.2568 | 97728.8 | 99926.8 | 86078.9 | 0 | 0 | 85993.2 | 634.158 | 0 | 0 | 0 | 1470.36 | 84522.9 | 660 | 81766 | 80130.7031
6752 | 2008-10-09 07:00 | 307 | 778 | 55 | 18.87 | 9.08 | 0 | 18.8991 | 112.491 | 63.4802 | 0 | 307 | 347.388 | 68.9278 | 2.8763 | 307.119 | 64.5053 | 0.015014 | 288.084 | 62.118 | 0.011313 | 339.707 | 339.616 | 762685 | 24.777 | 722928 | 721890 | 660308 | 0 | 0 | 656636 | 698.448 | 0 | 0 | 0 | 553.865 | 656082 | 703.303 | 646037 | 633116.375
6753 | 2008-10-09 08:00 | 514 | 896 | 69 | 20.89 | 9.08 | 0 | 29.792 | 123.686 | 49.177 | 0 | 514 | 585.499 | 83.5324 | 4.8158 | 585.372 | 78.1728 | 0.025137 | 569.868 | 75.2796 | 0.018941 | 625.812 | 625.808 | 1405410 | 31.7748 | 1378870 | 1338740 | 1303700 | 0 | 0 | 1290480 | 707.854 | 0 | 0 | 0 | 0 | 1290480 | 707.854 | 1269260 | 1243878.875
6754 | 2008-10-09 09:00 | 674 | 948 | 76 | 22.9 | 6.93 | 0 | 39.16 | 137.796 | 35.4063 | 0 | 674 | 771.841 | 91.7088 | 6.3149 | 771.841 | 85.8246 | 0.032961 | 763.085 | 82.6483 | 0.024837 | 820.385 | 820.382 | 1842380 | 39.2352 | 1835480 | 1724990 | 1680540 | 0 | 0 | 1657720 | 691.527 | 0 | 0 | 0 | 0 | 1657720 | 691.527 | 1627690 | 1595135
6755 | 2008-10-09 10:00 | 780 | 973 | 83 | 24.92 | 6.93 | 0 | 45.9406 | 155.883 | 23.1429 | 0 | 780 | 891.864 | 99.7188 | 7.308 | 891.864 | 93.3206 | 0.038145 | 887.962 | 89.8669 | 0.028743 | 948.522 | 948.519 | 2130140 | 43.8066 | 2138130 | 1969270 | 1919650 | 0 | 0 | 1889110 | 681.165 | 0 | 0 | 0 | 0 | 1889110 | 681.165 | 1851320 | 1814289.625
6756 | 2008-10-09 11:00 | 821 | 982 | 84 | 25.6 | 6.93 | 0 | 48.7898 | 177.56 | 16.262 | 0 | 821 | 940.471 | 100.84 | 7.6921 | 940.471 | 94.3699 | 0.04015 | 938.511 | 90.8774 | 0.030254 | 998.536 | 998.53 | 2242450 | 45.4824 | 2256510 | 2062860 | 2013760 | 0 | 0 | 1979830 | 677.034 | 0 | 0 | 0 | 0 | 1979830 | 677.034 | 1938620 | 1899847.875
6757 | 2008-10-09 12:00 | 795 | 976 | 84 | 26.29 | 10.07 | 0 | 46.9048 | 199.667 | 20.9812 | 0 | 795 | 909.123 | 100.869 | 7.4485 | 909.123 | 94.397 | 0.038879 | 905.895 | 90.9035 | 0.029296 | 966.923 | 966.919 | 2171450 | 42.1119 | 2181660 | 2025380 | 1975730 | 0 | 0 | 1943920 | 686.52 | 0 | 0 | 0 | 0 | 1943920 | 686.52 | 1904040 | 1865959.25
6758 | 2008-10-09 13:00 | 701 | 955 | 78 | 26.98 | 10.07 | 0 | 40.8351 | 218.62 | 32.6012 | 0 | 701 | 802.651 | 94.0342 | 6.5678 | 802.651 | 88.0008 | 0.034282 | 795.145 | 84.7439 | 0.025832 | 853.517 | 853.515 | 1916770 | 40.9462 | 1913620 | 1784850 | 1740900 | 0 | 0 | 1716100 | 686.712 | 0 | 0 | 0 | 0 | 1716100 | 686.712 | 1684290 | 1650599.625
6759 | 2008-10-09 14:00 | 551 | 910 | 71 | 26.96 | 10.07 | 0 | 31.9035 | 233.488 | 46.176 | 0 | 551 | 628.912 | 85.9209 | 5.1624 | 628.912 | 80.408 | 0.026946 | 614.945 | 77.4322 | 0.020304 | 671.626 | 671.621 | 1508290 | 37.9499 | 1485930 | 1403440 | 1367320 | 0 | 0 | 1352090 | 690.16 | 0 | 0 | 0 | 0 | 1352090 | 690.16 | 1330330 | 1303724.375
6760 | 2008-10-09 15:00 | 336 | 769 | 57 | 26.93 | 9.01 | 0 | 21.2586 | 245.18 | 60.4003 | 0 | 336 | 380.08 | 71.8326 | 3.1481 | 380.08 | 67.2237 | 0.016432 | 360.609 | 64.7358 | 0.012382 | 412.597 | 412.595 | 926587 | 34.1376 | 886029 | 849981 | 827708 | 0 | 0 | 822032 | 687.684 | 0 | 0 | 0 | 0 | 822032 | 687.684 | 810207 | 794003.125
6761 | 2008-10-09 16:00 | 139 | 557 | 45 | 26.91 | 9.01 | 0 | 9.6397 | 254.879 | 74.9032 | 0 | 139 | 146.205 | 55.5912 | 1.3023 | 146.205 | 52.0244 | 0.0067977 | 125.448 | 50.099 | 0.0051222 | 170.286 | 170.285 | 382417 | 29.8847 | 343805 | 335712 | 327933 | 0 | 0 | 326973 | 665.175 | 0 | 0 | 0 | 0 | 326973 | 665.175 | 320828 | 314411.3125
6762 | 2008-10-09 17:00 | 5 | 96 | 2 | 25.35 | 9.01 | 0 | -2.4985 | 263.552 | 89.5471 | 0 | 5 | 0.27259 | 1.502 | 0.046846 | 0 | 1.4056 | 0 | 0 | 1.3536 | 0 | 1.313 | 1.3129 | 2948.53 | 25.3729 | 420.252 | 420.426 | 418.459 | 0 | 0 | 418.441 | 194.603 | 0 | 0 | 0 | 418.441 | 0 | 660 | 0 | 0
6763 | 2008-10-09 18:00 | 0 | 0 | 0 | 23.79 | 12.19 | 0
6764 | 2008-10-09 19:00 | 0 | 0 | 0 | 22.23 | 12.19 | 0
6765 | 2008-10-09 20:00 | 0 | 0 | 0 | 21.1 | 12.19 | 0
6766 | 2008-10-09 21:00 | 0 | 0 | 0 | 19.97 | 9.51 | 0
6767 | 2008-10-09 22:00 | 0 | 0 | 0 | 18.85 | 9.51 | 0
6768 | 2008-10-09 23:00 | 0 | 0 | 0 | 17.89 | 9.51 | 0
6769 | 2008-10-10 | 0 | 0 | 0 | 16.94 | 12.82 | 0
6770 | 2008-10-10 01:00 | 0 | 0 | 0 | 15.99 | 12.82 | 0
6771 | 2008-10-10 02:00 | 0 | 0 | 0 | 15.12 | 12.82 | 0
6772 | 2008-10-10 03:00 | 0 | 0 | 0 | 14.24 | 8.64 | 0
6773 | 2008-10-10 04:00 | 0 | 0 | 0 | 13.37 | 8.64 | 0
6774 | 2008-10-10 05:00 | 0 | 26 | 0 | 12.6 | 8.64 | 0
6775 | 2008-10-10 06:00 | 90 | 465 | 32 | 11.83 | 10.09 | 0 | 6.978 | 103.408 | 78.0313 | 0 | 90 | 99.0053 | 39.9506 | 0.84323 | 19.4317 | 37.3873 | 0.0044014 | 15.7182 | 36.0036 | 0.0033165 | 50.1733 | 50.155 | 112648 | 12.6497 | 91292.8 | 96937.7 | 83964.5 | 0 | 0 | 83890.1 | 663.96 | 0 | 0 | 0 | 35.8085 | 83854.3 | 666.256 | 81062.1 | 79440.875
6776 | 2008-10-10 07:00 | 292 | 717 | 62 | 11.06 | 10.09 | 0 | 18.7058 | 112.841 | 63.5096 | 0 | 292 | 319.888 | 76.7694 | 2.7358 | 281.57 | 71.8438 | 0.01428 | 264.086 | 69.1849 | 0.01076 | 323.283 | 323.172 | 725756 | 16.3417 | 685484 | 710417 | 648483 | 0 | 0 | 645173 | 721.743 | 0 | 0 | 0 | 389.31 | 644784 | 723.96 | 634244 | 621558.75
6777 | 2008-10-10 08:00 | 472 | 769 | 93 | 13.1 | 10.09 | 0 | 29.563 | 124.041 | 49.2372 | 0 | 472 | 501.56 | 114.339 | 4.4223 | 501.33 | 107.003 | 0.023083 | 488.006 | 103.042 | 0.017393 | 573.334 | 573.326 | 1287540 | 22.47 | 1256640 | 1270070 | 1232460 | 0 | 0 | 1221550 | 737.103 | 0 | 0 | 0 | 0 | 1221550 | 737.103 | 1200380 | 1176372
6778 | 2008-10-10 09:00 | 628 | 848 | 97 | 15.14 | 5.94 | 0 | 38.8819 | 138.137 | 35.5201 | 0 | 628 | 688.506 | 121.557 | 5.8839 | 688.506 | 113.758 | 0.030712 | 680.635 | 109.548 | 0.023142 | 766.5 | 766.495 | 1721350 | 31.4013 | 1708580 | 1662260 | 1619880 | 0 | 0 | 1599990 | 715.103 | 0 | 0 | 0 | 0 | 1599990 | 715.103 | 1571030 | 1539609.125
6779 | 2008-10-10 10:00 | 709 | 745 | 178 | 17.17 | 5.94 | 0 | 45.6067 | 156.154 | 23.3613 | 0 | 709 | 682.201 | 218.162 | 6.6428 | 682.201 | 204.164 | 0.034673 | 679.155 | 196.608 | 0.026127 | 849.516 | 849.509 | 1907790 | 35.1925 | 1904180 | 1822500 | 1775390 | 0 | 0 | 1751000 | 706.346 | 0 | 0 | 0 | 0 | 1751000 | 706.346 | 1717580 | 1683226.5
6780 | 2008-10-10 11:00 | 802 | 912 | 122 | 18.14 | 5.94 | 0 | 48.4143 | 177.678 | 16.6319 | 0 | 802 | 871.1 | 143.625 | 7.5141 | 871.1 | 134.41 | 0.039221 | 869.198 | 129.435 | 0.029554 | 968.703 | 968.692 | 2175440 | 38.691 | 2185870 | 2060820 | 2009500 | 0 | 0 | 1977520 | 696.361 | 0 | 0 | 0 | 0 | 1977520 | 696.361 | 1936350 | 1897626.375
6781 | 2008-10-10 12:00 | 789 | 976 | 83 | 19.11 | 10.29 | 0 | 46.5237 | 199.605 | 21.3147 | 0 | 789 | 906.359 | 99.9086 | 7.3923 | 906.359 | 93.4983 | 0.038585 | 903.032 | 90.0379 | 0.029075 | 963.306 | 963.3 | 2163330 | 34.662 | 2173100 | 2085630 | 2032230 | 0 | 0 | 2000760 | 710.573 | 0 | 0 | 0 | 0 | 2000760 | 710.573 | 1958730 | 1919553.875
6782 | 2008-10-10 13:00 | 696 | 954 | 78 | 20.08 | 10.29 | 0 | 40.478 | 218.436 | 32.8451 | 0 | 696 | 799.817 | 94.2112 | 6.521 | 799.817 | 88.1664 | 0.034037 | 792.208 | 84.9034 | 0.025648 | 850.823 | 850.817 | 1910720 | 33.816 | 1907260 | 1836630 | 1790560 | 0 | 0 | 1765950 | 709.528 | 0 | 0 | 0 | 0 | 1765950 | 709.528 | 1731970 | 1697333.75
6783 | 2008-10-10 14:00 | 546 | 908 | 71 | 19.71 | 10.29 | 0 | 31.5783 | 233.249 | 46.3679 | 0 | 546 | 625.902 | 86.0931 | 5.1156 | 625.902 | 80.5692 | 0.026702 | 611.844 | 77.5874 | 0.02012 | 668.768 | 668.763 | 1501870 | 30.5069 | 1479240 | 1444460 | 1407020 | 0 | 0 | 1391980 | 714.668 | 0 | 0 | 0 | 0 | 1391980 | 714.668 | 1368290 | 1340926.125
6784 | 2008-10-10 15:00 | 348 | 813 | 57 | 19.35 | 11.74 | 0 | 20.9609 | 244.921 | 60.5614 | 0 | 348 | 399.809 | 72.0059 | 3.2605 | 399.809 | 67.3858 | 0.017019 | 379.127 | 64.8919 | 0.012824 | 430.711 | 430.708 | 967262 | 25.7202 | 927453 | 924452 | 899943 | 0 | 0 | 893764 | 716.646 | 0 | 0 | 0 | 0 | 893764 | 716.646 | 879614 | 862021.875
6785 | 2008-10-10 16:00 | 123 | 459 | 48 | 18.99 | 11.74 | 0 | 9.3614 | 254.612 | 75.0442 | 0 | 123 | 118.992 | 58.7428 | 1.1524 | 118.992 | 54.9737 | 0.0060152 | 101.888 | 52.9392 | 0.0045326 | 150.187 | 150.184 | 337275 | 21.2112 | 300234 | 305713 | 297853 | 0 | 0 | 297113 | 688.67 | 0 | 0 | 0 | 0 | 297113 | 688.67 | 290426 | 284617.5938
6786 | 2008-10-10 17:00 | 4 | 74 | 2 | 17.24 | 11.74 | 0 | -2.7656 | 263.277 | 89.6743 | 0 | 4 | 0.13067 | 1.4853 | 0.037477 | 0 | 1.39 | 0 | 0 | 1.3386 | 0 | 1.2984 | 1.2983 | 2915.62 | 17.2592 | 410.911 | 407.259 | 405.413 | 0 | 0 | 405.395 | 191.623 | 0 | 0 | 0 | 405.395 | 0 | 660 | 0 | 0
6787 | 2008-10-10 18:00 | 0 | 0 | 0 | 15.5 | 15.94 | 0
6788 | 2008-10-10 19:00 | 0 | 0 | 0 | 13.75 | 15.94 | 0
6789 | 2008-10-10 20:00 | 0 | 0 | 0 | 12.56 | 15.94 | 0
6790 | 2008-10-10 21:00 | 0 | 0 | 0 | 11.37 | 3.29 | 0
6791 | 2008-10-10 22:00 | 0 | 0 | 0 | 10.18 | 3.29 | 0
6792 | 2008-10-10 23:00 | 0 | 0 | 0 | 9.43 | 3.29 | 0
6793 | 2008-10-11 | 0 | 0 | 0 | 8.68 | 8.68 | 0
6794 | 2008-10-11 01:00 | 0 | 0 | 0 | 7.93 | 8.68 | 0
6795 | 2008-10-11 02:00 | 0 | 0 | 0 | 7.13 | 8.68 | 0
6796 | 2008-10-11 03:00 | 0 | 0 | 0 | 6.32 | 9.26 | 0
6797 | 2008-10-11 04:00 | 0 | 0 | 0 | 5.51 | 9.26 | 0
6798 | 2008-10-11 05:00 | 0 | 22 | 0 | 5.37 | 9.26 | 0
6799 | 2008-10-11 06:00 | 85 | 436 | 32 | 5.23 | 8.1 | 0 | 6.8068 | 103.752 | 78.0432 | 0 | 85 | 92.6435 | 41.2234 | 0.79638 | 15.8413 | 38.5784 | 0.0041569 | 12.8102 | 37.1506 | 0.0031323 | 48.465 | 48.4494 | 108818 | 6.1259 | 87644.2 | 95996.9 | 84877.9 | 0 | 0 | 84809 | 686.285 | 0 | 0 | 0 | 0 | 84809 | 686.285 | 81824.7 | 80188.2031
6800 | 2008-10-11 07:00 | 306 | 752 | 67 | 5.09 | 8.1 | 0 | 18.5114 | 113.188 | 63.5419 | 0 | 306 | 335.393 | 82.2503 | 2.867 | 293.889 | 76.9729 | 0.014965 | 275.602 | 74.1242 | 0.011276 | 339.246 | 339.06 | 761432 | 11.3595 | 721555 | 763051 | 695662 | 0 | 0 | 692054 | 742.418 | 0 | 0 | 0 | 0 | 692054 | 742.418 | 680130 | 666527.625
6801 | 2008-10-11 08:00 | 484 | 813 | 86 | 6.64 | 8.1 | 0 | 29.3327 | 124.39 | 49.3011 | 0 | 484 | 529.782 | 106.891 | 4.5347 | 529.321 | 100.033 | 0.02367 | 515.2 | 96.331 | 0.017836 | 593.202 | 593.199 | 1332170 | 17.6088 | 1302870 | 1343500 | 1303420 | 0 | 0 | 1291710 | 752.506 | 0 | 0 | 0 | 0 | 1291710 | 752.506 | 1268260 | 1242898.625
6802 | 2008-10-11 09:00 | 646 | 867 | 106 | 8.18 | 6.44 | 0 | 38.603 | 138.471 | 35.6383 | 0 | 646 | 703.398 | 131.938 | 6.0525 | 703.398 | 123.473 | 0.031592 | 695.293 | 118.903 | 0.023805 | 789.793 | 789.785 | 1773660 | 24.4059 | 1763390 | 1767460 | 1720450 | 0 | 0 | 1699470 | 739.435 | 0 | 0 | 0 | 0 | 1699470 | 739.435 | 1666810 | 1633476.375
6803 | 2008-10-11 10:00 | 721 | 831 | 132 | 9.73 | 6.44 | 0 | 45.273 | 156.418 | 23.584 | 0 | 721 | 759.786 | 162.85 | 6.7552 | 759.786 | 152.401 | 0.03526 | 756.324 | 146.761 | 0.026569 | 876.018 | 876.01 | 1967300 | 27.7274 | 1966740 | 1944090 | 1890680 | 0 | 0 | 1865010 | 733.303 | 0 | 0 | 0 | 0 | 1865010 | 733.303 | 1827440 | 1790894.375
6804 | 2008-10-11 11:00 | 795 | 909 | 121 | 10.69 | 6.44 | 0 | 48.0402 | 177.791 | 17.001 | 0 | 795 | 866.775 | 142.771 | 7.4485 | 866.775 | 133.611 | 0.038879 | 864.795 | 128.666 | 0.029296 | 963.685 | 963.673 | 2164160 | 30.4884 | 2173980 | 2124220 | 2066920 | 0 | 0 | 2035660 | 725.574 | 791.708 | 0 | 0 | 0 | 2034830 | 726.889 | 1991630 | 1951793.25
6805 | 2008-10-11 12:00 | 784 | 975 | 83 | 11.66 | 6.52 | 0 | 46.1447 | 199.541 | 21.6472 | 0 | 784 | 903.575 | 100.092 | 7.3455 | 903.575 | 93.6697 | 0.038341 | 900.147 | 90.203 | 0.028891 | 960.667 | 960.665 | 2157400 | 31.2958 | 2166850 | 2109980 | 2051350 | 0 | 0 | 2020370 | 723.158 | 0 | 0 | 0 | 0 | 2020370 | 723.158 | 1977660 | 1938107.25
6806 | 2008-10-11 13:00 | 691 | 953 | 78 | 12.62 | 6.52 | 0 | 40.1231 | 218.253 | 33.0888 | 0 | 691 | 796.961 | 94.388 | 6.4741 | 796.961 | 88.3319 | 0.033793 | 789.248 | 85.0628 | 0.025464 | 848.106 | 848.103 | 1904620 | 29.9551 | 1900850 | 1861220 | 1810820 | 0 | 0 | 1786710 | 725.033 | 0 | 0 | 0 | 0 | 1786710 | 725.033 | 1751760 | 1716722.625
6807 | 2008-10-11 14:00 | 523 | 881 | 66 | 12.64 | 6.52 | 0 | 31.2553 | 233.011 | 46.559 | 0 | 523 | 605.637 | 80.5148 | 4.9001 | 605.637 | 75.3488 | 0.025577 | 591.88 | 72.5602 | 0.019273 | 644.525 | 644.523 | 1447430 | 25.8139 | 1422550 | 1417440 | 1379110 | 0 | 0 | 1365160 | 728.83 | 0 | 0 | 0 | 0 | 1365160 | 728.83 | 1341440 | 1314611.25
6808 | 2008-10-11 15:00 | 325 | 764 | 55 | 12.65 | 5.29 | 0 | 20.6654 | 244.663 | 60.7211 | 0 | 325 | 374.165 | 69.9082 | 3.045 | 374.165 | 65.4228 | 0.015894 | 354.62 | 63.0015 | 0.011976 | 405.104 | 405.099 | 909749 | 21.6129 | 868908 | 881766 | 858249 | 0 | 0 | 852800 | 728.197 | 0 | 0 | 0 | 0 | 852800 | 728.197 | 838806 | 822030
6809 | 2008-10-11 16:00 | 113 | 375 | 53 | 12.66 | 5.29 | 0 | 9.0856 | 254.345 | 75.1835 | 0 | 113 | 97.1658 | 63.585 | 1.0587 | 97.1658 | 59.5052 | 0.0055262 | 83.0259 | 57.303 | 0.0041641 | 136.123 | 136.124 | 305699 | 15.6718 | 269958 | 282149 | 274300 | 0 | 0 | 273701 | 705.349 | 0 | 0 | 0 | 0 | 273701 | 705.349 | 266767 | 261431.4219
6810 | 2008-10-11 17:00 | 3 | 57 | 1 | 12.09 | 5.29 | 0 | -3.0301 | 263.003 | 89.7992 | 0 | 3 | 0.080568 | 0.74678 | 0.028108 | 0 | 0.69887 | 0 | 0 | 0.673 | 0 | 0.65281 | 0.65277 | 1465.95 | 12.1044 | 104.203 | 102.609 | 101.889 | 0 | 0 | 101.885 | 100.401 | 0 | 0 | 0 | 101.885 | 0 | 660 | 0 | 0
6811 | 2008-10-11 18:00 | 0 | 0 | 0 | 11.51 | 3.8 | 0
6812 | 2008-10-11 19:00 | 0 | 0 | 0 | 10.94 | 3.8 | 0
6813 | 2008-10-11 20:00 | 0 | 0 | 0 | 10.52 | 3.8 | 0
6814 | 2008-10-11 21:00 | 0 | 0 | 0 | 10.1 | 3.7 | 0
6815 | 2008-10-11 22:00 | 0 | 0 | 0 | 9.68 | 3.7 | 0
6816 | 2008-10-11 23:00 | 0 | 0 | 0 | 9.06 | 3.7 | 0
6817 | 2008-10-12 | 0 | 0 | 0 | 8.44 | 5.66 | 0
6818 | 2008-10-12 01:00 | 0 | 0 | 0 | 7.82 | 5.66 | 0
6819 | 2008-10-12 02:00 | 0 | 0 | 0 | 6.73 | 5.66 | 0
6820 | 2008-10-12 03:00 | 0 | 0 | 0 | 5.64 | 10.25 | 0
6821 | 2008-10-12 04:00 | 0 | 0 | 0 | 4.55 | 10.25 | 0
6822 | 2008-10-12 05:00 | 0 | 20 | 0 | 4.24 | 10.25 | 0
6823 | 2008-10-12 06:00 | 87 | 466 | 32 | 3.93 | 7.22 | 0 | 6.6345 | 104.093 | 78.0576 | 0 | 87 | 98.5074 | 40.1113 | 0.81512 | 15.092 | 37.5377 | 0.0042547 | 12.1999 | 36.1484 | 0.003206 | 46.901 | 46.856 | 105239 | 4.8459 | 84480.8 | 93063.4 | 83270.7 | 0 | 0 | 83203.6 | 687.813 | 0 | 0 | 0 | 0 | 83203.6 | 687.813 | 80256 | 78650.8828
6824 | 2008-10-12 07:00 | 298 | 774 | 55 | 3.62 | 7.22 | 0 | 18.3157 | 113.532 | 63.5771 | 0 | 298 | 344.097 | 69.4971 | 2.792 | 300.11 | 65.0381 | 0.014573 | 281.395 | 62.6311 | 0.010981 | 333.716 | 333.517 | 748975 | 10.1395 | 709328 | 753637 | 685138 | 0 | 0 | 681689 | 749.755 | 0 | 0 | 0 | 0 | 681689 | 749.755 | 669650 | 656256.9375
6825 | 2008-10-12 08:00 | 499 | 890 | 67 | 5.39 | 7.22 | 0 | 29.1012 | 124.735 | 49.3686 | 0 | 499 | 578.415 | 81.7602 | 4.6752 | 577.563 | 76.5143 | 0.024403 | 562.094 | 73.6826 | 0.018388 | 616.721 | 616.699 | 1384940 | 17.4451 | 1357640 | 1400730 | 1355280 | 0 | 0 | 1342680 | 754.077 | 0 | 0 | 0 | 0 | 1342680 | 754.077 | 1318080 | 1291713.75
6826 | 2008-10-12 09:00 | 659 | 943 | 75 | 7.17 | 4.25 | 0 | 38.3233 | 138.799 | 35.7609 | 0 | 659 | 764.225 | 91.0804 | 6.1743 | 764.225 | 85.2365 | 0.032228 | 755.347 | 82.082 | 0.024284 | 812.329 | 812.325 | 1824280 | 26.4031 | 1816490 | 1805500 | 1758730 | 0 | 0 | 1736490 | 733.727 | 0 | 0 | 0 | 0 | 1736490 | 733.727 | 1702910 | 1668853.5
6827 | 2008-10-12 10:00 | 766 | 972 | 81 | 8.95 | 4.25 | 0 | 44.9395 | 156.675 | 23.8109 | 0 | 766 | 887.218 | 97.9672 | 7.1768 | 887.218 | 91.6815 | 0.037461 | 883.091 | 88.2884 | 0.028227 | 942.265 | 942.263 | 2116080 | 31.2596 | 2123320 | 2067770 | 2013260 | 0 | 0 | 1983290 | 721.634 | 0 | 0 | 0 | 0 | 1983290 | 721.634 | 1941870 | 1903035
6828 | 2008-10-12 11:00 | 806 | 980 | 84 | 10.14 | 4.25 | 0 | 47.6676 | 177.9 | 17.3692 | 0 | 806 | 932.131 | 101.393 | 7.5516 | 932.131 | 94.8877 | 0.039417 | 929.904 | 91.376 | 0.029701 | 990.67 | 990.665 | 2224780 | 33.5956 | 2237870 | 2157750 | 2100340 | 0 | 0 | 2067150 | 715.022 | 22749.1 | 0 | 0 | 0 | 2043460 | 733.609 | 1999980 | 1959983.125
6829 | 2008-10-12 12:00 | 756 | 894 | 117 | 11.33 | 1.6 | 0 | 45.7679 | 199.476 | 21.9785 | 0 | 756 | 826.998 | 146.652 | 7.0831 | 826.998 | 137.242 | 0.036971 | 823.757 | 132.163 | 0.027859 | 927.27 | 927.26 | 2082380 | 37.5 | 2087830 | 1978400 | 1928420 | 0 | 0 | 1899160 | 699.916 | 0 | 0 | 0 | 0 | 1899160 | 699.916 | 1860810 | 1823591
6830 | 2008-10-12 13:00 | 684 | 950 | 77 | 12.52 | 1.6 | 0 | 39.7704 | 218.07 | 33.3321 | 0 | 684 | 792.776 | 93.4132 | 6.4085 | 792.776 | 87.4196 | 0.03345 | 784.971 | 84.1843 | 0.025206 | 843.105 | 843.103 | 1893390 | 36.3149 | 1889060 | 1798880 | 1751550 | 0 | 0 | 1727530 | 702.265 | 0 | 0 | 0 | 0 | 1727530 | 702.265 | 1694960 | 1661061.625
6831 | 2008-10-12 14:00 | 534 | 906 | 69 | 12.79 | 1.6 | 0 | 30.9346 | 232.775 | 46.7493 | 0 | 534 | 619.801 | 84.1409 | 5.0032 | 619.801 | 78.7423 | 0.026115 | 605.563 | 75.8281 | 0.019678 | 660.968 | 660.967 | 1484370 | 31.4445 | 1461010 | 1420630 | 1383210 | 0 | 0 | 1368560 | 712.476 | 0 | 0 | 0 | 0 | 1368560 | 712.476 | 1345480 | 1318570
6832 | 2008-10-12 15:00 | 340 | 810 | 58 | 13.06 | 4.83 | 0 | 20.3723 | 244.406 | 60.8795 | 0 | 340 | 394.218 | 73.4761 | 3.1855 | 394.218 | 68.7617 | 0.016627 | 373.425 | 66.2169 | 0.012529 | 426.465 | 426.462 | 957723 | 22.7819 | 917728 | 926554 | 901854 | 0 | 0 | 895790 | 725.733 | 0 | 0 | 0 | 0 | 895790 | 725.733 | 881200 | 863576.375
6833 | 2008-10-12 16:00 | 125 | 526 | 44 | 13.33 | 4.83 | 0 | 8.8124 | 254.079 | 75.3208 | 0 | 125 | 133.982 | 54.9676 | 1.1711 | 133.982 | 51.4407 | 0.006113 | 114.245 | 49.537 | 0.0046063 | 158.873 | 158.87 | 356781 | 16.9517 | 319021 | 331286 | 322597 | 0 | 0 | 321774 | 706.663 | 0 | 0 | 0 | 0 | 321774 | 706.663 | 314560 | 308268.6875
6834 | 2008-10-12 17:00 | 3 | 74 | 1 | 12.84 | 4.83 | 0 | -3.2917 | 262.728 | 89.9216 | 0 | 3 | 0.031445 | 0.73794 | 0.028108 | 0 | 0.6906 | 0 | 0 | 0.66504 | 0 | 0.64509 | 0.64506 | 1448.64 | 12.8547 | 101.776 | 100.31 | 99.5827 | 0 | 0 | 99.5787 | 99.3304 | 0 | 0 | 0 | 99.5787 | 0 | 660 | 0 | 0
6835 | 2008-10-12 18:00 | 0 | 0 | 0 | 12.35 | 10.65 | 0
6836 | 2008-10-12 19:00 | 0 | 0 | 0 | 11.87 | 10.65 | 0
6837 | 2008-10-12 20:00 | 0 | 0 | 0 | 10.84 | 10.65 | 0
6838 | 2008-10-12 21:00 | 0 | 0 | 0 | 9.81 | 7.69 | 0
6839 | 2008-10-12 22:00 | 0 | 0 | 0 | 8.78 | 7.69 | 0
6840 | 2008-10-12 23:00 | 0 | 0 | 0 | 8.17 | 7.69 | 0
6841 | 2008-10-13 | 0 | 0 | 0 | 7.57 | 10.75 | 0
6842 | 2008-10-13 01:00 | 0 | 0 | 0 | 6.96 | 10.75 | 0
6843 | 2008-10-13 02:00 | 0 | 0 | 0 | 6.15 | 10.75 | 0
6844 | 2008-10-13 03:00 | 0 | 0 | 0 | 5.34 | 11.85 | 0
6845 | 2008-10-13 04:00 | 0 | 0 | 0 | 4.53 | 11.85 | 0
6846 | 2008-10-13 05:00 | 0 | 17 | 0 | 4.24 | 11.85 | 0
6847 | 2008-10-13 06:00 | 87 | 480 | 32 | 3.95 | 15.16 | 0 | 6.4613 | 104.431 | 78.0742 | 0 | 87 | 100.998 | 40.166 | 0.81512 | 13.8847 | 37.5888 | 0.0042547 | 11.2193 | 36.1977 | 0.003206 | 45.9976 | 45.984 | 103280 | 4.5075 | 82707.6 | 91318.5 | 81827.4 | 0 | 0 | 81761.3 | 679.953 | 0 | 0 | 0 | 0 | 81761.3 | 679.953 | 78915.5 | 77337.1641
6848 | 2008-10-13 07:00 | 296 | 776 | 54 | 3.66 | 15.16 | 0 | 18.1188 | 113.871 | 63.6153 | 0 | 296 | 345.813 | 68.5709 | 2.7733 | 300.144 | 64.1713 | 0.014476 | 281.382 | 61.7964 | 0.010908 | 332.893 | 332.838 | 747446 | 7.6949 | 707899 | 760316 | 686546 | 0 | 0 | 683094 | 752.231 | 0 | 0 | 0 | -5.3272 | 683100 | 752.583 | 671036 | 657615.1875
6849 | 2008-10-13 08:00 | 497 | 892 | 67 | 5.69 | 15.16 | 0 | 28.8686 | 125.076 | 49.4396 | 0 | 497 | 579.133 | 81.9313 | 4.6565 | 577.846 | 76.6744 | 0.024305 | 562.305 | 73.8367 | 0.018315 | 617.076 | 617.06 | 1385750 | 13.1704 | 1358510 | 1425910 | 1377460 | 0 | 0 | 1364870 | 766.274 | 0 | 0 | 0 | 0 | 1364870 | 766.274 | 1339040 | 1312258.5
6850 | 2008-10-13 09:00 | 646 | 927 | 76 | 7.71 | 13.9 | 0 | 38.043 | 139.121 | 35.8877 | 0 | 646 | 749.361 | 92.4071 | 6.0525 | 749.361 | 86.4781 | 0.031592 | 740.582 | 83.2776 | 0.023805 | 799.167 | 799.16 | 1794710 | 18.1205 | 1785470 | 1836130 | 1783280 | 0 | 0 | 1761990 | 761.297 | 0 | 0 | 0 | 0 | 1761990 | 761.297 | 1725620 | 1691104.625
6851 | 2008-10-13 10:00 | 762 | 971 | 82 | 9.74 | 13.9 | 0 | 44.6064 | 156.926 | 24.0416 | 0 | 762 | 884.337 | 99.2988 | 7.1394 | 884.337 | 92.9276 | 0.037265 | 880.136 | 89.4884 | 0.02808 | 940.563 | 940.56 | 2112260 | 21.9924 | 2119300 | 2145200 | 2087760 | 0 | 0 | 2057900 | 750.428 | 14204.6 | 0 | 0 | 0 | 2044840 | 764.53 | 1998570 | 1958598.125
6852 | 2008-10-13 11:00 | 788 | 959 | 85 | 11.02 | 13.9 | 0 | 47.2966 | 178.003 | 17.7362 | 0 | 788 | 911.158 | 102.728 | 7.383 | 911.158 | 96.1366 | 0.038537 | 908.884 | 92.5786 | 0.029038 | 971.447 | 971.44 | 2181610 | 23.6747 | 2192370 | 2204000 | 2145000 | 0 | 0 | 2113120 | 745.717 | 69368.8 | 0 | 0 | 0 | 2044980 | 777.384 | 1997250 | 1957308
6853 | 2008-10-13 12:00 | 747 | 886 | 118 | 12.3 | 10.18 | 0 | 45.3933 | 199.409 | 22.3086 | 0 | 747 | 817.369 | 148.013 | 6.9988 | 817.369 | 138.516 | 0.036531 | 814.062 | 133.39 | 0.027527 | 919.055 | 919.048 | 2063960 | 27.2377 | 2068440 | 2048970 | 1992530 | 0 | 0 | 1964210 | 735.078 | 0 | 0 | 0 | 0 | 1964210 | 735.078 | 1923390 | 1884926
6854 | 2008-10-13 13:00 | 675 | 895 | 108 | 13.58 | 10.18 | 0 | 39.4201 | 217.888 | 33.5747 | 0 | 675 | 743.943 | 135.093 | 6.3242 | 743.943 | 126.426 | 0.03301 | 736.495 | 121.747 | 0.024874 | 832.518 | 832.506 | 1869590 | 27.1111 | 1864060 | 1847400 | 1796790 | 0 | 0 | 1773500 | 732.56 | 0 | 0 | 0 | 0 | 1773500 | 732.56 | 1738810 | 1704036.75
6855 | 2008-10-13 14:00 | 504 | 858 | 68 | 14.06 | 10.18 | 0 | 30.6163 | 232.539 | 46.9386 | 0 | 504 | 584.53 | 83.1575 | 4.7221 | 584.53 | 77.822 | 0.024648 | 570.952 | 74.9418 | 0.018573 | 626.535 | 626.533 | 1407030 | 24.2433 | 1380540 | 1384820 | 1345510 | 0 | 0 | 1332460 | 735.083 | 0 | 0 | 0 | 0 | 1332460 | 735.083 | 1309140 | 1282960.625
6856 | 2008-10-13 15:00 | 309 | 734 | 57 | 14.54 | 9.97 | 0 | 20.0818 | 244.15 | 61.0363 | 0 | 309 | 355.406 | 72.5194 | 2.8951 | 355.406 | 67.8664 | 0.015111 | 336.48 | 65.3548 | 0.011387 | 389.791 | 389.788 | 875361 | 20.9574 | 833999 | 848806 | 825579 | 0 | 0 | 820543 | 728.889 | 0 | 0 | 0 | 0 | 820543 | 728.889 | 807050 | 790908.8125
6857 | 2008-10-13 16:00 | 93 | 118 | 75 | 15.03 | 9.97 | 0 | 8.5419 | 253.813 | 75.4561 | 0 | 93 | 30.4324 | 81.6814 | 0.87134 | 30.4324 | 76.4406 | 0.0045481 | 25.8948 | 73.6116 | 0.0034271 | 96.5245 | 96.5215 | 216762 | 16.6191 | 185773 | 193554 | 188388 | 0 | 0 | 188090 | 687.093 | 0 | 0 | 0 | 0 | 188090 | 687.093 | 182616 | 178963.6719
6858 | 2008-10-13 17:00 | 2 | 15 | 2 | 14.24 | 9.97 | 0 | -3.5504 | 262.453 | 90 | 0 | 2 | 0 | 1.9739 | 0.018738 | 0 | 1.8472 | 0 | 0 | 1.7789 | 0 | 1.7255 | 1.7253 | 3874.69 | 14.2684 | 723.549 | 715.187 | 711.83 | 0 | 0 | 711.799 | 254.168 | 0 | 0 | 0 | 711.799 | 0 | 660 | 0 | 0
6859 | 2008-10-13 18:00 | 0 | 0 | 0 | 13.46 | 14.51 | 0
6860 | 2008-10-13 19:00 | 0 | 0 | 0 | 12.67 | 14.51 | 0
6861 | 2008-10-13 20:00 | 0 | 0 | 0 | 12.4 | 14.51 | 0
6862 | 2008-10-13 21:00 | 0 | 0 | 0 | 12.12 | 12.8 | 0
6863 | 2008-10-13 22:00 | 0 | 0 | 0 | 11.84 | 12.8 | 0
6864 | 2008-10-13 23:00 | 0 | 0 | 0 | 11.4 | 12.8 | 0
6865 | 2008-10-14 | 0 | 0 | 0 | 10.95 | 10.29 | 0
6866 | 2008-10-14 01:00 | 0 | 0 | 0 | 10.5 | 10.29 | 0
6867 | 2008-10-14 02:00 | 0 | 0 | 0 | 10.14 | 10.29 | 0
6868 | 2008-10-14 03:00 | 0 | 0 | 0 | 9.77 | 13.94 | 0
6869 | 2008-10-14 04:00 | 0 | 0 | 0 | 9.41 | 13.94 | 0
6870 | 2008-10-14 05:00 | 0 | 14 | 0 | 9.29 | 13.94 | 0
6871 | 2008-10-14 06:00 | 85 | 478 | 31 | 9.16 | 9.69 | 0 | 6.287 | 104.766 | 78.0934 | 0 | 85 | 101.737 | 39.3193 | 0.79638 | 12.1252 | 36.7965 | 0.0041569 | 9.793 | 35.4347 | 0.0031323 | 43.8739 | 43.8608 | 98514.3 | 9.8947 | 78406.2 | 84436 | 74680.9 | 0 | 0 | 74620.4 | 647.927 | 0 | 0 | 0 | 218.915 | 74401.5 | 661.731 | 71902.5 | 70464.4219
6872 | 2008-10-14 07:00 | 296 | 746 | 66 | 9.04 | 9.69 | 0 | 17.9208 | 114.207 | 63.6565 | 0 | 296 | 331.695 | 81.709 | 2.7733 | 286.391 | 76.4664 | 0.014476 | 268.442 | 73.6365 | 0.010908 | 331.826 | 331.763 | 745024 | 14.5969 | 705264 | 735948 | 669182 | 0 | 0 | 665685 | 727.395 | 0 | 0 | 0 | 644.525 | 665040 | 730.322 | 653964 | 640885.0625
6873 | 2008-10-14 08:00 | 457 | 766 | 90 | 11.31 | 9.69 | 0 | 28.6349 | 125.411 | 49.5143 | 0 | 457 | 497.213 | 111.914 | 4.2817 | 495.723 | 104.734 | 0.022349 | 482.333 | 100.858 | 0.016841 | 565.711 | 565.68 | 1270370 | 20.7849 | 1238960 | 1261010 | 1219570 | 0 | 0 | 1208980 | 740.101 | 0 | 0 | 0 | 0 | 1208980 | 740.101 | 1187900 | 1164145.75
6874 | 2008-10-14 09:00 | 619 | 837 | 107 | 13.57 | 9.53 | 0 | 37.7621 | 139.437 | 36.0186 | 0 | 619 | 676.24 | 133.741 | 5.7995 | 676.24 | 125.16 | 0.030272 | 668.248 | 120.528 | 0.02281 | 765.135 | 765.128 | 1718280 | 26.5125 | 1705360 | 1694320 | 1646680 | 0 | 0 | 1627160 | 733.532 | 0 | 0 | 0 | 0 | 1627160 | 733.532 | 1596820 | 1564885.625
6875 | 2008-10-14 10:00 | 743 | 902 | 115 | 15.84 | 9.53 | 0 | 44.2738 | 157.17 | 24.2759 | 0 | 743 | 820.054 | 144.615 | 6.9613 | 820.054 | 135.337 | 0.036336 | 816.077 | 130.328 | 0.02738 | 918.039 | 918.031 | 2061660 | 31.369 | 2066020 | 2011060 | 1958020 | 0 | 0 | 1929450 | 719.617 | 0 | 0 | 0 | 0 | 1929450 | 719.617 | 1889880 | 1852084.25
6876 | 2008-10-14 11:00 | 797 | 926 | 123 | 17.19 | 9.53 | 0 | 46.9273 | 178.102 | 18.102 | 0 | 797 | 877.004 | 145.695 | 7.4673 | 877.004 | 136.347 | 0.038977 | 874.721 | 131.301 | 0.02937 | 975.869 | 975.862 | 2191540 | 33.6972 | 2202830 | 2123120 | 2070700 | 0 | 0 | 2038300 | 713.41 | 1075.33 | 0 | 0 | 0 | 2037170 | 715.343 | 1993840 | 1953967
6877 | 2008-10-14 12:00 | 739 | 881 | 117 | 18.54 | 5.44 | 0 | 45.0212 | 199.341 | 22.6371 | 0 | 739 | 811.574 | 147.108 | 6.9238 | 811.574 | 137.67 | 0.03614 | 808.187 | 132.575 | 0.027232 | 912.565 | 912.562 | 2049380 | 38.5353 | 2053090 | 1936480 | 1888160 | 0 | 0 | 1859850 | 696.299 | 0 | 0 | 0 | 0 | 1859850 | 696.299 | 1822930 | 1786470
6878 | 2008-10-14 13:00 | 674 | 950 | 76 | 19.89 | 5.44 | 0 | 39.0724 | 217.707 | 33.8165 | 0 | 674 | 788.247 | 92.6063 | 6.3149 | 788.247 | 86.6645 | 0.032961 | 780.221 | 83.4571 | 0.024837 | 837.792 | 837.787 | 1881450 | 38.2469 | 1876510 | 1771590 | 1726310 | 0 | 0 | 1702450 | 694.637 | 0 | 0 | 0 | 0 | 1702450 | 694.637 | 1670890 | 1637470.125
6879 | 2008-10-14 14:00 | 523 | 902 | 68 | 20.41 | 5.44 | 0 | 30.3005 | 232.304 | 47.1267 | 0 | 523 | 613.58 | 83.3262 | 4.9001 | 613.58 | 77.9799 | 0.025577 | 599.168 | 75.0939 | 0.019273 | 654.053 | 654.047 | 1468820 | 34.741 | 1444820 | 1384450 | 1349570 | 0 | 0 | 1335080 | 699.452 | 0 | 0 | 0 | 0 | 1335080 | 699.452 | 1313290 | 1287022.5
6880 | 2008-10-14 15:00 | 308 | 745 | 56 | 20.94 | 5.34 | 0 | 19.7939 | 243.895 | 61.1915 | 0 | 308 | 358.599 | 71.5589 | 2.8857 | 358.599 | 66.9675 | 0.015062 | 339.321 | 64.4891 | 0.01135 | 391.706 | 391.704 | 879668 | 29.5785 | 838366 | 821221 | 799727 | 0 | 0 | 794607 | 699.916 | 0 | 0 | 0 | 0 | 794607 | 699.916 | 782691 | 767037.125
6881 | 2008-10-14 16:00 | 92 | 100 | 77 | 21.46 | 5.34 | 0 | 8.2742 | 253.548 | 75.5892 | 0 | 92 | 25.9403 | 84.8859 | 0.86197 | 24.9969 | 79.4395 | 0.0044992 | 21.2247 | 76.4995 | 0.0033902 | 94.7957 | 94.7952 | 212886 | 23.5506 | 182156 | 183478 | 178628 | 0 | 0 | 178338 | 659.776 | 0 | 0 | 0 | -12.561 | 178351 | 661.141 | 173464 | 169994.9375
6882 | 2008-10-14 17:00 | 2 | 12 | 2 | 20.78 | 5.34 | 0 | -3.8059 | 262.178 | 90 | 0 | 2 | 0 | 1.9744 | 0.018738 | 0 | 1.8477 | 0 | 0 | 1.7793 | 0 | 1.7259 | 1.7258 | 3875.78 | 20.8181 | 723.949 | 720.8 | 717.281 | 0 | 0 | 717.25 | 256.005 | 0 | 0 | 0 | 717.25 | 0 | 660 | 0 | 0
6883 | 2008-10-14 18:00 | 0 | 0 | 0 | 20.09 | 4.76 | 0
6884 | 2008-10-14 19:00 | 0 | 0 | 0 | 19.4 | 4.76 | 0
6885 | 2008-10-14 20:00 | 0 | 0 | 0 | 18.93 | 4.76 | 0
6886 | 2008-10-14 21:00 | 0 | 0 | 0 | 18.45 | 8.25 | 0
6887 | 2008-10-14 22:00 | 0 | 0 | 0 | 17.97 | 8.25 | 0
6888 | 2008-10-14 23:00 | 0 | 0 | 0 | 17.38 | 8.25 | 0
6889 | 2008-10-15 | 0 | 0 | 0 | 16.78 | 7.37 | 0
6890 | 2008-10-15 01:00 | 0 | 0 | 0 | 16.18 | 7.37 | 0
6891 | 2008-10-15 02:00 | 0 | 0 | 0 | 15.6 | 7.37 | 0
6892 | 2008-10-15 03:00 | 0 | 0 | 0 | 15.03 | 6.48 | 0
6893 | 2008-10-15 04:00 | 0 | 0 | 0 | 14.45 | 6.48 | 0
6894 | 2008-10-15 05:00 | 0 | 10 | 0 | 14.16 | 6.48 | 0
6895 | 2008-10-15 06:00 | 82 | 468 | 31 | 13.86 | 6.81 | 0 | 6.1118 | 105.098 | 78.1149 | 0 | 82 | 98.6519 | 39.3539 | 0.76828 | 10.1317 | 36.8288 | 0.0040101 | 8.1785 | 35.4658 | 0.0030217 | 42.338 | 42.3369 | 95094.5 | 14.7095 | 75265.3 | 79204.9 | 70101.2 | 0 | 0 | 70046.3 | 631.482 | 0 | 0 | 0 | 368.098 | 69678.2 | 660 | 67327.5 | 65980.9766
6896 | 2008-10-15 07:00 | 288 | 769 | 54 | 13.57 | 6.81 | 0 | 17.7216 | 114.539 | 63.7007 | 0 | 288 | 340.6 | 68.9392 | 2.6983 | 292.5 | 64.516 | 0.014084 | 274.116 | 62.1283 | 0.010613 | 326.168 | 326.048 | 732196 | 20.112 | 692691 | 705499 | 637807 | 0 | 0 | 634463 | 711.484 | 0 | 0 | 0 | 2884.38 | 631579 | 716.271 | 621283 | 608857.8125
6897 | 2008-10-15 08:00 | 479 | 871 | 65 | 15.59 | 6.81 | 0 | 28.4003 | 125.742 | 49.5925 | 0 | 479 | 564.228 | 79.9589 | 4.4879 | 562.128 | 74.8286 | 0.023425 | 546.875 | 72.0593 | 0.017651 | 600.383 | 600.364 | 1348250 | 27.6361 | 1319680 | 1304460 | 1261660 | 0 | 0 | 1249670 | 718.879 | 0 | 0 | 0 | 0 | 1249670 | 718.879 | 1228790 | 1204215.875
6898 | 2008-10-15 09:00 | 621 | 851 | 104 | 17.61 | 3.27 | 0 | 37.4808 | 139.747 | 36.1537 | 0 | 621 | 686.029 | 130.608 | 5.8183 | 686.029 | 122.228 | 0.03037 | 677.849 | 117.704 | 0.022884 | 771.708 | 771.704 | 1733060 | 37.0983 | 1720840 | 1632470 | 1591040 | 0 | 0 | 1570890 | 697.212 | 0 | 0 | 0 | 0 | 1570890 | 697.212 | 1543380 | 1512515.625
6899 | 2008-10-15 10:00 | 737 | 946 | 82 | 19.63 | 3.27 | 0 | 43.9417 | 157.407 | 24.5137 | 0 | 737 | 858.822 | 99.6583 | 6.9051 | 858.822 | 93.264 | 0.036042 | 854.568 | 89.8124 | 0.027159 | 916.075 | 916.068 | 2057260 | 42.764 | 2061380 | 1907250 | 1861010 | 0 | 0 | 1832410 | 682.339 | 0 | 0 | 0 | 0 | 1832410 | 682.339 | 1796660 | 1760722.25
6900 | 2008-10-15 11:00 | 784 | 967 | 84 | 21.15 | 3.27 | 0 | 46.5598 | 178.195 | 18.4663 | 0 | 784 | 914.425 | 101.942 | 7.3455 | 914.425 | 95.401 | 0.038341 | 911.943 | 91.8702 | 0.028891 | 973.727 | 973.721 | 2186730 | 45.74 | 2197760 | 2006280 | 1958370 | 0 | 0 | 1926050 | 674.884 | 0 | 0 | 0 | 0 | 1926050 | 674.884 | 1886920 | 1849177.125
6901 | 2008-10-15 12:00 | 763 | 921 | 117 | 22.67 | 3.62 | 0 | 44.6516 | 199.271 | 22.9639 | 0 | 763 | 846.343 | 147.333 | 7.1487 | 846.343 | 137.88 | 0.037314 | 842.7 | 132.777 | 0.028117 | 946.241 | 946.232 | 2125000 | 46.0202 | 2132720 | 1943980 | 1898590 | 0 | 0 | 1868050 | 673.505 | 0 | 0 | 0 | 0 | 1868050 | 673.505 | 1831120 | 1794495
6902 | 2008-10-15 13:00 | 623 | 779 | 137 | 24.19 | 3.62 | 0 | 38.7273 | 217.525 | 34.0573 | 0 | 623 | 643.592 | 171.451 | 5.837 | 643.592 | 160.45 | 0.030467 | 636.929 | 154.512 | 0.022958 | 767.721 | 767.711 | 1724090 | 43.1349 | 1711440 | 1579080 | 1541050 | 0 | 0 | 1520980 | 676.014 | 0 | 0 | 0 | 0 | 1520980 | 676.014 | 1495740 | 1465823.5
6903 | 2008-10-15 14:00 | 518 | 860 | 89 | 24.58 | 3.62 | 0 | 29.9874 | 232.071 | 47.3136 | 0 | 518 | 581.933 | 111.632 | 4.8533 | 581.933 | 104.469 | 0.025332 | 568.114 | 100.603 | 0.019089 | 648.674 | 648.67 | 1456750 | 40.5873 | 1432250 | 1336000 | 1303120 | 0 | 0 | 1288830 | 679.234 | 0 | 0 | 0 | 0 | 1288830 | 679.234 | 1268960 | 1243581
6904 | 2008-10-15 15:00 | 301 | 722 | 60 | 24.97 | 1.8 | 0 | 19.5087 | 243.64 | 61.3449 | 0 | 301 | 346.064 | 76.2057 | 2.8201 | 346.064 | 71.3162 | 0.01472 | 327.284 | 68.6769 | 0.011092 | 384.093 | 384.09 | 862566 | 35.6659 | 821027 | 781702 | 762470 | 0 | 0 | 757498 | 677.159 | 0 | 0 | 0 | 0 | 757498 | 677.159 | 747000 | 732060.375
6905 | 2008-10-15 16:00 | 111 | 330 | 64 | 25.36 | 1.8 | 0 | 8.0095 | 253.283 | 75.7201 | 0 | 111 | 83.2007 | 75.2396 | 1.04 | 77.149 | 70.4121 | 0.0054284 | 65.3676 | 67.8062 | 0.0040904 | 129.183 | 129.165 | 290072 | 28.9569 | 255110 | 250080 | 241746 | 0 | 0 | 241211 | 658.004 | 0 | 0 | 0 | 46.7486 | 241164 | 660.051 | 235489 | 230779.0312
6906 | 2008-10-15 17:00 | 2 | 36 | 1 | 24.64 | 1.8 | 0 | -4.0582 | 261.904 | 90 | 0 | 2 | 0 | 0.70275 | 0.018738 | 0 | 0.65766 | 0 | 0 | 0.63332 | 0 | 0.61432 | 0.61431 | 1379.59 | 24.6571 | 92.3213 | 92.2839 | 91.6108 | 0 | 0 | 91.6071 | 95.2709 | 0 | 0 | 0 | 91.6071 | 0 | 660 | 0 | 0
6907 | 2008-10-15 18:00 | 0 | 0 | 0 | 23.91 | 3.78 | 0
6908 | 2008-10-15 19:00 | 0 | 0 | 0 | 23.19 | 3.78 | 0
6909 | 2008-10-15 20:00 | 0 | 0 | 0 | 22.2 | 3.78 | 0
6910 | 2008-10-15 21:00 | 0 | 0 | 0 | 21.21 | 3.46 | 0
6911 | 2008-10-15 22:00 | 0 | 0 | 0 | 20.23 | 3.46 | 0
6912 | 2008-10-15 23:00 | 0 | 0 | 0 | 19.64 | 3.46 | 0
6913 | 2008-10-16 | 0 | 0 | 0 | 19.05 | 3.67 | 0
6914 | 2008-10-16 01:00 | 0 | 0 | 0 | 18.46 | 3.67 | 0
6915 | 2008-10-16 02:00 | 0 | 0 | 0 | 17.84 | 3.67 | 0
6916 | 2008-10-16 03:00 | 0 | 0 | 0 | 17.22 | 2.31 | 0
6917 | 2008-10-16 04:00 | 0 | 0 | 0 | 16.6 | 2.31 | 0
6918 | 2008-10-16 05:00 | 0 | 4 | 0 | 15.99 | 2.31 | 0
6919 | 2008-10-16 06:00 | 68 | 230 | 44 | 15.38 | 2.61 | 0 | 5.9357 | 105.427 | 78.139 | 0 | 68 | 47.7016 | 54.1985 | 0.63711 | 4.2939 | 50.7211 | 0.0033255 | 3.464 | 48.8439 | 0.0025058 | 50.7411 | 50.726 | 113926 | 16.7183 | 91494.2 | 95434.4 | 90146.3 | 0 | 0 | 90070 | 654.443 | 0 | 0 | 0 | 94.5664 | 89975.4 | 660 | 87043.5 | 85302.5938
6920 | 2008-10-16 07:00 | 174 | 159 | 126 | 14.77 | 2.61 | 0 | 17.5214 | 114.866 | 63.7478 | 0 | 174 | 70.5218 | 133.033 | 1.6302 | 60.2593 | 124.497 | 0.0085093 | 56.4606 | 119.889 | 0.0064119 | 171.066 | 171.065 | 384162 | 19.2832 | 345746 | 354976 | 336168 | 0 | 0 | 335260 | 701.6 | 0 | 0 | 0 | 0 | 335260 | 701.6 | 328241 | 321676.2812
6921 | 2008-10-16 08:00 | 486 | 686 | 163 | 16.78 | 2.61 | 0 | 28.1647 | 126.067 | 49.6743 | 0 | 486 | 442.839 | 191.056 | 4.5534 | 440.774 | 178.797 | 0.023767 | 428.757 | 172.18 | 0.017909 | 582.926 | 582.903 | 1309050 | 32.1587 | 1279000 | 1239190 | 1197430 | 0 | 0 | 1186060 | 700.846 | 0 | 0 | 0 | 0 | 1186060 | 700.846 | 1167350 | 1144002.125
6922 | 2008-10-16 09:00 | 645 | 893 | 106 | 18.8 | 3.62 | 0 | 37.199 | 140.05 | 36.2926 | 0 | 645 | 718.568 | 133.069 | 6.0431 | 718.568 | 124.531 | 0.031543 | 709.921 | 119.923 | 0.023768 | 804.971 | 804.965 | 1807750 | 38.6642 | 1799150 | 1695010 | 1652070 | 0 | 0 | 1630060 | 692.16 | 0 | 0 | 0 | 0 | 1630060 | 692.16 | 1600890 | 1568872
6923 | 2008-10-16 10:00 | 704 | 804 | 151 | 20.81 | 3.62 | 0 | 43.6104 | 157.637 | 24.7547 | 0 | 704 | 728.065 | 189.942 | 6.5959 | 728.065 | 177.755 | 0.034429 | 724.382 | 171.176 | 0.025943 | 868.717 | 868.7 | 1950870 | 42.247 | 1949460 | 1807460 | 1762630 | 0 | 0 | 1736980 | 683.327 | 0 | 0 | 0 | 0 | 1736980 | 683.327 | 1704530 | 1670443.5
6924 | 2008-10-16 11:00 | 689 | 632 | 234 | 22.51 | 3.62 | 0 | 46.1943 | 178.284 | 18.829 | 0 | 689 | 596.725 | 280.824 | 6.4554 | 596.725 | 262.805 | 0.033695 | 595.038 | 253.079 | 0.02539 | 822.698 | 822.691 | 1847550 | 42.8116 | 1840920 | 1701800 | 1658400 | 0 | 0 | 1635360 | 678.863 | 0 | 0 | 0 | 0 | 1635360 | 678.863 | 1606420 | 1574293
6925 | 2008-10-16 12:00 | 744 | 858 | 147 | 24.2 | 3.4 | 0 | 44.2847 | 199.199 | 23.2889 | 0 | 744 | 785.361 | 180.564 | 6.9707 | 785.361 | 168.979 | 0.036385 | 781.878 | 162.725 | 0.027417 | 916.292 | 916.285 | 2057740 | 47.1417 | 2061890 | 1869060 | 1823850 | 0 | 0 | 1795310 | 669.429 | 0 | 0 | 0 | 0 | 1795310 | 669.429 | 1761110 | 1725886.875
6926 | 2008-10-16 13:00 | 664 | 948 | 77 | 25.9 | 3.4 | 0 | 38.385 | 217.344 | 34.297 | 0 | 664 | 780.969 | 94.1113 | 6.2212 | 780.969 | 88.0729 | 0.032472 | 772.75 | 84.8134 | 0.024469 | 831.861 | 831.857 | 1868130 | 46.7278 | 1862530 | 1690480 | 1650380 | 0 | 0 | 1626790 | 667.479 | 0 | 0 | 0 | 0 | 1626790 | 667.479 | 1598470 | 1566496.875
6927 | 2008-10-16 14:00 | 505 | 889 | 65 | 26.32 | 3.4 | 0 | 29.6771 | 231.838 | 47.499 | 0 | 505 | 600.401 | 80.1771 | 4.7315 | 600.401 | 75.0328 | 0.024697 | 585.986 | 72.2558 | 0.018609 | 638.513 | 638.507 | 1433920 | 42.3067 | 1408510 | 1303140 | 1272030 | 0 | 0 | 1258190 | 674.131 | 0 | 0 | 0 | 0 | 1258190 | 674.131 | 1239230 | 1214441.875
6928 | 2008-10-16 15:00 | 315 | 788 | 55 | 26.74 | 4.91 | 0 | 19.2265 | 243.386 | 61.4964 | 0 | 315 | 376.782 | 70.7628 | 2.9513 | 376.782 | 66.2225 | 0.015405 | 356.144 | 63.7717 | 0.011608 | 407.329 | 407.33 | 914757 | 35.9775 | 873999 | 831150 | 809806 | 0 | 0 | 804240 | 679.794 | 0 | 0 | 0 | 0 | 804240 | 679.794 | 792989 | 777129.625
6929 | 2008-10-16 16:00 | 87 | 525 | 15 | 27.16 | 4.91 | 0 | 7.7479 | 253.019 | 75.8486 | 0 | 87 | 130.571 | 20.6959 | 0.81512 | 121.074 | 19.368 | 0.0042547 | 102.366 | 18.6512 | 0.003206 | 117.39 | 117.368 | 263578 | 29.8217 | 230001 | 224424 | 215510 | 0 | 0 | 215070 | 648.106 | 0 | 0 | 0 | 816.011 | 214254 | 660 | 208867 | 204689.3594
6930 | 2008-10-16 17:00 | 1 | 51 | 0 | 26.02 | 4.91 | 0 | -4.3072 | 261.63 | 90 | 0 | 1 | 0 | 0 | 0.0093692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.02 | 0 | 0 | 0 | 0 | 0 | 0 | 660 | 0 | 0 | 0 | 0 | 0 | 660 | 0 | 0
6931 | 2008-10-16 18:00 | 0 | 0 | 0 | 24.88 | 4.13 | 0
6932 | 2008-10-16 19:00 | 0 | 0 | 0 | 23.74 | 4.13 | 0
6933 | 2008-10-16 20:00 | 0 | 0 | 0 | 22.96 | 4.13 | 0
6934 | 2008-10-16 21:00 | 0 | 0 | 0 | 22.17 | 2.5 | 0
6935 | 2008-10-16 22:00 | 0 | 0 | 0 | 21.39 | 2.5 | 0
6936 | 2008-10-16 23:00 | 0 | 0 | 0 | 20.83 | 2.5 | 0
6937 | 2008-10-17 | 0 | 0 | 0 | 20.28 | 2.63 | 0
6938 | 2008-10-17 01:00 | 0 | 0 | 0 | 19.72 | 2.63 | 0
6939 | 2008-10-17 02:00 | 0 | 0 | 0 | 19.19 | 2.63 | 0
6940 | 2008-10-17 03:00 | 0 | 0 | 0 | 18.65 | 5.13 | 0
6941 | 2008-10-17 04:00 | 0 | 0 | 0 | 18.11 | 5.13 | 0
6942 | 2008-10-17 05:00 | 0 | 4 | 0 | 17.37 | 5.13 | 0
6943 | 2008-10-17 06:00 | 76 | 450 | 30 | 16.62 | 2.3 | 0 | 5.7586 | 105.751 | 78.1656 | 0 | 76 | 94.0215 | 38.5179 | 0.71206 | 7.1615 | 36.0466 | 0.0037167 | 5.7736 | 34.7125 | 0.0028006 | 39.2742 | 39.2763 | 88219.1 | 17.6778 | 69036.7 | 71605.3 | 64407 | 0 | 0 | 64361.8 | 630.751 | 0 | 0 | 0 | 1374.94 | 62986.9 | 660 | 60834.1 | 59617.3789
6944 | 2008-10-17 07:00 | 285 | 770 | 56 | 15.88 | 2.3 | 0 | 17.3202 | 115.19 | 63.798 | 0 | 285 | 339.63 | 71.5085 | 2.6702 | 288.491 | 66.9204 | 0.013938 | 270.247 | 64.4437 | 0.010502 | 324.66 | 324.544 | 728818 | 24.6209 | 689453 | 687441 | 617241 | 0 | 0 | 613974 | 698.584 | 0 | 0 | 0 | 960.163 | 613014 | 702.407 | 603350 | 591283.3125
6945 | 2008-10-17 08:00 | 479 | 882 | 66 | 18.01 | 2.3 | 0 | 27.9283 | 126.387 | 49.7595 | 0 | 479 | 569.633 | 81.4562 | 4.4879 | 566.247 | 76.2299 | 0.023425 | 550.732 | 73.4086 | 0.017651 | 605.433 | 605.397 | 1359570 | 34.3151 | 1331480 | 1277560 | 1230600 | 0 | 0 | 1218340 | 693.644 | 0 | 0 | 0 | 0 | 1218340 | 693.644 | 1199310 | 1175323
6946 | 2008-10-17 09:00 | 636 | 936 | 75 | 20.14 | 2.08 | 0 | 36.9171 | 140.347 | 36.4355 | 0 | 636 | 751.407 | 91.9404 | 5.9588 | 751.407 | 86.0413 | 0.031103 | 742.279 | 82.857 | 0.023437 | 800.405 | 800.402 | 1797500 | 42.0159 | 1788390 | 1659090 | 1618520 | 0 | 0 | 1596670 | 680.776 | 0 | 0 | 0 | 0 | 1596670 | 680.776 | 1568910 | 1537535
6947 | 2008-10-17 10:00 | 743 | 969 | 80 | 22.28 | 2.08 | 0 | 43.2799 | 157.86 | 24.9986 | 0 | 743 | 876.489 | 97.6948 | 6.9613 | 876.489 | 91.4265 | 0.036336 | 871.959 | 88.0429 | 0.02738 | 931.228 | 931.223 | 2091290 | 47.7313 | 2097210 | 1895960 | 1850340 | 0 | 0 | 1820630 | 665.589 | 0 | 0 | 0 | 0 | 1820630 | 665.589 | 1785570 | 1749855.875
6948 | 2008-10-17 11:00 | 782 | 977 | 83 | 23.46 | 2.08 | 0 | 45.8309 | 178.368 | 19.1899 | 0 | 782 | 920.357 | 101.145 | 7.3267 | 920.357 | 94.6552 | 0.038243 | 917.649 | 91.1521 | 0.028817 | 978.565 | 978.559 | 2197590 | 50.2051 | 2209210 | 1974510 | 1928760 | 0 | 0 | 1896040 | 660.567 | 0 | 0 | 0 | 148.936 | 1895890 | 661.149 | 1858040 | 1820877.125
6949 | 2008-10-17 12:00 | 753 | 970 | 82 | 24.65 | 2.92 | 0 | 43.9205 | 199.126 | 23.6119 | 0 | 753 | 886.347 | 100.021 | 7.055 | 886.347 | 93.6039 | 0.036825 | 882.298 | 90.1396 | 0.027748 | 943.291 | 943.288 | 2118380 | 49.0298 | 2125750 | 1910120 | 1863860 | 0 | 0 | 1833500 | 663.282 | 0 | 0 | 0 | -62.4222 | 1833560 | 663.516 | 1798050 | 1762092.125
6950 | 2008-10-17 13:00 | 637 | 872 | 101 | 25.84 | 2.92 | 0 | 38.0457 | 217.164 | 34.5354 | 0 | 637 | 716.456 | 128.019 | 5.9682 | 716.456 | 119.805 | 0.031152 | 708.793 | 115.371 | 0.023474 | 799.462 | 799.46 | 1795390 | 46.5025 | 1786180 | 1622430 | 1583720 | 0 | 0 | 1561940 | 666.56 | 0 | 0 | 0 | 0 | 1561940 | 666.56 | 1535760 | 1505040.25
6951 | 2008-10-17 14:00 | 507 | 898 | 67 | 26.63 | 2.92 | 0 | 29.3698 | 231.606 | 47.6828 | 0 | 507 | 603.989 | 82.6718 | 4.7502 | 603.989 | 77.3674 | 0.024794 | 589.331 | 74.5041 | 0.018683 | 643.938 | 643.935 | 1446110 | 43.2728 | 1421180 | 1308920 | 1277710 | 0 | 0 | 1263560 | 669.689 | 0 | 0 | 0 | 0 | 1263560 | 669.689 | 1244690 | 1219793
6952 | 2008-10-17 15:00 | 296 | 746 | 54 | 27.42 | 3.85 | 0 | 18.9473 | 243.133 | 61.646 | 0 | 296 | 353.96 | 69.7942 | 2.7733 | 353.96 | 65.316 | 0.014476 | 334.393 | 62.8987 | 0.010908 | 385.383 | 385.381 | 865468 | 36.7872 | 823969 | 780351 | 761946 | 0 | 0 | 756943 | 674.614 | 0 | 0 | 0 | 0 | 756943 | 674.614 | 746550 | 731618.875
6953 | 2008-10-17 16:00 | 101 | 0 | 101 | 28.21 | 3.85 | 0 | 7.4895 | 252.755 | 75.9747 | 0 | 101 | 0 | 113.711 | 0.94629 | 0 | 106.415 | 0.0049393 | 0 | 102.476 | 0.0037219 | 99.4057 | 99.4039 | 223236 | 30.6261 | 191844 | 186374 | 181574 | 0 | 0 | 181254 | 638.161 | 0 | 0 | 0 | 2819.2 | 178435 | 660 | 173565 | 170094.0156
6954 | 2008-10-17 17:00 | 1 | 0 | 1 | 27.67 | 3.85 | 0 | -4.5527 | 261.355 | 90 | 0 | 1 | 0 | 1.0027 | 0.0093692 | 0 | 0.9384 | 0 | 0 | 0.90367 | 0 | 0.87656 | 0.87651 | 1968.42 | 27.6913 | 187.711 | 188.301 | 187.422 | 0 | 0 | 187.414 | 130.777 | 0 | 0 | 0 | 187.414 | 0 | 660 | 0 | 0
6955 | 2008-10-17 18:00 | 0 | 0 | 0 | 27.13 | 3.52 | 0
6956 | 2008-10-17 19:00 | 0 | 0 | 0 | 26.58 | 3.52 | 0
6957 | 2008-10-17 20:00 | 0 | 0 | 0 | 25.82 | 3.52 | 0
6958 | 2008-10-17 21:00 | 0 | 0 | 0 | 25.06 | 4.07 | 0
6959 | 2008-10-17 22:00 | 0 | 0 | 0 | 24.3 | 4.07 | 0
6960 | 2008-10-17 23:00 | 0 | 0 | 0 | 23.59 | 4.07 | 0
6961 | 2008-10-18 | 0 | 0 | 0 | 22.87 | 5.77 | 0
6962 | 2008-10-18 01:00 | 0 | 0 | 0 | 22.16 | 5.77 | 0
6963 | 2008-10-18 02:00 | 0 | 0 | 0 | 21.58 | 5.77 | 0
6964 | 2008-10-18 03:00 | 0 | 0 | 0 | 20.99 | 4.22 | 0
6965 | 2008-10-18 04:00 | 0 | 0 | 0 | 20.41 | 4.22 | 0
6966 | 2008-10-18 05:00 | 0 | 1 | 0 | 19.81 | 4.22 | 0
6967 | 2008-10-18 06:00 | 74 | 446 | 29 | 19.22 | 3.76 | 0 | 5.5806 | 106.073 | 78.1948 | 0 | 74 | 94.671 | 37.6733 | 0.69332 | 6.0465 | 35.2561 | 0.0036189 | 4.8711 | 33.9513 | 0.0027269 | 37.6603 | 37.6601 | 84584.3 | 20.1408 | 65798.2 | 67411.3 | 61632.2 | 0 | 0 | 61589.6 | 623.405 | 0 | 0 | 0 | 2585.82 | 59003.8 | 660 | 56973.1 | 55833.6016
6968 | 2008-10-18 07:00 | 275 | 755 | 53 | 18.63 | 3.76 | 0 | 17.118 | 115.509 | 63.8513 | 0 | 275 | 332.39 | 68.3616 | 2.5765 | 280.751 | 63.9754 | 0.013449 | 262.936 | 61.6077 | 0.010134 | 314.817 | 314.688 | 706690 | 26.3243 | 667295 | 660500 | 590550 | 0 | 0 | 587481 | 690.495 | 0 | 0 | 0 | 216.667 | 587265 | 696.691 | 578084 | 566522.0625
6969 | 2008-10-18 08:00 | 469 | 869 | 66 | 20.57 | 3.76 | 0 | 27.6911 | 126.702 | 49.8483 | 0 | 469 | 559.195 | 81.6257 | 4.3942 | 555.046 | 76.3884 | 0.022936 | 539.759 | 73.5613 | 0.017283 | 594.938 | 594.909 | 1336020 | 35.1159 | 1307140 | 1249540 | 1201220 | 0 | 0 | 1189290 | 686.208 | 0 | 0 | 0 | 91.2788 | 1189200 | 687.381 | 1171090 | 1147666.625
6970 | 2008-10-18 09:00 | 609 | 851 | 102 | 22.52 | 7.36 | 0 | 36.6349 | 140.637 | 36.5821 | 0 | 609 | 682.275 | 129.01 | 5.7059 | 682.275 | 120.732 | 0.029783 | 673.906 | 116.264 | 0.022442 | 766.487 | 766.479 | 1721320 | 37.3705 | 1708550 | 1618840 | 1577150 | 0 | 0 | 1557270 | 695.822 | 0 | 0 | 0 | 0 | 1557270 | 695.822 | 1530220 | 1499618.625
6971 | 2008-10-18 10:00 | 738 | 968 | 80 | 24.46 | 7.36 | 0 | 42.9504 | 158.077 | 25.2453 | 0 | 738 | 873.474 | 97.8691 | 6.9145 | 873.474 | 91.5897 | 0.036091 | 868.862 | 88.2 | 0.027196 | 928.377 | 928.371 | 2084890 | 42.4472 | 2090470 | 1937260 | 1889610 | 0 | 0 | 1860170 | 683.62 | 0 | 0 | 0 | 0 | 1860170 | 683.62 | 1823400 | 1786931
6972 | 2008-10-18 11:00 | 777 | 924 | 120 | 25.15 | 7.36 | 0 | 45.4697 | 178.447 | 19.549 | 0 | 777 | 868.489 | 151.919 | 7.2799 | 868.489 | 142.172 | 0.037998 | 865.832 | 136.91 | 0.028633 | 972.688 | 972.684 | 2184410 | 43.9957 | 2195320 | 2020480 | 1969760 | 0 | 0 | 1937600 | 680.698 | 0 | 0 | 0 | 0 | 1937600 | 680.698 | 1898000 | 1860035.5
6973 | 2008-10-18 12:00 | 688 | 767 | 161 | 25.84 | 8.92 | 0 | 43.5593 | 199.051 | 23.9327 | 0 | 688 | 699.008 | 202.091 | 6.446 | 699.008 | 189.124 | 0.033646 | 695.721 | 182.125 | 0.025353 | 851.535 | 851.529 | 1912320 | 40.7988 | 1908940 | 1781640 | 1736180 | 0 | 0 | 1711570 | 687.244 | 0 | 0 | 0 | 0 | 1711570 | 687.244 | 1679900 | 1646297.5
6974 | 2008-10-18 13:00 | 653 | 844 | 138 | 26.53 | 8.92 | 0 | 37.7094 | 216.983 | 34.7723 | 0 | 653 | 691.621 | 173.313 | 6.1181 | 691.621 | 162.193 | 0.031934 | 684.103 | 156.19 | 0.024063 | 815.108 | 815.097 | 1830510 | 40.8488 | 1823030 | 1700680 | 1659410 | 0 | 0 | 1636800 | 686.001 | 0 | 0 | 0 | 0 | 1636800 | 686.001 | 1607590 | 1575442
6975 | 2008-10-18 14:00 | 469 | 805 | 78 | 26.64 | 8.92 | 0 | 29.0655 | 231.374 | 47.865 | 0 | 469 | 539.953 | 99.7888 | 4.3942 | 539.953 | 93.3862 | 0.022936 | 526.708 | 89.93 | 0.017283 | 598.156 | 598.152 | 1343290 | 37.1477 | 1314380 | 1245340 | 1214410 | 0 | 0 | 1202310 | 688.601 | 0 | 0 | 0 | 0 | 1202310 | 688.601 | 1183850 | 1160171.125
6976 | 2008-10-18 15:00 | 283 | 716 | 54 | 26.74 | 8.42 | 0 | 18.6713 | 242.881 | 61.7934 | 0 | 283 | 338.096 | 69.9609 | 2.6515 | 338.096 | 65.4721 | 0.01384 | 319.235 | 63.049 | 0.010429 | 370.826 | 370.823 | 832774 | 33.4607 | 790868 | 760802 | 742032 | 0 | 0 | 737416 | 684.188 | 0 | 0 | 0 | 0 | 737416 | 684.188 | 726938 | 712398.9375
6977 | 2008-10-18 16:00 | 65 | 0 | 65 | 26.85 | 8.42 | 0 | 7.2345 | 252.492 | 76.0983 | 0 | 65 | 0 | 66.9567 | 0.609 | 0 | 62.6607 | 0.0031788 | 0 | 60.3416 | 0.0023953 | 58.5337 | 58.5297 | 131442 | 27.9108 | 107125 | 105478 | 102807 | 0 | 0 | 102699 | 622.644 | 0 | 0 | 0 | 5211.46 | 97487.1 | 660 | 94353 | 92465.8984
6978 | 2008-10-18 17:00 | 1 | 0 | 1 | 25.39 | 8.42 | 0 | -4.7946 | 261.082 | 90 | 0 | 1 | 0 | 1.003 | 0.0093692 | 0 | 0.9386 | 0 | 0 | 0.90387 | 0 | 0.87675 | 0.87673 | 1968.91 | 25.4059 | 187.823 | 187.912 | 187.017 | 0 | 0 | 187.009 | 130.728 | 0 | 0 | 0 | 187.009 | 0 | 660 | 0 | 0
6979 | 2008-10-18 18:00 | 0 | 0 | 0 | 23.93 | 9.52 | 0
6980 | 2008-10-18 19:00 | 0 | 0 | 0 | 22.47 | 9.52 | 0
6981 | 2008-10-18 20:00 | 0 | 0 | 0 | 21.47 | 9.52 | 0
6982 | 2008-10-18 21:00 | 0 | 0 | 0 | 20.48 | 8.96 | 0
6983 | 2008-10-18 22:00 | 0 | 0 | 0 | 19.48 | 8.96 | 0
6984 | 2008-10-18 23:00 | 0 | 0 | 0 | 18.74 | 8.96 | 0
6985 | 2008-10-19 | 0 | 0 | 0 | 17.99 | 9.89 | 0
6986 | 2008-10-19 01:00 | 0 | 0 | 0 | 17.24 | 9.89 | 0
6987 | 2008-10-19 02:00 | 0 | 0 | 0 | 16.89 | 9.89 | 0
6988 | 2008-10-19 03:00 | 0 | 0 | 0 | 16.53 | 5.39 | 0
6989 | 2008-10-19 04:00 | 0 | 0 | 0 | 16.17 | 5.39 | 0
6990 | 2008-10-19 05:00 | 0 | 0 | 0 | 15.77 | 5.39 | 0
6991 | 2008-10-19 06:00 | 70 | 437 | 27 | 15.38 | 5.35 | 0 | 5.4017 | 106.39 | 78.2265 | 0 | 70 | 93.2022 | 35.9723 | 0.65585 | 5.1419 | 33.6642 | 0.0034233 | 4.139 | 32.4183 | 0.0025795 | 35.4631 | 35.4786 | 79685.5 | 16.1619 | 61469.6 | 64289.3 | 59292.6 | 0 | 0 | 59254.1 | 631.207 | 0 | 0 | 0 | 1259.65 | 57994.4 | 660 | 55995.1 | 54875.207
6992 | 2008-10-19 07:00 | 278 | 765 | 55 | 14.98 | 5.35 | 0 | 16.9149 | 115.824 | 63.9075 | 0 | 278 | 337.102 | 70.7522 | 2.6046 | 282.906 | 66.2126 | 0.013595 | 264.89 | 63.7621 | 0.010244 | 318.803 | 318.726 | 715751 | 22.0045 | 676532 | 682872 | 610320 | 0 | 0 | 607153 | 702.507 | 0 | 0 | 0 | 2491.25 | 604662 | 710.716 | 594788 | 582892.1875
6993 | 2008-10-19 08:00 | 473 | 882 | 67 | 17.13 | 5.35 | 0 | 27.4532 | 127.011 | 49.9404 | 0 | 473 | 566.772 | 82.9583 | 4.4316 | 561.786 | 77.6355 | 0.023132 | 546.23 | 74.7623 | 0.01743 | 602.38 | 602.337 | 1352700 | 30.4051 | 1324510 | 1293170 | 1241830 | 0 | 0 | 1229550 | 699.734 | 0 | 0 | 0 | 0 | 1229550 | 699.734 | 1210030 | 1185827
6994 | 2008-10-19 09:00 | 629 | 939 | 74 | 19.27 | 2.63 | 0 | 36.3527 | 140.921 | 36.7323 | 0 | 629 | 750.392 | 91.1157 | 5.8932 | 750.392 | 85.2696 | 0.030761 | 741.097 | 82.1138 | 0.023179 | 798.537 | 798.535 | 1793310 | 40.3097 | 1784000 | 1668090 | 1625800 | 0 | 0 | 1604260 | 688.677 | 0 | 0 | 0 | 0 | 1604260 | 688.677 | 1576000 | 1544484.75
6995 | 2008-10-19 10:00 | 733 | 967 | 80 | 21.42 | 2.63 | 0 | 42.6219 | 158.287 | 25.4945 | 0 | 733 | 870.426 | 98.0428 | 6.8676 | 870.426 | 91.7522 | 0.035847 | 865.731 | 88.3565 | 0.027011 | 925.491 | 925.487 | 2078410 | 45.8046 | 2083650 | 1900870 | 1855000 | 0 | 0 | 1825890 | 674.216 | 0 | 0 | 0 | 0 | 1825890 | 674.216 | 1790500 | 1754691.25
6996 | 2008-10-19 11:00 | 772 | 976 | 83 | 22.5 | 2.63 | 0 | 45.1108 | 178.521 | 19.906 | 0 | 772 | 914.41 | 101.501 | 7.233 | 914.41 | 94.9885 | 0.037754 | 911.505 | 91.473 | 0.028448 | 972.916 | 972.91 | 2184920 | 48.1341 | 2195850 | 1982010 | 1933940 | 0 | 0 | 1901660 | 666.8 | 0 | 0 | 0 | 0 | 1901660 | 666.8 | 1863530 | 1826261.125
6997 | 2008-10-19 12:00 | 738 | 964 | 80 | 23.58 | 5.08 | 0 | 43.201 | 198.974 | 24.2511 | 0 | 738 | 876.379 | 98.0471 | 6.9145 | 876.379 | 91.7562 | 0.036091 | 872.138 | 88.3604 | 0.027196 | 931.71 | 931.704 | 2092370 | 44.477 | 2098350 | 1926370 | 1879750 | 0 | 0 | 1850130 | 677.685 | 0 | 0 | 0 | 0 | 1850130 | 677.685 | 1813800 | 1777526.125
6998 | 2008-10-19 13:00 | 629 | 873 | 100 | 24.66 | 5.08 | 0 | 37.3762 | 216.803 | 35.0075 | 0 | 629 | 713.771 | 127.284 | 5.8932 | 713.771 | 119.118 | 0.030761 | 705.888 | 114.709 | 0.023179 | 796.001 | 795.998 | 1787610 | 42.5133 | 1778030 | 1645690 | 1604240 | 0 | 0 | 1582730 | 680.177 | 0 | 0 | 0 | 0 | 1582730 | 680.177 | 1555430 | 1524320.75
6999 | 2008-10-19 14:00 | 486 | 879 | 64 | 24.67 | 5.08 | 0 | 28.7644 | 231.144 | 48.0453 | 0 | 486 | 586.283 | 79.4993 | 4.5534 | 586.283 | 74.3985 | 0.023767 | 571.75 | 71.6451 | 0.017909 | 624.11 | 624.108 | 1401590 | 38.668 | 1374900 | 1293770 | 1260800 | 0 | 0 | 1247630 | 685.076 | 0 | 0 | 0 | 0 | 1247630 | 685.076 | 1228380 | 1203810.625
7000 | 2008-10-19 15:00 | 293 | 758 | 54 | 24.67 | 4.38 | 0 | 18.3985 | 242.629 | 61.9386 | 0 | 293 | 356.214 | 70.126 | 2.7452 | 356.214 | 65.6265 | 0.014329 | 336.163 | 63.1978 | 0.010797 | 387.39 | 387.386 | 869974 | 33.7643 | 828534 | 796011 | 776600 | 0 | 0 | 771566 | 685.219 | 0 | 0 | 0 | 0 | 771566 | 685.219 | 760563 | 745351.375
7001 | 2008-10-19 16:00 | 93 | 0 | 93 | 24.68 | 4.38 | 0 | 6.9829 | 252.23 | 76.2192 | 0 | 93 | 0 | 106.017 | 0.87134 | 0 | 99.2147 | 0.0045481 | 0 | 95.5428 | 0.0034271 | 92.6798 | 92.6758 | 208126 | 26.8557 | 177706 | 176025 | 171516 | 0 | 0 | 171238 | 647.719 | 0 | 0 | 0 | 695.645 | 170542 | 660 | 165807 | 162490.7656
7002 | 2008-10-19 17:00 | 1 | 0 | 1 | 23.85 | 4.38 | 0 | -5.0328 | 260.808 | 90 | 0 | 1 | 0 | 1.0032 | 0.0093692 | 0 | 0.9388 | 0 | 0 | 0.90406 | 0 | 0.87694 | 0.87691 | 1969.31 | 23.8706 | 187.883 | 187.634 | 186.759 | 0 | 0 | 186.751 | 130.586 | 0 | 0 | 0 | 186.751 | 0 | 660 | 0 | 0
7003 | 2008-10-19 18:00 | 0 | 0 | 0 | 23.01 | 3.77 | 0
7004 | 2008-10-19 19:00 | 0 | 0 | 0 | 22.18 | 3.77 | 0
7005 | 2008-10-19 20:00 | 0 | 0 | 0 | 21.34 | 3.77 | 0
7006 | 2008-10-19 21:00 | 0 | 0 | 0 | 20.51 | 3.38 | 0
7007 | 2008-10-19 22:00 | 0 | 0 | 0 | 19.67 | 3.38 | 0
7008 | 2008-10-19 23:00 | 0 | 0 | 0 | 18.98 | 3.38 | 0
7009 | 2008-10-20 | 0 | 0 | 0 | 18.28 | 3.12 | 0
7010 | 2008-10-20 01:00 | 0 | 0 | 0 | 17.59 | 3.12 | 0
7011 | 2008-10-20 02:00 | 0 | 0 | 0 | 16.55 | 3.12 | 0
7012 | 2008-10-20 03:00 | 0 | 0 | 0 | 15.51 | 3.51 | 0
7013 | 2008-10-20 04:00 | 0 | 0 | 0 | 14.48 | 3.51 | 0
7014 | 2008-10-20 05:00 | 0 | 0 | 0 | 13.98 | 3.51 | 0
7015 | 2008-10-20 06:00 | 67 | 422 | 26 | 13.48 | 5.08 | 0 | 5.222 | 106.704 | 78.2608 | 0 | 67 | 91.6527 | 35.1292 | 0.62774 | 4.3499 | 32.8753 | 0.0032766 | 3.4984 | 31.6586 | 0.002469 | 34.1046 | 34.0989 | 76583.5 | 14.2448 | 58711.9 | 62008.3 | 57513.1 | 0 | 0 | 57478.1 | 640.127 | 0 | 0 | 0 | 668.201 | 56809.9 | 660 | 54847.7 | 53750.7461
7016 | 2008-10-20 07:00 | 272 | 758 | 54 | 12.99 | 5.08 | 0 | 16.7109 | 116.134 | 63.9667 | 0 | 272 | 332.746 | 69.8176 | 2.5484 | 277.538 | 65.338 | 0.013302 | 259.797 | 62.9199 | 0.010023 | 313.045 | 313.099 | 703110 | 20.0124 | 663889 | 675917 | 602018 | 0 | 0 | 599031 | 714.677 | 0 | 0 | 0 | 1564.09 | 597467 | 717.94 | 587470 | 575721
7017 | 2008-10-20 08:00 | 448 | 800 | 83 | 15.58 | 5.08 | 0 | 27.2146 | 127.315 | 50.036 | 0 | 448 | 512.637 | 105.382 | 4.1974 | 507.422 | 98.6206 | 0.021909 | 493.293 | 94.9707 | 0.016509 | 570.632 | 570.619 | 1281470 | 28.3783 | 1250710 | 1231910 | 1180860 | 0 | 0 | 1169890 | 704.328 | 0 | 0 | 0 | 0 | 1169890 | 704.328 | 1151380 | 1128350
7018 | 2008-10-20 09:00 | 603 | 894 | 78 | 18.17 | 2.14 | 0 | 36.0705 | 141.198 | 36.886 | 0 | 603 | 713.188 | 95.9453 | 5.6496 | 713.188 | 89.7893 | 0.029489 | 704.263 | 86.4662 | 0.022221 | 767.029 | 767.025 | 1722540 | 39.0499 | 1709830 | 1607640 | 1567140 | 0 | 0 | 1547220 | 690.523 | 0 | 0 | 0 | 0 | 1547220 | 690.523 | 1520670 | 1490252.5
7019 | 2008-10-20 10:00 | 718 | 951 | 80 | 20.76 | 2.14 | 0 | 42.2946 | 158.49 | 25.7459 | 0 | 718 | 853.959 | 98.2158 | 6.7271 | 853.959 | 91.9141 | 0.035113 | 849.253 | 88.5124 | 0.026458 | 909.658 | 909.654 | 2042850 | 45.5225 | 2046220 | 1868960 | 1824920 | 0 | 0 | 1796670 | 673.487 | 0 | 0 | 0 | 0 | 1796670 | 673.487 | 1762350 | 1727099
7020 | 2008-10-20 11:00 | 767 | 975 | 83 | 22.39 | 2.14 | 0 | 44.7543 | 178.59 | 20.2608 | 0 | 767 | 911.388 | 101.678 | 7.1862 | 911.388 | 95.154 | 0.03751 | 908.382 | 91.6324 | 0.028264 | 970.041 | 970.039 | 2178460 | 48.7963 | 2189050 | 1969610 | 1922490 | 0 | 0 | 1890130 | 662.292 | 0 | 0 | 0 | -16.7514 | 1890150 | 662.368 | 1852510 | 1815458.75
7021 | 2008-10-20 12:00 | 738 | 969 | 81 | 24.02 | 3.54 | 0 | 42.8459 | 198.896 | 24.5671 | 0 | 738 | 878.676 | 99.387 | 6.9145 | 878.676 | 93.0101 | 0.036091 | 874.303 | 89.5679 | 0.027196 | 934.981 | 934.976 | 2099710 | 47.2144 | 2106080 | 1908770 | 1861980 | 0 | 0 | 1832140 | 668.231 | 0 | 0 | 0 | 0 | 1832140 | 668.231 | 1796610 | 1760681.625
7022 | 2008-10-20 13:00 | 631 | 927 | 74 | 25.65 | 3.54 | 0 | 37.0464 | 216.624 | 35.241 | 0 | 631 | 755.103 | 91.3 | 5.912 | 755.103 | 85.442 | 0.030859 | 746.631 | 82.2799 | 0.023252 | 804.066 | 804.063 | 1805720 | 45.5968 | 1797020 | 1639420 | 1601380 | 0 | 0 | 1579270 | 669.327 | 0 | 0 | 0 | 0 | 1579270 | 669.327 | 1552440 | 1521392
7023 | 2008-10-20 14:00 | 492 | 893 | 67 | 25.89 | 3.54 | 0 | 28.4667 | 230.915 | 48.2236 | 0 | 492 | 594.036 | 83.1758 | 4.6097 | 594.036 | 77.8391 | 0.024061 | 579.155 | 74.9584 | 0.01813 | 634.508 | 634.505 | 1424940 | 41.6305 | 1399160 | 1298600 | 1267020 | 0 | 0 | 1253360 | 675.632 | 0 | 0 | 0 | 0 | 1253360 | 675.632 | 1234430 | 1209741.25
7024 | 2008-10-20 15:00 | 295 | 775 | 54 | 26.13 | 2.89 | 0 | 18.1292 | 242.379 | 62.0814 | 0 | 295 | 362.642 | 70.289 | 2.7639 | 362.642 | 65.7791 | 0.014427 | 342.048 | 63.3447 | 0.010871 | 393.242 | 393.237 | 883111 | 36.3136 | 841858 | 799169 | 779894 | 0 | 0 | 774692 | 676.784 | 0 | 0 | 0 | 0 | 774692 | 676.784 | 763971 | 748691.25
7025 | 2008-10-20 16:00 | 76 | 517 | 14 | 26.37 | 2.89 | 0 | 6.7349 | 251.968 | 76.3374 | 0 | 76 | 124.875 | 20.0469 | 0.71206 | 106.709 | 18.7607 | 0.0037167 | 89.4559 | 18.0664 | 0.0028006 | 104.299 | 104.285 | 234198 | 29.0707 | 202753 | 198401 | 183699 | 0 | 0 | 183368 | 645.948 | 0 | 0 | 0 | 1122.75 | 182246 | 660 | 177314 | 173767.4844
7026 | 2008-10-20 17:00 | 0 | 29 | 0 | 25.3 | 2.89 | 0
7027 | 2008-10-20 18:00 | 0 | 0 | 0 | 24.23 | 5.47 | 0
7028 | 2008-10-20 19:00 | 0 | 0 | 0 | 23.16 | 5.47 | 0
7029 | 2008-10-20 20:00 | 0 | 0 | 0 | 22.22 | 5.47 | 0
7030 | 2008-10-20 21:00 | 0 | 0 | 0 | 21.28 | 2.02 | 0
7031 | 2008-10-20 22:00 | 0 | 0 | 0 | 20.35 | 2.02 | 0
7032 | 2008-10-20 23:00 | 0 | 0 | 0 | 19.47 | 2.02 | 0
7033 | 2008-10-21 | 0 | 0 | 0 | 18.59 | 1.05 | 0
7034 | 2008-10-21 01:00 | 0 | 0 | 0 | 17.71 | 1.05 | 0
7035 | 2008-10-21 02:00 | 0 | 0 | 0 | 16.98 | 1.05 | 0
7036 | 2008-10-21 03:00 | 0 | 0 | 0 | 16.26 | 2.95 | 0
7037 | 2008-10-21 04:00 | 0 | 0 | 0 | 15.54 | 2.95 | 0
7038 | 2008-10-21 05:00 | 0 | 0 | 0 | 15.11 | 2.95 | 0
7039 | 2008-10-21 06:00 | 62 | 384 | 26 | 14.68 | 4.71 | 0 | 5.0414 | 107.014 | 78.2978 | 0 | 62 | 83.0912 | 35.1496 | 0.58089 | 3.5138 | 32.8943 | 0.0030321 | 2.8233 | 31.6769 | 0.0022847 | 33.4674 | 33.4638 | 75156.1 | 15.4488 | 57392.7 | 60274.2 | 57224.5 | 0 | 0 | 57189.2 | 634.822 | 0 | 0 | 0 | 1057.32 | 56131.9 | 660 | 54190.5 | 53106.707
7040 | 2008-10-21 07:00 | 254 | 695 | 56 | 14.26 | 4.71 | 0 | 16.5061 | 116.44 | 64.029 | 0 | 254 | 305.182 | 72.1773 | 2.3798 | 252.829 | 67.5462 | 0.012422 | 236.603 | 65.0464 | 0.00936 | 292.609 | 292.602 | 657076 | 20.9827 | 617556 | 626262 | 556955 | 0 | 0 | 554364 | 710.296 | 0 | 0 | 0 | 326.069 | 554037 | 712.571 | 544801 | 533905.4375
7041 | 2008-10-21 08:00 | 436 | 779 | 83 | 16.61 | 4.71 | 0 | 26.9755 | 127.613 | 50.1349 | 0 | 436 | 498.813 | 105.57 | 4.085 | 492.835 | 98.7968 | 0.021322 | 479.033 | 95.1404 | 0.016067 | 556.964 | 556.933 | 1250740 | 29.4058 | 1218970 | 1195140 | 1137540 | 0 | 0 | 1127210 | 700.27 | 0 | 0 | 0 | -2.2604 | 1127210 | 700.295 | 1109760 | 1087566.125
7042 | 2008-10-21 09:00 | 568 | 770 | 119 | 18.95 | 4.27 | 0 | 35.7885 | 141.469 | 37.0432 | 0 | 568 | 612.836 | 151.974 | 5.3217 | 612.836 | 142.223 | 0.027778 | 605.088 | 136.96 | 0.020931 | 719.807 | 719.798 | 1616490 | 35.9701 | 1598860 | 1524090 | 1486090 | 0 | 0 | 1468540 | 698.392 | 0 | 0 | 0 | 0 | 1468540 | 698.392 | 1443820 | 1414943.125
7043 | 2008-10-21 10:00 | 676 | 828 | 124 | 21.3 | 4.27 | 0 | 41.9686 | 158.686 | 25.9994 | 0 | 676 | 741.917 | 156.296 | 6.3336 | 741.917 | 146.268 | 0.033059 | 737.74 | 140.854 | 0.024911 | 852.261 | 852.255 | 1913940 | 41.4521 | 1910650 | 1777800 | 1734020 | 0 | 0 | 1709370 | 685.732 | 0 | 0 | 0 | 0 | 1709370 | 685.732 | 1677800 | 1644241.5
7044 | 2008-10-21 11:00 | 744 | 901 | 115 | 22.91 | 4.27 | 0 | 44.4003 | 178.654 | 20.6133 | 0 | 744 | 841.443 | 146.865 | 6.9707 | 841.443 | 137.442 | 0.036385 | 838.566 | 132.355 | 0.027417 | 941.82 | 941.816 | 2115080 | 45.1799 | 2122260 | 1942040 | 1895440 | 0 | 0 | 1865080 | 674.632 | 0 | 0 | 0 | 0 | 1865080 | 674.632 | 1828250 | 1791680.75
7045 | 2008-10-21 12:00 | 685 | 793 | 151 | 24.51 | 4.48 | 0 | 42.494 | 198.815 | 24.8804 | 0 | 685 | 717.141 | 191.577 | 6.4179 | 717.141 | 179.285 | 0.033499 | 713.473 | 172.65 | 0.025243 | 859.564 | 859.552 | 1930330 | 44.5574 | 1927870 | 1768240 | 1723840 | 0 | 0 | 1698720 | 675.112 | 0 | 0 | 0 | 0 | 1698720 | 675.112 | 1667780 | 1634420.25
7046 | 2008-10-21 13:00 | 621 | 876 | 98 | 26.12 | 4.48 | 0 | 36.7199 | 216.444 | 35.4724 | 0 | 621 | 712.369 | 125.395 | 5.8183 | 712.369 | 117.349 | 0.03037 | 704.252 | 113.006 | 0.022884 | 792.762 | 792.759 | 1780340 | 44.6096 | 1770400 | 1622550 | 1581500 | 0 | 0 | 1560190 | 673.351 | 0 | 0 | 0 | 0 | 1560190 | 673.351 | 1533830 | 1503150.125
7047 | 2008-10-21 14:00 | 478 | 879 | 64 | 26.47 | 4.48 | 0 | 28.1724 | 230.686 | 48.3998 | 0 | 478 | 582.189 | 79.8258 | 4.4785 | 582.189 | 74.7041 | 0.023376 | 567.454 | 71.9393 | 0.017614 | 620.228 | 620.228 | 1392870 | 40.9356 | 1365840 | 1271660 | 1242150 | 0 | 0 | 1229140 | 678.968 | 0 | 0 | 0 | 0 | 1229140 | 678.968 | 1210570 | 1186358.125
7048 | 2008-10-21 15:00 | 295 | 781 | 55 | 26.82 | 4.1 | 0 | 17.8634 | 242.129 | 62.2218 | 0 | 295 | 364.637 | 71.5772 | 2.7639 | 364.637 | 66.9847 | 0.014427 | 343.749 | 64.5056 | 0.010871 | 396.017 | 396.014 | 889348 | 36.2889 | 848189 | 805305 | 785356 | 0 | 0 | 780084 | 677.061 | 0 | 0 | 0 | 0 | 780084 | 677.061 | 769277 | 753891.8125
7049 | 2008-10-21 16:00 | 74 | 521 | 14 | 27.17 | 4.1 | 0 | 6.4906 | 251.707 | 76.4527 | 0 | 74 | 124.336 | 20.2362 | 0.69332 | 101.727 | 18.9378 | 0.0036189 | 85.0994 | 18.2369 | 0.0027269 | 100.239 | 100.217 | 225064 | 29.5663 | 194638 | 189880 | 172221 | 0 | 0 | 171918 | 641.392 | 0 | 0 | 0 | 1784.13 | 170134 | 660 | 165406 | 162098.0938
7050 | 2008-10-21 17:00 | 0 | 24 | 0 | 26.16 | 4.1 | 0
7051 | 2008-10-21 18:00 | 0 | 0 | 0 | 25.16 | 5.3 | 0
7052 | 2008-10-21 19:00 | 0 | 0 | 0 | 24.15 | 5.3 | 0
7053 | 2008-10-21 20:00 | 0 | 0 | 0 | 23.08 | 5.3 | 0
7054 | 2008-10-21 21:00 | 0 | 0 | 0 | 22 | 7.68 | 0
7055 | 2008-10-21 22:00 | 0 | 0 | 0 | 20.92 | 7.68 | 0
7056 | 2008-10-21 23:00 | 0 | 0 | 0 | 20.04 | 7.68 | 0
7057 | 2008-10-22 | 0 | 0 | 0 | 19.16 | 11.97 | 0
7058 | 2008-10-22 01:00 | 0 | 0 | 0 | 18.28 | 11.97 | 0
7059 | 2008-10-22 02:00 | 0 | 0 | 0 | 17.48 | 11.97 | 0
7060 | 2008-10-22 03:00 | 0 | 0 | 0 | 16.68 | 8.05 | 0
7061 | 2008-10-22 04:00 | 0 | 0 | 0 | 15.88 | 8.05 | 0
7062 | 2008-10-22 05:00 | 0 | 0 | 0 | 15.78 | 8.05 | 0
7063 | 2008-10-22 06:00 | 61 | 404 | 23 | 15.67 | 9.08 | 0 | 4.8601 | 107.32 | 78.3374 | 0 | 61 | 88.2943 | 32.1893 | 0.57152 | 3.5973 | 30.1239 | 0.0029831 | 2.8874 | 29.0091 | 0.0022479 | 30.9418 | 30.9471 | 69502.8 | 16.2083 | 52538.8 | 54971.2 | 52194.8 | 0 | 0 | 52164 | 629.95 | 0 | 0 | 0 | 1464.43 | 50699.6 | 660 | 48930.4 | 47951.7773
7064 | 2008-10-22 07:00 | 253 | 719 | 51 | 15.57 | 9.08 | 0 | 16.3005 | 116.741 | 64.0942 | 0 | 253 | 314.429 | 66.8108 | 2.3704 | 258.742 | 62.5241 | 0.012373 | 242.067 | 60.2102 | 0.0093231 | 293.218 | 293.137 | 658271 | 20.6686 | 619021 | 629072 | 556774 | 0 | 0 | 554185 | 712.344 | 0 | 0 | 0 | 144.902 | 554040 | 714.632 | 544727 | 533832.0625
7065 | 2008-10-22 08:00 | 452 | 863 | 64 | 17.08 | 9.08 | 0 | 26.736 | 127.906 | 50.237 | 0 | 452 | 551.635 | 79.9589 | 4.2349 | 543.864 | 74.8286 | 0.022105 | 528.542 | 72.0592 | 0.016656 | 582.599 | 582.585 | 1308350 | 27.213 | 1278740 | 1265920 | 1202370 | 0 | 0 | 1190940 | 704.02 | 0 | 0 | 0 | 3012.47 | 1187930 | 708.354 | 1168900 | 1145520.625
7066 | 2008-10-22 09:00 | 611 | 927 | 74 | 18.59 | 6.98 | 0 | 35.5068 | 141.733 | 37.2036 | 0 | 611 | 736.427 | 91.6195 | 5.7246 | 736.427 | 85.741 | 0.02988 | 727.019 | 82.5678 | 0.022516 | 785.321 | 785.318 | 1763630 | 34.1773 | 1752880 | 1684860 | 1641290 | 0 | 0 | 1620480 | 707.65 | 0 | 0 | 0 | 0 | 1620480 | 707.65 | 1591130 | 1559309.625
7067 | 2008-10-22 10:00 | 712 | 955 | 79 | 20.1 | 6.98 | 0 | 41.644 | 158.876 | 26.2546 | 0 | 712 | 854.323 | 97.3886 | 6.6709 | 854.323 | 91.1399 | 0.03482 | 849.409 | 87.7669 | 0.026237 | 909.086 | 909.079 | 2041560 | 38.1438 | 2044860 | 1932130 | 1883950 | 0 | 0 | 1855820 | 696.873 | 0 | 0 | 0 | 0 | 1855820 | 696.873 | 1819040 | 1782654.5
7068 | 2008-10-22 11:00 | 746 | 957 | 83 | 21.09 | 6.98 | 0 | 44.049 | 178.714 | 20.9633 | 0 | 746 | 890.465 | 102.029 | 6.9894 | 890.465 | 95.4825 | 0.036483 | 887.309 | 91.9487 | 0.02749 | 949.906 | 949.901 | 2133230 | 39.944 | 2141390 | 2007400 | 1957820 | 0 | 0 | 1927040 | 692.128 | 0 | 0 | 0 | 0 | 1927040 | 692.128 | 1887750 | 1849995
7069 | 2008-10-22 12:00 | 699 | 878 | 111 | 22.07 | 6.72 | 0 | 42.1455 | 198.733 | 25.191 | 0 | 699 | 792.944 | 141.996 | 6.5491 | 792.944 | 132.885 | 0.034184 | 788.777 | 127.967 | 0.025758 | 889.267 | 889.259 | 1997060 | 40.0154 | 1998030 | 1871810 | 1826670 | 0 | 0 | 1799650 | 689.91 | 0 | 0 | 0 | 0 | 1799650 | 689.91 | 1764920 | 1729620.125
7070 | 2008-10-22 13:00 | 623 | 929 | 73 | 23.05 | 6.72 | 0 | 36.397 | 216.264 | 35.7018 | 0 | 623 | 752.701 | 90.4592 | 5.837 | 752.701 | 84.6552 | 0.030467 | 743.992 | 81.5222 | 0.022958 | 800.771 | 800.766 | 1798320 | 39.2096 | 1789250 | 1681550 | 1639850 | 0 | 0 | 1618090 | 690.54 | 0 | 0 | 0 | 0 | 1618090 | 690.54 | 1589340 | 1557557.625
7071 | 2008-10-22 14:00 | 482 | 852 | 84 | 23.28 | 6.72 | 0 | 27.8817 | 230.458 | 48.5738 | 0 | 482 | 563.114 | 107.307 | 4.516 | 563.114 | 100.422 | 0.023572 | 548.716 | 96.7051 | 0.017762 | 626.076 | 626.072 | 1406000 | 35.9142 | 1379480 | 1314640 | 1281340 | 0 | 0 | 1268080 | 694.008 | 0 | 0 | 0 | 0 | 1268080 | 694.008 | 1247980 | 1223016.25
7072 | 2008-10-22 15:00 | 259 | 622 | 71 | 23.5 | 5.02 | 0 | 17.6012 | 241.88 | 62.3597 | 0 | 259 | 288.424 | 90.9537 | 2.4266 | 288.424 | 85.118 | 0.012666 | 271.76 | 81.9678 | 0.0095442 | 343.125 | 343.122 | 770563 | 31.2259 | 728086 | 707585 | 689843 | 0 | 0 | 685902 | 688.878 | 0 | 0 | 0 | 0 | 685902 | 688.878 | 675995 | 662475.3125
7073 | 2008-10-22 16:00 | 64 | 415 | 18 | 23.73 | 5.02 | 0 | 6.2501 | 251.447 | 76.5651 | 0 | 64 | 98.1708 | 25.8444 | 0.59963 | 76.7488 | 24.1862 | 0.0031299 | 64.0698 | 23.2911 | 0.0023584 | 84.7423 | 84.7004 | 190217 | 25.6371 | 162293 | 161503 | 144202 | 0 | 0 | 143985 | 640.944 | 0 | 0 | 0 | 402.727 | 143582 | 660 | 139364 | 136576.5781
7074 | 2008-10-22 17:00 | 0 | 15 | 0 | 22.68 | 5.02 | 0
7075 | 2008-10-22 18:00 | 0 | 0 | 0 | 21.64 | 9.3 | 0
7076 | 2008-10-22 19:00 | 0 | 0 | 0 | 20.59 | 9.3 | 0
7077 | 2008-10-22 20:00 | 0 | 0 | 0 | 19.51 | 9.3 | 0
7078 | 2008-10-22 21:00 | 0 | 0 | 0 | 18.43 | 11.72 | 0
7079 | 2008-10-22 22:00 | 0 | 0 | 0 | 17.35 | 11.72 | 0
7080 | 2008-10-22 23:00 | 0 | 0 | 0 | 16.71 | 11.72 | 0
7081 | 2008-10-23 | 0 | 0 | 0 | 16.07 | 10.77 | 0
7082 | 2008-10-23 01:00 | 0 | 0 | 0 | 15.43 | 10.77 | 0
7083 | 2008-10-23 02:00 | 0 | 0 | 0 | 14.77 | 10.77 | 0
7084 | 2008-10-23 03:00 | 0 | 0 | 0 | 14.12 | 7.58 | 0
7085 | 2008-10-23 04:00 | 0 | 0 | 0 | 13.47 | 7.58 | 0
7086 | 2008-10-23 05:00 | 0 | 0 | 0 | 12.85 | 7.58 | 0
7087 | 2008-10-23 06:00 | 55 | 359 | 22 | 12.24 | 8.74 | 0 | 4.6779 | 107.621 | 78.3797 | 0 | 55 | 76.4025 | 30.8544 | 0.51531 | 3.2421 | 28.8747 | 0.0026897 | 2.5994 | 27.8061 | 0.0020268 | 29.4953 | 29.495 | 66242.7 | 12.764 | 49688.5 | 52898.6 | 50209.2 | 0 | 0 | 50182.1 | 640.306 | 0 | 0 | 0 | 581.637 | 49600.5 | 660 | 47865.8 | 46908.457
7088 | 2008-10-23 07:00 | 263 | 753 | 54 | 11.63 | 8.74 | 0 | 16.0941 | 117.037 | 64.1625 | 0 | 263 | 328.575 | 70.3063 | 2.4641 | 268.366 | 65.7953 | 0.012862 | 250.996 | 63.3602 | 0.0096916 | 304.935 | 304.819 | 684500 | 17.0451 | 645518 | 666105 | 590289 | 0 | 0 | 587461 | 723.318 | 0 | 0 | 0 | 253.65 | 587207 | 725.065 | 577117 | 565574.25
7089 | 2008-10-23 08:00 | 455 | 876 | 65 | 13.98 | 8.74 | 0 | 26.4961 | 128.193 | 50.3424 | 0 | 455 | 557.895 | 81.299 | 4.263 | 548.822 | 76.0827 | 0.022251 | 533.265 | 73.2669 | 0.016767 | 588.352 | 588.344 | 1321290 | 24.4319 | 1292260 | 1294550 | 1225190 | 0 | 0 | 1213560 | 711.123 | 0 | 0 | 0 | 1453.99 | 1212100 | 714.924 | 1192290 | 1168442.25
7090 | 2008-10-23 09:00 | 611 | 934 | 73 | 16.33 | 3.25 | 0 | 35.2254 | 141.99 | 37.3671 | 0 | 611 | 741.309 | 90.6116 | 5.7246 | 741.309 | 84.7978 | 0.02988 | 731.737 | 81.6595 | 0.022516 | 789.017 | 789.011 | 1771920 | 36.2818 | 1761570 | 1677380 | 1636230 | 0 | 0 | 1615060 | 699.631 | 0 | 0 | 0 | 0 | 1615060 | 699.631 | 1586130 | 1554403.125
7091 | 2008-10-23 10:00 | 697 | 934 | 82 | 18.68 | 3.25 | 0 | 41.3209 | 159.059 | 26.5115 | 0 | 697 | 833.484 | 101.071 | 6.5304 | 833.484 | 94.5858 | 0.034086 | 828.586 | 91.0853 | 0.025685 | 892.107 | 892.102 | 2003440 | 41.2386 | 2004750 | 1867600 | 1820830 | 0 | 0 | 1793750 | 686.687 | 0 | 0 | 0 | 0 | 1793750 | 686.687 | 1759290 | 1724101
7092 | 2008-10-23 11:00 | 738 | 952 | 82 | 20.22 | 3.25 | 0 | 43.7004 | 178.769 | 21.3107 | 0 | 738 | 884.579 | 101.032 | 6.9145 | 884.579 | 94.55 | 0.036091 | 881.333 | 91.0508 | 0.027196 | 943.239 | 943.23 | 2118250 | 44.0715 | 2125610 | 1955140 | 1907060 | 0 | 0 | 1876790 | 679.39 | 0 | 0 | 0 | 0 | 1876790 | 679.39 | 1839460 | 1802673.375
7093 | 2008-10-23 12:00 | 723 | 966 | 81 | 21.76 | 2.48 | 0 | 41.8004 | 198.649 | 25.4986 | 0 | 723 | 869.368 | 99.906 | 6.774 | 869.368 | 93.4959 | 0.035358 | 864.677 | 90.0356 | 0.026643 | 926.097 | 926.094 | 2079760 | 46.4052 | 2085080 | 1896800 | 1849380 | 0 | 0 | 1820150 | 670.795 | 0 | 0 | 0 | 0 | 1820150 | 670.795 | 1785020 | 1749323.625
7094 | 2008-10-23 13:00 | 627 | 940 | 75 | 23.3 | 2.48 | 0 | 36.0778 | 216.085 | 35.9289 | 0 | 627 | 759.03 | 92.9745 | 5.8745 | 759.03 | 87.009 | 0.030663 | 750.113 | 83.7889 | 0.023105 | 808.907 | 808.903 | 1816580 | 44.8265 | 1808420 | 1655870 | 1615500 | 0 | 0 | 1593210 | 672.58 | 0 | 0 | 0 | 0 | 1593210 | 672.58 | 1565820 | 1534507.625
7095 | 2008-10-23 14:00 | 476 | 886 | 66 | 23.73 | 2.48 | 0 | 27.5946 | 230.231 | 48.7454 | 0 | 476 | 583.655 | 82.5063 | 4.4597 | 583.655 | 77.2125 | 0.023278 | 568.582 | 74.355 | 0.017541 | 623.666 | 623.663 | 1400580 | 40.3269 | 1373850 | 1282780 | 1251380 | 0 | 0 | 1238210 | 679.898 | 0 | 0 | 0 | 0 | 1238210 | 679.898 | 1219410 | 1195021
7096 | 2008-10-23 15:00 | 264 | 710 | 52 | 24.16 | 1.95 | 0 | 17.3429 | 241.633 | 62.4949 | 0 | 264 | 328.451 | 68.4997 | 2.4735 | 328.451 | 64.1046 | 0.012911 | 309.313 | 61.7321 | 0.0097285 | 359.924 | 359.918 | 808285 | 34.0828 | 766123 | 734733 | 716862 | 0 | 0 | 712513 | 681.12 | 0 | 0 | 0 | 0 | 712513 | 681.12 | 702498 | 688447.625
7097 | 2008-10-23 16:00 | 63 | 473 | 12 | 24.59 | 1.95 | 0 | 6.0135 | 251.187 | 76.6745 | 0 | 63 | 112.202 | 17.8478 | 0.59026 | 87.7185 | 16.7027 | 0.003081 | 73.0751 | 16.0845 | 0.0023216 | 86.4871 | 86.4949 | 194246 | 26.9746 | 166470 | 164416 | 145288 | 0 | 0 | 145062 | 640.325 | 0 | 0 | 0 | 1155.45 | 143907 | 660 | 139682 | 136888.1562
7098 | 2008-10-23 17:00 | 0 | 13 | 0 | 23.81 | 1.95 | 0
7099 | 2008-10-23 18:00 | 0 | 0 | 0 | 23.04 | 2.57 | 0
7100 | 2008-10-23 19:00 | 0 | 0 | 0 | 22.26 | 2.57 | 0
7101 | 2008-10-23 20:00 | 0 | 0 | 0 | 21.57 | 2.57 | 0
7102 | 2008-10-23 21:00 | 0 | 0 | 0 | 20.88 | 2.82 | 0
7103 | 2008-10-23 22:00 | 0 | 0 | 0 | 20.2 | 2.82 | 0
7104 | 2008-10-23 23:00 | 0 | 0 | 0 | 19.46 | 2.82 | 0
7105 | 2008-10-24 | 0 | 0 | 0 | 18.72 | 2.24 | 0
7106 | 2008-10-24 01:00 | 0 | 0 | 0 | 17.98 | 2.24 | 0
7107 | 2008-10-24 02:00 | 0 | 0 | 0 | 17.46 | 2.24 | 0
7108 | 2008-10-24 03:00 | 0 | 0 | 0 | 16.93 | 2.1 | 0
7109 | 2008-10-24 04:00 | 0 | 0 | 0 | 16.41 | 2.1 | 0
7110 | 2008-10-24 05:00 | 0 | 0 | 0 | 15.99 | 2.1 | 0
7111 | 2008-10-24 06:00 | 55 | 390 | 20 | 15.56 | 2.04 | 0 | 4.4951 | 107.919 | 78.4246 | 0 | 55 | 80.7239 | 28.5422 | 0.51531 | 3.5113 | 26.7108 | 0.0026897 | 2.8119 | 25.7223 | 0.0020268 | 27.6801 | 27.6699 | 62143.4 | 16.3183 | 46217.5 | 48315.2 | 45629 | 0 | 0 | 45604.8 | 623.54 | 0 | 0 | 0 | 1925.8 | 43679 | 660 | 42136.4 | 41293.7031
7112 | 2008-10-24 07:00 | 254 | 739 | 51 | 15.14 | 2.04 | 0 | 15.8872 | 117.328 | 64.2337 | 0 | 254 | 322.361 | 67.1405 | 2.3798 | 261.343 | 62.8327 | 0.012422 | 244.35 | 60.5073 | 0.00936 | 295.721 | 295.645 | 663893 | 23.2419 | 624956 | 626415 | 554602 | 0 | 0 | 551921 | 699.364 | 0 | 0 | 0 | 468.352 | 551453 | 703.846 | 542454 | 531604.625
7113 | 2008-10-24 08:00 | 446 | 865 | 64 | 17.02 | 2.04 | 0 | 26.2559 | 128.474 | 50.4509 | 0 | 446 | 549.83 | 80.2895 | 4.1787 | 539.746 | 75.138 | 0.021811 | 524.349 | 72.3572 | 0.016435 | 578.821 | 578.752 | 1299760 | 32.8802 | 1270040 | 1225510 | 1153540 | 0 | 0 | 1142500 | 687.356 | 0 | 0 | 0 | 7293.89 | 1135210 | 693.422 | 1117920 | 1095562.625
7114 | 2008-10-24 09:00 | 592 | 906 | 74 | 18.9 | 2.8 | 0 | 34.9444 | 142.241 | 37.5336 | 0 | 592 | 717.152 | 91.9524 | 5.5466 | 717.152 | 86.0526 | 0.028951 | 707.792 | 82.8678 | 0.021815 | 766.961 | 766.956 | 1722390 | 38.8808 | 1709660 | 1608750 | 1568630 | 0 | 0 | 1548640 | 690.575 | 0 | 0 | 0 | 0 | 1548640 | 690.575 | 1522040 | 1491595.625
7115 | 2008-10-24 10:00 | 690 | 928 | 83 | 20.78 | 2.8 | 0 | 40.9995 | 159.235 | 26.7698 | 0 | 690 | 826.067 | 102.413 | 6.4648 | 826.067 | 95.8421 | 0.033744 | 821.109 | 92.2951 | 0.025427 | 886.027 | 886.021 | 1989780 | 43.8627 | 1990380 | 1831830 | 1789510 | 0 | 0 | 1762720 | 678.527 | 0 | 0 | 0 | 0 | 1762720 | 678.527 | 1729500 | 1694910.875
7116 | 2008-10-24 11:00 | 729 | 944 | 83 | 22.17 | 2.8 | 0 | 43.3548 | 178.819 | 21.6554 | 0 | 729 | 874.572 | 102.376 | 6.8302 | 874.572 | 95.8074 | 0.035651 | 871.251 | 92.2616 | 0.026864 | 934.633 | 934.631 | 2098940 | 46.5191 | 2105270 | 1914280 | 1868930 | 0 | 0 | 1839110 | 670.689 | 0 | 0 | 0 | 0 | 1839110 | 670.689 | 1803290 | 1767221.5
7117 | 2008-10-24 12:00 | 717 | 915 | 113 | 23.57 | 2.6 | 0 | 41.459 | 198.564 | 25.8031 | 0 | 717 | 821.314 | 144.69 | 6.7177 | 821.314 | 135.406 | 0.035064 | 816.766 | 130.395 | 0.026422 | 918.772 | 918.765 | 2063320 | 47.8258 | 2067760 | 1868330 | 1824110 | 0 | 0 | 1795170 | 664.67 | 0 | 0 | 0 | 0 | 1795170 | 664.67 | 1761060 | 1725838.625
7118 | 2008-10-24 13:00 | 572 | 758 | 130 | 24.96 | 2.6 | 0 | 35.7623 | 215.906 | 36.1536 | 0 | 572 | 610.666 | 165.7 | 5.3592 | 610.666 | 155.068 | 0.027973 | 603.384 | 149.329 | 0.021078 | 730.153 | 730.143 | 1639720 | 44.2361 | 1623150 | 1489350 | 1452510 | 0 | 0 | 1434420 | 671.987 | 0 | 0 | 0 | 0 | 1434420 | 671.987 | 1411550 | 1383319.25
7119 | 2008-10-24 14:00 | 472 | 850 | 83 | 25.49 | 2.6 | 0 | 27.3114 | 230.005 | 48.9145 | 0 | 472 | 557.171 | 106.527 | 4.4223 | 557.171 | 99.6919 | 0.023083 | 542.639 | 96.0024 | 0.017393 | 619.499 | 619.493 | 1391220 | 41.8449 | 1364130 | 1264590 | 1234060 | 0 | 0 | 1221040 | 674.696 | 0 | 0 | 0 | 0 | 1221040 | 674.696 | 1202850 | 1178790.625
7120 | 2008-10-24 15:00 | 277 | 763 | 53 | 26.01 | 2.21 | 0 | 17.0884 | 241.386 | 62.6273 | 0 | 277 | 350.489 | 69.7913 | 2.5953 | 350.489 | 65.3134 | 0.013546 | 329.899 | 62.8962 | 0.010207 | 381.021 | 381.019 | 855674 | 36.3337 | 814046 | 772573 | 753149 | 0 | 0 | 748281 | 676.135 | 0 | 0 | 0 | 0 | 748281 | 676.135 | 737950 | 723190.6875
7121 | 2008-10-24 16:00 | 65 | 509 | 12 | 26.54 | 2.21 | 0 | 5.781 | 250.928 | 76.7808 | 0 | 65 | 120.325 | 18.0468 | 0.609 | 89.6929 | 16.8889 | 0.0031788 | 74.5663 | 16.2638 | 0.0023953 | 88.1076 | 88.098 | 197848 | 28.927 | 169880 | 166103 | 146183 | 0 | 0 | 145950 | 633.664 | 0 | 0 | 0 | 2232.38 | 143717 | 660 | 139496 | 136706.5156
7122 | 2008-10-24 17:00 | 0 | 9 | 0 | 25.71 | 2.21 | 0
7123 | 2008-10-24 18:00 | 0 | 0 | 0 | 24.89 | 2.34 | 0
7124 | 2008-10-24 19:00 | 0 | 0 | 0 | 24.06 | 2.34 | 0
7125 | 2008-10-24 20:00 | 0 | 0 | 0 | 23.32 | 2.34 | 0
7126 | 2008-10-24 21:00 | 0 | 0 | 0 | 22.57 | 1.59 | 0
7127 | 2008-10-24 22:00 | 0 | 0 | 0 | 21.82 | 1.59 | 0
7128 | 2008-10-24 23:00 | 0 | 0 | 0 | 21.14 | 1.59 | 0
7129 | 2008-10-25 | 0 | 0 | 0 | 20.46 | 1.76 | 0
7130 | 2008-10-25 01:00 | 0 | 0 | 0 | 19.78 | 1.76 | 0
7131 | 2008-10-25 02:00 | 0 | 0 | 0 | 19.23 | 1.76 | 0
7132 | 2008-10-25 03:00 | 0 | 0 | 0 | 18.67 | 3.1 | 0
7133 | 2008-10-25 04:00 | 0 | 0 | 0 | 18.12 | 3.1 | 0
7134 | 2008-10-25 05:00 | 0 | 0 | 0 | 17.34 | 3.1 | 0
7135 | 2008-10-25 06:00 | 54 | 390 | 20 | 16.57 | 3.57 | 0 | 4.3116 | 108.212 | 78.4723 | 0 | 54 | 78.0993 | 28.1805 | 0.50594 | 3.4726 | 26.3724 | 0.0026408 | 2.7774 | 25.3963 | 0.0019899 | 27.3305 | 27.3195 | 61355.4 | 17.2464 | 45537.3 | 47393.8 | 44801 | 0 | 0 | 44777.1 | 618.272 | 0 | 0 | 0 | 2556.36 | 42220.8 | 660 | 40725.9 | 39911.3828
7136 | 2008-10-25 07:00 | 246 | 725 | 50 | 15.8 | 3.57 | 0 | 15.6796 | 117.614 | 64.3078 | 0 | 246 | 314.415 | 66.1803 | 2.3048 | 252.834 | 61.9341 | 0.01203 | 236.316 | 59.6419 | 0.0090652 | 287.088 | 287.073 | 644636 | 22.9075 | 605769 | 608413 | 538074 | 0 | 0 | 535544 | 699.609 | 0 | 0 | 0 | 1423.83 | 534120 | 707.14 | 525249 | 514743.7812
7137 | 2008-10-25 08:00 | 448 | 875 | 65 | 17.74 | 3.57 | 0 | 26.0155 | 128.749 | 50.5625 | 0 | 448 | 554.692 | 81.6325 | 4.1974 | 543.271 | 76.3948 | 0.021909 | 527.673 | 73.5675 | 0.016509 | 583.22 | 583.229 | 1309810 | 32.1799 | 1280550 | 1239570 | 1158220 | 0 | 0 | 1147040 | 687.135 | 0 | 0 | 0 | 5289.69 | 1141750 | 695.19 | 1124220 | 1101735.75
7138 | 2008-10-25 09:00 | 604 | 934 | 74 | 19.68 | 1.85 | 0 | 34.6641 | 142.485 | 37.703 | 0 | 604 | 737.268 | 92.1179 | 5.659 | 737.268 | 86.2074 | 0.029538 | 727.539 | 83.0169 | 0.022258 | 786.261 | 786.255 | 1765720 | 41.5021 | 1755080 | 1631880 | 1590240 | 0 | 0 | 1569330 | 683.657 | 0 | 0 | 0 | 0 | 1569330 | 683.657 | 1542330 | 1511481.625
7139 | 2008-10-25 10:00 | 682 | 880 | 110 | 21.62 | 1.85 | 0 | 40.6799 | 159.404 | 27.0292 | 0 | 682 | 781.678 | 141.308 | 6.3898 | 781.678 | 132.242 | 0.033353 | 776.885 | 127.347 | 0.025132 | 877.13 | 877.127 | 1969810 | 45.9642 | 1969380 | 1794570 | 1749160 | 0 | 0 | 1723110 | 672.52 | 0 | 0 | 0 | 0 | 1723110 | 672.52 | 1691400 | 1657573
7140 | 2008-10-25 11:00 | 742 | 920 | 116 | 23.26 | 1.85 | 0 | 43.0121 | 178.864 | 21.9972 | 0 | 742 | 850.877 | 148.844 | 6.952 | 850.877 | 139.294 | 0.036287 | 847.537 | 134.138 | 0.027343 | 952.252 | 952.251 | 2138510 | 49.6892 | 2146960 | 1923190 | 1880510 | 0 | 0 | 1849360 | 659.81 | 0 | 0 | 0 | -31.4424 | 1849390 | 660.311 | 1813330 | 1777063.5
7141 | 2008-10-25 12:00 | 683 | 874 | 110 | 24.91 | 0.95 | 0 | 41.1212 | 198.476 | 26.1044 | 0 | 683 | 782.403 | 141.452 | 6.3992 | 782.403 | 132.376 | 0.033402 | 777.959 | 127.477 | 0.025169 | 878.297 | 878.292 | 1972420 | 50.8047 | 1972120 | 1755810 | 1714930 | 0 | 0 | 1688620 | 655.573 | 0 | 0 | 0 | 1367.57 | 1687250 | 660 | 1657100 | 1623953.5
7142 | 2008-10-25 13:00 | 618 | 939 | 75 | 26.56 | 0.95 | 0 | 35.4508 | 215.726 | 36.3757 | 0 | 618 | 753.779 | 93.3078 | 5.7902 | 753.779 | 87.321 | 0.030223 | 744.658 | 84.0893 | 0.022773 | 803.907 | 803.902 | 1805360 | 50.2615 | 1796640 | 1602580 | 1566350 | 0 | 0 | 1544170 | 653.403 | 0 | 0 | 0 | 1699.48 | 1542470 | 660 | 1517130 | 1486790.625
7143 | 2008-10-25 14:00 | 467 | 883 | 66 | 27.03 | 0.95 | 0 | 27.0321 | 229.78 | 49.081 | 0 | 467 | 577.904 | 82.8385 | 4.3754 | 577.904 | 77.5235 | 0.022838 | 562.684 | 74.6544 | 0.017209 | 618.235 | 618.233 | 1388400 | 45.2574 | 1361190 | 1241380 | 1211590 | 0 | 0 | 1198620 | 663.425 | 0 | 0 | 0 | 0 | 1198620 | 663.425 | 1181450 | 1157818.875
7144 | 2008-10-25 15:00 | 276 | 764 | 55 | 27.5 | 1.68 | 0 | 16.8379 | 241.14 | 62.7568 | 0 | 276 | 349.255 | 72.1833 | 2.5859 | 349.255 | 67.5519 | 0.013498 | 328.57 | 65.0519 | 0.010171 | 381.823 | 381.819 | 857466 | 38.2185 | 815861 | 767322 | 748215 | 0 | 0 | 743323 | 669.874 | 0 | 0 | 0 | 0 | 743323 | 669.874 | 733293 | 718626.75
7145 | 2008-10-25 16:00 | 63 | 509 | 12 | 27.97 | 1.68 | 0 | 5.5526 | 250.67 | 76.8839 | 0 | 63 | 119.607 | 18.2572 | 0.59026 | 85.6171 | 17.0858 | 0.003081 | 71.0333 | 16.4535 | 0.0023216 | 84.8644 | 84.8228 | 190490 | 30.3512 | 162977 | 158142 | 138217 | 0 | 0 | 138001 | 625.634 | 0 | 0 | 0 | 3932.58 | 134069 | 660 | 130054 | 127452.7812
7146 | 2008-10-25 17:00 | 0 | 4 | 0 | 26.97 | 1.68 | 0
7147 | 2008-10-25 18:00 | 0 | 0 | 0 | 25.96 | 0.73 | 0
7148 | 2008-10-25 19:00 | 0 | 0 | 0 | 24.96 | 0.73 | 0
7149 | 2008-10-25 20:00 | 0 | 0 | 0 | 24.35 | 0.73 | 0
7150 | 2008-10-25 21:00 | 0 | 0 | 0 | 23.74 | 0.77 | 0
7151 | 2008-10-25 22:00 | 0 | 0 | 0 | 23.13 | 0.77 | 0
7152 | 2008-10-25 23:00 | 0 | 0 | 0 | 22.35 | 0.77 | 0
7153 | 2008-10-26 | 0 | 0 | 0 | 21.57 | 2.57 | 0
7154 | 2008-10-26 01:00 | 0 | 0 | 0 | 20.78 | 2.57 | 0
7155 | 2008-10-26 02:00 | 0 | 0 | 0 | 20.22 | 2.57 | 0
7156 | 2008-10-26 03:00 | 0 | 0 | 0 | 19.65 | 3.9 | 0
7157 | 2008-10-26 04:00 | 0 | 0 | 0 | 19.08 | 3.9 | 0
7158 | 2008-10-26 05:00 | 0 | 0 | 0 | 18.05 | 3.9 | 0
7159 | 2008-10-26 06:00 | 50 | 373 | 18 | 17.01 | 6.74 | 0 | 4.1274 | 108.5 | 78.5226 | 0 | 50 | 73.1888 | 25.8374 | 0.46846 | 3.3922 | 24.1796 | 0.0024452 | 2.7094 | 23.2848 | 0.0018425 | 25.2162 | 25.2106 | 56618.8 | 17.5181 | 41509.5 | 43148.7 | 40650.3 | 0 | 0 | 40630 | 613.915 | 0 | 0 | 0 | 2966.48 | 37663.5 | 660 | 36319.9 | 35593.5156
7160 | 2008-10-26 07:00 | 252 | 744 | 53 | 15.97 | 6.74 | 0 | 15.4716 | 117.895 | 64.3848 | 0 | 252 | 322.51 | 69.6647 | 2.361 | 257.263 | 65.1949 | 0.012324 | 240.372 | 62.782 | 0.0092863 | 294.069 | 294.055 | 660328 | 21.8965 | 621575 | 627508 | 554129 | 0 | 0 | 551488 | 706.278 | 0 | 0 | 0 | 1550.6 | 549938 | 710.596 | 540757 | 529941.75
7161 | 2008-10-26 08:00 | 424 | 795 | 79 | 17.93 | 6.74 | 0 | 25.7749 | 129.018 | 50.6772 | 0 | 424 | 502.769 | 101.997 | 3.9726 | 491.203 | 95.4532 | 0.020735 | 477.006 | 91.9205 | 0.015624 | 551.874 | 551.857 | 1239350 | 29.0523 | 1207620 | 1185470 | 1101890 | 0 | 0 | 1092020 | 696.302 | 0 | 0 | 0 | 10990.5 | 1081030 | 703.643 | 1064200 | 1042917.9375
7162 | 2008-10-26 09:00 | 558 | 803 | 105 | 19.89 | 5.37 | 0 | 34.3844 | 142.722 | 37.8751 | 0 | 558 | 633.166 | 133.984 | 5.228 | 633.166 | 125.387 | 0.027289 | 624.717 | 120.747 | 0.020563 | 723.12 | 723.112 | 1623930 | 35.8063 | 1606640 | 1532670 | 1494770 | 0 | 0 | 1477070 | 699.594 | 0 | 0 | 0 | 0 | 1477070 | 699.594 | 1452110 | 1423069.25
7163 | 2008-10-26 10:00 | 640 | 804 | 121 | 21.85 | 5.37 | 0 | 40.3622 | 159.567 | 27.2896 | 0 | 640 | 712.204 | 153.962 | 5.9963 | 712.204 | 144.083 | 0.031299 | 707.744 | 138.751 | 0.023584 | 821.123 | 821.115 | 1844020 | 39.9234 | 1837200 | 1721180 | 1678750 | 0 | 0 | 1655800 | 688.144 | 0 | 0 | 0 | 0 | 1655800 | 688.144 | 1625920 | 1593404.75
7164 | 2008-10-26 11:00 | 671 | 744 | 168 | 23.59 | 5.37 | 0 | 42.6726 | 178.904 | 22.336 | 0 | 671 | 686.419 | 212.914 | 6.2867 | 686.419 | 199.253 | 0.032815 | 683.635 | 191.879 | 0.024727 | 849.273 | 849.266 | 1907240 | 42.283 | 1903600 | 1764460 | 1720690 | 0 | 0 | 1696180 | 682.231 | 0 | 0 | 0 | 0 | 1696180 | 682.231 | 1665140 | 1631836.5
7165 | 2008-10-26 12:00 | 707 | 864 | 144 | 25.33 | 3.14 | 0 | 40.7873 | 198.387 | 26.4023 | 0 | 707 | 771.946 | 179.254 | 6.624 | 771.946 | 167.753 | 0.034575 | 767.451 | 161.545 | 0.026053 | 901.151 | 901.144 | 2023740 | 48.2836 | 2026100 | 1826430 | 1783260 | 0 | 0 | 1755380 | 662.722 | 0 | 0 | 0 | -50.5244 | 1755430 | 663.023 | 1722790 | 1688336.75
7166 | 2008-10-26 13:00 | 587 | 856 | 95 | 27.07 | 3.14 | 0 | 35.1432 | 215.547 | 36.595 | 0 | 587 | 686.234 | 122.9 | 5.4997 | 686.234 | 115.015 | 0.028707 | 677.809 | 110.758 | 0.021631 | 764.932 | 764.921 | 1717820 | 46.5538 | 1704880 | 1547690 | 1510190 | 0 | 0 | 1490260 | 664.826 | 0 | 0 | 0 | 0 | 1490260 | 664.826 | 1466320 | 1436991
7167 | 2008-10-26 14:00 | 453 | 836 | 77 | 27.66 | 3.14 | 0 | 26.7569 | 229.555 | 49.2448 | 0 | 453 | 545.226 | 100.071 | 4.2443 | 545.226 | 93.6498 | 0.022154 | 530.728 | 90.1839 | 0.016693 | 602.301 | 602.3 | 1352610 | 43.0016 | 1324050 | 1220480 | 1191070 | 0 | 0 | 1178730 | 668.4 | 0 | 0 | 0 | 0 | 1178730 | 668.4 | 1161740 | 1138502.625
7168 | 2008-10-26 15:00 | 248 | 676 | 55 | 28.25 | 4.17 | 0 | 16.5916 | 240.895 | 62.8833 | 0 | 248 | 308.076 | 72.3268 | 2.3236 | 308.076 | 67.6862 | 0.012128 | 289.685 | 65.1812 | 0.0091389 | 344.229 | 344.224 | 773040 | 36.4429 | 730581 | 692664 | 675890 | 0 | 0 | 671907 | 671.319 | 0 | 0 | 0 | 0 | 671907 | 671.319 | 662792 | 649536.25
7169 | 2008-10-26 16:00 | 43 | 338 | 10 | 28.84 | 4.17 | 0 | 5.3285 | 250.413 | 76.9838 | 0 | 43 | 80.0347 | 15.5501 | 0.40288 | 57.2903 | 14.5524 | 0.0021029 | 47.4365 | 14.0138 | 0.0015846 | 59.6084 | 59.5861 | 133815 | 30.2582 | 110375 | 107197 | 93720.4 | 0 | 0 | 93614.3 | 604.308 | 0 | 0 | 0 | 6472.86 | 87141.5 | 660 | 84286.5 | 82600.7344
7170 | 2008-10-26 17:00 | 0 | 0 | 0 | 27.55 | 4.17 | 0
7171 | 2008-10-26 18:00 | 0 | 0 | 0 | 26.27 | 4.12 | 0
7172 | 2008-10-26 19:00 | 0 | 0 | 0 | 24.98 | 4.12 | 0
7173 | 2008-10-26 20:00 | 0 | 0 | 0 | 24.21 | 4.12 | 0
7174 | 2008-10-26 21:00 | 0 | 0 | 0 | 23.44 | 1.96 | 0
7175 | 2008-10-26 22:00 | 0 | 0 | 0 | 22.68 | 1.96 | 0
7176 | 2008-10-26 23:00 | 0 | 0 | 0 | 21.88 | 1.96 | 0
7177 | 2008-10-27 | 0 | 0 | 0 | 21.07 | 3.57 | 0
7178 | 2008-10-27 01:00 | 0 | 0 | 0 | 20.27 | 3.57 | 0
7179 | 2008-10-27 02:00 | 0 | 0 | 0 | 19.86 | 3.57 | 0
7180 | 2008-10-27 03:00 | 0 | 0 | 0 | 19.45 | 2.71 | 0
7181 | 2008-10-27 04:00 | 0 | 0 | 0 | 19.04 | 2.71 | 0
7182 | 2008-10-27 05:00 | 0 | 0 | 0 | 18.28 | 2.71 | 0
7183 | 2008-10-27 06:00 | 47 | 357 | 17 | 17.51 | 2.9 | 0 | 3.9426 | 108.784 | 78.5755 | 0 | 47 | 68.302 | 24.4817 | 0.44035 | 3.2912 | 22.911 | 0.0022985 | 2.6249 | 22.063 | 0.001732 | 23.949 | 23.929 | 53742.1 | 18.1293 | 39063.5 | 40470.3 | 38001.4 | 0 | 0 | 37983.5 | 607.936 | 0 | 0 | 0 | 3478.38 | 34505.2 | 660 | 33267.6 | 32602.2715
7184 | 2008-10-27 07:00 | 243 | 730 | 51 | 16.75 | 2.9 | 0 | 15.263 | 118.171 | 64.4647 | 0 | 243 | 314.396 | 67.607 | 2.2767 | 248.557 | 63.2692 | 0.011884 | 232.154 | 60.9277 | 0.0089546 | 284.298 | 284.318 | 638469 | 24.1081 | 599807 | 598885 | 527356 | 0 | 0 | 524888 | 697.341 | 0 | 0 | 0 | 404.419 | 524483 | 700.758 | 515903 | 505584.875
7185 | 2008-10-27 08:00 | 438 | 867 | 65 | 18.55 | 2.9 | 0 | 25.5344 | 129.281 | 50.7947 | 0 | 438 | 546.972 | 81.9648 | 4.1037 | 533.04 | 76.7057 | 0.02142 | 517.528 | 73.8669 | 0.01614 | 573.669 | 573.625 | 1288240 | 33.3953 | 1258420 | 1211110 | 1103980 | 0 | 0 | 1093870 | 694.265 | 0 | 0 | 0 | 0 | 1093870 | 694.265 | 1077160 | 1055613.75
7186 | 2008-10-27 09:00 | 592 | 879 | 100 | 20.36 | 2.17 | 0 | 34.1056 | 142.952 | 38.0498 | 0 | 592 | 690.965 | 128.546 | 5.5466 | 690.965 | 120.298 | 0.028951 | 681.641 | 115.846 | 0.021815 | 773.584 | 773.578 | 1737260 | 41.3761 | 1725240 | 1604950 | 1565270 | 0 | 0 | 1544970 | 682.774 | 0 | 0 | 0 | 0 | 1544970 | 682.774 | 1518750 | 1488375.125
7187 | 2008-10-27 10:00 | 650 | 785 | 146 | 22.16 | 2.17 | 0 | 40.0465 | 159.723 | 27.5506 | 0 | 650 | 694.499 | 187.068 | 6.09 | 694.499 | 175.066 | 0.031788 | 690.058 | 168.586 | 0.023953 | 832.908 | 832.897 | 1870480 | 44.7877 | 1864990 | 1708300 | 1665880 | 0 | 0 | 1642300 | 673.86 | 0 | 0 | 0 | 0 | 1642300 | 673.86 | 1613280 | 1581016.375
7188 | 2008-10-27 11:00 | 725 | 909 | 115 | 24.08 | 2.17 | 0 | 42.3363 | 178.94 | 22.6716 | 0 | 725 | 835.754 | 148.095 | 6.7927 | 835.754 | 138.593 | 0.035456 | 832.255 | 133.463 | 0.026717 | 936.773 | 936.765 | 2103740 | 49.5295 | 2110320 | 1891590 | 1847410 | 0 | 0 | 1817370 | 661.075 | 0 | 0 | 0 | 69.9977 | 1817300 | 662.14 | 1782420 | 1746769.375
7189 | 2008-10-27 12:00 | 698 | 958 | 78 | 26 | 2.69 | 0 | 40.4573 | 198.295 | 26.6967 | 0 | 698 | 853.633 | 97.0463 | 6.5397 | 853.633 | 90.8197 | 0.034135 | 848.54 | 87.4585 | 0.025722 | 907.943 | 907.94 | 2039010 | 49.8271 | 2042170 | 1827430 | 1783290 | 0 | 0 | 1755200 | 659.858 | 0 | 0 | 0 | -26.649 | 1755220 | 660.926 | 1722640 | 1688185.125
7190 | 2008-10-27 13:00 | 599 | 925 | 72 | 27.91 | 2.69 | 0 | 34.8398 | 215.368 | 36.8116 | 0 | 599 | 738.55 | 90.0905 | 5.6122 | 738.55 | 84.3101 | 0.029294 | 729.353 | 81.1899 | 0.022073 | 786.248 | 786.246 | 1765710 | 48.5435 | 1755060 | 1578390 | 1540250 | 0 | 0 | 1519250 | 660.622 | 0 | 0 | 0 | 22.1102 | 1519230 | 661.46 | 1494570 | 1464681
7191 | 2008-10-27 14:00 | 458 | 879 | 67 | 28.57 | 2.69 | 0 | 26.4858 | 229.331 | 49.4057 | 0 | 458 | 570.487 | 84.3493 | 4.2911 | 570.487 | 78.9372 | 0.022398 | 555.175 | 76.0158 | 0.016877 | 612.271 | 612.264 | 1374990 | 44.6377 | 1347270 | 1232300 | 1202360 | 0 | 0 | 1189630 | 664.212 | 0 | 0 | 0 | 0 | 1189630 | 664.212 | 1172610 | 1149156.5
7192 | 2008-10-27 15:00 | 253 | 723 | 49 | 29.22 | 1.8 | 0 | 16.3494 | 240.65 | 63.0068 | 0 | 253 | 328.932 | 65.6992 | 2.3704 | 328.932 | 61.4838 | 0.012373 | 309.143 | 59.2083 | 0.0093231 | 357.31 | 357.309 | 802426 | 39.1701 | 760208 | 711396 | 694395 | 0 | 0 | 690100 | 663.436 | 0 | 0 | 0 | 0 | 690100 | 663.436 | 681010 | 667390.125
7193 | 2008-10-27 16:00 | 43 | 355 | 9 | 29.88 | 1.8 | 0 | 5.1087 | 250.157 | 77.0803 | 0 | 43 | 85.3702 | 14.2525 | 0.40288 | 61.1095 | 13.338 | 0.0021029 | 50.4992 | 12.8444 | 0.0015846 | 61.4448 | 61.4216 | 137937 | 31.5904 | 114237 | 110118 | 96345.5 | 0 | 0 | 96233.1 | 604.468 | 0 | 0 | 0 | 7904.11 | 88329 | 660 | 85441.4 | 83732.5781
7194 | 2008-10-27 17:00 | 0 | 0 | 0 | 28.79 | 1.8 | 0
7195 | 2008-10-27 18:00 | 0 | 0 | 0 | 27.7 | 3.49 | 0
7196 | 2008-10-27 19:00 | 0 | 0 | 0 | 26.61 | 3.49 | 0
7197 | 2008-10-27 20:00 | 0 | 0 | 0 | 25.81 | 3.49 | 0
7198 | 2008-10-27 21:00 | 0 | 0 | 0 | 25 | 3.79 | 0
7199 | 2008-10-27 22:00 | 0 | 0 | 0 | 24.19 | 3.79 | 0
7200 | 2008-10-27 23:00 | 0 | 0 | 0 | 23.44 | 3.79 | 0
7201 | 2008-10-28 | 0 | 0 | 0 | 22.68 | 5.06 | 0
7202 | 2008-10-28 01:00 | 0 | 0 | 0 | 21.92 | 5.06 | 0
7203 | 2008-10-28 02:00 | 0 | 0 | 0 | 21.21 | 5.06 | 0
7204 | 2008-10-28 03:00 | 0 | 0 | 0 | 20.5 | 3.26 | 0
7205 | 2008-10-28 04:00 | 0 | 0 | 0 | 19.79 | 3.26 | 0
7206 | 2008-10-28 05:00 | 0 | 0 | 0 | 18.88 | 3.26 | 0
7207 | 2008-10-28 06:00 | 43 | 312 | 17 | 17.96 | 3.11 | 0 | 3.7573 | 109.063 | 78.6312 | 0 | 43 | 58.9106 | 24.1599 | 0.40288 | 2.8586 | 22.6098 | 0.0021029 | 2.2764 | 21.773 | 0.0015846 | 23.3295 | 23.3306 | 52396.2 | 18.5555 | 37883.1 | 39173 | 36938.8 | 0 | 0 | 36922.1 | 605.162 | 0 | 0 | 0 | 3815.16 | 33106.9 | 660 | 31916.4 | 31278.0977
7208 | 2008-10-28 07:00 | 244 | 711 | 59 | 17.04 | 3.11 | 0 | 15.0541 | 118.441 | 64.5474 | 0 | 244 | 306.11 | 76.3198 | 2.2861 | 239.92 | 71.423 | 0.011933 | 224.003 | 68.7796 | 0.0089915 | 284.008 | 283.976 | 637698 | 24.2877 | 598821 | 597511 | 528074 | 0 | 0 | 525616 | 699.52 | 0 | 0 | 0 | 0 | 525616 | 699.52 | 517023 | 506682.125
7209 | 2008-10-28 08:00 | 413 | 786 | 78 | 18.9 | 3.11 | 0 | 25.2939 | 129.538 | 50.9151 | 0 | 413 | 494.329 | 101.212 | 3.8695 | 480.58 | 94.7184 | 0.020197 | 466.496 | 91.2129 | 0.015219 | 540.992 | 540.975 | 1214910 | 32.7069 | 1182570 | 1141560 | 1044190 | 0 | 0 | 1035310 | 701.082 | 0 | 0 | 0 | 0 | 1035310 | 701.082 | 1019350 | 998960.625
7210 | 2008-10-28 09:00 | 580 | 870 | 97 | 20.75 | 1.85 | 0 | 33.8277 | 143.175 | 38.2269 | 0 | 580 | 681.571 | 125.321 | 5.4341 | 681.571 | 117.28 | 0.028364 | 672.268 | 112.94 | 0.021373 | 761.672 | 761.661 | 1710490 | 41.8895 | 1697210 | 1574960 | 1536030 | 0 | 0 | 1516350 | 681.106 | 0 | 0 | 0 | 0 | 1516350 | 681.106 | 1491060 | 1461240.125
7211 | 2008-10-28 10:00 | 662 | 866 | 110 | 22.61 | 1.85 | 0 | 39.733 | 159.873 | 27.8123 | 0 | 662 | 763.807 | 141.895 | 6.2024 | 763.807 | 132.791 | 0.032375 | 758.819 | 127.876 | 0.024395 | 860.118 | 860.115 | 1931590 | 46.482 | 1929190 | 1753410 | 1709760 | 0 | 0 | 1684590 | 669.032 | 0 | 0 | 0 | 0 | 1684590 | 669.032 | 1654280 | 1621198.5
7212 | 2008-10-28 11:00 | 656 | 724 | 173 | 24.54 | 1.85 | 0 | 42.0034 | 178.972 | 23.0041 | 0 | 656 | 664.387 | 218.897 | 6.1462 | 664.387 | 204.852 | 0.032081 | 661.517 | 197.27 | 0.024174 | 833.047 | 833.039 | 1870790 | 47.6605 | 1865320 | 1685430 | 1645040 | 0 | 0 | 1621390 | 664.318 | 0 | 0 | 0 | 0 | 1621390 | 664.318 | 1593350 | 1561481
7213 | 2008-10-28 12:00 | 668 | 826 | 137 | 26.47 | 1.26 | 0 | 40.1313 | 198.202 | 26.9876 | 0 | 668 | 734.129 | 172.094 | 6.2586 | 734.129 | 161.052 | 0.032668 | 729.643 | 155.092 | 0.024616 | 858.217 | 858.21 | 1927320 | 51.2503 | 1924700 | 1709540 | 1670230 | 0 | 0 | 1644970 | 652.419 | 0 | 0 | 0 | 2740.06 | 1642230 | 660 | 1613620 | 1581346.25
7214 | 2008-10-28 13:00 | 591 | 874 | 97 | 28.41 | 1.26 | 0 | 34.5406 | 215.189 | 37.0251 | 0 | 591 | 695.595 | 125.565 | 5.5372 | 695.595 | 117.509 | 0.028902 | 686.811 | 113.16 | 0.021778 | 775.993 | 775.984 | 1742660 | 50.8161 | 1730910 | 1539270 | 1504380 | 0 | 0 | 1483680 | 649.641 | 0 | 0 | 0 | 3518.71 | 1480160 | 660 | 1456660 | 1427521.875
7215 | 2008-10-28 14:00 | 420 | 791 | 71 | 28.95 | 1.26 | 0 | 26.219 | 229.108 | 49.5636 | 0 | 420 | 512.361 | 93.4811 | 3.9351 | 512.361 | 87.4832 | 0.02054 | 498.482 | 84.2455 | 0.015477 | 565.26 | 565.262 | 1269430 | 45.2716 | 1237890 | 1128060 | 1100240 | 0 | 0 | 1089390 | 659.552 | 0 | 0 | 0 | -29.9834 | 1089420 | 660.447 | 1074650 | 1053160.75
7216 | 2008-10-28 15:00 | 261 | 680 | 72 | 29.5 | 1.44 | 0 | 16.1116 | 240.407 | 63.1271 | 0 | 261 | 307.847 | 93.0884 | 2.4454 | 307.847 | 87.1157 | 0.012764 | 289.186 | 83.8916 | 0.0096179 | 361.895 | 361.889 | 812709 | 39.8238 | 770588 | 718862 | 703217 | 0 | 0 | 698759 | 659.751 | 0 | 0 | 0 | -32.5334 | 698792 | 660.745 | 689682 | 675887.875
7217 | 2008-10-28 16:00 | 43 | 328 | 12 | 30.04 | 1.44 | 0 | 4.8935 | 249.902 | 77.1734 | 0 | 43 | 79.104 | 18.798 | 0.40288 | 53.8141 | 17.5919 | 0.0021029 | 44.3846 | 16.9408 | 0.0015846 | 59.4872 | 59.4656 | 133545 | 31.7364 | 110077 | 106010 | 92462 | 0 | 0 | 92358.1 | 602.316 | 0 | 0 | 0 | 9086.56 | 83271.6 | 660 | 80524.1 | 78913.6406
7218 | 2008-10-28 17:00 | 0 | 0 | 0 | 29.03 | 1.44 | 0
7219 | 2008-10-28 18:00 | 0 | 0 | 0 | 28.02 | 3.43 | 0
7220 | 2008-10-28 19:00 | 0 | 0 | 0 | 27.01 | 3.43 | 0
7221 | 2008-10-28 20:00 | 0 | 0 | 0 | 26.4 | 3.43 | 0
7222 | 2008-10-28 21:00 | 0 | 0 | 0 | 25.79 | 3.38 | 0
7223 | 2008-10-28 22:00 | 0 | 0 | 0 | 25.18 | 3.38 | 0
7224 | 2008-10-28 23:00 | 0 | 0 | 0 | 24.13 | 3.38 | 0
7225 | 2008-10-29 | 0 | 0 | 0 | 23.09 | 3.72 | 0
7226 | 2008-10-29 01:00 | 0 | 0 | 0 | 22.04 | 3.72 | 0
7227 | 2008-10-29 02:00 | 0 | 0 | 0 | 21.51 | 3.72 | 0
7228 | 2008-10-29 03:00 | 0 | 0 | 0 | 20.98 | 5.18 | 0
7229 | 2008-10-29 04:00 | 0 | 0 | 0 | 20.44 | 5.18 | 0
7230 | 2008-10-29 05:00 | 0 | 0 | 0 | 19.82 | 5.18 | 0
7231 | 2008-10-29 06:00 | 42 | 339 | 14 | 19.19 | 8.02 | 0 | 3.5715 | 109.337 | 78.6895 | 0 | 42 | 63.121 | 20.6592 | 0.39351 | 3.0659 | 19.3336 | 0.002054 | 2.4376 | 18.6181 | 0.0015477 | 20.4255 | 20.4077 | 45832.7 | 19.5693 | 32447.7 | 33372.6 | 30954.4 | 0 | 0 | 30941.5 | 592.378 | 0 | 0 | 0 | 5082.4 | 25859.1 | 660 | 24918.4 | 24420.0742
7232 | 2008-10-29 07:00 | 231 | 687 | 55 | 18.56 | 8.02 | 0 | 14.8449 | 118.706 | 64.633 | 0 | 231 | 294.302 | 72.2302 | 2.1643 | 228.39 | 67.5958 | 0.011297 | 213.154 | 65.0941 | 0.0085124 | 269.909 | 269.912 | 606105 | 23.5761 | 567368 | 568800 | 502058 | 0 | 0 | 499849 | 703.627 | 0 | 0 | 0 | 0 | 499849 | 703.627 | 491418 | 481589.5312
7233 | 2008-10-29 08:00 | 408 | 780 | 78 | 20.41 | 8.02 | 0 | 25.0536 | 129.788 | 51.0383 | 0 | 408 | 490.014 | 101.377 | 3.8226 | 475.26 | 94.8726 | 0.019953 | 461.232 | 91.3615 | 0.015035 | 536.03 | 536.014 | 1203760 | 30.3714 | 1171130 | 1142740 | 1047900 | 0 | 0 | 1039080 | 706.395 | 0 | 0 | 0 | 0 | 1039080 | 706.395 | 1022800 | 1002348.6875
7234 | 2008-10-29 09:00 | 580 | 873 | 99 | 22.27 | 4.22 | 0 | 33.5508 | 143.392 | 38.4063 | 0 | 580 | 681.997 | 127.776 | 5.4341 | 681.997 | 119.577 | 0.028364 | 672.581 | 115.152 | 0.021373 | 764.122 | 764.119 | 1716020 | 40.3974 | 1702990 | 1591370 | 1552430 | 0 | 0 | 1532560 | 684.836 | 0 | 0 | 0 | 0 | 1532560 | 684.836 | 1506650 | 1476519.75
7235 | 2008-10-29 10:00 | 685 | 959 | 78 | 24.13 | 4.22 | 0 | 39.4217 | 160.016 | 28.0742 | 0 | 685 | 843.402 | 97.3682 | 6.4179 | 843.402 | 91.1209 | 0.033499 | 837.779 | 87.7485 | 0.025243 | 897.786 | 897.78 | 2016180 | 45.4282 | 2018150 | 1844040 | 1798990 | 0 | 0 | 1771480 | 672.843 | 0 | 0 | 0 | 0 | 1771480 | 672.843 | 1738060 | 1703303.125
7236 | 2008-10-29 11:00 | 722 | 969 | 80 | 25.73 | 4.22 | 0 | 41.6739 | 178.998 | 23.3331 | 0 | 722 | 886.607 | 99.6808 | 6.7646 | 886.607 | 93.2851 | 0.035309 | 882.658 | 89.8327 | 0.026606 | 943.342 | 943.336 | 2118480 | 48.109 | 2125850 | 1918690 | 1873870 | 0 | 0 | 1843310 | 664.678 | 0 | 0 | 0 | 0 | 1843310 | 664.678 | 1807420 | 1771272.875
7237 | 2008-10-29 12:00 | 693 | 910 | 112 | 27.34 | 5.66 | 0 | 39.8096 | 198.107 | 27.2746 | 0 | 693 | 806.582 | 144.509 | 6.4929 | 806.582 | 135.237 | 0.033891 | 801.538 | 130.232 | 0.025537 | 903.841 | 903.837 | 2029790 | 46.8645 | 2032470 | 1844720 | 1799730 | 0 | 0 | 1771860 | 668.876 | 0 | 0 | 0 | 0 | 1771860 | 668.876 | 1738520 | 1703745.625
7238 | 2008-10-29 13:00 | 561 | 782 | 122 | 28.94 | 5.66 | 0 | 34.2458 | 215.01 | 37.2354 | 0 | 561 | 621.085 | 157.671 | 5.2561 | 621.085 | 147.554 | 0.027435 | 613.134 | 142.093 | 0.020673 | 732.59 | 732.589 | 1645210 | 44.7652 | 1628890 | 1490970 | 1455050 | 0 | 0 | 1436850 | 670.757 | 0 | 0 | 0 | 0 | 1436850 | 670.757 | 1413970 | 1385695.125
7239 | 2008-10-29 14:00 | 449 | 844 | 80 | 29 | 5.66 | 0 | 25.9566 | 228.886 | 49.7184 | 0 | 449 | 545.077 | 103.973 | 4.2068 | 545.077 | 97.3016 | 0.021958 | 530.178 | 93.7006 | 0.016546 | 605.178 | 605.174 | 1359060 | 42.0728 | 1330740 | 1232170 | 1202670 | 0 | 0 | 1190230 | 672.981 | 0 | 0 | 0 | 0 | 1190230 | 672.981 | 1172770 | 1149318.25
7240 | 2008-10-29 15:00 | 255 | 744 | 51 | 29.07 | 6.09 | 0 | 15.8783 | 240.166 | 63.2441 | 0 | 255 | 335.674 | 68.2837 | 2.3891 | 335.674 | 63.9025 | 0.012471 | 315.176 | 61.5375 | 0.0093968 | 365.422 | 365.419 | 820640 | 36.748 | 778602 | 737338 | 719994 | 0 | 0 | 715491 | 672.088 | 0 | 0 | 0 | 0 | 715491 | 672.088 | 705758 | 691642.4375
7241 | 2008-10-29 16:00 | 41 | 352 | 8 | 29.14 | 6.09 | 0 | 4.6828 | 249.649 | 77.263 | 0 | 41 | 83.629 | 12.7316 | 0.38414 | 53.9217 | 11.9147 | 0.0020051 | 44.3893 | 11.4738 | 0.0015109 | 54.1887 | 54.1927 | 121704 | 30.2787 | 99752.2 | 96840.1 | 81607.2 | 0 | 0 | 81521.5 | 602.147 | 0 | 0 | 0 | 7346.99 | 74174.5 | 660 | 71687.3 | 70253.5859
7242 | 2008-10-29 17:00 | 0 | 0 | 0 | 27.88 | 6.09 | 0
7243 | 2008-10-29 18:00 | 0 | 0 | 0 | 26.63 | 6.43 | 0
7244 | 2008-10-29 19:00 | 0 | 0 | 0 | 25.37 | 6.43 | 0
7245 | 2008-10-29 20:00 | 0 | 0 | 0 | 24.5 | 6.43 | 0
7246 | 2008-10-29 21:00 | 0 | 0 | 0 | 23.62 | 4.5 | 0
7247 | 2008-10-29 22:00 | 0 | 0 | 0 | 22.75 | 4.5 | 0
7248 | 2008-10-29 23:00 | 0 | 0 | 0 | 22.01 | 4.5 | 0
7249 | 2008-10-30 | 0 | 0 | 0 | 21.27 | 5.92 | 0
7250 | 2008-10-30 01:00 | 0 | 0 | 0 | 20.53 | 5.92 | 0
7251 | 2008-10-30 02:00 | 0 | 0 | 0 | 20.66 | 5.92 | 0
7252 | 2008-10-30 03:00 | 0 | 0 | 0 | 20.79 | 4.78 | 0
7253 | 2008-10-30 04:00 | 0 | 0 | 0 | 20.91 | 4.78 | 0
7254 | 2008-10-30 05:00 | 0 | 0 | 0 | 20.84 | 4.78 | 0
7255 | 2008-10-30 06:00 | 29 | 101 | 21 | 20.77 | 6.92 | 0 | 3.3852 | 109.607 | 78.7505 | 0 | 29 | 17.9386 | 27.7407 | 0.27171 | 0.90252 | 25.9608 | 0.0014182 | 0.71633 | 25 | 0.0010687 | 24.9459 | 24.9434 | 56017.5 | 21.267 | 40746.9 | 41571.4 | 40129.5 | 0 | 0 | 40111.7 | 601.528 | 0 | 0 | 0 | 5126.08 | 34985.6 | 660 | 33729.8 | 33055.25
7256 | 2008-10-30 07:00 | 220 | 499 | 94 | 20.7 | 6.92 | 0 | 14.6354 | 118.966 | 64.7213 | 0 | 220 | 212.947 | 114.121 | 2.0612 | 163.639 | 106.798 | 0.010759 | 152.661 | 102.846 | 0.0081071 | 247.849 | 247.837 | 556543 | 25.638 | 516443 | 513615 | 463700 | 0 | 0 | 461856 | 694.423 | 0 | 0 | 0 | 0 | 461856 | 694.423 | 454142 | 445058.9062
7257 | 2008-10-30 08:00 | 197 | 134 | 141 | 22.35 | 6.92 | 0 | 24.8135 | 130.033 | 51.1642 | 0 | 197 | 83.6785 | 149.92 | 1.8457 | 80.9507 | 140.301 | 0.0096341 | 78.5438 | 135.109 | 0.0072595 | 207.25 | 207.228 | 465383 | 26.4789 | 424718 | 421692 | 401658 | 0 | 0 | 400303 | 686.35 | 0 | 0 | 0 | 0 | 400303 | 686.35 | 393729 | 385854.2188
7258 | 2008-10-30 09:00 | 430 | 356 | 235 | 24 | 6.28 | 0 | 33.2751 | 143.602 | 38.5878 | 0 | 430 | 277.809 | 265.743 | 4.0288 | 277.809 | 248.693 | 0.021029 | 273.928 | 239.489 | 0.015846 | 498.03 | 498.022 | 1118430 | 34.3372 | 1082230 | 1037920 | 1010750 | 0 | 0 | 1002420 | 691.997 | 0 | 0 | 0 | 0 | 1002420 | 691.997 | 987766 | 968010.625
7259 | 2008-10-30 10:00 | 527 | 422 | 262 | 25.65 | 6.28 | 0 | 39.1128 | 160.153 | 28.3362 | 0 | 527 | 369.735 | 297.3 | 4.9376 | 369.735 | 278.225 | 0.025773 | 367.218 | 267.928 | 0.01942 | 616.11 | 616.102 | 1383610 | 38.4382 | 1356230 | 1277480 | 1244320 | 0 | 0 | 1231550 | 686.358 | 0 | 0 | 0 | 0 | 1231550 | 686.358 | 1212580 | 1188326
7260 | 2008-10-30 11:00 | 680 | 770 | 173 | 25.65 | 6.28 | 0 | 41.348 | 179.02 | 23.6586 | 0 | 680 | 702.946 | 219.307 | 6.3711 | 702.946 | 205.236 | 0.033255 | 699.721 | 197.64 | 0.025058 | 870.465 | 870.452 | 1954820 | 43.7176 | 1953610 | 1799100 | 1756060 | 0 | 0 | 1730330 | 679.723 | 0 | 0 | 0 | 0 | 1730330 | 679.723 | 1698200 | 1664231
7261 | 2008-10-30 12:00 | 687 | 753 | 209 | 25.64 | 10.45 | 0 | 39.4921 | 198.01 | 27.5578 | 0 | 687 | 666.333 | 255.796 | 6.4367 | 666.333 | 239.383 | 0.033597 | 662.069 | 230.524 | 0.025316 | 865.84 | 865.83 | 1944430 | 39.4827 | 1942690 | 1824220 | 1778890 | 0 | 0 | 1753350 | 691.078 | 0 | 0 | 0 | 0 | 1753350 | 691.078 | 1720180 | 1685775.875
7262 | 2008-10-30 13:00 | 249 | 37 | 228 | 25.64 | 10.45 | 0 | 33.9555 | 214.831 | 37.4425 | 0 | 249 | 29.851 | 238.357 | 2.3329 | 29.851 | 223.063 | 0.012177 | 29.4636 | 214.808 | 0.0091757 | 236.952 | 236.945 | 532118 | 29.4282 | 490265 | 480112 | 467469 | 0 | 0 | 465607 | 679.684 | 0 | 0 | 0 | 0 | 465607 | 679.684 | 458629 | 449456.125
7263 | 2008-10-30 14:00 | 128 | 0 | 128 | 25.27 | 10.45 | 0 | 25.6988 | 228.665 | 49.87 | 0 | 128 | 0 | 121.431 | 1.1993 | 0 | 113.639 | 0.0062597 | 0 | 109.434 | 0.0047168 | 106.155 | 106.148 | 238381 | 26.9671 | 206075 | 204034 | 198537 | 0 | 0 | 198175 | 656.054 | 0 | 0 | 0 | 170.942 | 198004 | 660 | 192833 | 188975.9375
7264 | 2008-10-30 15:00 | 114 | 34 | 105 | 24.9 | 12.91 | 0 | 15.6495 | 239.925 | 63.3578 | 0 | 114 | 14.961 | 106.089 | 1.0681 | 14.961 | 99.2825 | 0.0055751 | 14.0408 | 95.6082 | 0.0042009 | 106.364 | 106.361 | 238861 | 26.3677 | 206524 | 205102 | 199536 | 0 | 0 | 199172 | 657.542 | 0 | 0 | 0 | 40.4437 | 199131 | 660 | 193944 | 190064.7969
7265 | 2008-10-30 16:00 | 18 | 16 | 17 | 24.53 | 12.91 | 0 | 4.4767 | 249.396 | 77.349 | 0 | 18 | 2.5174 | 13.2745 | 0.16865 | 1.6231 | 12.4227 | 0.00088028 | 1.3337 | 11.963 | 0.00066331 | 12.8985 | 12.8984 | 28966.5 | 24.708 | 18431.1 | 18459.2 | 17945.6 | 0 | 0 | 17941.4 | 550.208 | 0 | 0 | 0 | 12524.2 | 5417.16 | 660 | 5213.07 | 5108.8105
7266 | 2008-10-30 17:00 | 0 | 0 | 0 | 23.61 | 12.91 | 0
7267 | 2008-10-30 18:00 | 0 | 0 | 0 | 22.7 | 11.69 | 0
7268 | 2008-10-30 19:00 | 0 | 0 | 0 | 21.79 | 11.69 | 0
7269 | 2008-10-30 20:00 | 0 | 0 | 0 | 20.95 | 11.69 | 0
7270 | 2008-10-30 21:00 | 0 | 0 | 0 | 20.1 | 10.61 | 0
7271 | 2008-10-30 22:00 | 0 | 0 | 0 | 19.26 | 10.61 | 0
7272 | 2008-10-30 23:00 | 0 | 0 | 0 | 18.75 | 10.61 | 0
7273 | 2008-10-31 | 0 | 0 | 0 | 18.24 | 9.1 | 0
7274 | 2008-10-31 01:00 | 0 | 0 | 0 | 17.73 | 9.1 | 0
7275 | 2008-10-31 02:00 | 0 | 0 | 0 | 18.14 | 9.1 | 0
7276 | 2008-10-31 03:00 | 0 | 0 | 0 | 18.54 | 7.38 | 0
7277 | 2008-10-31 04:00 | 0 | 0 | 0 | 18.94 | 7.38 | 0
7278 | 2008-10-31 05:00 | 0 | 0 | 0 | 18.44 | 7.38 | 0
7279 | 2008-10-31 06:00 | 6 | 0 | 6 | 17.93 | 9.42 | 0 | 3.1985 | 109.871 | 78.8141 | 0 | 6 | 0 | 4.9966 | 0.056215 | 0 | 4.676 | 0.00029342 | 0 | 4.5029 | 0.0002211 | 4.368 | 4.3678 | 9809.07 | 18.0044 | 4051.08 | 4126.65 | 4059.92 | 0 | 0 | 4059.65 | 486.087 | 0 | 0 | 0 | 4059.65 | 0 | 660 | 0 | 0
7280 | 2008-10-31 07:00 | 66 | 0 | 66 | 17.43 | 9.42 | 0 | 14.4257 | 119.22 | 64.8123 | 0 | 66 | 0 | 61.8229 | 0.61837 | 0 | 57.8562 | 0.0032277 | 0 | 55.715 | 0.0024321 | 54.0459 | 54.043 | 121367 | 18.3504 | 98032.8 | 101447 | 98823.6 | 0 | 0 | 98732.5 | 651.526 | 0 | 0 | 0 | 157.266 | 98575.2 | 660 | 95412.4 | 93504.1797
7281 | 2008-10-31 08:00 | 110 | 0 | 110 | 18.55 | 9.42 | 0 | 24.5738 | 130.271 | 51.2927 | 0 | 110 | 0 | 103.488 | 1.0306 | 0 | 96.8476 | 0.0053795 | 0 | 93.2633 | 0.0040535 | 90.4693 | 90.4673 | 203167 | 20.0907 | 173081 | 177363 | 172477 | 0 | 0 | 172216 | 670.987 | 0 | 0 | 0 | 0 | 172216 | 670.987 | 167282 | 163936.8125
7282 | 2008-10-31 09:00 | 175 | 3 | 173 | 19.67 | 8.73 | 0 | 33.0006 | 143.805 | 38.7713 | 0 | 175 | 2.863 | 165.423 | 1.6396 | 2.863 | 154.809 | 0.0085582 | 2.8225 | 149.08 | 0.0064488 | 147.352 | 147.342 | 330893 | 22.2892 | 294116 | 297958 | 289509 | 0 | 0 | 288804 | 684.969 | 0 | 0 | 0 | 0 | 288804 | 684.969 | 282243 | 276598.4062
7283 | 2008-10-31 10:00 | 160 | 0 | 160 | 20.79 | 8.73 | 0 | 38.8064 | 160.283 | 28.5982 | 0 | 160 | 0 | 151.187 | 1.4991 | 0 | 141.487 | 0.0078247 | 0 | 136.251 | 0.005896 | 132.169 | 132.163 | 296804 | 23.1393 | 261475 | 263839 | 256843 | 0 | 0 | 256274 | 676.619 | 0 | 0 | 0 | 0 | 256274 | 676.619 | 250119 | 245116.4531
7284 | 2008-10-31 11:00 | 243 | 9 | 237 | 21.4 | 8.73 | 0 | 41.0258 | 179.038 | 23.9805 | 0 | 243 | 8.3518 | 229.379 | 2.2767 | 8.3518 | 214.661 | 0.011884 | 8.3123 | 206.717 | 0.0089546 | 208.587 | 208.579 | 468417 | 25.1077 | 427627 | 427376 | 415625 | 0 | 0 | 414200 | 690.894 | 0 | 0 | 0 | 0 | 414200 | 690.894 | 407494 | 399343.9062
7285 | 2008-10-31 12:00 | 232 | 8 | 227 | 22.02 | 7.73 | 0 | 39.1789 | 197.912 | 27.8369 | 0 | 232 | 6.9987 | 219.505 | 2.1737 | 6.9987 | 205.421 | 0.011346 | 6.9529 | 197.818 | 0.0085493 | 198.636 | 198.62 | 446052 | 25.7793 | 405741 | 404215 | 393330 | 0 | 0 | 392035 | 685.891 | 0 | 0 | 0 | 0 | 392035 | 685.891 | 385594 | 377882.1875
7286 | 2008-10-31 13:00 | 204 | 6 | 201 | 22.64 | 7.73 | 0 | 33.6698 | 214.652 | 37.6462 | 0 | 204 | 4.2846 | 194.252 | 1.9113 | 4.2846 | 181.789 | 0.0099764 | 4.2282 | 175.061 | 0.0075175 | 173.918 | 173.907 | 390551 | 25.9315 | 351707 | 350112 | 340768 | 0 | 0 | 339777 | 679.771 | 0 | 0 | 0 | 0 | 339777 | 679.771 | 333264 | 326598.8125
7287 | 2008-10-31 14:00 | 298 | 195 | 214 | 22.9 | 7.73 | 0 | 25.4455 | 228.445 | 50.0182 | 0 | 298 | 125.622 | 233.781 | 2.792 | 125.622 | 218.781 | 0.014573 | 122.128 | 210.684 | 0.010981 | 322.838 | 322.825 | 724985 | 29.0101 | 682277 | 669837 | 652739 | 0 | 0 | 649256 | 693.237 | 0 | 0 | 0 | 0 | 649256 | 693.237 | 639736 | 626941.6875
7288 | 2008-10-31 15:00 | 62 | 0 | 62 | 23.17 | 7.3 | 0 | 15.4254 | 239.685 | 63.468 | 0 | 62 | 0 | 57.4681 | 0.58089 | 0 | 53.7808 | 0.0030321 | 0 | 51.7904 | 0.0022847 | 50.2389 | 50.2358 | 112817 | 24.147 | 90360.3 | 90765.8 | 88531.9 | 0 | 0 | 88453.5 | 628.904 | 0 | 0 | 0 | 3044.63 | 85408.8 | 660 | 82601.1 | 80949.0469
7289 | 2008-10-31 16:00 | 9 | 0 | 9 | 23.44 | 7.3 | 0 | 4.2754 | 249.144 | 77.4315 | 0 | 9 | 0 | 7.4635 | 0.084323 | 0 | 6.9847 | 0.00044014 | 0 | 6.7262 | 0.00033165 | 6.5247 | 6.5244 | 14652.2 | 23.5669 | 7448.26 | 7494.53 | 7350.32 | 0 | 0 | 7349.5 | 510.484 | 0 | 0 | 0 | 7349.5 | 0 | 660 | 0 | 0
7290 | 2008-10-31 17:00 | 0 | 0 | 0 | 22.69 | 7.3 | 0
7291 | 2008-10-31 18:00 | 0 | 0 | 0 | 21.95 | 6.76 | 0
7292 | 2008-10-31 19:00 | 0 | 0 | 0 | 21.21 | 6.76 | 0
7293 | 2008-10-31 20:00 | 0 | 0 | 0 | 20.36 | 6.76 | 0
7294 | 2008-10-31 21:00 | 0 | 0 | 0 | 20.08 | 7.2 | 0
7295 | 2008-10-31 22:00 | 0 | 0 | 0 | 19.3 | 7.14 | 0
7296 | 2008-10-31 23:00 | 0 | 0 | 0 | 18.52 | 7.08 | 0
7297 | 2009-11-01 | 0 | 0 | 0 | 17.75 | 7.03 | 0
7298 | 2009-11-01 01:00 | 0 | 0 | 0 | 16.97 | 6.97 | 0
7299 | 2009-11-01 02:00 | 0 | 0 | 0 | 16.19 | 6.91 | 0
7300 | 2009-11-01 03:00 | 0 | 0 | 0 | 14.91 | 6.35 | 0
7301 | 2009-11-01 04:00 | 0 | 0 | 0 | 14.32 | 6.35 | 0
7302 | 2009-11-01 05:00 | 0 | 0 | 0 | 13.63 | 6.35 | 0
7303 | 2009-11-01 06:00 | 37 | 325 | 12 | 12.95 | 6.74 | 0 | 3.0572 | 110.067 | 78.8639 | 0 | 37 | 55.5 | 17.7135 | 0.34666 | 2.736 | 16.5769 | 0.0018094 | 2.1645 | 15.9634 | 0.0013635 | 17.5854 | 17.5836 | 39491.5 | 13.3044 | 27182.3 | 28842.2 | 26660 | 0 | 0 | 26650.5 | 603.658 | 0 | 0 | 0 | 2166.83 | 24483.6 | 660 | 23590.8 | 23119.0137
7304 | 2009-11-01 07:00 | 228 | 718 | 51 | 12.26 | 6.74 | 0 | 14.2672 | 119.408 | 64.8829 | 0 | 228 | 304.861 | 68.2531 | 2.1362 | 221.437 | 63.8739 | 0.01115 | 206.425 | 61.51 | 0.0084019 | 259.905 | 259.92 | 583669 | 17.4985 | 545512 | 561358 | 490396 | 0 | 0 | 488385 | 724.017 | 0 | 0 | 0 | 0 | 488385 | 724.017 | 479510 | 469919.9062
7305 | 2009-11-01 08:00 | 423 | 864 | 67 | 14.07 | 6.74 | 0 | 24.393 | 130.447 | 51.3914 | 0 | 423 | 537.884 | 89.1949 | 3.9632 | 517.893 | 83.472 | 0.020687 | 502.29 | 80.3827 | 0.015588 | 565.208 | 565.194 | 1269300 | 25.4612 | 1239270 | 1234990 | 1131900 | 0 | 0 | 1122120 | 725.179 | 0 | 0 | 0 | 0 | 1122120 | 725.179 | 1103360 | 1081297.625
7306 | 2009-11-01 09:00 | 577 | 927 | 76 | 15.88 | 3.36 | 0 | 32.7941 | 143.954 | 38.9112 | 0 | 577 | 719.76 | 95.5825 | 5.406 | 719.76 | 89.4498 | 0.028218 | 709.499 | 86.1393 | 0.021263 | 771.789 | 771.783 | 1733230 | 35.2548 | 1721020 | 1646170 | 1603750 | 0 | 0 | 1583630 | 703.902 | 0 | 0 | 0 | 0 | 1583630 | 703.902 | 1555520 | 1524408.75
7307 | 2009-11-01 10:00 | 677 | 957 | 82 | 17.69 | 3.36 | 0 | 38.5766 | 160.376 | 28.796 | 0 | 677 | 836.203 | 102.546 | 6.343 | 836.203 | 95.9661 | 0.033108 | 830.303 | 92.4144 | 0.024948 | 895.06 | 895.057 | 2010070 | 40.1594 | 2011720 | 1883390 | 1838740 | 0 | 0 | 1811270 | 688.702 | 0 | 0 | 0 | 0 | 1811270 | 688.702 | 1776160 | 1740638.875
7308 | 2009-11-01 11:00 | 713 | 967 | 83 | 19.38 | 3.36 | 0 | 40.7848 | 179.048 | 24.2213 | 0 | 713 | 879.55 | 103.677 | 6.6803 | 879.55 | 97.0245 | 0.034869 | 875.304 | 93.4337 | 0.026274 | 939.701 | 939.695 | 2110320 | 42.97 | 2117250 | 1957370 | 1911200 | 0 | 0 | 1880950 | 681.454 | 0 | 0 | 0 | 0 | 1880950 | 681.454 | 1843440 | 1806576
7309 | 2009-11-01 12:00 | 668 | 940 | 79 | 21.08 | 1.63 | 0 | 38.9453 | 197.836 | 28.0452 | 0 | 668 | 827.007 | 98.9945 | 6.2586 | 827.007 | 92.6429 | 0.032668 | 821.505 | 89.2142 | 0.024616 | 883.422 | 883.417 | 1983940 | 45.9626 | 1984230 | 1808200 | 1764370 | 0 | 0 | 1737720 | 670.88 | 0 | 0 | 0 | 0 | 1737720 | 670.88 | 1705540 | 1671425.625
7310 | 2009-11-01 13:00 | 588 | 931 | 76 | 22.77 | 1.63 | 0 | 33.457 | 214.516 | 37.7978 | 0 | 588 | 733.836 | 95.5919 | 5.5091 | 733.836 | 89.4586 | 0.028756 | 724.093 | 86.1478 | 0.021668 | 785.955 | 785.946 | 1765030 | 44.9072 | 1754350 | 1605420 | 1566570 | 0 | 0 | 1545500 | 670.815 | 0 | 0 | 0 | 0 | 1545500 | 670.815 | 1519690 | 1489293.5
7311 | 2009-11-01 14:00 | 439 | 872 | 67 | 23.35 | 1.63 | 0 | 25.2572 | 228.279 | 50.128 | 0 | 439 | 558.916 | 85.1334 | 4.1131 | 558.916 | 79.6711 | 0.021469 | 543.269 | 76.7225 | 0.016177 | 601.408 | 601.406 | 1350600 | 40.2894 | 1321960 | 1234280 | 1202900 | 0 | 0 | 1190670 | 678.651 | 0 | 0 | 0 | 0 | 1190670 | 678.651 | 1172930 | 1149473.5
7312 | 2009-11-01 15:00 | 237 | 734 | 44 | 23.93 | 1.71 | 0 | 15.2592 | 239.505 | 63.549 | 0 | 237 | 326.645 | 60.6197 | 2.2205 | 326.645 | 56.7302 | 0.01159 | 306.311 | 54.6307 | 0.0087335 | 350.122 | 350.12 | 786277 | 33.7389 | 743919 | 714522 | 696675 | 0 | 0 | 692564 | 680.818 | 0 | 0 | 0 | 0 | 692564 | 680.818 | 682840 | 669183.4375
7313 | 2009-11-01 16:00 | 35 | 330 | 7 | 24.51 | 1.71 | 0 | 4.1265 | 248.955 | 77.4913 | 0 | 35 | 69.7063 | 11.0477 | 0.32792 | 42.4686 | 10.3389 | 0.0017117 | 34.788 | 9.9562 | 0.0012898 | 43.4031 | 43.3833 | 97428.2 | 25.7254 | 78050.9 | 77574 | 63688.4 | 0 | 0 | 63634.1 | 602.181 | 0 | 0 | 0 | 4716.4 | 58917.7 | 660 | 56888.2 | 55750.4375
7314 | 2009-11-01 17:00 | 0 | 0 | 0 | 23.79 | 1.71 | 0
7315 | 2009-11-01 18:00 | 0 | 0 | 0 | 23.08 | 2.56 | 0
7316 | 2009-11-01 19:00 | 0 | 0 | 0 | 22.36 | 2.56 | 0
7317 | 2009-11-01 20:00 | 0 | 0 | 0 | 21.64 | 2.56 | 0
7318 | 2009-11-01 21:00 | 0 | 0 | 0 | 20.92 | 2.35 | 0
7319 | 2009-11-01 22:00 | 0 | 0 | 0 | 20.2 | 2.35 | 0
7320 | 2009-11-01 23:00 | 0 | 0 | 0 | 19.47 | 2.35 | 0
7321 | 2009-11-02 | 0 | 0 | 0 | 18.74 | 1.78 | 0
7322 | 2009-11-02 01:00 | 0 | 0 | 0 | 18.02 | 1.78 | 0
7323 | 2009-11-02 02:00 | 0 | 0 | 0 | 17.53 | 1.78 | 0
7324 | 2009-11-02 03:00 | 0 | 0 | 0 | 17.05 | 1.82 | 0
7325 | 2009-11-02 04:00 | 0 | 0 | 0 | 16.57 | 1.82 | 0
7326 | 2009-11-02 05:00 | 0 | 0 | 0 | 16.11 | 1.82 | 0
7327 | 2009-11-02 06:00 | 34 | 366 | 6 | 15.65 | 2.36 | 0 | 2.8699 | 110.323 | 78.9321 | 0 | 34 | 61.7839 | 8.9185 | 0.31855 | 3.1323 | 8.3463 | 0.0016627 | 2.4731 | 8.0374 | 0.0012529 | 10.1964 | 10.1967 | 22902.8 | 15.9235 | 14149.6 | 14740.9 | 13298.9 | 0 | 0 | 13294 | 559.092 | 0 | 0 | 0 | 6072.01 | 7221.94 | 660 | 6952.87 | 6813.8081
7328 | 2009-11-02 07:00 | 224 | 731 | 46 | 15.19 | 2.36 | 0 | 14.0575 | 119.652 | 64.9785 | 0 | 224 | 309.955 | 62.8326 | 2.0987 | 213.895 | 58.8011 | 0.010955 | 199.304 | 56.6249 | 0.0082545 | 248.259 | 248.484 | 557988 | 21.8557 | 520388 | 524204 | 455197 | 0 | 0 | 453367 | 707.338 | 0 | 0 | 0 | 0 | 453367 | 707.338 | 445409 | 436500.875
7329 | 2009-11-02 08:00 | 387 | 777 | 69 | 16.61 | 2.36 | 0 | 24.1542 | 130.674 | 51.5242 | 0 | 387 | 483.522 | 91.6917 | 3.6259 | 464.43 | 85.8086 | 0.018926 | 450.329 | 82.6329 | 0.014261 | 516.987 | 516.995 | 1161050 | 30.4786 | 1127480 | 1098580 | 1011310 | 0 | 0 | 1003030 | 704.316 | 0 | 0 | 0 | 0 | 1003030 | 704.316 | 987522 | 967771.0625
7330 | 2009-11-02 09:00 | 534 | 832 | 88 | 18.04 | 2.85 | 0 | 32.5222 | 144.144 | 39.0978 | 0 | 534 | 643.807 | 115.769 | 5.0032 | 643.807 | 108.341 | 0.026115 | 634.518 | 104.331 | 0.019678 | 716.703 | 716.695 | 1609520 | 36.6495 | 1591580 | 1512450 | 1474720 | 0 | 0 | 1457350 | 696.791 | 0 | 0 | 0 | 0 | 1457350 | 696.791 | 1432950 | 1404291.375
7331 | 2009-11-02 10:00 | 679 | 931 | 104 | 19.46 | 2.85 | 0 | 38.2749 | 160.495 | 29.0572 | 0 | 679 | 811.428 | 135.841 | 6.3617 | 811.428 | 127.125 | 0.033206 | 805.586 | 122.42 | 0.025021 | 900.191 | 900.184 | 2021580 | 42.834 | 2023830 | 1871680 | 1824060 | 0 | 0 | 1796530 | 682.196 | 0 | 0 | 0 | 0 | 1796530 | 682.196 | 1762050 | 1726813.125
7332 | 2009-11-02 11:00 | 715 | 992 | 73 | 21.46 | 2.85 | 0 | 40.4694 | 179.058 | 24.5366 | 0 | 715 | 899.826 | 91.9158 | 6.699 | 899.826 | 86.0183 | 0.034966 | 895.36 | 82.8348 | 0.026348 | 948.874 | 948.869 | 2130920 | 46.0981 | 2138950 | 1948960 | 1902190 | 0 | 0 | 1871400 | 672.528 | 0 | 0 | 0 | 0 | 1871400 | 672.528 | 1834360 | 1797668.625
7333 | 2009-11-02 12:00 | 648 | 890 | 94 | 23.45 | 2.76 | 0 | 38.6401 | 197.734 | 28.317 | 0 | 648 | 781.047 | 116.794 | 6.0713 | 781.047 | 109.301 | 0.03169 | 775.739 | 105.256 | 0.023879 | 854.588 | 854.582 | 1919180 | 45.7728 | 1916140 | 1747370 | 1707750 | 0 | 0 | 1682680 | 669.402 | 0 | 0 | 0 | 0 | 1682680 | 669.402 | 1652430 | 1619379.875
7334 | 2009-11-02 13:00 | 590 | 959 | 66 | 25.45 | 2.76 | 0 | 33.1796 | 214.338 | 37.9952 | 0 | 590 | 754.561 | 83.7937 | 5.5278 | 754.561 | 78.4173 | 0.028854 | 744.415 | 75.5151 | 0.021742 | 795.353 | 795.351 | 1786160 | 46.2256 | 1776500 | 1615710 | 1577620 | 0 | 0 | 1556070 | 667.666 | 0 | 0 | 0 | 0 | 1556070 | 667.666 | 1530040 | 1499437.75
7335 | 2009-11-02 14:00 | 440 | 905 | 58 | 25.74 | 2.76 | 0 | 25.0123 | 228.06 | 50.2702 | 0 | 440 | 577.47 | 74.5138 | 4.1225 | 577.47 | 69.7328 | 0.021518 | 561.17 | 67.1521 | 0.016214 | 609.488 | 609.484 | 1368740 | 41.6605 | 1340790 | 1243910 | 1213290 | 0 | 0 | 1200730 | 675.232 | 0 | 0 | 0 | 0 | 1200730 | 675.232 | 1182940 | 1159284.25
7336 | 2009-11-02 15:00 | 240 | 779 | 38 | 26.04 | 3.51 | 0 | 15.0435 | 239.267 | 63.653 | 0 | 240 | 345.398 | 50.8215 | 2.2486 | 332.11 | 47.5607 | 0.011737 | 311.299 | 45.8005 | 0.0088441 | 346.396 | 346.363 | 777841 | 34.6494 | 735515 | 703262 | 682315 | 0 | 0 | 678328 | 677.75 | 0 | 0 | 0 | 0 | 678328 | 677.75 | 668908 | 655530.0625
7337 | 2009-11-02 16:00 | 34 | 344 | 5 | 26.34 | 3.51 | 0 | 3.9338 | 248.705 | 77.5672 | 0 | 34 | 71.7646 | 7.9504 | 0.31855 | 41.1734 | 7.4403 | 0.0016627 | 33.6699 | 7.1649 | 0.0012529 | 39.611 | 39.6151 | 88966.6 | 27.3247 | 71234.6 | 70169.6 | 55020.7 | 0 | 0 | 54974 | 585.808 | 0 | 0 | 0 | 4827.02 | 50147 | 660 | 48393.8 | 47425.9023
7338 | 2009-11-02 17:00 | 0 | 0 | 0 | 25.39 | 3.51 | 0
7339 | 2009-11-02 18:00 | 0 | 0 | 0 | 24.43 | 5.2 | 0
7340 | 2009-11-02 19:00 | 0 | 0 | 0 | 23.48 | 5.2 | 0
7341 | 2009-11-02 20:00 | 0 | 0 | 0 | 22.55 | 5.2 | 0
7342 | 2009-11-02 21:00 | 0 | 0 | 0 | 21.63 | 3.32 | 0
7343 | 2009-11-02 22:00 | 0 | 0 | 0 | 20.7 | 3.32 | 0
7344 | 2009-11-02 23:00 | 0 | 0 | 0 | 19.79 | 3.32 | 0
7345 | 2009-11-03 | 0 | 0 | 0 | 18.89 | 3.28 | 0
7346 | 2009-11-03 01:00 | 0 | 0 | 0 | 17.98 | 3.28 | 0
7347 | 2009-11-03 02:00 | 0 | 0 | 0 | 17.47 | 3.28 | 0
7348 | 2009-11-03 03:00 | 0 | 0 | 0 | 16.96 | 3.83 | 0
7349 | 2009-11-03 04:00 | 0 | 0 | 0 | 16.45 | 3.83 | 0
7350 | 2009-11-03 05:00 | 0 | 0 | 0 | 16.06 | 3.83 | 0
7351 | 2009-11-03 06:00 | 32 | 366 | 5 | 15.68 | 4.28 | 0 | 2.6825 | 110.573 | 79.003 | 0 | 32 | 59.2009 | 7.4527 | 0.29981 | 3.0758 | 6.9745 | 0.0015649 | 2.4234 | 6.7164 | 0.0011792 | 8.8667 | 8.8622 | 19904.2 | 15.8894 | 11886.8 | 12363.3 | 10971.8 | 0 | 0 | 10967.7 | 554.056 | 0 | 0 | 0 | 6433.4 | 4534.33 | 660 | 4365.42 | 4278.1147
7352 | 2009-11-03 07:00 | 228 | 764 | 45 | 15.29 | 4.28 | 0 | 13.8478 | 119.89 | 65.0767 | 0 | 228 | 322.202 | 61.8372 | 2.1362 | 219.87 | 57.8696 | 0.01115 | 204.776 | 55.7279 | 0.0084019 | 252.697 | 252.651 | 567354 | 21.2602 | 530000 | 535500 | 465390 | 0 | 0 | 463480 | 709.837 | 0 | 0 | 0 | 0 | 463480 | 709.837 | 455346 | 446238.625
7353 | 2009-11-03 08:00 | 411 | 885 | 53 | 16.7 | 4.28 | 0 | 23.9161 | 130.895 | 51.6593 | 0 | 411 | 547.807 | 68.5983 | 3.8508 | 524.827 | 64.1969 | 0.0201 | 508.766 | 61.8211 | 0.015145 | 553.484 | 553.47 | 1242980 | 29.7786 | 1212420 | 1184970 | 1086080 | 0 | 0 | 1076650 | 710.31 | 0 | 0 | 0 | 0 | 1076650 | 710.31 | 1059440 | 1038251.9375
7354 | 2009-11-03 09:00 | 566 | 945 | 63 | 18.11 | 3.45 | 0 | 32.2519 | 144.328 | 39.2859 | 0 | 566 | 729.552 | 80.3176 | 5.303 | 729.552 | 75.1643 | 0.02768 | 718.901 | 72.3825 | 0.020857 | 767.565 | 767.563 | 1723750 | 37.2647 | 1711090 | 1621950 | 1580690 | 0 | 0 | 1560710 | 695.841 | 0 | 0 | 0 | 0 | 1560710 | 695.841 | 1533560 | 1502884.875
7355 | 2009-11-03 10:00 | 665 | 974 | 67 | 19.51 | 3.45 | 0 | 37.9761 | 160.607 | 29.3179 | 0 | 665 | 847.356 | 84.9107 | 6.2305 | 847.356 | 79.4626 | 0.032521 | 841.132 | 76.5218 | 0.024505 | 890.148 | 890.144 | 1999040 | 41.7238 | 2000120 | 1859140 | 1813160 | 0 | 0 | 1786190 | 684.913 | 0 | 0 | 0 | 0 | 1786190 | 684.913 | 1752020 | 1716977
7356 | 2009-11-03 11:00 | 710 | 992 | 72 | 21.57 | 3.45 | 0 | 40.1581 | 179.063 | 24.8478 | 0 | 710 | 897.72 | 90.8592 | 6.6521 | 897.72 | 85.0295 | 0.034722 | 893.141 | 81.8826 | 0.026164 | 945.799 | 945.793 | 2124020 | 45.1725 | 2131680 | 1950750 | 1902290 | 0 | 0 | 1871840 | 675.806 | 0 | 0 | 0 | 0 | 1871840 | 675.806 | 1834740 | 1798043
7357 | 2009-11-03 12:00 | 679 | 984 | 70 | 23.63 | 1.44 | 0 | 38.3397 | 197.63 | 28.5844 | 0 | 679 | 862.086 | 88.529 | 6.3617 | 862.086 | 82.8489 | 0.033206 | 856.102 | 79.7827 | 0.025021 | 907.833 | 907.828 | 2038750 | 49.528 | 2041900 | 1829790 | 1787110 | 0 | 0 | 1758890 | 660.266 | 0 | 0 | 0 | 123.1 | 1758770 | 661.498 | 1726050 | 1691526.125
7358 | 2009-11-03 13:00 | 575 | 948 | 61 | 25.69 | 1.44 | 0 | 32.9071 | 214.159 | 38.1888 | 0 | 575 | 743.621 | 77.8778 | 5.3873 | 743.621 | 72.8811 | 0.02812 | 733.496 | 70.1838 | 0.021189 | 779.59 | 779.588 | 1750760 | 47.9297 | 1739390 | 1568800 | 1530520 | 0 | 0 | 1509920 | 662.746 | 0 | 0 | 0 | 0 | 1509920 | 662.746 | 1485510 | 1455803.625
7359 | 2009-11-03 14:00 | 436 | 818 | 94 | 26.12 | 1.44 | 0 | 24.7724 | 227.842 | 50.4087 | 0 | 436 | 520.17 | 123.13 | 4.085 | 520.17 | 115.23 | 0.021322 | 505.369 | 110.965 | 0.016067 | 597.86 | 597.856 | 1342640 | 43.1753 | 1313700 | 1209850 | 1179910 | 0 | 0 | 1167830 | 669.769 | 0 | 0 | 0 | 0 | 1167830 | 669.769 | 1151000 | 1127979.5
7360 | 2009-11-03 15:00 | 190 | 369 | 95 | 26.54 | 1.8 | 0 | 14.8328 | 239.031 | 63.7533 | 0 | 190 | 164.112 | 116.515 | 1.7801 | 157.799 | 109.039 | 0.0092918 | 147.848 | 105.003 | 0.0070016 | 245.272 | 245.257 | 550789 | 33.3698 | 508735 | 488797 | 475307 | 0 | 0 | 473317 | 669.009 | 0 | 0 | 0 | 0 | 473317 | 669.009 | 466584 | 457251.9688
7361 | 2009-11-03 16:00 | 26 | 160 | 13 | 26.97 | 1.8 | 0 | 3.7462 | 248.458 | 77.6393 | 0 | 26 | 31.9867 | 20.976 | 0.2436 | 18.2171 | 19.6301 | 0.0012715 | 14.8729 | 18.9036 | 0.00095811 | 32.7642 | 32.7515 | 73551.7 | 27.882 | 56179 | 55256.5 | 48346.6 | 0 | 0 | 48317.5 | 591.192 | 0 | 0 | 0 | 8868.5 | 39449 | 660 | 38043.6 | 37282.7344
7362 | 2009-11-03 17:00 | 0 | 0 | 0 | 26.19 | 1.8 | 0
7363 | 2009-11-03 18:00 | 0 | 0 | 0 | 25.41 | 2.68 | 0
7364 | 2009-11-03 19:00 | 0 | 0 | 0 | 24.63 | 2.68 | 0
7365 | 2009-11-03 20:00 | 0 | 0 | 0 | 23.82 | 2.68 | 0
7366 | 2009-11-03 21:00 | 0 | 0 | 0 | 23.01 | 3.12 | 0
7367 | 2009-11-03 22:00 | 0 | 0 | 0 | 22.2 | 3.12 | 0
7368 | 2009-11-03 23:00 | 0 | 0 | 0 | 21.42 | 3.12 | 0
7369 | 2009-11-04 | 0 | 0 | 0 | 20.65 | 2.39 | 0
7370 | 2009-11-04 01:00 | 0 | 0 | 0 | 19.87 | 2.39 | 0
7371 | 2009-11-04 02:00 | 0 | 0 | 0 | 19.27 | 2.39 | 0
7372 | 2009-11-04 03:00 | 0 | 0 | 0 | 18.67 | 3.04 | 0
7373 | 2009-11-04 04:00 | 0 | 0 | 0 | 18.07 | 3.04 | 0
7374 | 2009-11-04 05:00 | 0 | 0 | 0 | 17.5 | 3.04 | 0
7375 | 2009-11-04 06:00 | 30 | 364 | 4 | 16.93 | 4.49 | 0 | 2.4948 | 110.817 | 79.0763 | 0 | 30 | 56.6325 | 5.9812 | 0.28108 | 2.7754 | 5.5974 | 0.0014671 | 2.1819 | 5.3902 | 0.0011055 | 7.346 | 7.3454 | 16498.4 | 17.1012 | 9346.81 | 9641.68 | 8416.04 | 0 | 0 | 8412.83 | 529.702 | 0 | 0 | 0 | 5069.27 | 3343.56 | 660 | 3218.89 | 3154.5088
7376 | 2009-11-04 07:00 | 226 | 762 | 46 | 16.36 | 4.49 | 0 | 13.6382 | 120.122 | 65.1774 | 0 | 226 | 320.478 | 63.1049 | 2.1174 | 216.084 | 59.056 | 0.011052 | 201.152 | 56.8704 | 0.0083282 | 250.29 | 250.352 | 562202 | 22.1951 | 524958 | 528155 | 459233 | 0 | 0 | 457347 | 704.404 | 0 | 0 | 0 | 0 | 457347 | 704.404 | 449445 | 440456.5312
7377 | 2009-11-04 08:00 | 414 | 891 | 57 | 17.61 | 4.49 | 0 | 23.6787 | 131.109 | 51.7967 | 0 | 414 | 549.761 | 73.6157 | 3.8789 | 525.184 | 68.8923 | 0.020246 | 508.984 | 66.3427 | 0.015256 | 558.081 | 558.16 | 1253520 | 30.6195 | 1223400 | 1191170 | 1091030 | 0 | 0 | 1081420 | 706.882 | 0 | 0 | 0 | 0 | 1081420 | 706.882 | 1064300 | 1043010.125
7378 | 2009-11-04 09:00 | 548 | 921 | 61 | 18.86 | 3.06 | 0 | 31.9833 | 144.505 | 39.4754 | 0 | 548 | 709.711 | 78.0264 | 5.1343 | 709.711 | 73.02 | 0.0268 | 699.225 | 70.3176 | 0.020194 | 746.476 | 746.475 | 1676390 | 37.9749 | 1661510 | 1569720 | 1532260 | 0 | 0 | 1513340 | 693.361 | 0 | 0 | 0 | 0 | 1513340 | 693.361 | 1487690 | 1457938.75
7379 | 2009-11-04 10:00 | 669 | 982 | 70 | 20.11 | 3.06 | 0 | 37.6802 | 160.713 | 29.5777 | 0 | 669 | 852.252 | 88.6757 | 6.268 | 852.252 | 82.9861 | 0.032717 | 845.867 | 79.9148 | 0.024653 | 898.032 | 898.028 | 2016740 | 43.1057 | 2018740 | 1864620 | 1818510 | 0 | 0 | 1791080 | 681.472 | 0 | 0 | 0 | 0 | 1791080 | 681.472 | 1756810 | 1721674
7380 | 2009-11-04 11:00 | 702 | 988 | 71 | 21.74 | 3.06 | 0 | 39.8508 | 179.064 | 25.155 | 0 | 702 | 891.331 | 89.7966 | 6.5772 | 891.331 | 84.0351 | 0.034331 | 886.661 | 80.925 | 0.025869 | 938.584 | 938.58 | 2107810 | 45.7741 | 2114610 | 1929590 | 1884180 | 0 | 0 | 1854100 | 673.528 | 0 | 0 | 0 | 0 | 1854100 | 673.528 | 1817680 | 1781330.25
7381 | 2009-11-04 12:00 | 664 | 640 | 271 | 23.36 | 2.87 | 0 | 38.044 | 197.525 | 28.8474 | 0 | 664 | 558.576 | 321.06 | 6.2212 | 558.576 | 300.46 | 0.032472 | 554.619 | 289.34 | 0.024469 | 818.664 | 818.658 | 1838500 | 44.5889 | 1831420 | 1678940 | 1637620 | 0 | 0 | 1614770 | 673.12 | 0 | 0 | 0 | 0 | 1614770 | 673.12 | 1586670 | 1554937.75
7382 | 2009-11-04 13:00 | 116 | 0 | 116 | 24.98 | 2.87 | 0 | 32.6395 | 213.98 | 38.3785 | 0 | 116 | 0 | 108.276 | 1.0868 | 0 | 101.329 | 0.0056729 | 0 | 97.5789 | 0.0042746 | 94.6557 | 94.6496 | 212558 | 27.4344 | 181847 | 179594 | 174800 | 0 | 0 | 174511 | 647.506 | 0 | 0 | 0 | 799.244 | 173712 | 660 | 168922 | 165543.5156
7383 | 2009-11-04 14:00 | 83 | 0 | 83 | 25.37 | 2.87 | 0 | 24.5374 | 227.625 | 50.5436 | 0 | 83 | 0 | 76.7299 | 0.77765 | 0 | 71.8067 | 0.004059 | 0 | 69.1492 | 0.0030586 | 67.0777 | 67.0747 | 150633 | 27.1093 | 124575 | 123199 | 120180 | 0 | 0 | 120036 | 631.048 | 0 | 0 | 0 | 3255.73 | 116780 | 660 | 113161 | 110897.9844
7384 | 2009-11-04 15:00 | 197 | 320 | 116 | 25.75 | 5.46 | 0 | 14.627 | 238.796 | 63.8499 | 0 | 197 | 141.366 | 134.7 | 1.8457 | 130.489 | 126.057 | 0.0096341 | 122.21 | 121.392 | 0.0072595 | 236.301 | 236.285 | 530639 | 30.9206 | 488918 | 475276 | 458692 | 0 | 0 | 456873 | 675.614 | 0 | 0 | 0 | 0 | 456873 | 675.614 | 450122 | 441119.9062
7385 | 2009-11-04 16:00 | 27 | 136 | 16 | 26.13 | 5.46 | 0 | 3.5636 | 248.211 | 77.7076 | 0 | 27 | 26.9185 | 22.667 | 0.25297 | 14.3745 | 21.2127 | 0.0013204 | 11.7173 | 20.4276 | 0.00099496 | 31.1815 | 31.1675 | 69994.9 | 26.812 | 52959.6 | 52414.4 | 46808.4 | 0 | 0 | 46782 | 592.544 | 0 | 0 | 0 | 7972.6 | 38809.4 | 660 | 37425.2 | 36676.6836
7386 | 2009-11-04 17:00 | 0 | 0 | 0 | 25.46 | 5.46 | 0
7387 | 2009-11-04 18:00 | 0 | 0 | 0 | 24.79 | 5.02 | 0
7388 | 2009-11-04 19:00 | 0 | 0 | 0 | 24.12 | 5.02 | 0
7389 | 2009-11-04 20:00 | 0 | 0 | 0 | 22.97 | 5.02 | 0
7390 | 2009-11-04 21:00 | 0 | 0 | 0 | 21.83 | 6.06 | 0
7391 | 2009-11-04 22:00 | 0 | 0 | 0 | 20.68 | 6.06 | 0
7392 | 2009-11-04 23:00 | 0 | 0 | 0 | 19.97 | 6.06 | 0
7393 | 2009-11-05 | 0 | 0 | 0 | 19.26 | 6.98 | 0
7394 | 2009-11-05 01:00 | 0 | 0 | 0 | 18.54 | 6.98 | 0
7395 | 2009-11-05 02:00 | 0 | 0 | 0 | 18.27 | 6.98 | 0
7396 | 2009-11-05 03:00 | 0 | 0 | 0 | 17.99 | 7.34 | 0
7397 | 2009-11-05 04:00 | 0 | 0 | 0 | 17.71 | 7.34 | 0
7398 | 2009-11-05 05:00 | 0 | 0 | 0 | 17 | 7.34 | 0
7399 | 2009-11-05 06:00 | 27 | 331 | 4 | 16.29 | 4.36 | 0 | 2.307 | 111.056 | 79.1522 | 0 | 27 | 49.7541 | 5.9524 | 0.25297 | 2.4792 | 5.5705 | 0.0013204 | 1.9445 | 5.3643 | 0.00099496 | 7.0905 | 7.0821 | 15906.9 | 16.4565 | 8829.33 | 9131.79 | 8235.58 | 0 | 0 | 8232.72 | 530.905 | 0 | 0 | 0 | 5265.08 | 2967.64 | 660 | 2856.72 | 2799.5857
7400 | 2009-11-05 07:00 | 221 | 757 | 45 | 15.58 | 4.36 | 0 | 13.4289 | 120.349 | 65.2806 | 0 | 221 | 316.91 | 62.1085 | 2.0706 | 210.837 | 58.1235 | 0.010808 | 196.169 | 55.9724 | 0.0081439 | 244.585 | 244.605 | 549300 | 21.3299 | 512260 | 517325 | 451432 | 0 | 0 | 449613 | 706.893 | 0 | 0 | 0 | 0 | 449613 | 706.893 | 441738 | 432902.8125
7401 | 2009-11-05 08:00 | 404 | 884 | 53 | 17.12 | 4.36 | 0 | 23.4422 | 131.316 | 51.9361 | 0 | 404 | 543.974 | 68.8837 | 3.7852 | 518.157 | 64.464 | 0.019757 | 502.043 | 62.0783 | 0.014887 | 547.212 | 547.181 | 1228860 | 29.9825 | 1198070 | 1169590 | 1074280 | 0 | 0 | 1064980 | 706.959 | 0 | 0 | 0 | 0 | 1064980 | 706.959 | 1048160 | 1027197.3125
7402 | 2009-11-05 09:00 | 548 | 882 | 85 | 18.65 | 5.88 | 0 | 31.7165 | 144.675 | 39.6661 | 0 | 548 | 677.944 | 112.749 | 5.1343 | 677.944 | 105.515 | 0.0268 | 667.806 | 101.61 | 0.020194 | 746.353 | 746.349 | 1676110 | 34.5452 | 1661210 | 1593880 | 1552740 | 0 | 0 | 1533910 | 704.238 | 0 | 0 | 0 | 0 | 1533910 | 704.238 | 1507260 | 1477117.5
7403 | 2009-11-05 10:00 | 609 | 789 | 131 | 20.19 | 5.88 | 0 | 37.3875 | 160.812 | 29.8366 | 0 | 609 | 682.87 | 171.652 | 5.7059 | 682.87 | 160.639 | 0.029783 | 677.653 | 154.693 | 0.022442 | 807.398 | 807.391 | 1813190 | 37.3853 | 1804860 | 1710300 | 1667000 | 0 | 0 | 1644810 | 696.05 | 0 | 0 | 0 | 0 | 1644810 | 696.05 | 1615060 | 1582757.5
7404 | 2009-11-05 11:00 | 684 | 870 | 132 | 21.14 | 5.88 | 0 | 39.5478 | 179.06 | 25.4581 | 0 | 684 | 782.761 | 168.709 | 6.4085 | 782.761 | 157.885 | 0.03345 | 778.552 | 152.041 | 0.025206 | 902.7 | 902.692 | 2027220 | 40.3649 | 2029770 | 1898650 | 1851270 | 0 | 0 | 1823560 | 689.805 | 0 | 0 | 0 | 0 | 1823560 | 689.805 | 1788000 | 1752238.75
7405 | 2009-11-05 12:00 | 634 | 888 | 92 | 22.09 | 6.29 | 0 | 37.7533 | 197.417 | 29.1059 | 0 | 634 | 773.456 | 114.979 | 5.9401 | 773.456 | 107.602 | 0.031005 | 767.866 | 103.619 | 0.023363 | 845.364 | 845.357 | 1898460 | 39.6255 | 1894380 | 1777420 | 1732150 | 0 | 0 | 1707900 | 691.183 | 0 | 0 | 0 | 0 | 1707900 | 691.183 | 1676250 | 1642722.625
7406 | 2009-11-05 13:00 | 577 | 848 | 124 | 23.04 | 6.29 | 0 | 32.3771 | 213.801 | 38.5642 | 0 | 577 | 661.46 | 161.321 | 5.406 | 661.46 | 150.97 | 0.028218 | 652.235 | 145.383 | 0.021263 | 773.71 | 773.701 | 1737540 | 39.0891 | 1725530 | 1622290 | 1581870 | 0 | 0 | 1561520 | 690.023 | 0 | 0 | 0 | 0 | 1561520 | 690.023 | 1534550 | 1503856.5
7407 | 2009-11-05 14:00 | 356 | 549 | 130 | 23.14 | 6.29 | 0 | 24.3076 | 227.409 | 50.6746 | 0 | 356 | 347.934 | 158.841 | 3.3354 | 347.934 | 148.649 | 0.01741 | 337.879 | 143.148 | 0.013119 | 466.609 | 466.604 | 1047880 | 32.8189 | 1009840 | 975063 | 949539 | 0 | 0 | 942240 | 694.929 | 0 | 0 | 0 | 0 | 942240 | 694.929 | 928345 | 909778.5
7408 | 2009-11-05 15:00 | 145 | 168 | 103 | 23.24 | 6.75 | 0 | 14.4264 | 238.562 | 63.9427 | 0 | 145 | 74.0531 | 113.343 | 1.3585 | 68.3554 | 106.07 | 0.0070911 | 63.9926 | 102.145 | 0.0053433 | 161.158 | 161.151 | 361906 | 26.4858 | 324038 | 321671 | 311048 | 0 | 0 | 310209 | 675.08 | 0 | 0 | 0 | 0 | 310209 | 675.08 | 303818 | 297741.75
7409 | 2009-11-05 16:00 | 19 | 70 | 13 | 23.34 | 6.75 | 0 | 3.3862 | 247.966 | 77.772 | 0 | 19 | 14.6071 | 18.5968 | 0.17802 | 7.2199 | 17.4036 | 0.00092918 | 5.8765 | 16.7595 | 0.00070016 | 21.9576 | 21.9502 | 49295.1 | 23.7821 | 35179.2 | 35405.7 | 32870.9 | 0 | 0 | 32857.9 | 585.214 | 0 | 0 | 0 | 7760.6 | 25097.3 | 660 | 24181.5 | 23697.8262
7410 | 2009-11-05 17:00 | 0 | 0 | 0 | 22.39 | 6.75 | 0
7411 | 2009-11-05 18:00 | 0 | 0 | 0 | 21.45 | 7.96 | 0
7412 | 2009-11-05 19:00 | 0 | 0 | 0 | 20.51 | 7.96 | 0
7413 | 2009-11-05 20:00 | 0 | 0 | 0 | 19.13 | 7.96 | 0
7414 | 2009-11-05 21:00 | 0 | 0 | 0 | 17.75 | 7.39 | 0
7415 | 2009-11-05 22:00 | 0 | 0 | 0 | 16.37 | 7.39 | 0
7416 | 2009-11-05 23:00 | 0 | 0 | 0 | 15.41 | 7.39 | 0
7417 | 2009-11-06 | 0 | 0 | 0 | 14.45 | 6.22 | 0
7418 | 2009-11-06 01:00 | 0 | 0 | 0 | 13.49 | 6.22 | 0
7419 | 2009-11-06 02:00 | 0 | 0 | 0 | 13.09 | 6.22 | 0
7420 | 2009-11-06 03:00 | 0 | 0 | 0 | 12.68 | 7.6 | 0
7421 | 2009-11-06 04:00 | 0 | 0 | 0 | 12.27 | 7.6 | 0
7422 | 2009-11-06 05:00 | 0 | 0 | 0 | 11.86 | 7.6 | 0
7423 | 2009-11-06 06:00 | 26 | 369 | 1 | 11.46 | 4.57 | 0 | 2.1191 | 111.29 | 79.2306 | 0 | 26 | 53.6942 | 1.5204 | 0.2436 | 2.7352 | 1.4228 | 0.0012715 | 2.1401 | 1.3702 | 0.00095811 | 3.4059 | 3.4021 | 7642.06 | 11.5389 | 4144.52 | 4388.32 | 3558.95 | 0 | 0 | 3556.89 | 607.857 | 0 | 0 | 0 | 565.408 | 2991.48 | 660 | 2879.79 | 2822.1909
7424 | 2009-11-06 07:00 | 211 | 745 | 40 | 11.05 | 4.57 | 0 | 13.2199 | 120.569 | 65.3861 | 0 | 211 | 311.435 | 54.0936 | 1.9769 | 204.56 | 50.6228 | 0.010319 | 190.231 | 48.7493 | 0.0077754 | 231.819 | 231.853 | 520660 | 16.4258 | 484216 | 499661 | 433402 | 0 | 0 | 431774 | 721.133 | 0 | 0 | 0 | 0 | 431774 | 721.133 | 423732 | 415256.9375
7425 | 2009-11-06 08:00 | 399 | 880 | 53 | 12.84 | 4.57 | 0 | 23.2066 | 131.517 | 52.0776 | 0 | 399 | 539.654 | 69.0257 | 3.7383 | 512.699 | 64.5969 | 0.019513 | 496.623 | 62.2062 | 0.014703 | 542.079 | 542.086 | 1217430 | 25.409 | 1186380 | 1181470 | 1084540 | 0 | 0 | 1075480 | 724.055 | 0 | 0 | 0 | 0 | 1075480 | 724.055 | 1057650 | 1036495.1875
7426 | 2009-11-06 09:00 | 559 | 950 | 64 | 14.63 | 1.63 | 0 | 31.4517 | 144.839 | 39.8579 | 0 | 559 | 728.238 | 81.9496 | 5.2374 | 728.238 | 76.6916 | 0.027337 | 717.216 | 73.8533 | 0.020599 | 767.357 | 767.355 | 1723290 | 36.2435 | 1710610 | 1628920 | 1585030 | 0 | 0 | 1565260 | 701.49 | 0 | 0 | 0 | 0 | 1565260 | 701.49 | 1537780 | 1507027.75
7427 | 2009-11-06 10:00 | 628 | 888 | 94 | 16.42 | 1.63 | 0 | 37.0979 | 160.905 | 30.0942 | 0 | 628 | 765.972 | 124.778 | 5.8839 | 765.972 | 116.772 | 0.030712 | 760.005 | 112.45 | 0.023142 | 846.304 | 846.303 | 1900580 | 40.2572 | 1896610 | 1774280 | 1732270 | 0 | 0 | 1707810 | 687.982 | 0 | 0 | 0 | 0 | 1707810 | 687.982 | 1676240 | 1642713.125
7428 | 2009-11-06 11:00 | 677 | 965 | 68 | 17.97 | 1.63 | 0 | 39.2491 | 179.052 | 25.7568 | 0 | 677 | 866.919 | 86.4395 | 6.343 | 866.919 | 80.8934 | 0.033108 | 862.137 | 77.8996 | 0.024948 | 911.86 | 911.856 | 2047800 | 43.6536 | 2051430 | 1890120 | 1843470 | 0 | 0 | 1815140 | 679.324 | 0 | 0 | 0 | 0 | 1815140 | 679.324 | 1780050 | 1744451.375
7429 | 2009-11-06 12:00 | 666 | 981 | 71 | 19.51 | 2.83 | 0 | 37.4675 | 197.308 | 29.3596 | 0 | 666 | 852.488 | 90.1595 | 6.2399 | 852.488 | 84.3747 | 0.03257 | 846.207 | 81.252 | 0.024542 | 899.659 | 899.654 | 2020390 | 42.9012 | 2022580 | 1869950 | 1825110 | 0 | 0 | 1797350 | 679.76 | 0 | 0 | 0 | 0 | 1797350 | 679.76 | 1762890 | 1727634
7430 | 2009-11-06 13:00 | 572 | 955 | 65 | 21.05 | 2.83 | 0 | 32.1199 | 213.622 | 38.7458 | 0 | 572 | 743.708 | 83.1503 | 5.3592 | 743.708 | 77.8152 | 0.027973 | 733.216 | 74.9353 | 0.021078 | 783.927 | 783.925 | 1760500 | 41.4323 | 1749600 | 1627330 | 1586580 | 0 | 0 | 1565770 | 684.128 | 0 | 0 | 0 | 0 | 1565770 | 684.128 | 1538870 | 1508092.75
7431 | 2009-11-06 14:00 | 424 | 898 | 58 | 21.26 | 2.83 | 0 | 24.083 | 227.194 | 50.8017 | 0 | 424 | 566.865 | 75.1041 | 3.9726 | 566.865 | 70.2853 | 0.020735 | 550.362 | 67.6841 | 0.015624 | 599.52 | 599.516 | 1346360 | 36.8476 | 1317560 | 1250010 | 1217750 | 0 | 0 | 1205640 | 690.755 | 0 | 0 | 0 | 0 | 1205640 | 690.755 | 1187010 | 1163269.5
7432 | 2009-11-06 15:00 | 228 | 771 | 38 | 21.48 | 3.27 | 0 | 14.231 | 238.33 | 64.0315 | 0 | 228 | 338.428 | 51.451 | 2.1362 | 312.389 | 48.1499 | 0.01115 | 292.337 | 46.3679 | 0.0084019 | 328.552 | 328.521 | 737778 | 29.7764 | 695507 | 679955 | 649797 | 0 | 0 | 646334 | 694.101 | 0 | 0 | 0 | 0 | 646334 | 694.101 | 636830 | 624093.125
7433 | 2009-11-06 16:00 | 30 | 317 | 5 | 21.69 | 3.27 | 0 | 3.214 | 247.723 | 77.8324 | 0 | 30 | 60.5667 | 7.8211 | 0.28108 | 29.9365 | 7.3193 | 0.0014671 | 24.3317 | 7.0484 | 0.0011055 | 30.4398 | 30.4234 | 68325.1 | 22.4583 | 52706.4 | 53285.1 | 41111.4 | 0 | 0 | 41085.2 | 581.524 | 0 | 0 | 0 | 3206.16 | 37879 | 660 | 36526.8 | 35796.2695
7434 | 2009-11-06 17:00 | 0 | 0 | 0 | 20.61 | 3.27 | 0
7435 | 2009-11-06 18:00 | 0 | 0 | 0 | 19.52 | 3.95 | 0
7436 | 2009-11-06 19:00 | 0 | 0 | 0 | 18.43 | 3.95 | 0
7437 | 2009-11-06 20:00 | 0 | 0 | 0 | 17.24 | 3.95 | 0
7438 | 2009-11-06 21:00 | 0 | 0 | 0 | 16.05 | 5.15 | 0
7439 | 2009-11-06 22:00 | 0 | 0 | 0 | 14.86 | 5.15 | 0
7440 | 2009-11-06 23:00 | 0 | 0 | 0 | 13.96 | 5.15 | 0
7441 | 2009-11-07 | 0 | 0 | 0 | 13.06 | 5.26 | 0
7442 | 2009-11-07 01:00 | 0 | 0 | 0 | 12.16 | 5.26 | 0
7443 | 2009-11-07 02:00 | 0 | 0 | 0 | 11.52 | 5.26 | 0
7444 | 2009-11-07 03:00 | 0 | 0 | 0 | 10.87 | 6.23 | 0
7445 | 2009-11-07 04:00 | 0 | 0 | 0 | 10.23 | 6.23 | 0
7446 | 2009-11-07 05:00 | 0 | 0 | 0 | 9.95 | 6.23 | 0
7447 | 2009-11-07 06:00 | 11 | 22 | 10 | 9.67 | 4.58 | 0 | 1.9313 | 111.518 | 79.3115 | 0 | 11 | 2.1318 | 10.266 | 0.10306 | 0.10076 | 9.6073 | 0.00053795 | 0.078638 | 9.2518 | 0.00040535 | 9.0509 | 9.0502 | 20324.6 | 9.8797 | 11682.6 | 12520.9 | 12236 | 0 | 0 | 12234.3 | 582.112 | 0 | 0 | 0 | 2963.63 | 9270.63 | 660 | 8923.51 | 8745.04
7448 | 2009-11-07 07:00 | 194 | 504 | 80 | 9.39 | 4.58 | 0 | 13.0113 | 120.783 | 65.494 | 0 | 194 | 210.027 | 100.564 | 1.8176 | 136.059 | 94.1113 | 0.0094874 | 126.461 | 90.6283 | 0.007149 | 210.583 | 210.538 | 472796 | 14.2684 | 434348 | 454205 | 408486 | 0 | 0 | 407155 | 724.042 | 0 | 0 | 0 | 0 | 407155 | 724.042 | 399209 | 391224.3438
7449 | 2009-11-07 08:00 | 375 | 825 | 53 | 11.15 | 4.58 | 0 | 22.9721 | 131.712 | 52.221 | 0 | 375 | 505.436 | 69.1672 | 3.5135 | 478.957 | 64.7293 | 0.018339 | 463.814 | 62.3337 | 0.013819 | 510.376 | 510.432 | 1146340 | 22.9773 | 1113050 | 1120180 | 1029960 | 0 | 0 | 1021900 | 729.742 | 0 | 0 | 0 | 0 | 1021900 | 729.742 | 1004820 | 984726.75
7450 | 2009-11-07 09:00 | 530 | 908 | 61 | 12.9 | 4.07 | 0 | 31.189 | 144.995 | 40.0506 | 0 | 530 | 693.25 | 78.4302 | 4.9657 | 693.25 | 73.398 | 0.025919 | 682.63 | 70.6816 | 0.019531 | 730.731 | 730.728 | 1641030 | 30.4066 | 1624510 | 1587140 | 1545070 | 0 | 0 | 1527110 | 718.467 | 0 | 0 | 0 | 0 | 1527110 | 718.467 | 1500150 | 1470150.625
7451 | 2009-11-07 10:00 | 631 | 943 | 68 | 14.66 | 4.07 | 0 | 36.8116 | 160.992 | 30.3505 | 0 | 631 | 810.835 | 86.67 | 5.912 | 810.835 | 81.1091 | 0.030859 | 804.396 | 78.1073 | 0.023252 | 856.051 | 856.044 | 1922460 | 35.1688 | 1919590 | 1837430 | 1789000 | 0 | 0 | 1764200 | 705.507 | 0 | 0 | 0 | 0 | 1764200 | 705.507 | 1730370 | 1695759.375
7452 | 2009-11-07 11:00 | 691 | 989 | 71 | 16.15 | 4.07 | 0 | 38.9549 | 179.04 | 26.0511 | 0 | 691 | 885.958 | 90.2129 | 6.4741 | 885.958 | 84.4247 | 0.033793 | 880.949 | 81.3002 | 0.025464 | 933.406 | 933.405 | 2096190 | 38.5122 | 2102370 | 1983320 | 1932830 | 0 | 0 | 1903160 | 695.86 | 0 | 0 | 0 | 0 | 1903160 | 695.86 | 1864700 | 1827410.375
7453 | 2009-11-07 12:00 | 661 | 980 | 70 | 17.64 | 2.64 | 0 | 37.1869 | 197.197 | 29.6085 | 0 | 661 | 850.123 | 89.088 | 6.1931 | 850.123 | 83.3719 | 0.032326 | 843.739 | 80.2864 | 0.024358 | 896.328 | 896.322 | 2012910 | 41.2405 | 2014710 | 1876900 | 1830110 | 0 | 0 | 1802830 | 688.083 | 0 | 0 | 0 | 0 | 1802830 | 688.083 | 1768030 | 1732667
7454 | 2009-11-07 13:00 | 545 | 927 | 57 | 19.12 | 2.64 | 0 | 31.868 | 213.443 | 38.9232 | 0 | 545 | 719.099 | 73.5014 | 5.1062 | 719.099 | 68.7854 | 0.026653 | 708.838 | 66.2397 | 0.020083 | 751.845 | 751.843 | 1688450 | 38.9163 | 1674120 | 1574920 | 1537410 | 0 | 0 | 1518110 | 689.016 | 0 | 0 | 0 | 0 | 1518110 | 689.016 | 1492490 | 1462635.625
7455 | 2009-11-07 14:00 | 418 | 813 | 90 | 19.33 | 2.64 | 0 | 23.8636 | 226.98 | 50.9248 | 0 | 418 | 511.052 | 119.288 | 3.9163 | 511.052 | 111.634 | 0.020442 | 496.066 | 107.503 | 0.015403 | 585.477 | 585.47 | 1314820 | 34.7456 | 1284870 | 1230650 | 1200620 | 0 | 0 | 1189040 | 696.446 | 0 | 0 | 0 | 0 | 1189040 | 696.446 | 1170470 | 1147064
7456 | 2009-11-07 15:00 | 179 | 359 | 92 | 19.54 | 3.52 | 0 | 14.0409 | 238.099 | 64.1164 | 0 | 179 | 156.542 | 114.164 | 1.6771 | 144.497 | 106.839 | 0.0087538 | 135.172 | 102.885 | 0.0065962 | 230.921 | 230.907 | 518561 | 25.2758 | 477031 | 476252 | 458258 | 0 | 0 | 456541 | 695.118 | 0 | 0 | 0 | 0 | 456541 | 695.118 | 449190 | 440205.8438
7457 | 2009-11-07 16:00 | 23 | 145 | 12 | 19.74 | 3.52 | 0 | 3.0472 | 247.481 | 77.8888 | 0 | 23 | 26.5276 | 18.8452 | 0.21549 | 13.0003 | 17.636 | 0.0011248 | 10.5522 | 16.9833 | 0.00084756 | 26.7103 | 26.6927 | 59945.4 | 20.4031 | 44359.9 | 45430 | 40389.9 | 0 | 0 | 40370.8 | 605.874 | 0 | 0 | 0 | 3655.61 | 36715.2 | 660 | 35401.2 | 34693.1406
7458 | 2009-11-07 17:00 | 0 | 0 | 0 | 18.93 | 3.52 | 0
7459 | 2009-11-07 18:00 | 0 | 0 | 0 | 18.11 | 2.85 | 0
7460 | 2009-11-07 19:00 | 0 | 0 | 0 | 17.3 | 2.85 | 0
7461 | 2009-11-07 20:00 | 0 | 0 | 0 | 16.42 | 2.85 | 0
7462 | 2009-11-07 21:00 | 0 | 0 | 0 | 15.54 | 1.62 | 0
7463 | 2009-11-07 22:00 | 0 | 0 | 0 | 14.67 | 1.62 | 0
7464 | 2009-11-07 23:00 | 0 | 0 | 0 | 13.92 | 1.62 | 0
7465 | 2009-11-08 | 0 | 0 | 0 | 13.17 | 2.75 | 0
7466 | 2009-11-08 01:00 | 0 | 0 | 0 | 12.43 | 2.75 | 0
7467 | 2009-11-08 02:00 | 0 | 0 | 0 | 11.84 | 2.75 | 0
7468 | 2009-11-08 03:00 | 0 | 0 | 0 | 11.25 | 6.06 | 0
7469 | 2009-11-08 04:00 | 0 | 0 | 0 | 10.67 | 6.06 | 0
7470 | 2009-11-08 05:00 | 0 | 0 | 0 | 10.14 | 6.06 | 0
7471 | 2009-11-08 06:00 | 21 | 348 | 0 | 9.6 | 7.79 | 0 | 1.7436 | 111.74 | 79.3948 | 0 | 21 | 44.4235 | 0 | 0.19675 | 2.1384 | 0 | 0.001027 | 1.6644 | 0 | 0.00077386 | 1.6152 | 1.6133 | 3625.15 | 9.6304 | 2756.28 | 2972.77 | 2445.47 | 0 | 0 | 2444.23 | 639.877 | 0 | 0 | 0 | 174.354 | 2269.88 | 660.001 | 2184.75 | 2141.0535
7472 | 2009-11-08 07:00 | 210 | 746 | 44 | 9.07 | 7.79 | 0 | 12.8031 | 120.992 | 65.604 | 0 | 210 | 309.405 | 61.3541 | 1.9675 | 189.574 | 57.4175 | 0.01027 | 176.104 | 55.2925 | 0.0077386 | 224.462 | 224.425 | 503971 | 13.3016 | 467813 | 489794 | 421281 | 0 | 0 | 419725 | 717.681 | 0 | 0 | 0 | 0 | 419725 | 717.681 | 411965 | 403725.8125
7473 | 2009-11-08 08:00 | 397 | 884 | 56 | 10.78 | 7.79 | 0 | 22.7388 | 131.899 | 52.3661 | 0 | 397 | 538.689 | 72.9875 | 3.7196 | 508.853 | 68.3045 | 0.019415 | 492.628 | 65.7766 | 0.01463 | 541.667 | 541.71 | 1216590 | 20.9941 | 1185660 | 1203490 | 1108130 | 0 | 0 | 1099020 | 738.341 | 0 | 0 | 0 | 0 | 1099020 | 738.341 | 1080080 | 1058476.75
7474 | 2009-11-08 09:00 | 542 | 939 | 60 | 12.5 | 4.35 | 0 | 30.9285 | 145.144 | 40.244 | 0 | 542 | 715.824 | 77.3378 | 5.0781 | 715.824 | 72.3757 | 0.026506 | 704.725 | 69.6971 | 0.019973 | 751.209 | 751.203 | 1687010 | 30.1699 | 1672620 | 1635910 | 1593090 | 0 | 0 | 1574080 | 719.387 | 0 | 0 | 0 | 0 | 1574080 | 719.387 | 1545740 | 1514824.125
7475 | 2009-11-08 10:00 | 648 | 925 | 99 | 14.21 | 4.35 | 0 | 36.5289 | 161.073 | 30.6052 | 0 | 648 | 793.851 | 131.001 | 6.0713 | 793.851 | 122.596 | 0.03169 | 787.427 | 118.059 | 0.023879 | 878.344 | 878.346 | 1972540 | 34.8706 | 1972240 | 1890460 | 1839080 | 0 | 0 | 1813050 | 708.328 | 0 | 0 | 0 | 0 | 1813050 | 708.328 | 1777550 | 1741998.875
7476 | 2009-11-08 11:00 | 641 | 871 | 99 | 15.73 | 4.35 | 0 | 38.6653 | 179.023 | 26.3409 | 0 | 641 | 777.445 | 131.511 | 6.0057 | 777.445 | 123.073 | 0.031348 | 772.941 | 118.518 | 0.023621 | 864.738 | 864.73 | 1941960 | 36.0703 | 1940090 | 1849750 | 1806330 | 0 | 0 | 1780820 | 702.409 | 0 | 0 | 0 | 0 | 1780820 | 702.409 | 1746500 | 1711567.25
7477 | 2009-11-08 12:00 | 624 | 930 | 67 | 17.25 | 2.08 | 0 | 36.9114 | 197.085 | 29.8525 | 0 | 624 | 804.375 | 85.5777 | 5.8464 | 804.375 | 80.0869 | 0.030516 | 798.222 | 77.1229 | 0.022995 | 849.107 | 849.101 | 1906870 | 40.4568 | 1903210 | 1778880 | 1735380 | 0 | 0 | 1710750 | 686.99 | 0 | 0 | 0 | 0 | 1710750 | 686.99 | 1679110 | 1645523.875
7478 | 2009-11-08 13:00 | 527 | 893 | 60 | 18.76 | 2.08 | 0 | 31.6215 | 213.265 | 39.0962 | 0 | 527 | 691.263 | 77.315 | 4.9376 | 691.263 | 72.3543 | 0.025773 | 681.291 | 69.6765 | 0.01942 | 728.457 | 728.453 | 1635920 | 38.6694 | 1619170 | 1524680 | 1485240 | 0 | 0 | 1467310 | 690.144 | 0 | 0 | 0 | 0 | 1467310 | 690.144 | 1442940 | 1414078.875
7479 | 2009-11-08 14:00 | 405 | 887 | 50 | 19.26 | 2.08 | 0 | 23.6497 | 226.767 | 51.0438 | 0 | 405 | 556.404 | 65.5501 | 3.7945 | 556.404 | 61.3443 | 0.019806 | 539.975 | 59.0739 | 0.014924 | 581.092 | 581.089 | 1304980 | 35.1418 | 1274680 | 1218640 | 1187910 | 0 | 0 | 1176520 | 695.331 | 0 | 0 | 0 | 0 | 1176520 | 695.331 | 1158270 | 1135103.5
7480 | 2009-11-08 15:00 | 219 | 766 | 35 | 19.76 | 1.89 | 0 | 13.8562 | 237.87 | 64.1973 | 0 | 219 | 334.426 | 47.9459 | 2.0519 | 308.695 | 44.8696 | 0.01071 | 288.67 | 43.209 | 0.0080702 | 321.93 | 321.895 | 722897 | 28.6701 | 680560 | 668698 | 639118 | 0 | 0 | 635780 | 695.26 | 0 | 0 | 0 | 0 | 635780 | 695.26 | 626394 | 613866.375
7481 | 2009-11-08 16:00 | 28 | 305 | 5 | 20.26 | 1.89 | 0 | 2.8858 | 247.241 | 77.9412 | 0 | 28 | 55.2304 | 7.7626 | 0.26234 | 24.9766 | 7.2645 | 0.0013693 | 20.2477 | 6.9957 | 0.0010318 | 26.4271 | 26.4189 | 59333.1 | 20.9913 | 44845.4 | 45688.1 | 34602.1 | 0 | 0 | 34581.8 | 559.014 | 0 | 0 | 0 | 3202.27 | 31379.5 | 660 | 30247.1 | 29642.168
7482 | 2009-11-08 17:00 | 0 | 0 | 0 | 19.8 | 1.89 | 0
7483 | 2009-11-08 18:00 | 0 | 0 | 0 | 19.33 | 2.31 | 0
7484 | 2009-11-08 19:00 | 0 | 0 | 0 | 18.87 | 2.31 | 0
7485 | 2009-11-08 20:00 | 0 | 0 | 0 | 18.15 | 2.31 | 0
7486 | 2009-11-08 21:00 | 0 | 0 | 0 | 17.43 | 2.74 | 0
7487 | 2009-11-08 22:00 | 0 | 0 | 0 | 16.72 | 2.74 | 0
7488 | 2009-11-08 23:00 | 0 | 0 | 0 | 16.08 | 2.74 | 0
7489 | 2009-11-09 | 0 | 0 | 0 | 15.45 | 4.46 | 0
7490 | 2009-11-09 01:00 | 0 | 0 | 0 | 14.81 | 4.46 | 0
7491 | 2009-11-09 02:00 | 0 | 0 | 0 | 14.26 | 4.46 | 0
7492 | 2009-11-09 03:00 | 0 | 0 | 0 | 13.7 | 1.31 | 0
7493 | 2009-11-09 04:00 | 0 | 0 | 0 | 13.14 | 1.31 | 0
7494 | 2009-11-09 05:00 | 0 | 0 | 0 | 12.68 | 1.31 | 0
7495 | 2009-11-09 06:00 | 19 | 246 | 3 | 12.22 | 1.97 | 0 | 1.556 | 111.957 | 79.4805 | 0 | 19 | 33.5761 | 4.4144 | 0.17802 | 1.6308 | 4.1312 | 0.00092918 | 1.2658 | 3.9783 | 0.00070016 | 5.0874 | 5.0825 | 11415.1 | 12.3599 | 5505.24 | 5725.54 | 4969.17 | 0 | 0 | 4967.98 | 527.239 | 0 | 0 | 0 | 2978.81 | 1989.16 | 660.001 | 1914.39 | 1876.1049
7496 | 2009-11-09 07:00 | 162 | 438 | 66 | 11.76 | 1.97 | 0 | 12.5956 | 121.193 | 65.7163 | 0 | 162 | 181.047 | 87.4186 | 1.5178 | 109.279 | 81.8097 | 0.0079225 | 101.457 | 78.782 | 0.0059698 | 174.838 | 174.77 | 392475 | 16.5719 | 355801 | 368367 | 329074 | 0 | 0 | 328162 | 706.079 | 0 | 0 | 0 | 0 | 328162 | 706.079 | 321363 | 314936.1562
7497 | 2009-11-09 08:00 | 354 | 706 | 84 | 13.23 | 1.97 | 0 | 22.5067 | 132.08 | 52.5129 | 0 | 354 | 429.26 | 112.319 | 3.3167 | 404.23 | 105.112 | 0.017312 | 391.231 | 101.222 | 0.013045 | 477.692 | 477.65 | 1072720 | 26.381 | 1036990 | 1028290 | 954374 | 0 | 0 | 947243 | 716.356 | 0 | 0 | 0 | 0 | 947243 | 716.356 | 932196 | 913552.25
7498 | 2009-11-09 09:00 | 505 | 855 | 70 | 14.7 | 1.83 | 0 | 30.6703 | 145.287 | 40.4381 | 0 | 505 | 649.057 | 89.636 | 4.7315 | 649.057 | 83.8848 | 0.024697 | 638.871 | 80.7803 | 0.018609 | 698.08 | 698.075 | 1567690 | 34.1006 | 1547900 | 1487710 | 1448170 | 0 | 0 | 1431760 | 704.403 | 0 | 0 | 0 | 0 | 1431760 | 704.403 | 1407630 | 1379474
7499 | 2009-11-09 10:00 | 591 | 829 | 102 | 16.17 | 1.83 | 0 | 36.2496 | 161.147 | 30.8582 | 0 | 591 | 709.917 | 134.658 | 5.5372 | 709.917 | 126.018 | 0.028902 | 704.064 | 121.354 | 0.021778 | 800.677 | 800.671 | 1798100 | 38.4219 | 1789030 | 1687240 | 1646090 | 0 | 0 | 1624280 | 693.154 | 0 | 0 | 0 | 0 | 1624280 | 693.154 | 1595260 | 1563359.125
7500 | 2009-11-09 11:00 | 654 | 904 | 94 | 17.81 | 1.83 | 0 | 38.3803 | 179.003 | 26.6261 | 0 | 654 | 806.296 | 117.949 | 6.1275 | 806.296 | 110.381 | 0.031983 | 801.514 | 106.296 | 0.0241 | 880.599 | 880.595 | 1977600 | 42.2831 | 1977560 | 1833300 | 1788090 | 0 | 0 | 1761630 | 682.171 | 0 | 0 | 0 | 0 | 1761630 | 682.171 | 1728370 | 1693798.625
7501 | 2009-11-09 12:00 | 637 | 805 | 158 | 19.44 | 3.53 | 0 | 36.6413 | 196.97 | 30.0915 | 0 | 637 | 694.438 | 203.26 | 5.9682 | 694.438 | 190.218 | 0.031152 | 689.029 | 183.178 | 0.023474 | 846.064 | 846.049 | 1900010 | 40.4422 | 1896010 | 1772280 | 1728820 | 0 | 0 | 1704440 | 687.404 | 0 | 0 | 0 | 0 | 1704440 | 687.404 | 1672990 | 1639531.125
7502 | 2009-11-09 13:00 | 434 | 433 | 209 | 21.07 | 3.53 | 0 | 31.3805 | 213.086 | 39.2648 | 0 | 434 | 334.54 | 251.096 | 4.0662 | 334.54 | 234.986 | 0.021224 | 329.663 | 226.289 | 0.015993 | 539.288 | 539.275 | 1211070 | 34.4569 | 1177610 | 1129070 | 1100520 | 0 | 0 | 1090720 | 694.307 | 0 | 0 | 0 | 0 | 1090720 | 694.307 | 1074250 | 1052762
7503 | 2009-11-09 14:00 | 412 | 749 | 114 | 21.6 | 3.53 | 0 | 23.4413 | 226.555 | 51.1586 | 0 | 412 | 469.813 | 146.07 | 3.8601 | 469.813 | 136.698 | 0.020148 | 455.849 | 131.638 | 0.015182 | 569.877 | 569.869 | 1279780 | 35.7464 | 1248600 | 1190340 | 1161280 | 0 | 0 | 1150260 | 690.675 | 0 | 0 | 0 | 0 | 1150260 | 690.675 | 1132770 | 1110113.375
7504 | 2009-11-09 15:00 | 188 | 524 | 64 | 22.13 | 3.17 | 0 | 13.6769 | 237.642 | 64.2741 | 0 | 188 | 227.638 | 86.1938 | 1.7614 | 210.123 | 80.6635 | 0.009194 | 196.425 | 77.6782 | 0.0069279 | 265.887 | 265.855 | 597045 | 28.8883 | 554758 | 544541 | 522535 | 0 | 0 | 520255 | 687.582 | 0 | 0 | 0 | 0 | 520255 | 687.582 | 512424 | 502175.875
7505 | 2009-11-09 16:00 | 23 | 205 | 8 | 22.65 | 3.17 | 0 | 2.7299 | 247.003 | 77.9895 | 0 | 23 | 35.8776 | 13.0282 | 0.21549 | 14.861 | 12.1923 | 0.0011248 | 12.0332 | 11.7411 | 0.00084756 | 23.0619 | 23.0412 | 51747.4 | 23.2357 | 37692.1 | 38004.1 | 30942.2 | 0 | 0 | 30928.5 | 571.06 | 0 | 0 | 0 | 6250.68 | 24677.8 | 660 | 23777 | 23301.4453
7506 | 2009-11-09 17:00 | 0 | 0 | 0 | 22.11 | 3.17 | 0
7507 | 2009-11-09 18:00 | 0 | 0 | 0 | 21.56 | 3.29 | 0
7508 | 2009-11-09 19:00 | 0 | 0 | 0 | 21.01 | 3.29 | 0
7509 | 2009-11-09 20:00 | 0 | 0 | 0 | 20.55 | 3.29 | 0
7510 | 2009-11-09 21:00 | 0 | 0 | 0 | 20.08 | 4.14 | 0
7511 | 2009-11-09 22:00 | 0 | 0 | 0 | 19.61 | 4.14 | 0
7512 | 2009-11-09 23:00 | 0 | 0 | 0 | 18.9 | 4.14 | 0
7513 | 2009-11-10 | 0 | 0 | 0 | 18.19 | 5.31 | 0
7514 | 2009-11-10 01:00 | 0 | 0 | 0 | 17.48 | 5.31 | 0
7515 | 2009-11-10 02:00 | 0 | 0 | 0 | 17.07 | 5.31 | 0
7516 | 2009-11-10 03:00 | 0 | 0 | 0 | 16.67 | 2.41 | 0
7517 | 2009-11-10 04:00 | 0 | 0 | 0 | 16.26 | 2.41 | 0
7518 | 2009-11-10 05:00 | 0 | 0 | 0 | 15.55 | 2.41 | 0
7519 | 2009-11-10 06:00 | 17 | 314 | 0 | 14.85 | 1.8 | 0 | 1.3686 | 112.167 | 79.5685 | 0 | 17 | 35.3795 | 0 | 0.15928 | 1.5834 | 0 | 0.00083137 | 1.2253 | 0 | 0.00062646 | 1.1891 | 1.1771 | 2643.99 | 14.8828 | 1908.88 | 2006.02 | 1680.36 | 0 | 0 | 1679.7 | 611.88 | 0 | 0 | 0 | 127.54 | 1552.16 | 660.001 | 1493.71 | 1463.8345
7520 | 2009-11-10 07:00 | 203 | 739 | 44 | 14.14 | 1.8 | 0 | 12.3887 | 121.389 | 65.8306 | 0 | 203 | 303.438 | 61.5767 | 1.902 | 172.785 | 57.6258 | 0.0099275 | 160.324 | 55.4931 | 0.0074806 | 209.35 | 209.229 | 469844 | 19.9665 | 434552 | 440336 | 376689 | 0 | 0 | 375346 | 694.487 | 0 | 0 | 0 | 1175.41 | 374170 | 698.642 | 367421 | 360072.625
7521 | 2009-11-10 08:00 | 368 | 808 | 62 | 15.51 | 1.8 | 0 | 22.2761 | 132.255 | 52.6613 | 0 | 368 | 489.611 | 84.6616 | 3.4479 | 459.808 | 79.2295 | 0.017997 | 444.893 | 76.2973 | 0.013561 | 505.568 | 505.58 | 1135450 | 29.5891 | 1101990 | 1076710 | 998742 | 0 | 0 | 990693 | 706.949 | 0 | 0 | 0 | 0 | 990693 | 706.949 | 975280 | 955773.875
7522 | 2009-11-10 09:00 | 537 | 941 | 62 | 16.89 | 0.67 | 0 | 30.4145 | 145.423 | 40.6325 | 0 | 537 | 712.054 | 80.0498 | 5.0313 | 712.054 | 74.9137 | 0.026262 | 700.743 | 72.1411 | 0.019789 | 749.717 | 749.713 | 1683670 | 39.4152 | 1669120 | 1566540 | 1527370 | 0 | 0 | 1508290 | 687.845 | 0 | 0 | 0 | 0 | 1508290 | 687.845 | 1482990 | 1453334.625
7523 | 2009-11-10 10:00 | 642 | 976 | 70 | 18.26 | 0.67 | 0 | 35.9741 | 161.216 | 31.1093 | 0 | 642 | 833.71 | 89.5013 | 6.015 | 833.71 | 83.7588 | 0.031397 | 826.708 | 80.6589 | 0.023658 | 880.169 | 880.163 | 1976630 | 44.7046 | 1976550 | 1811800 | 1766620 | 0 | 0 | 1740340 | 676.415 | 0 | 0 | 0 | 0 | 1740340 | 676.415 | 1707940 | 1673779.75
7524 | 2009-11-10 11:00 | 678 | 986 | 71 | 19.73 | 0.67 | 0 | 38.1002 | 178.978 | 26.9065 | 0 | 678 | 877.239 | 90.6149 | 6.3523 | 877.239 | 84.8009 | 0.033157 | 871.914 | 81.6625 | 0.024984 | 924.993 | 924.988 | 2077290 | 47.5214 | 2082470 | 1884380 | 1839700 | 0 | 0 | 1810420 | 667.268 | 0 | 0 | 0 | 0 | 1810420 | 667.268 | 1775710 | 1740196.25
7525 | 2009-11-10 12:00 | 648 | 927 | 100 | 21.2 | 1.56 | 0 | 36.3766 | 196.854 | 30.3254 | 0 | 648 | 797.548 | 132.598 | 6.0713 | 797.548 | 124.09 | 0.03169 | 791.227 | 119.497 | 0.023879 | 883.425 | 883.421 | 1983950 | 46.1997 | 1984240 | 1806190 | 1761470 | 0 | 0 | 1734980 | 671.35 | 0 | 0 | 0 | 0 | 1734980 | 671.35 | 1702880 | 1668822.25
7526 | 2009-11-10 13:00 | 503 | 772 | 105 | 22.67 | 1.56 | 0 | 31.1451 | 212.908 | 39.4289 | 0 | 503 | 594.386 | 140.161 | 4.7127 | 594.386 | 131.168 | 0.024599 | 585.63 | 126.314 | 0.018536 | 690.603 | 690.599 | 1550910 | 42.2131 | 1530390 | 1417180 | 1381440 | 0 | 0 | 1365360 | 678.419 | 0 | 0 | 0 | 0 | 1365360 | 678.419 | 1343810 | 1316938.125
7527 | 2009-11-10 14:00 | 409 | 811 | 89 | 23.07 | 1.56 | 0 | 23.2384 | 226.345 | 51.2691 | 0 | 409 | 507.434 | 118.669 | 3.832 | 507.434 | 111.055 | 0.020002 | 492.254 | 106.945 | 0.015072 | 581.237 | 581.23 | 1305300 | 39.5181 | 1275010 | 1194550 | 1165770 | 0 | 0 | 1154320 | 680.191 | 0 | 0 | 0 | 0 | 1154320 | 680.191 | 1137260 | 1114518.125
7528 | 2009-11-10 15:00 | 187 | 576 | 52 | 23.48 | 2.4 | 0 | 13.5032 | 237.416 | 64.3467 | 0 | 187 | 250.299 | 72.8866 | 1.752 | 221.411 | 68.21 | 0.0091451 | 206.91 | 65.6856 | 0.006891 | 264.425 | 264.401 | 593780 | 30.5538 | 551913 | 537108 | 506691 | 0 | 0 | 504490 | 681.945 | 0 | 0 | 0 | 0 | 504490 | 681.945 | 497006 | 487066.2812
7529 | 2009-11-10 16:00 | 22 | 222 | 6 | 23.88 | 2.4 | 0 | 2.5795 | 246.766 | 78.0338 | 0 | 22 | 38.1306 | 9.1737 | 0.20612 | 15.6993 | 8.5851 | 0.0010759 | 12.6983 | 8.2674 | 0.00081071 | 20.3375 | 20.331 | 45661.2 | 24.4239 | 32785.2 | 32839.2 | 25807 | 0 | 0 | 25796.1 | 555.376 | 0 | 0 | 0 | 6979.62 | 18816.5 | 660 | 18123.2 | 17760.7227
7530 | 2009-11-10 17:00 | 0 | 0 | 0 | 23.13 | 2.4 | 0
7531 | 2009-11-10 18:00 | 0 | 0 | 0 | 22.37 | 2.65 | 0
7532 | 2009-11-10 19:00 | 0 | 0 | 0 | 21.61 | 2.65 | 0
7533 | 2009-11-10 20:00 | 0 | 0 | 0 | 21.21 | 2.65 | 0
7534 | 2009-11-10 21:00 | 0 | 0 | 0 | 20.8 | 3.85 | 0
7535 | 2009-11-10 22:00 | 0 | 0 | 0 | 20.4 | 3.85 | 0
7536 | 2009-11-10 23:00 | 0 | 0 | 0 | 19.82 | 3.85 | 0
7537 | 2009-11-11 | 0 | 0 | 0 | 19.24 | 5.17 | 0
7538 | 2009-11-11 01:00 | 0 | 0 | 0 | 18.66 | 5.17 | 0
7539 | 2009-11-11 02:00 | 0 | 0 | 0 | 18.31 | 5.17 | 0
7540 | 2009-11-11 03:00 | 0 | 0 | 0 | 17.96 | 6.35 | 0
7541 | 2009-11-11 04:00 | 0 | 0 | 0 | 17.61 | 6.35 | 0
7542 | 2009-11-11 05:00 | 0 | 0 | 0 | 17.11 | 6.35 | 0
7543 | 2009-11-11 06:00 | 7 | 18 | 6 | 16.61 | 7.96 | 0 | 1.1816 | 112.372 | 79.6588 | 0 | 7 | 2.0633 | 6.0045 | 0.065585 | 0.093239 | 5.6193 | 0.00034233 | 0.071931 | 5.4113 | 0.00025795 | 5.319 | 5.3186 | 11944.1 | 16.7092 | 5517.59 | 5678.3 | 5560 | 0 | 0 | 5559.53 | 515.468 | 0 | 0 | 0 | 5515.12 | 44.407 | 660.029 | 42.7199 | 41.8656
7544 | 2009-11-11 07:00 | 113 | 131 | 85 | 16.1 | 7.96 | 0 | 12.1826 | 121.579 | 65.9469 | 0 | 113 | 54.0798 | 94.9829 | 1.0587 | 30.3018 | 88.8887 | 0.0055262 | 28.0996 | 85.599 | 0.0041641 | 110.292 | 110.279 | 247654 | 18.1572 | 215182 | 222333 | 208102 | 0 | 0 | 207739 | 686.829 | 0 | 0 | 0 | 0 | 207739 | 686.829 | 201988 | 197947.7969
7545 | 2009-11-11 08:00 | 278 | 340 | 151 | 17.48 | 7.96 | 0 | 22.047 | 132.423 | 52.811 | 0 | 278 | 204.506 | 173.999 | 2.6046 | 191.509 | 162.835 | 0.013595 | 185.242 | 156.809 | 0.010244 | 331.8 | 331.817 | 745192 | 23.6699 | 703113 | 706837 | 668812 | 0 | 0 | 665322 | 712.765 | 0 | 0 | 0 | 0 | 665322 | 712.765 | 654853 | 641756
7546 | 2009-11-11 09:00 | 335 | 185 | 242 | 18.85 | 6.63 | 0 | 30.1613 | 145.552 | 40.8272 | 0 | 335 | 140.061 | 266.921 | 3.1387 | 140.061 | 249.795 | 0.016383 | 137.809 | 240.55 | 0.012345 | 367.021 | 367.011 | 824212 | 26.299 | 782230 | 777612 | 756616 | 0 | 0 | 752141 | 708.274 | 0 | 0 | 0 | 0 | 752141 | 708.274 | 740548 | 725736.9375
7547 | 2009-11-11 10:00 | 340 | 117 | 272 | 20.23 | 6.63 | 0 | 35.7023 | 161.278 | 31.3583 | 0 | 340 | 99.5028 | 292.658 | 3.1855 | 99.5028 | 273.88 | 0.016627 | 98.6517 | 263.744 | 0.012529 | 351.536 | 351.522 | 789430 | 27.3647 | 747118 | 739113 | 719503 | 0 | 0 | 715399 | 703.498 | 0 | 0 | 0 | 0 | 715399 | 703.498 | 704543 | 690451.9375
7548 | 2009-11-11 11:00 | 494 | 381 | 261 | 21.07 | 6.63 | 0 | 37.8249 | 178.949 | 27.1821 | 0 | 494 | 337.981 | 300.538 | 4.6284 | 337.981 | 281.255 | 0.024159 | 335.883 | 270.846 | 0.018204 | 588.545 | 588.539 | 1321710 | 33.0153 | 1292020 | 1247260 | 1214380 | 0 | 0 | 1202710 | 701.98 | 0 | 0 | 0 | 0 | 1202710 | 701.98 | 1183600 | 1159927.625
7549 | 2009-11-11 12:00 | 485 | 381 | 261 | 21.92 | 9.28 | 0 | 36.1174 | 196.737 | 30.5541 | 0 | 485 | 327.254 | 300.391 | 4.5441 | 327.254 | 281.117 | 0.023718 | 324.616 | 270.714 | 0.017872 | 577.487 | 577.47 | 1296850 | 31.8403 | 1266270 | 1228820 | 1195700 | 0 | 0 | 1184520 | 706.145 | 0 | 0 | 0 | 0 | 1184520 | 706.145 | 1165580 | 1142272
7550 | 2009-11-11 13:00 | 189 | 24 | 177 | 22.76 | 9.28 | 0 | 30.9154 | 212.73 | 39.5882 | 0 | 189 | 17.9997 | 170.873 | 1.7708 | 17.9997 | 159.909 | 0.0092429 | 17.7319 | 153.991 | 0.0069647 | 166.578 | 166.571 | 374077 | 25.6215 | 335746 | 334721 | 326016 | 0 | 0 | 325105 | 678.79 | 0 | 0 | 0 | 0 | 325105 | 678.79 | 318607 | 312234.4062
7551 | 2009-11-11 14:00 | 311 | 350 | 174 | 22.64 | 9.28 | 0 | 23.0412 | 226.135 | 51.3754 | 0 | 311 | 218.495 | 200.657 | 2.9138 | 218.495 | 187.782 | 0.015209 | 211.919 | 180.832 | 0.01146 | 380.98 | 380.973 | 855570 | 29.1847 | 813948 | 798706 | 777928 | 0 | 0 | 773093 | 700.581 | 0 | 0 | 0 | 0 | 773093 | 700.581 | 761475 | 746245.125
7552 | 2009-11-11 15:00 | 101 | 51 | 89 | 22.52 | 8.3 | 0 | 13.3351 | 237.192 | 64.4151 | 0 | 101 | 22.4681 | 89.0773 | 0.94629 | 19.875 | 83.3619 | 0.0049393 | 18.5676 | 80.2767 | 0.0037219 | 95.8826 | 95.8725 | 215306 | 24.2707 | 184442 | 185106 | 179424 | 0 | 0 | 179131 | 659.824 | 0 | 0 | 0 | 2.9061 | 179128 | 660.154 | 174244 | 170759.5781
7553 | 2009-11-11 16:00 | 12 | 19 | 11 | 22.41 | 8.3 | 0 | 2.4347 | 246.532 | 78.0738 | 0 | 12 | 2.3753 | 8.6777 | 0.11243 | 0.97206 | 8.1209 | 0.00058685 | 0.78547 | 7.8203 | 0.0004422 | 8.3481 | 8.3466 | 18744.4 | 22.5624 | 10495.7 | 10619.1 | 10276 | 0 | 0 | 10274.4 | 526.202 | 0 | 0 | 0 | 9944.8 | 329.639 | 660 | 317.12 | 310.7776
7554 | 2009-11-11 17:00 | 0 | 0 | 0 | 21.35 | 8.3 | 0
7555 | 2009-11-11 18:00 | 0 | 0 | 0 | 20.29 | 10.43 | 0
7556 | 2009-11-11 19:00 | 0 | 0 | 0 | 19.23 | 10.43 | 0
7557 | 2009-11-11 20:00 | 0 | 0 | 0 | 18.43 | 10.43 | 0
7558 | 2009-11-11 21:00 | 0 | 0 | 0 | 17.63 | 9.45 | 0
7559 | 2009-11-11 22:00 | 0 | 0 | 0 | 16.83 | 9.45 | 0
7560 | 2009-11-11 23:00 | 0 | 0 | 0 | 16.12 | 9.45 | 0
7561 | 2009-11-12 | 0 | 0 | 0 | 15.41 | 10.2 | 0
7562 | 2009-11-12 01:00 | 0 | 0 | 0 | 14.7 | 10.2 | 0
7563 | 2009-11-12 02:00 | 0 | 0 | 0 | 14.63 | 10.2 | 0
7564 | 2009-11-12 03:00 | 0 | 0 | 0 | 14.56 | 8.05 | 0
7565 | 2009-11-12 04:00 | 0 | 0 | 0 | 14.49 | 8.05 | 0
7566 | 2009-11-12 05:00 | 0 | 0 | 0 | 13.96 | 8.05 | 0
7567 | 2009-11-12 06:00 | 13 | 228 | 0 | 13.42 | 10 | 0 | 0.99495 | 112.57 | 79.7513 | 0 | 13 | 26.5859 | 0 | 0.1218 | 1.2207 | 0 | 0.00063575 | 0.93865 | 0 | 0.00047905 | 0.91096 | 0.90931 | 2042.32 | 13.4349 | 1398.65 | 1482.57 | 1214.74 | 0 | 0 | 1214.38 | 605.466 | 0 | 0 | 0 | 126.286 | 1088.1 | 660.001 | 1047.01 | 1026.0717
7568 | 2009-11-12 07:00 | 164 | 460 | 68 | 12.88 | 10 | 0 | 11.9773 | 121.762 | 66.0651 | 0 | 164 | 187.674 | 89.4372 | 1.5366 | 103.266 | 83.6987 | 0.0080203 | 95.702 | 80.6011 | 0.0060434 | 171.02 | 170.924 | 383839 | 15.6889 | 347714 | 361874 | 317778 | 0 | 0 | 316925 | 707.359 | 0 | 0 | 0 | 0 | 316925 | 707.359 | 310151 | 303947.6875
7569 | 2009-11-12 08:00 | 285 | 386 | 142 | 14.57 | 10 | 0 | 21.8195 | 132.583 | 52.9621 | 0 | 285 | 231.743 | 173.281 | 2.6702 | 216.281 | 162.163 | 0.013938 | 209.142 | 156.161 | 0.010502 | 354.354 | 354.369 | 795839 | 20.3935 | 754253 | 769148 | 724801 | 0 | 0 | 720852 | 726.86 | 0 | 0 | 0 | 0 | 720852 | 726.86 | 709058 | 694876.5625
7570 | 2009-11-12 09:00 | 431 | 519 | 173 | 16.26 | 7.85 | 0 | 29.9108 | 145.674 | 41.022 | 0 | 431 | 390.354 | 211.531 | 4.0381 | 390.354 | 197.959 | 0.021078 | 384.002 | 190.633 | 0.015883 | 557.411 | 557.403 | 1251780 | 26.7303 | 1219650 | 1210420 | 1178010 | 0 | 0 | 1167630 | 722.582 | 0 | 0 | 0 | 0 | 1167630 | 722.582 | 1148240 | 1125275
7571 | 2009-11-12 10:00 | 435 | 283 | 271 | 17.95 | 7.85 | 0 | 35.4345 | 161.334 | 31.6051 | 0 | 435 | 240.915 | 312.303 | 4.0756 | 240.915 | 292.265 | 0.021273 | 238.817 | 281.449 | 0.01603 | 504.673 | 504.648 | 1133310 | 27.4294 | 1097520 | 1085810 | 1055780 | 0 | 0 | 1047330 | 717.795 | 0 | 0 | 0 | 0 | 1047330 | 717.795 | 1030540 | 1009927.875
7572 | 2009-11-12 11:00 | 293 | 40 | 269 | 18.2 | 7.85 | 0 | 37.5546 | 178.916 | 27.4528 | 0 | 293 | 34.9414 | 287.035 | 2.7452 | 34.9414 | 268.619 | 0.014329 | 34.7197 | 258.677 | 0.010797 | 284.605 | 284.601 | 639142 | 23.546 | 596426 | 600313 | 583511 | 0 | 0 | 580844 | 708.321 | 0 | 0 | 0 | 0 | 580844 | 708.321 | 571768 | 560332.6875
7573 | 2009-11-12 12:00 | 332 | 92 | 278 | 18.45 | 11.46 | 0 | 35.8639 | 196.617 | 30.7774 | 0 | 332 | 79.1906 | 300.3 | 3.1106 | 79.1906 | 281.032 | 0.016236 | 78.5415 | 270.631 | 0.012234 | 338.71 | 338.69 | 760611 | 23.544 | 718092 | 722715 | 702714 | 0 | 0 | 698924 | 715.862 | 0 | 0 | 0 | 0 | 698924 | 715.862 | 687886 | 674128.5625
7574 | 2009-11-12 13:00 | 416 | 405 | 210 | 18.7 | 11.46 | 0 | 30.6914 | 212.552 | 39.7428 | 0 | 416 | 310.332 | 241.484 | 3.8976 | 310.332 | 225.99 | 0.020344 | 305.669 | 217.627 | 0.01533 | 507.612 | 507.604 | 1139950 | 26.3345 | 1104340 | 1097860 | 1069900 | 0 | 0 | 1061300 | 720.95 | 0 | 0 | 0 | 0 | 1061300 | 720.95 | 1044070 | 1023190.5625
7575 | 2009-11-12 14:00 | 221 | 150 | 163 | 18.36 | 11.46 | 0 | 22.8498 | 225.927 | 51.4771 | 0 | 221 | 93.0272 | 178.687 | 2.0706 | 93.0272 | 167.222 | 0.010808 | 90.2104 | 161.033 | 0.0081439 | 243.714 | 243.704 | 547297 | 22.0254 | 505244 | 512150 | 498821 | 0 | 0 | 496862 | 707.535 | 0 | 0 | 0 | 0 | 496862 | 707.535 | 488661 | 478887.6562
7576 | 2009-11-12 15:00 | 209 | 409 | 116 | 18.01 | 9.65 | 0 | 13.1727 | 236.97 | 64.4793 | 0 | 209 | 175.824 | 140.526 | 1.9582 | 155.531 | 131.509 | 0.010221 | 145.258 | 126.642 | 0.0077017 | 263.751 | 263.729 | 592271 | 22.4382 | 550137 | 556327 | 529669 | 0 | 0 | 527461 | 709.443 | 0 | 0 | 0 | 0 | 527461 | 709.443 | 518872 | 508494.8438
7577 | 2009-11-12 16:00 | 24 | 152 | 13 | 17.67 | 9.65 | 0 | 2.2956 | 246.3 | 78.1098 | 0 | 24 | 26.0507 | 19.0665 | 0.22486 | 9.6618 | 17.8432 | 0.0011737 | 7.8003 | 17.1828 | 0.00088441 | 24.2344 | 24.2152 | 54383.8 | 18.0766 | 39626.7 | 41082 | 35998.2 | 0 | 0 | 35983.2 | 609.473 | 0 | 0 | 0 | 2689.26 | 33293.9 | 660 | 32095.5 | 31453.6094
7578 | 2009-11-12 17:00 | 0 | 0 | 0 | 16.67 | 9.65 | 0
7579 | 2009-11-12 18:00 | 0 | 0 | 0 | 15.68 | 9.9 | 0
7580 | 2009-11-12 19:00 | 0 | 0 | 0 | 14.68 | 9.9 | 0
7581 | 2009-11-12 20:00 | 0 | 0 | 0 | 14 | 9.9 | 0
7582 | 2009-11-12 21:00 | 0 | 0 | 0 | 13.32 | 9.46 | 0
7583 | 2009-11-12 22:00 | 0 | 0 | 0 | 12.64 | 9.46 | 0
7584 | 2009-11-12 23:00 | 0 | 0 | 0 | 11.68 | 9.46 | 0
7585 | 2009-11-13 | 0 | 0 | 0 | 10.72 | 8.45 | 0
7586 | 2009-11-13 01:00 | 0 | 0 | 0 | 9.76 | 8.45 | 0
7587 | 2009-11-13 02:00 | 0 | 0 | 0 | 9.07 | 8.45 | 0
7588 | 2009-11-13 03:00 | 0 | 0 | 0 | 8.39 | 7.19 | 0
7589 | 2009-11-13 04:00 | 0 | 0 | 0 | 7.71 | 7.19 | 0
7590 | 2009-11-13 05:00 | 0 | 0 | 0 | 7.31 | 7.19 | 0
7591 | 2009-11-13 06:00 | 11 | 309 | 0 | 6.92 | 8.61 | 0 | 0.80876 | 112.763 | 79.846 | 0 | 11 | 22.2901 | 0 | 0.10306 | 0.91569 | 0 | 0.00053795 | 0.70177 | 0 | 0.00040535 | 0.68111 | 0.68023 | 1527.33 | 6.9322 | 988.642 | 1077.95 | 929.728 | 0 | 0 | 929.507 | 618.684 | 0 | 0 | 0 | 50.5315 | 878.975 | 660.002 | 845.756 | 828.8411
7592 | 2009-11-13 07:00 | 177 | 686 | 37 | 6.53 | 8.61 | 0 | 11.7731 | 121.938 | 66.1851 | 0 | 177 | 277.057 | 53.8916 | 1.6583 | 149.649 | 50.4338 | 0.008656 | 138.601 | 48.5672 | 0.0065225 | 181.559 | 181.48 | 407530 | 9.7802 | 373588 | 397317 | 332171 | 0 | 0 | 331157 | 714.508 | 0 | 0 | 0 | 4.1758 | 331153 | 714.766 | 324391 | 317902.875
7593 | 2009-11-13 08:00 | 354 | 798 | 61 | 8.11 | 8.61 | 0 | 21.5937 | 132.738 | 53.1144 | 0 | 354 | 477.863 | 83.877 | 3.3167 | 444.571 | 78.4953 | 0.017312 | 429.766 | 75.5903 | 0.013045 | 490.208 | 490.241 | 1100990 | 16.89 | 1066820 | 1101640 | 1018720 | 0 | 0 | 1011250 | 749.402 | 0 | 0 | 0 | 0 | 1011250 | 749.402 | 993458 | 973588.5625
7594 | 2009-11-13 09:00 | 491 | 858 | 67 | 9.69 | 4.14 | 0 | 29.663 | 145.789 | 41.2167 | 0 | 491 | 644.461 | 86.5527 | 4.6003 | 644.461 | 80.9993 | 0.024012 | 633.847 | 78.0016 | 0.018093 | 690.51 | 690.504 | 1550700 | 26.1571 | 1530160 | 1522420 | 1481650 | 0 | 0 | 1465660 | 730.38 | 0 | 0 | 0 | 0 | 1465660 | 730.38 | 1439750 | 1410955.875
7595 | 2009-11-13 10:00 | 584 | 858 | 91 | 11.28 | 4.14 | 0 | 35.1707 | 161.385 | 31.8495 | 0 | 584 | 727.018 | 122.269 | 5.4716 | 727.018 | 114.424 | 0.02856 | 720.574 | 110.189 | 0.021521 | 805.862 | 805.864 | 1809760 | 30.4982 | 1801260 | 1759400 | 1710260 | 0 | 0 | 1688510 | 721.811 | 0 | 0 | 0 | 0 | 1688510 | 721.811 | 1656680 | 1623550
7596 | 2009-11-13 11:00 | 650 | 916 | 97 | 12.29 | 4.14 | 0 | 37.2895 | 178.879 | 27.7184 | 0 | 650 | 808.032 | 129.89 | 6.09 | 808.032 | 121.556 | 0.031788 | 802.794 | 117.058 | 0.023953 | 892.28 | 892.271 | 2003810 | 33.5688 | 2005130 | 1933090 | 1886860 | 0 | 0 | 1859670 | 710.707 | 0 | 0 | 0 | 0 | 1859670 | 710.707 | 1822560 | 1786113.25
7597 | 2009-11-13 12:00 | 623 | 963 | 64 | 13.31 | 2.97 | 0 | 35.616 | 196.496 | 30.9954 | 0 | 623 | 822.838 | 82.5269 | 5.837 | 822.838 | 77.2318 | 0.030467 | 815.985 | 74.3735 | 0.022958 | 863.67 | 863.664 | 1939580 | 35.558 | 1937590 | 1851500 | 1804630 | 0 | 0 | 1779360 | 705.278 | 0 | 0 | 0 | 0 | 1779360 | 705.278 | 1745030 | 1710126.625
7598 | 2009-11-13 13:00 | 544 | 948 | 64 | 14.33 | 2.97 | 0 | 30.4733 | 212.374 | 39.8926 | 0 | 544 | 726.192 | 82.8544 | 5.0969 | 726.192 | 77.5383 | 0.026604 | 715.178 | 74.6686 | 0.020047 | 766.17 | 766.166 | 1720610 | 34.0664 | 1707800 | 1642120 | 1598130 | 0 | 0 | 1578400 | 707.914 | 0 | 0 | 0 | 0 | 1578400 | 707.914 | 1550320 | 1519309.5
7599 | 2009-11-13 14:00 | 398 | 887 | 57 | 14.29 | 2.97 | 0 | 22.6641 | 225.72 | 51.5745 | 0 | 398 | 550 | 74.8614 | 3.729 | 550 | 70.0582 | 0.019464 | 533.252 | 67.4653 | 0.014666 | 582.71 | 582.706 | 1308610 | 29.3005 | 1278440 | 1254630 | 1221720 | 0 | 0 | 1210290 | 713.611 | 0 | 0 | 0 | 0 | 1210290 | 713.611 | 1190460 | 1166654.5
7600 | 2009-11-13 15:00 | 190 | 631 | 48 | 14.24 | 3.85 | 0 | 13.016 | 236.749 | 64.5392 | 0 | 190 | 271.042 | 66.7797 | 1.7801 | 229.333 | 62.495 | 0.0092918 | 214.126 | 60.1821 | 0.0070016 | 266.086 | 266.029 | 597439 | 20.7062 | 556253 | 565930 | 523541 | 0 | 0 | 521352 | 712.562 | 0 | 0 | 0 | 0 | 521352 | 712.562 | 512731 | 502476.7188
7601 | 2009-11-13 16:00 | 21 | 231 | 5 | 14.2 | 3.85 | 0 | 2.1622 | 246.07 | 78.1415 | 0 | 21 | 37.7922 | 7.6345 | 0.19675 | 14.0093 | 7.1447 | 0.001027 | 11.3011 | 6.8803 | 0.00077386 | 17.6367 | 17.6295 | 39595.4 | 14.6285 | 27882.3 | 29336.8 | 21787.6 | 0 | 0 | 21779.7 | 573.888 | 0 | 0 | 0 | 2512.27 | 19267.5 | 660 | 18558.1 | 18186.9062
7602 | 2009-11-13 17:00 | 0 | 0 | 0 | 13.44 | 3.85 | 0
7603 | 2009-11-13 18:00 | 0 | 0 | 0 | 12.67 | 7.11 | 0
7604 | 2009-11-13 19:00 | 0 | 0 | 0 | 11.91 | 7.11 | 0
7605 | 2009-11-13 20:00 | 0 | 0 | 0 | 11.06 | 7.11 | 0
7606 | 2009-11-13 21:00 | 0 | 0 | 0 | 10.21 | 6.92 | 0
7607 | 2009-11-13 22:00 | 0 | 0 | 0 | 9.36 | 6.92 | 0
7608 | 2009-11-13 23:00 | 0 | 0 | 0 | 8.6 | 6.92 | 0
7609 | 2009-11-14 | 0 | 0 | 0 | 7.84 | 7.43 | 0
7610 | 2009-11-14 01:00 | 0 | 0 | 0 | 7.07 | 7.43 | 0
7611 | 2009-11-14 02:00 | 0 | 0 | 0 | 6.46 | 7.43 | 0
7612 | 2009-11-14 03:00 | 0 | 0 | 0 | 5.85 | 5.96 | 0
7613 | 2009-11-14 04:00 | 0 | 0 | 0 | 5.24 | 5.96 | 0
7614 | 2009-11-14 05:00 | 0 | 0 | 0 | 4.89 | 5.96 | 0
7615 | 2009-11-14 06:00 | 9 | 272 | 0 | 4.54 | 3.29 | 0 | 0.62313 | 112.949 | 79.9428 | 0 | 9 | 18.0652 | 0 | 0.084323 | 0.75174 | 0 | 0.00044014 | 0.57409 | 0 | 0.00033165 | 0.55719 | 0.5561 | 1248.77 | 4.554 | 764.888 | 839.797 | 718.352 | 0 | 0 | 718.217 | 614.44 | 0 | 0 | 0 | 46.7909 | 671.426 | 660.002 | 646.018 | 633.0981
7616 | 2009-11-14 07:00 | 182 | 695 | 42 | 4.19 | 3.29 | 0 | 11.5699 | 122.108 | 66.3069 | 0 | 182 | 280.497 | 59.7438 | 1.7052 | 148.999 | 55.9105 | 0.0089006 | 137.909 | 53.8413 | 0.0067068 | 186.005 | 185.94 | 417535 | 8.8795 | 383267 | 408169 | 339102 | 0 | 0 | 338036 | 707.294 | 0 | 0 | 0 | 49.934 | 337986 | 708.055 | 331324 | 324698
7617 | 2009-11-14 08:00 | 339 | 765 | 61 | 6.2 | 3.29 | 0 | 21.3698 | 132.885 | 53.2677 | 0 | 339 | 456.289 | 84.0056 | 3.1762 | 423.309 | 78.6157 | 0.016578 | 409.086 | 75.7062 | 0.012492 | 470.26 | 470.213 | 1056000 | 18.0589 | 1020630 | 1048120 | 970351 | 0 | 0 | 963387 | 738.965 | 0 | 0 | 0 | 0 | 963387 | 738.965 | 946998 | 928057.5625
7618 | 2009-11-14 09:00 | 487 | 858 | 67 | 8.2 | 2.36 | 0 | 29.4182 | 145.897 | 41.4112 | 0 | 487 | 641.296 | 86.6849 | 4.5628 | 641.296 | 81.123 | 0.023816 | 630.606 | 78.1207 | 0.017946 | 687.483 | 687.482 | 1543910 | 26.642 | 1523080 | 1512210 | 1470900 | 0 | 0 | 1455160 | 730.544 | 0 | 0 | 0 | 0 | 1455160 | 730.544 | 1429470 | 1400882
7619 | 2009-11-14 10:00 | 590 | 878 | 89 | 10.21 | 2.36 | 0 | 34.911 | 161.429 | 32.0913 | 0 | 590 | 741.648 | 120.011 | 5.5278 | 741.648 | 112.311 | 0.028854 | 734.96 | 108.154 | 0.021742 | 817.842 | 817.837 | 1836650 | 32.1489 | 1829470 | 1774260 | 1728000 | 0 | 0 | 1705380 | 715.163 | 0 | 0 | 0 | 0 | 1705380 | 715.163 | 1673210 | 1639744.125
7620 | 2009-11-14 11:00 | 656 | 928 | 99 | 11.41 | 2.36 | 0 | 37.0296 | 178.838 | 27.9789 | 0 | 656 | 816.798 | 132.409 | 6.1462 | 816.798 | 123.913 | 0.032081 | 811.393 | 119.327 | 0.024174 | 902.822 | 902.816 | 2027500 | 35.6285 | 2030060 | 1939510 | 1889360 | 0 | 0 | 1861790 | 706.17 | 0 | 0 | 0 | 0 | 1861790 | 706.17 | 1824670 | 1788176
7621 | 2009-11-14 12:00 | 598 | 886 | 87 | 12.6 | 3.17 | 0 | 35.3739 | 196.374 | 31.2078 | 0 | 598 | 754.962 | 110.487 | 5.6028 | 754.962 | 103.398 | 0.029245 | 748.575 | 99.571 | 0.022037 | 822.723 | 822.717 | 1847620 | 33.5144 | 1840990 | 1774840 | 1727590 | 0 | 0 | 1704720 | 710.368 | 0 | 0 | 0 | 0 | 1704720 | 710.368 | 1672690 | 1639234.125
7622 | 2009-11-14 13:00 | 540 | 947 | 64 | 13.8 | 3.17 | 0 | 30.2612 | 212.197 | 40.0374 | 0 | 540 | 723.172 | 82.9785 | 5.0594 | 723.172 | 77.6544 | 0.026408 | 712.103 | 74.7805 | 0.019899 | 763.297 | 763.292 | 1714160 | 33.2038 | 1701050 | 1641870 | 1599340 | 0 | 0 | 1579640 | 709.785 | 0 | 0 | 0 | 0 | 1579640 | 709.785 | 1551460 | 1520428.25
7623 | 2009-11-14 14:00 | 390 | 883 | 53 | 14.07 | 3.17 | 0 | 22.4844 | 225.515 | 51.6672 | 0 | 390 | 546.547 | 70.0465 | 3.654 | 546.547 | 65.5522 | 0.019073 | 529.814 | 63.1262 | 0.014372 | 575.166 | 575.164 | 1291680 | 28.6913 | 1260910 | 1240720 | 1206860 | 0 | 0 | 1195840 | 717.752 | 0 | 0 | 0 | 0 | 1195840 | 717.752 | 1176110 | 1152588.125
7624 | 2009-11-14 15:00 | 197 | 684 | 44 | 14.35 | 2.93 | 0 | 12.8651 | 236.53 | 64.5948 | 0 | 197 | 294.802 | 62.434 | 1.8457 | 249.437 | 58.4281 | 0.0096341 | 232.838 | 56.2657 | 0.0072595 | 280.438 | 280.405 | 629724 | 21.5924 | 588524 | 596131 | 549396 | 0 | 0 | 546996 | 714.134 | 0 | 0 | 0 | 0 | 546996 | 714.134 | 538065 | 527303.6875
7625 | 2009-11-14 16:00 | 22 | 247 | 5 | 14.62 | 2.93 | 0 | 2.0345 | 245.842 | 78.169 | 0 | 22 | 40.0624 | 7.6123 | 0.20612 | 13.2186 | 7.1238 | 0.0010759 | 10.6559 | 6.8602 | 0.00081071 | 16.9913 | 16.9709 | 38117.6 | 15.0583 | 26888.9 | 28196.9 | 20386.2 | 0 | 0 | 20378.5 | 574.325 | 0 | 0 | 0 | 3511.6 | 16866.9 | 660 | 16243.7 | 15918.7793
7626 | 2009-11-14 17:00 | 0 | 0 | 0 | 13.79 | 2.93 | 0
7627 | 2009-11-14 18:00 | 0 | 0 | 0 | 12.96 | 4.7 | 0
7628 | 2009-11-14 19:00 | 0 | 0 | 0 | 12.13 | 4.7 | 0
7629 | 2009-11-14 20:00 | 0 | 0 | 0 | 11.38 | 4.7 | 0
7630 | 2009-11-14 21:00 | 0 | 0 | 0 | 10.63 | 4.59 | 0
7631 | 2009-11-14 22:00 | 0 | 0 | 0 | 9.88 | 4.59 | 0
7632 | 2009-11-14 23:00 | 0 | 0 | 0 | 9.22 | 4.59 | 0
7633 | 2009-11-15 | 0 | 0 | 0 | 8.55 | 10.22 | 0
7634 | 2009-11-15 01:00 | 0 | 0 | 0 | 7.89 | 10.22 | 0
7635 | 2009-11-15 02:00 | 0 | 0 | 0 | 6.91 | 10.22 | 0
7636 | 2009-11-15 03:00 | 0 | 0 | 0 | 5.94 | 6.8 | 0
7637 | 2009-11-15 04:00 | 0 | 0 | 0 | 4.97 | 6.8 | 0
7638 | 2009-11-15 05:00 | 0 | 0 | 0 | 4.33 | 6.8 | 0
7639 | 2009-11-15 06:00 | 6 | 230 | 0 | 3.7 | 9.36 | 0 | 0.43813 | 113.129 | 80.0417 | 0 | 6 | 11.9263 | 0 | 0.056215 | 0.46515 | 0 | 0.00029342 | 0.35392 | 0 | 0.0002211 | 0.34352 | 0.34367 | 771.681 | 3.7059 | 417.422 | 457.02 | 404.721 | 0 | 0 | 404.672 | 591.132 | 0 | 0 | 0 | 48.0512 | 356.62 | 660.006 | 343.099 | 336.2374
7640 | 2009-11-15 07:00 | 185 | 717 | 43 | 3.07 | 9.36 | 0 | 11.3678 | 122.272 | 66.4303 | 0 | 185 | 288.071 | 60.9183 | 1.7333 | 150.106 | 57.0096 | 0.0090473 | 138.841 | 54.8998 | 0.0068173 | 187.935 | 187.871 | 421879 | 6.2815 | 387707 | 418310 | 344188 | 0 | 0 | 343108 | 719.685 | 0 | 0 | 0 | 411.078 | 342697 | 723.328 | 335666 | 328952.9688
7641 | 2009-11-15 08:00 | 370 | 873 | 55 | 4.45 | 9.36 | 0 | 21.1479 | 133.026 | 53.4219 | 0 | 370 | 520.305 | 72.7478 | 3.4666 | 481.165 | 68.0802 | 0.018094 | 464.851 | 65.5606 | 0.013635 | 514.513 | 514.511 | 1155470 | 13.2451 | 1123380 | 1176850 | 1085690 | 0 | 0 | 1077390 | 757.835 | 0 | 0 | 0 | 0 | 1077390 | 757.835 | 1057900 | 1036739.625
7642 | 2009-11-15 09:00 | 521 | 941 | 63 | 5.84 | 6.85 | 0 | 29.1765 | 145.999 | 41.6054 | 0 | 521 | 702.487 | 81.9164 | 4.8814 | 702.487 | 76.6605 | 0.025479 | 690.637 | 73.8233 | 0.019199 | 741.545 | 741.543 | 1665320 | 20.6808 | 1649930 | 1679410 | 1629470 | 0 | 0 | 1611250 | 752.158 | 0 | 0 | 0 | 0 | 1611250 | 752.158 | 1580240 | 1548634.875
7643 | 2009-11-15 10:00 | 608 | 959 | 64 | 7.22 | 6.85 | 0 | 34.6557 | 161.467 | 32.3305 | 0 | 608 | 808.359 | 82.7812 | 5.6965 | 808.359 | 77.4698 | 0.029734 | 800.944 | 74.6027 | 0.022405 | 849.302 | 849.301 | 1907320 | 24.2175 | 1903680 | 1909520 | 1859210 | 0 | 0 | 1834920 | 741.948 | 0 | 0 | 0 | 0 | 1834920 | 741.948 | 1797980 | 1762024.25
7644 | 2009-11-15 11:00 | 629 | 943 | 66 | 8.33 | 6.85 | 0 | 36.7749 | 178.793 | 28.2342 | 0 | 629 | 828.524 | 85.1178 | 5.8932 | 828.524 | 79.6565 | 0.030761 | 822.93 | 76.7084 | 0.023179 | 872.671 | 872.668 | 1959790 | 25.7951 | 1958840 | 1952020 | 1897680 | 0 | 0 | 1872280 | 739.898 | 0 | 0 | 0 | 0 | 1872280 | 739.898 | 1834330 | 1797638.625
7645 | 2009-11-15 12:00 | 623 | 970 | 66 | 9.43 | 5.03 | 0 | 35.1377 | 196.25 | 31.4147 | 0 | 623 | 825.92 | 85.2215 | 5.837 | 825.92 | 79.7536 | 0.030467 | 818.827 | 76.8019 | 0.022958 | 868.783 | 868.779 | 1951060 | 28.9791 | 1949650 | 1916990 | 1866400 | 0 | 0 | 1840910 | 726.576 | 0 | 0 | 0 | 0 | 1840910 | 726.576 | 1804200 | 1768118.875
7646 | 2009-11-15 13:00 | 537 | 946 | 64 | 10.54 | 5.03 | 0 | 30.0551 | 212.02 | 40.1772 | 0 | 537 | 721.593 | 83.1006 | 5.0313 | 721.593 | 77.7687 | 0.026262 | 710.451 | 74.8905 | 0.019789 | 761.8 | 761.799 | 1710810 | 27.6818 | 1697540 | 1678140 | 1632120 | 0 | 0 | 1612630 | 728.605 | 0 | 0 | 0 | 0 | 1612630 | 728.605 | 1582870 | 1551209.5
7647 | 2009-11-15 14:00 | 384 | 881 | 50 | 11.07 | 5.03 | 0 | 22.3106 | 225.311 | 51.7553 | 0 | 384 | 544.62 | 66.4248 | 3.5978 | 544.62 | 62.1628 | 0.018779 | 527.861 | 59.8622 | 0.01415 | 570.105 | 570.102 | 1280300 | 23.8983 | 1249130 | 1254850 | 1219470 | 0 | 0 | 1208700 | 734.183 | 0 | 0 | 0 | 0 | 1208700 | 734.183 | 1187920 | 1164163.375
7648 | 2009-11-15 15:00 | 193 | 666 | 46 | 11.6 | 4.83 | 0 | 12.7201 | 236.313 | 64.6459 | 0 | 193 | 285.877 | 64.7896 | 1.8083 | 241.886 | 60.6326 | 0.0094385 | 225.736 | 58.3887 | 0.0071121 | 275.608 | 275.557 | 618835 | 17.8817 | 577618 | 594971 | 549082 | 0 | 0 | 546746 | 723.683 | 0 | 0 | 0 | 0 | 546746 | 723.683 | 537521 | 526770.9375
7649 | 2009-11-15 16:00 | 21 | 237 | 5 | 12.13 | 4.83 | 0 | 1.9127 | 245.617 | 78.1924 | 0 | 21 | 37.6325 | 7.5911 | 0.19675 | 12.4041 | 7.1041 | 0.001027 | 9.9934 | 6.8412 | 0.00077386 | 16.3303 | 16.3201 | 36655.5 | 12.502 | 25616.7 | 27197.1 | 19902.7 | 0 | 0 | 19895.7 | 584.922 | 0 | 0 | 0 | 2706.64 | 17189.1 | 660 | 16554.2 | 16223.1553
7650 | 2009-11-15 17:00 | 0 | 0 | 0 | 11.37 | 4.83 | 0
7651 | 2009-11-15 18:00 | 0 | 0 | 0 | 10.61 | 6.91 | 0
7652 | 2009-11-15 19:00 | 0 | 0 | 0 | 9.85 | 6.91 | 0
7653 | 2009-11-15 20:00 | 0 | 0 | 0 | 9.29 | 6.91 | 0
7654 | 2009-11-15 21:00 | 0 | 0 | 0 | 8.72 | 7.47 | 0
7655 | 2009-11-15 22:00 | 0 | 0 | 0 | 8.16 | 7.47 | 0
7656 | 2009-11-15 23:00 | 0 | 0 | 0 | 7.6 | 7.47 | 0
7657 | 2009-11-16 | 0 | 0 | 0 | 7.03 | 9.64 | 0
7658 | 2009-11-16 01:00 | 0 | 0 | 0 | 6.46 | 9.64 | 0
7659 | 2009-11-16 02:00 | 0 | 0 | 0 | 6.25 | 9.64 | 0
7660 | 2009-11-16 03:00 | 0 | 0 | 0 | 6.04 | 6.17 | 0
7661 | 2009-11-16 04:00 | 0 | 0 | 0 | 5.83 | 6.17 | 0
7662 | 2009-11-16 05:00 | 0 | 0 | 0 | 5.48 | 6.17 | 0
7663 | 2009-11-16 06:00 | 6 | 280 | 0 | 5.13 | 5.79 | 0 | 0.25386 | 113.303 | 80.1425 | 0 | 6 | 11.8067 | 0 | 0.056215 | 0.43481 | 0 | 0.00029342 | 0.32956 | 0 | 0.0002211 | 0.31989 | 0.31725 | 712.253 | 5.1368 | 402.529 | 438.752 | 386.625 | 0 | 0 | 386.578 | 588.374 | 0 | 0 | 0 | 57.3983 | 329.18 | 660.006 | 316.697 | 310.3631
7664 | 2009-11-16 07:00 | 181 | 712 | 43 | 4.77 | 5.79 | 0 | 11.1671 | 122.429 | 66.5553 | 0 | 181 | 283.498 | 60.9833 | 1.6958 | 138.529 | 57.0705 | 0.0088517 | 128.047 | 54.9584 | 0.0066699 | 177.521 | 177.394 | 398358 | 8.57 | 365103 | 389465 | 316450 | 0 | 0 | 315523 | 721.98 | 0 | 0 | 0 | 8.2453 | 315515 | 722.365 | 308690 | 302516.1562
7665 | 2009-11-16 08:00 | 366 | 871 | 55 | 6.12 | 5.79 | 0 | 20.9281 | 133.16 | 53.577 | 0 | 366 | 516.955 | 72.884 | 3.4291 | 476.342 | 68.2076 | 0.017899 | 460.046 | 65.6833 | 0.013487 | 509.97 | 509.964 | 1145260 | 17.0441 | 1112980 | 1147340 | 1059710 | 0 | 0 | 1051530 | 745.941 | 0 | 0 | 0 | 0 | 1051530 | 745.941 | 1033120 | 1012454.75
7666 | 2009-11-16 09:00 | 517 | 940 | 63 | 7.47 | 4.28 | 0 | 28.9379 | 146.094 | 41.799 | 0 | 517 | 699.481 | 82.0401 | 4.8439 | 699.481 | 76.7762 | 0.025283 | 687.541 | 73.9348 | 0.019052 | 738.65 | 738.645 | 1658810 | 24.9243 | 1643110 | 1643330 | 1598530 | 0 | 0 | 1580300 | 736.903 | 0 | 0 | 0 | 0 | 1580300 | 736.903 | 1551200 | 1520174.75
7667 | 2009-11-16 10:00 | 616 | 972 | 68 | 8.82 | 4.28 | 0 | 34.4047 | 161.5 | 32.5668 | 0 | 616 | 817.358 | 87.8175 | 5.7714 | 817.358 | 82.1829 | 0.030125 | 809.733 | 79.1414 | 0.0227 | 862.23 | 862.227 | 1936340 | 29.1946 | 1934190 | 1900010 | 1848710 | 0 | 0 | 1823690 | 726.404 | 0 | 0 | 0 | 0 | 1823690 | 726.404 | 1787540 | 1751789
7668 | 2009-11-16 11:00 | 633 | 958 | 65 | 10.55 | 4.28 | 0 | 36.5257 | 178.745 | 28.4841 | 0 | 633 | 838.806 | 83.9993 | 5.9307 | 838.806 | 78.6098 | 0.030956 | 833.03 | 75.7005 | 0.023326 | 881.491 | 881.488 | 1979590 | 31.3797 | 1979660 | 1926640 | 1875430 | 0 | 0 | 1849220 | 720.151 | 0 | 0 | 0 | 0 | 1849220 | 720.151 | 1812340 | 1776092.75
7669 | 2009-11-16 12:00 | 624 | 974 | 68 | 12.28 | 3.14 | 0 | 34.9075 | 196.125 | 31.6158 | 0 | 624 | 827.395 | 87.7949 | 5.8464 | 827.395 | 82.1618 | 0.030516 | 820.185 | 79.121 | 0.022995 | 872.349 | 872.345 | 1959070 | 34.5001 | 1958080 | 1879890 | 1831010 | 0 | 0 | 1805300 | 709.174 | 0 | 0 | 0 | 0 | 1805300 | 709.174 | 1770040 | 1734634.25
7670 | 2009-11-16 13:00 | 533 | 945 | 64 | 14 | 3.14 | 0 | 29.8551 | 211.843 | 40.3119 | 0 | 533 | 718.406 | 83.2205 | 4.9938 | 718.406 | 77.881 | 0.026066 | 707.22 | 74.9986 | 0.019641 | 758.771 | 758.766 | 1704000 | 33.327 | 1690410 | 1630680 | 1587380 | 0 | 0 | 1567950 | 708.817 | 0 | 0 | 0 | 0 | 1567950 | 708.817 | 1540140 | 1509338.25
7671 | 2009-11-16 14:00 | 387 | 883 | 55 | 14.63 | 3.14 | 0 | 22.1429 | 225.108 | 51.8387 | 0 | 387 | 544.243 | 72.7797 | 3.6259 | 544.243 | 68.11 | 0.018926 | 527.414 | 65.5893 | 0.014261 | 575.227 | 575.223 | 1291810 | 29.2819 | 1261040 | 1237640 | 1205280 | 0 | 0 | 1194170 | 714.441 | 0 | 0 | 0 | 0 | 1194170 | 714.441 | 1174630 | 1151139.125
7672 | 2009-11-16 15:00 | 197 | 708 | 42 | 15.26 | 3.44 | 0 | 12.5811 | 236.099 | 64.6926 | 0 | 197 | 304.188 | 60.3791 | 1.8457 | 257.378 | 56.505 | 0.0096341 | 240.143 | 54.4138 | 0.0072595 | 285.727 | 285.686 | 641585 | 22.3941 | 600408 | 605981 | 558071 | 0 | 0 | 555578 | 712.278 | 0 | 0 | 0 | 0 | 555578 | 712.278 | 546620 | 535687.5
7673 | 2009-11-16 16:00 | 20 | 248 | 4 | 15.88 | 3.44 | 0 | 1.7968 | 245.394 | 78.2114 | 0 | 20 | 37.5726 | 6.1187 | 0.18738 | 12.289 | 5.7261 | 0.00097808 | 9.8959 | 5.5142 | 0.00073701 | 14.9485 | 14.9393 | 33555.3 | 16.2531 | 23217.5 | 24200.9 | 17062.7 | 0 | 0 | 17056.9 | 572.239 | 0 | 0 | 0 | 3416.03 | 13640.9 | 660 | 13134.3 | 12871.5723
7674 | 2009-11-16 17:00 | 0 | 0 | 0 | 15.04 | 3.44 | 0
7675 | 2009-11-16 18:00 | 0 | 0 | 0 | 14.2 | 5.93 | 0
7676 | 2009-11-16 19:00 | 0 | 0 | 0 | 13.36 | 5.93 | 0
7677 | 2009-11-16 20:00 | 0 | 0 | 0 | 12.52 | 5.93 | 0
7678 | 2009-11-16 21:00 | 0 | 0 | 0 | 11.68 | 4.95 | 0
7679 | 2009-11-16 22:00 | 0 | 0 | 0 | 10.84 | 4.95 | 0
7680 | 2009-11-16 23:00 | 0 | 0 | 0 | 10.24 | 4.95 | 0
7681 | 2009-11-17 | 0 | 0 | 0 | 9.64 | 4.22 | 0
7682 | 2009-11-17 01:00 | 0 | 0 | 0 | 9.05 | 4.22 | 0
7683 | 2009-11-17 02:00 | 0 | 0 | 0 | 8.6 | 4.22 | 0
7684 | 2009-11-17 03:00 | 0 | 0 | 0 | 8.16 | 4.06 | 0
7685 | 2009-11-17 04:00 | 0 | 0 | 0 | 7.72 | 4.06 | 0
7686 | 2009-11-17 05:00 | 0 | 0 | 0 | 7.46 | 4.06 | 0
7687 | 2009-11-17 06:00 | 4 | 277 | 0 | 7.2 | 4 | 0 | 0.070399 | 113.47 | 80.2453 | 0 | 4 | 7.7899 | 0 | 0.037477 | 0.28688 | 0 | 0.00019562 | 0.21657 | 0 | 0.0001474 | 0.21021 | 0.21038 | 472.313 | 7.2051 | 225.868 | 239.841 | 212.062 | 0 | 0 | 212.045 | 542.055 | 0 | 0 | 0 | 106.229 | 105.816 | 660.019 | 101.797 | 99.7614
7688 | 2009-11-17 07:00 | 176 | 707 | 41 | 6.94 | 4 | 0 | 10.9677 | 122.579 | 66.6817 | 0 | 176 | 280.877 | 58.8824 | 1.649 | 134.289 | 55.1044 | 0.0086071 | 124.041 | 53.0651 | 0.0064856 | 171.799 | 171.805 | 385817 | 11.075 | 352999 | 372177 | 300179 | 0 | 0 | 299290 | 704.272 | 0 | 0 | 0 | 0 | 299290 | 704.272 | 293010 | 287149.3125
7689 | 2009-11-17 08:00 | 353 | 859 | 50 | 8.23 | 4 | 0 | 20.7104 | 133.287 | 53.7327 | 0 | 353 | 506.838 | 66.7902 | 3.3073 | 465.538 | 62.5048 | 0.017263 | 449.467 | 60.1916 | 0.013008 | 494.381 | 494.358 | 1110210 | 20.1282 | 1077100 | 1095710 | 1012180 | 0 | 0 | 1004410 | 731.257 | 0 | 0 | 0 | 0 | 1004410 | 731.257 | 987599 | 967847.125
7690 | 2009-11-17 09:00 | 513 | 939 | 63 | 9.53 | 2.73 | 0 | 28.7026 | 146.183 | 41.9919 | 0 | 513 | 696.406 | 82.162 | 4.8064 | 696.406 | 76.8904 | 0.025088 | 684.377 | 74.0447 | 0.018904 | 735.687 | 735.683 | 1652160 | 28.7853 | 1636150 | 1609740 | 1567430 | 0 | 0 | 1549220 | 723.445 | 0 | 0 | 0 | 0 | 1549220 | 723.445 | 1521460 | 1491030.125
7691 | 2009-11-17 10:00 | 611 | 971 | 67 | 10.82 | 2.73 | 0 | 34.1582 | 161.527 | 32.8 | 0 | 611 | 814.399 | 86.7071 | 5.7246 | 814.399 | 81.1438 | 0.02988 | 806.675 | 78.1407 | 0.022516 | 858.293 | 858.292 | 1927510 | 33.2844 | 1924900 | 1857810 | 1808510 | 0 | 0 | 1783570 | 712.092 | 0 | 0 | 0 | 0 | 1783570 | 712.092 | 1748970 | 1713991.875
7692 | 2009-11-17 11:00 | 648 | 981 | 69 | 12.9 | 2.73 | 0 | 36.282 | 178.693 | 28.7286 | 0 | 648 | 857.998 | 89.0356 | 6.0713 | 857.998 | 83.3229 | 0.03169 | 851.976 | 80.2392 | 0.023879 | 904.272 | 904.267 | 2030750 | 36.5677 | 2033480 | 1934750 | 1883580 | 0 | 0 | 1855940 | 703.42 | 0 | 0 | 0 | 0 | 1855940 | 703.42 | 1819060 | 1782674.5
7693 | 2009-11-17 12:00 | 620 | 973 | 68 | 14.99 | 1.73 | 0 | 34.6834 | 195.998 | 31.8112 | 0 | 620 | 824.341 | 87.9107 | 5.8089 | 824.341 | 82.2702 | 0.030321 | 817.055 | 79.2254 | 0.022847 | 869.414 | 869.411 | 1952480 | 39.3146 | 1951150 | 1833390 | 1788480 | 0 | 0 | 1762850 | 693.734 | 0 | 0 | 0 | 0 | 1762850 | 693.734 | 1729300 | 1694715.375
7694 | 2009-11-17 13:00 | 529 | 944 | 63 | 17.07 | 1.73 | 0 | 29.6613 | 211.667 | 40.4414 | 0 | 529 | 716.668 | 82.1061 | 4.9563 | 716.668 | 76.8381 | 0.02587 | 705.418 | 73.9943 | 0.019494 | 756.049 | 756.046 | 1697890 | 38.2228 | 1684010 | 1589250 | 1549260 | 0 | 0 | 1529920 | 693.097 | 0 | 0 | 0 | 0 | 1529920 | 693.097 | 1503790 | 1473713.375
7695 | 2009-11-17 14:00 | 385 | 882 | 55 | 17.61 | 1.73 | 0 | 21.9813 | 224.907 | 51.9174 | 0 | 385 | 543.79 | 72.9032 | 3.6071 | 543.79 | 68.2256 | 0.018828 | 526.898 | 65.7006 | 0.014187 | 574.834 | 574.829 | 1290920 | 33.6927 | 1260120 | 1212640 | 1182100 | 0 | 0 | 1170970 | 699.313 | 0 | 0 | 0 | 0 | 1170970 | 699.313 | 1152640 | 1129587.125
7696 | 2009-11-17 15:00 | 191 | 667 | 47 | 18.16 | 0.16 | 0 | 12.448 | 235.886 | 64.7349 | 0 | 191 | 285.127 | 66.0826 | 1.7895 | 241.25 | 61.8426 | 0.0093407 | 225.051 | 59.5538 | 0.0070384 | 276.073 | 276.028 | 619892 | 26.7444 | 578660 | 572344 | 529436 | 0 | 0 | 527078 | 694.167 | 0 | 0 | 0 | 0 | 527078 | 694.167 | 518971 | 508591.875
7697 | 2009-11-17 16:00 | 20 | 231 | 5 | 18.71 | 0.16 | 0 | 1.6867 | 245.173 | 78.2263 | 0 | 20 | 35.1806 | 7.5526 | 0.18738 | 10.1566 | 7.068 | 0.00097808 | 8.1757 | 6.8065 | 0.00073701 | 14.5334 | 14.5256 | 32625.3 | 19.1617 | 22132.5 | 22754.8 | 16897.9 | 0 | 0 | 16892.6 | 551.053 | 0 | 0 | 0 | 5246.04 | 11646.5 | 660 | 11212.6 | 10988.3623
7698 | 2009-11-17 17:00 | 0 | 0 | 0 | 17.71 | 0.16 | 0
7699 | 2009-11-17 18:00 | 0 | 0 | 0 | 16.71 | 3.8 | 0
7700 | 2009-11-17 19:00 | 0 | 0 | 0 | 15.72 | 3.8 | 0
7701 | 2009-11-17 20:00 | 0 | 0 | 0 | 15.18 | 3.8 | 0
7702 | 2009-11-17 21:00 | 0 | 0 | 0 | 14.65 | 5.72 | 0
7703 | 2009-11-17 22:00 | 0 | 0 | 0 | 14.12 | 5.72 | 0
7704 | 2009-11-17 23:00 | 0 | 0 | 0 | 13.39 | 5.72 | 0
7705 | 2009-11-18 | 0 | 0 | 0 | 12.66 | 6.17 | 0
7706 | 2009-11-18 01:00 | 0 | 0 | 0 | 11.93 | 6.17 | 0
7707 | 2009-11-18 02:00 | 0 | 0 | 0 | 11.53 | 6.17 | 0
7708 | 2009-11-18 03:00 | 0 | 0 | 0 | 11.14 | 6.49 | 0
7709 | 2009-11-18 04:00 | 0 | 0 | 0 | 10.74 | 6.49 | 0
7710 | 2009-11-18 05:00 | 0 | 0 | 0 | 10.33 | 6.49 | 0
7711 | 2009-11-18 06:00 | 3 | 278 | 0 | 9.93 | 6.18 | 0 | -0.11216 | 113.631 | 80.3499 | 0 | 3 | 5.7804 | 0 | 0.028108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.93 | 0 | 0 | 0 | 0 | 0 | 0 | 660 | 0 | 0 | 0 | 0 | 0 | 660 | 0 | 0
7712 | 2009-11-18 07:00 | 173 | 703 | 41 | 9.53 | 6.18 | 0 | 10.7698 | 122.723 | 66.8094 | 0 | 173 | 278.174 | 58.9486 | 1.6209 | 124.359 | 55.1663 | 0.0084604 | 114.787 | 53.1246 | 0.0063751 | 162.88 | 162.907 | 365833 | 12.9332 | 334230 | 349684 | 278264 | 0 | 0 | 277415 | 677.875 | 0 | 0 | 0 | 312.199 | 277103 | 681.608 | 271326 | 265899.4375
7713 | 2009-11-18 08:00 | 358 | 866 | 55 | 11.21 | 6.18 | 0 | 20.4951 | 133.407 | 53.8889 | 0 | 358 | 510.025 | 73.1524 | 3.3542 | 467.012 | 68.4588 | 0.017508 | 450.742 | 65.9251 | 0.013192 | 501.18 | 501.125 | 1125410 | 21.6786 | 1092750 | 1104800 | 1022350 | 0 | 0 | 1014310 | 726.213 | 0 | 0 | 0 | 0 | 1014310 | 726.213 | 997545 | 977594.25
7714 | 2009-11-18 09:00 | 507 | 936 | 62 | 12.89 | 6.04 | 0 | 28.4707 | 146.264 | 42.1839 | 0 | 507 | 691.705 | 81.048 | 4.7502 | 691.705 | 75.8478 | 0.024794 | 679.617 | 73.0407 | 0.018683 | 730.096 | 730.089 | 1639590 | 28.2796 | 1623010 | 1600330 | 1556450 | 0 | 0 | 1538610 | 725.66 | 0 | 0 | 0 | 0 | 1538610 | 725.66 | 1511070 | 1480850
7715 | 2009-11-18 10:00 | 607 | 970 | 67 | 14.56 | 6.04 | 0 | 33.9163 | 161.548 | 33.0301 | 0 | 607 | 811.368 | 86.8221 | 5.6871 | 811.368 | 81.2514 | 0.029685 | 803.547 | 78.2443 | 0.022368 | 855.359 | 855.358 | 1920920 | 32.5902 | 1917980 | 1856790 | 1807880 | 0 | 0 | 1783160 | 714.178 | 0 | 0 | 0 | 0 | 1783160 | 714.178 | 1748530 | 1713557.25
7716 | 2009-11-18 11:00 | 644 | 980 | 69 | 15.64 | 6.04 | 0 | 36.0439 | 178.637 | 28.9675 | 0 | 644 | 854.962 | 89.1493 | 6.0338 | 854.962 | 83.4293 | 0.031494 | 848.85 | 80.3417 | 0.023732 | 901.339 | 901.333 | 2024160 | 34.6393 | 2026550 | 1944700 | 1894100 | 0 | 0 | 1866610 | 709.793 | 0 | 0 | 0 | 0 | 1866610 | 709.793 | 1829280 | 1792692.25
7717 | 2009-11-18 12:00 | 617 | 972 | 69 | 16.71 | 5.44 | 0 | 34.4654 | 195.87 | 32.0007 | 0 | 617 | 821.204 | 89.2527 | 5.7808 | 821.204 | 83.5261 | 0.030174 | 813.847 | 80.4349 | 0.022737 | 867.475 | 867.472 | 1948120 | 35.7174 | 1946570 | 1858880 | 1813530 | 0 | 0 | 1787880 | 703.498 | 0 | 0 | 0 | 0 | 1787880 | 703.498 | 1753300 | 1718231.125
7718 | 2009-11-18 13:00 | 526 | 944 | 63 | 17.79 | 5.44 | 0 | 29.4738 | 211.491 | 40.5656 | 0 | 526 | 714.848 | 82.2203 | 4.9282 | 714.848 | 76.9449 | 0.025724 | 703.54 | 74.0972 | 0.019383 | 754.327 | 754.322 | 1694020 | 34.3181 | 1679960 | 1613530 | 1573630 | 0 | 0 | 1554300 | 704.617 | 0 | 0 | 0 | 0 | 1554300 | 704.617 | 1527040 | 1496499.125
7719 | 2009-11-18 14:00 | 380 | 879 | 54 | 17.63 | 5.44 | 0 | 21.8259 | 224.707 | 51.9912 | 0 | 380 | 539.945 | 71.7802 | 3.5603 | 539.945 | 67.1747 | 0.018584 | 523.1 | 64.6886 | 0.014003 | 570.168 | 570.165 | 1280450 | 30.123 | 1249290 | 1221570 | 1189430 | 0 | 0 | 1178530 | 711.319 | 0 | 0 | 0 | 0 | 1178530 | 711.319 | 1159460 | 1136270
7720 | 2009-11-18 15:00 | 167 | 512 | 58 | 17.48 | 4.85 | 0 | 12.321 | 235.676 | 64.7727 | 0 | 167 | 217.71 | 80.8711 | 1.5647 | 184.208 | 75.6823 | 0.008167 | 171.809 | 72.8813 | 0.006154 | 237.355 | 237.3 | 532916 | 22.8826 | 492019 | 496060 | 460744 | 0 | 0 | 459011 | 702.795 | 0 | 0 | 0 | 0 | 459011 | 702.795 | 451392 | 442364.3125
7721 | 2009-11-18 16:00 | 17 | 175 | 6 | 17.33 | 4.85 | 0 | 1.5826 | 244.955 | 78.2368 | 0 | 17 | 25.7762 | 9.5848 | 0.15928 | 7.436 | 8.9698 | 0.00083137 | 5.9841 | 8.6378 | 0.00062646 | 14.1838 | 14.1815 | 31851.2 | 17.6529 | 21163.6 | 21954 | 17770.8 | 0 | 0 | 17766 | 566.83 | 0 | 0 | 0 | 5149.82 | 12616.2 | 660 | 12146.6 | 11903.6953
7722 | 2009-11-18 17:00 | 0 | 0 | 0 | 15.94 | 4.85 | 0
7723 | 2009-11-18 18:00 | 0 | 0 | 0 | 14.55 | 6.29 | 0
7724 | 2009-11-18 19:00 | 0 | 0 | 0 | 13.17 | 6.29 | 0
7725 | 2009-11-18 20:00 | 0 | 0 | 0 | 12.23 | 6.29 | 0
7726 | 2009-11-18 21:00 | 0 | 0 | 0 | 11.3 | 8.53 | 0
7727 | 2009-11-18 22:00 | 0 | 0 | 0 | 10.36 | 8.53 | 0
7728 | 2009-11-18 23:00 | 0 | 0 | 0 | 9.66 | 8.53 | 0
7729 | 2009-11-19 | 0 | 0 | 0 | 8.95 | 7.47 | 0
7730 | 2009-11-19 01:00 | 0 | 0 | 0 | 8.25 | 7.47 | 0
7731 | 2009-11-19 02:00 | 0 | 0 | 0 | 7.48 | 7.47 | 0
7732 | 2009-11-19 03:00 | 0 | 0 | 0 | 6.71 | 8.83 | 0
7733 | 2009-11-19 04:00 | 0 | 0 | 0 | 5.94 | 8.83 | 0
7734 | 2009-11-19 05:00 | 0 | 0 | 0 | 5.83 | 8.83 | 0
7735 | 2009-11-19 06:00 | 2 | 351 | 0 | 5.72 | 10.28 | 0 | -0.29373 | 113.786 | 80.4563 | 0 | 2 | 3.8115 | 0 | 0.018738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.72 | 0 | 0 | 0 | 0 | 0 | 0 | 660 | 0 | 0 | 0 | 0 | 0 | 660 | 0 | 0
7736 | 2009-11-19 07:00 | 166 | 694 | 38 | 5.61 | 10.28 | 0 | 10.5735 | 122.86 | 66.9384 | 0 | 166 | 273.25 | 55.7069 | 1.5553 | 119.338 | 52.1327 | 0.0081181 | 110.072 | 50.2033 | 0.0061172 | 155.473 | 155.488 | 349166 | 8.1218 | 318145 | 340516 | 270026 | 0 | 0 | 269281 | 705.653 | 0 | 0 | 0 | 0 | 269281 | 705.653 | 263015 | 257755.0156
7737 | 2009-11-19 08:00 | 354 | 865 | 55 | 7.29 | 10.28 | 0 | 20.2822 | 133.52 | 54.0455 | 0 | 354 | 506.442 | 73.2843 | 3.3167 | 461.993 | 68.5822 | 0.017312 | 445.75 | 66.044 | 0.013045 | 496.453 | 496.391 | 1114780 | 15.3089 | 1081880 | 1123920 | 1036640 | 0 | 0 | 1028840 | 747.644 | 0 | 0 | 0 | 0 | 1028840 | 747.644 | 1010790 | 990575.625
7738 | 2009-11-19 09:00 | 505 | 936 | 63 | 8.97 | 6.06 | 0 | 28.2423 | 146.339 | 42.3749 | 0 | 505 | 690.04 | 82.4002 | 4.7315 | 690.04 | 77.1132 | 0.024697 | 677.839 | 74.2593 | 0.018609 | 729.553 | 729.548 | 1638390 | 24.3284 | 1621750 | 1626060 | 1581970 | 0 | 0 | 1564170 | 738.797 | 0 | 0 | 0 | 0 | 1564170 | 738.797 | 1535450 | 1504738.75
7739 | 2009-11-19 10:00 | 603 | 968 | 68 | 10.65 | 6.06 | 0 | 33.6791 | 161.564 | 33.2569 | 0 | 603 | 806.754 | 88.1658 | 5.6496 | 806.754 | 82.5089 | 0.029489 | 798.853 | 79.4553 | 0.022221 | 851.981 | 851.977 | 1913320 | 28.5858 | 1909990 | 1881120 | 1830650 | 0 | 0 | 1806230 | 728.435 | 0 | 0 | 0 | 0 | 1806230 | 728.435 | 1770610 | 1735193.875
7740 | 2009-11-19 11:00 | 641 | 979 | 70 | 12.29 | 6.06 | 0 | 35.8115 | 178.577 | 29.2009 | 0 | 641 | 851.848 | 90.4898 | 6.0057 | 851.848 | 84.6838 | 0.031348 | 845.647 | 81.5497 | 0.023621 | 899.404 | 899.401 | 2019820 | 31.2242 | 2021980 | 1969270 | 1917250 | 0 | 0 | 1889950 | 721.054 | 0 | 0 | 0 | 0 | 1889950 | 721.054 | 1851710 | 1814673.25
7741 | 2009-11-19 12:00 | 612 | 971 | 67 | 13.93 | 4.29 | 0 | 34.2537 | 195.741 | 32.1843 | 0 | 612 | 819.487 | 86.9039 | 5.734 | 819.487 | 81.328 | 0.029929 | 812.048 | 78.3181 | 0.022552 | 863.677 | 863.671 | 1939580 | 34.3254 | 1937590 | 1861620 | 1811590 | 0 | 0 | 1786400 | 708.796 | 0 | 0 | 0 | 0 | 1786400 | 708.796 | 1751770 | 1716735.75
7742 | 2009-11-19 13:00 | 515 | 937 | 58 | 15.57 | 4.29 | 0 | 29.2926 | 211.316 | 40.6845 | 0 | 515 | 708.296 | 76.1252 | 4.8251 | 708.296 | 71.2409 | 0.025186 | 697.009 | 68.6043 | 0.018978 | 742.663 | 742.661 | 1667840 | 33.1077 | 1652560 | 1595640 | 1551970 | 0 | 0 | 1533450 | 710.162 | 0 | 0 | 0 | 0 | 1533450 | 710.162 | 1506600 | 1476472
7743 | 2009-11-19 14:00 | 375 | 877 | 52 | 15.91 | 4.29 | 0 | 21.6768 | 224.51 | 52.0602 | 0 | 375 | 537.648 | 69.3972 | 3.5135 | 537.648 | 64.9446 | 0.018339 | 520.807 | 62.541 | 0.013819 | 565.861 | 565.861 | 1270780 | 29.2726 | 1239290 | 1216320 | 1186070 | 0 | 0 | 1175280 | 713.099 | 0 | 0 | 0 | 0 | 1175280 | 713.099 | 1156190 | 1133066
7744 | 2009-11-19 15:00 | 180 | 604 | 52 | 16.25 | 3.54 | 0 | 12.2001 | 235.468 | 64.806 | 0 | 180 | 257.836 | 74.3236 | 1.6865 | 218.16 | 69.5549 | 0.0088027 | 203.443 | 66.9807 | 0.0066331 | 262.318 | 262.315 | 589097 | 22.7574 | 547871 | 552365 | 511434 | 0 | 0 | 509316 | 706.792 | 0 | 0 | 0 | 0 | 509316 | 706.792 | 501003 | 490983.2812
7745 | 2009-11-19 16:00 | 18 | 203 | 5 | 16.6 | 3.54 | 0 | 1.4845 | 244.74 | 78.2432 | 0 | 18 | 30.4466 | 7.5194 | 0.16865 | 7.6186 | 7.037 | 0.00088028 | 6.13 | 6.7765 | 0.00066331 | 12.52 | 12.5138 | 28106.6 | 16.9104 | 18288.2 | 19016 | 14413.9 | 0 | 0 | 14410.3 | 554.172 | 0 | 0 | 0 | 5043.47 | 9366.82 | 660 | 9016.59 | 8836.2578
7746 | 2009-11-19 17:00 | 0 | 0 | 0 | 15.75 | 3.54 | 0
7747 | 2009-11-19 18:00 | 0 | 0 | 0 | 14.91 | 4.01 | 0
7748 | 2009-11-19 19:00 | 0 | 0 | 0 | 14.07 | 4.01 | 0
7749 | 2009-11-19 20:00 | 0 | 0 | 0 | 13.58 | 4.01 | 0
7750 | 2009-11-19 21:00 | 0 | 0 | 0 | 13.09 | 4.57 | 0
7751 | 2009-11-19 22:00 | 0 | 0 | 0 | 12.6 | 4.57 | 0
7752 | 2009-11-19 23:00 | 0 | 0 | 0 | 11.89 | 4.57 | 0
7753 | 2009-11-20 | 0 | 0 | 0 | 11.19 | 6.83 | 0
7754 | 2009-11-20 01:00 | 0 | 0 | 0 | 10.48 | 6.83 | 0
7755 | 2009-11-20 02:00 | 0 | 0 | 0 | 10.12 | 6.83 | 0
7756 | 2009-11-20 03:00 | 0 | 0 | 0 | 9.76 | 5.44 | 0
7757 | 2009-11-20 04:00 | 0 | 0 | 0 | 9.4 | 5.44 | 0
7758 | 2009-11-20 05:00 | 0 | 0 | 0 | 9 | 5.44 | 0
7759 | 2009-11-20 06:00 | 1 | 372 | 0 | 8.59 | 8.12 | 0 | -0.4742 | 113.933 | 80.5644 | 0 | 1 | 1.8844 | 0 | 0.0093692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.59 | 0 | 0 | 0 | 0 | 0 | 0 | 660 | 0 | 0 | 0 | 0 | 0 | 660 | 0 | 0
7760 | 2009-11-20 07:00 | 156 | 671 | 35 | 8.19 | 8.12 | 0 | 10.3789 | 122.991 | 67.0685 | 0 | 156 | 261.691 | 52.3551 | 1.4616 | 111.577 | 48.9959 | 0.0076291 | 102.838 | 47.1826 | 0.0057487 | 145.525 | 145.457 | 326643 | 10.8763 | 296274 | 313237 | 246491 | 0 | 0 | 245851 | 697.445 | 0 | 0 | 0 | 32.427 | 245819 | 698.314 | 239853 | 235056.0938
7761 | 2009-11-20 08:00 | 330 | 825 | 47 | 9.83 | 8.12 | 0 | 20.0719 | 133.627 | 54.2024 | 0 | 330 | 482.324 | 63.3776 | 3.0918 | 421.728 | 59.3112 | 0.016138 | 406.764 | 57.1161 | 0.012161 | 449.976 | 449.964 | 1010510 | 18.1398 | 975097 | 1001000 | 919975 | 0 | 0 | 913513 | 730.121 | 0 | 0 | 0 | 0 | 913513 | 730.121 | 898399 | 880431
7762 | 2009-11-20 09:00 | 497 | 931 | 61 | 11.48 | 9.04 | 0 | 28.0175 | 146.408 | 42.5648 | 0 | 497 | 683.609 | 80.0412 | 4.6565 | 683.609 | 74.9056 | 0.024305 | 671.381 | 72.1334 | 0.018315 | 721.226 | 721.224 | 1619690 | 24.0556 | 1602210 | 1608350 | 1563820 | 0 | 0 | 1546490 | 740.281 | 0 | 0 | 0 | 0 | 1546490 | 740.281 | 1518160 | 1487796.5
7763 | 2009-11-20 10:00 | 572 | 884 | 86 | 13.12 | 9.04 | 0 | 33.4467 | 161.574 | 33.4803 | 0 | 572 | 735.467 | 117.158 | 5.3592 | 735.467 | 109.641 | 0.027973 | 728.152 | 105.583 | 0.021078 | 808.743 | 808.734 | 1816220 | 27.2214 | 1808030 | 1790990 | 1742980 | 0 | 0 | 1720940 | 730.071 | 0 | 0 | 0 | 0 | 1720940 | 730.071 | 1687920 | 1654164
7764 | 2009-11-20 11:00 | 636 | 978 | 69 | 15.21 | 9.04 | 0 | 35.585 | 178.514 | 29.4285 | 0 | 636 | 848.654 | 89.3698 | 5.9588 | 848.654 | 83.6357 | 0.031103 | 842.367 | 80.5404 | 0.023437 | 895.243 | 895.238 | 2010480 | 30.8198 | 2012150 | 1963150 | 1911470 | 0 | 0 | 1884430 | 722.334 | 0 | 0 | 0 | 0 | 1884430 | 722.334 | 1846360 | 1809429.75
7765 | 2009-11-20 12:00 | 609 | 970 | 68 | 17.3 | 9.7 | 0 | 34.0483 | 195.61 | 32.3618 | 0 | 609 | 816.184 | 88.2442 | 5.7059 | 816.184 | 82.5823 | 0.029783 | 808.68 | 79.526 | 0.022442 | 861.582 | 861.577 | 1934890 | 31.7221 | 1932660 | 1878160 | 1830320 | 0 | 0 | 1805140 | 716.934 | 0 | 0 | 0 | 0 | 1805140 | 716.934 | 1769750 | 1734350.25
7766 | 2009-11-20 13:00 | 519 | 942 | 62 | 19.39 | 9.7 | 0 | 29.1179 | 211.141 | 40.7979 | 0 | 519 | 710.958 | 81.2033 | 4.8626 | 710.958 | 75.9932 | 0.025381 | 699.548 | 73.1807 | 0.019125 | 749.566 | 749.561 | 1683320 | 31.9371 | 1668760 | 1619720 | 1577900 | 0 | 0 | 1558940 | 713.018 | 0 | 0 | 0 | 0 | 1558940 | 713.018 | 1531260 | 1500630.125
7767 | 2009-11-20 14:00 | 377 | 878 | 55 | 19.42 | 9.7 | 0 | 21.5339 | 224.313 | 52.1243 | 0 | 377 | 538.595 | 73.2592 | 3.5322 | 538.595 | 68.5588 | 0.018437 | 521.661 | 66.0214 | 0.013893 | 570.066 | 570.063 | 1280220 | 28.9624 | 1249050 | 1227640 | 1195270 | 0 | 0 | 1184360 | 714.3 | 0 | 0 | 0 | 0 | 1184360 | 714.3 | 1165030 | 1141726.375
7768 | 2009-11-20 15:00 | 185 | 651 | 48 | 19.46 | 8.78 | 0 | 12.0853 | 235.262 | 64.8347 | 0 | 185 | 278.25 | 67.4059 | 1.7333 | 235.432 | 63.0811 | 0.0090473 | 219.521 | 60.7465 | 0.0068173 | 271.866 | 271.852 | 610514 | 24.2774 | 569288 | 570231 | 526994 | 0 | 0 | 524718 | 703.667 | 0 | 0 | 0 | 0 | 524718 | 703.667 | 516340 | 506013.0312
7769 | 2009-11-20 16:00 | 19 | 217 | 5 | 19.49 | 8.78 | 0 | 1.3924 | 244.528 | 78.2453 | 0 | 19 | 32.7829 | 7.505 | 0.17802 | 8.1185 | 7.0234 | 0.00092918 | 6.5319 | 6.7635 | 0.00070016 | 12.8972 | 12.8937 | 28960.3 | 19.7185 | 19021 | 19518 | 14703.5 | 0 | 0 | 14699.5 | 545.234 | 0 | 0 | 0 | 5691.13 | 9008.41 | 660 | 8671.45 | 8498.0234
7770 | 2009-11-20 17:00 | 0 | 0 | 0 | 17.95 | 8.78 | 0
7771 | 2009-11-20 18:00 | 0 | 0 | 0 | 16.4 | 11.33 | 0
7772 | 2009-11-20 19:00 | 0 | 0 | 0 | 14.86 | 11.33 | 0
7773 | 2009-11-20 20:00 | 0 | 0 | 0 | 14.06 | 11.33 | 0
7774 | 2009-11-20 21:00 | 0 | 0 | 0 | 13.26 | 9.53 | 0
7775 | 2009-11-20 22:00 | 0 | 0 | 0 | 12.47 | 9.53 | 0
7776 | 2009-11-20 23:00 | 0 | 0 | 0 | 11.57 | 9.53 | 0
7777 | 2009-11-21 | 0 | 0 | 0 | 10.67 | 10.92 | 0
7778 | 2009-11-21 01:00 | 0 | 0 | 0 | 9.77 | 10.92 | 0
7779 | 2009-11-21 02:00 | 0 | 0 | 0 | 9.15 | 10.92 | 0
7780 | 2009-11-21 03:00 | 0 | 0 | 0 | 8.52 | 10.12 | 0
7781 | 2009-11-21 04:00 | 0 | 0 | 0 | 7.9 | 10.12 | 0
7782 | 2009-11-21 05:00 | 0 | 0 | 0 | 7.33 | 10.12 | 0
7783 | 2009-11-21 06:00 | 10 | 166 | 3 | 6.77 | 10.04 | 0 | -0.6535 | 114.075 | 80.6741 | 0 | 10 | 13.0385 | 4.1128 | 0.093692 | 0 | 3.8489 | 0 | 0 | 3.7064 | 0 | 3.5952 | 3.595 | 8073.39 | 6.8289 | 2922.94 | 2980.88 | 2945.62 | 0 | 0 | 2945.47 | 482.371 | 0 | 0 | 0 | 2945.47 | 0 | 660 | 0 | 0
7784 | 2009-11-21 07:00 | 162 | 688 | 40 | 6.21 | 10.04 | 0 | 10.186 | 123.115 | 67.1996 | 0 | 162 | 267.34 | 58.0261 | 1.5178 | 111.13 | 54.3031 | 0.0079225 | 102.348 | 52.2933 | 0.0059698 | 150.008 | 149.838 | 336491 | 8.6663 | 305621 | 326441 | 258659 | 0 | 0 | 257965 | 698.969 | 0 | 0 | 0 | 0 | 257965 | 698.969 | 251859 | 246822.1094
7785 | 2009-11-21 08:00 | 330 | 834 | 47 | 7.83 | 10.04 | 0 | 19.8642 | 133.727 | 54.3595 | 0 | 330 | 485.306 | 63.4963 | 3.0918 | 422.963 | 59.4222 | 0.016138 | 407.818 | 57.2231 | 0.012161 | 451.101 | 450.866 | 1012530 | 15.2212 | 977295 | 1015710 | 929426 | 0 | 0 | 922959 | 737.814 | 0 | 0 | 0 | 0 | 922959 | 737.814 | 907345 | 889198.0625
7786 | 2009-11-21 09:00 | 486 | 874 | 79 | 9.46 | 6.13 | 0 | 27.7966 | 146.47 | 42.7533 | 0 | 486 | 640.857 | 107.791 | 4.5534 | 640.826 | 100.875 | 0.023767 | 629.231 | 97.1415 | 0.017909 | 704.599 | 704.594 | 1582340 | 24.2265 | 1563190 | 1568020 | 1524610 | 0 | 0 | 1507980 | 737.14 | 0 | 0 | 0 | 0 | 1507980 | 737.14 | 1480870 | 1451248.375
7787 | 2009-11-21 10:00 | 549 | 691 | 172 | 11.08 | 6.13 | 0 | 33.2193 | 161.579 | 33.7 | 0 | 549 | 572.51 | 219.084 | 5.1437 | 572.51 | 205.027 | 0.026848 | 566.728 | 197.439 | 0.020231 | 741.262 | 741.251 | 1664660 | 26.6147 | 1649240 | 1637770 | 1595620 | 0 | 0 | 1577140 | 730.879 | 0 | 0 | 0 | 0 | 1577140 | 730.879 | 1548330 | 1517360.875
7788 | 2009-11-21 11:00 | 227 | 41 | 203 | 12.08 | 6.13 | 0 | 35.3643 | 178.447 | 29.6504 | 0 | 227 | 36.0374 | 208.001 | 2.1268 | 36.0374 | 194.656 | 0.011101 | 35.7659 | 187.452 | 0.008365 | 216.529 | 216.524 | 486258 | 16.6178 | 445121 | 462406 | 449344 | 0 | 0 | 447813 | 721.1 | 0 | 0 | 0 | 0 | 447813 | 721.1 | 439762 | 430967.0625
7789 | 2009-11-21 12:00 | 569 | 706 | 177 | 13.08 | 3.31 | 0 | 33.8493 | 195.479 | 32.5333 | 0 | 569 | 593.323 | 224.955 | 5.3311 | 593.323 | 210.521 | 0.027827 | 587.802 | 202.73 | 0.020968 | 766.836 | 766.824 | 1722090 | 32.394 | 1709350 | 1655760 | 1611860 | 0 | 0 | 1592020 | 712.259 | 0 | 0 | 0 | 0 | 1592020 | 712.259 | 1563380 | 1532113.125
7790 | 2009-11-21 13:00 | 505 | 931 | 55 | 14.09 | 3.31 | 0 | 28.9496 | 210.967 | 40.9058 | 0 | 505 | 702.636 | 72.5701 | 4.7315 | 702.636 | 67.9138 | 0.024697 | 691.284 | 65.4004 | 0.018609 | 734.002 | 733.997 | 1648370 | 32.5772 | 1632190 | 1579600 | 1538850 | 0 | 0 | 1520640 | 710.633 | 0 | 0 | 0 | 0 | 1520640 | 710.633 | 1494150 | 1464271.625
7791 | 2009-11-21 14:00 | 374 | 877 | 55 | 14.59 | 3.31 | 0 | 21.3974 | 224.119 | 52.1834 | 0 | 374 | 536.107 | 73.3727 | 3.5041 | 536.107 | 68.6649 | 0.01829 | 519.194 | 66.1237 | 0.013782 | 567.771 | 567.768 | 1275060 | 28.8904 | 1243720 | 1222720 | 1190360 | 0 | 0 | 1179570 | 715.385 | 0 | 0 | 0 | 0 | 1179570 | 715.385 | 1160290 | 1137082
7792 | 2009-11-21 15:00 | 186 | 672 | 46 | 15.1 | 1.6 | 0 | 11.9767 | 235.059 | 64.8589 | 0 | 186 | 286.625 | 65.359 | 1.7427 | 231.492 | 61.1654 | 0.0090962 | 215.822 | 58.9017 | 0.0068542 | 266.489 | 266.377 | 598221 | 22.6179 | 558168 | 561836 | 508889 | 0 | 0 | 506731 | 706.029 | 0 | 0 | 0 | 0 | 506731 | 706.029 | 498470 | 488500.8125
7793 | 2009-11-21 16:00 | 18 | 221 | 4 | 15.6 | 1.6 | 0 | 1.3063 | 244.319 | 78.2431 | 0 | 18 | 32.7888 | 6.0648 | 0.16865 | 8.1089 | 5.6757 | 0.00088028 | 6.5245 | 5.4657 | 0.00066331 | 11.6311 | 11.6207 | 26101.3 | 15.928 | 16852.2 | 17585 | 12673.1 | 0 | 0 | 12669.9 | 539.257 | 0 | 0 | 0 | 3950.28 | 8719.61 | 660 | 8393.3 | 8225.4346
7794 | 2009-11-21 17:00 | 0 | 0 | 0 | 14.92 | 1.6 | 0
7795 | 2009-11-21 18:00 | 0 | 0 | 0 | 14.23 | 4.83 | 0
7796 | 2009-11-21 19:00 | 0 | 0 | 0 | 13.54 | 4.83 | 0
7797 | 2009-11-21 20:00 | 0 | 0 | 0 | 13.02 | 4.83 | 0
7798 | 2009-11-21 21:00 | 0 | 0 | 0 | 12.5 | 4.73 | 0
7799 | 2009-11-21 22:00 | 0 | 0 | 0 | 11.98 | 4.73 | 0
7800 | 2009-11-21 23:00 | 0 | 0 | 0 | 11.13 | 4.73 | 0
7801 | 2009-11-22 | 0 | 0 | 0 | 10.28 | 3.03 | 0
7802 | 2009-11-22 01:00 | 0 | 0 | 0 | 9.42 | 3.03 | 0
7803 | 2009-11-22 02:00 | 0 | 0 | 0 | 8.5 | 3.03 | 0
7804 | 2009-11-22 03:00 | 0 | 0 | 0 | 7.58 | 1.19 | 0
7805 | 2009-11-22 04:00 | 0 | 0 | 0 | 6.66 | 1.19 | 0
7806 | 2009-11-22 05:00 | 0 | 0 | 0 | 6.14 | 1.19 | 0
7807 | 2009-11-22 06:00 | 9 | 160 | 2 | 5.62 | 3.12 | 0 | -0.83152 | 114.21 | 80.7853 | 0 | 9 | 12.8844 | 2.7781 | 0.084323 | 0 | 2.5998 | 0 | 0 | 2.5036 | 0 | 2.4285 | 2.4284 | 5453.66 | 5.6819 | 1417.23 | 1396.83 | 1388.9 | 0 | 0 | 1388.84 | 358.409 | 0 | 0 | 0 | 1388.84 | 0 | 660 | 0 | 0
7808 | 2009-11-22 07:00 | 159 | 684 | 40 | 5.1 | 3.12 | 0 | 9.9951 | 123.232 | 67.3317 | 0 | 159 | 264.236 | 58.0607 | 1.4897 | 107.043 | 54.3355 | 0.0077758 | 98.5078 | 52.3245 | 0.0058592 | 146.313 | 146.335 | 328635 | 8.8323 | 297988 | 316971 | 250943 | 0 | 0 | 250254 | 681.134 | 0 | 0 | 0 | -2.782 | 250257 | 681.16 | 244548 | 239656.8281
7809 | 2009-11-22 08:00 | 343 | 858 | 55 | 6.94 | 3.12 | 0 | 19.6594 | 133.82 | 54.5166 | 0 | 343 | 496.912 | 73.67 | 3.2136 | 431.565 | 68.9432 | 0.016774 | 415.969 | 66.3917 | 0.01264 | 467.902 | 467.783 | 1050530 | 18.871 | 1016190 | 1038520 | 952625 | 0 | 0 | 945628 | 726.881 | 0 | 0 | 0 | 0 | 945628 | 726.881 | 930083 | 911481.75
7810 | 2009-11-22 09:00 | 491 | 931 | 61 | 8.77 | 3.85 | 0 | 27.5794 | 146.525 | 42.9404 | 0 | 491 | 679.918 | 80.2625 | 4.6003 | 679.852 | 75.1127 | 0.024012 | 667.41 | 72.3328 | 0.018093 | 717.569 | 717.567 | 1611470 | 26.2114 | 1593620 | 1585200 | 1541390 | 0 | 0 | 1524130 | 731.061 | 0 | 0 | 0 | 0 | 1524130 | 731.061 | 1496800 | 1466866.75
7811 | 2009-11-22 10:00 | 584 | 958 | 64 | 10.61 | 3.85 | 0 | 32.9969 | 161.578 | 33.9161 | 0 | 584 | 792.38 | 83.545 | 5.4716 | 792.38 | 78.1846 | 0.02856 | 784.257 | 75.291 | 0.021521 | 833.782 | 833.78 | 1872450 | 30.8762 | 1867060 | 1820820 | 1772670 | 0 | 0 | 1749240 | 720.49 | 0 | 0 | 0 | 0 | 1749240 | 720.49 | 1715570 | 1681257.25
7812 | 2009-11-22 11:00 | 629 | 816 | 161 | 12.4 | 3.85 | 0 | 35.1496 | 178.377 | 29.8664 | 0 | 629 | 704.943 | 209.347 | 5.8932 | 704.943 | 195.915 | 0.030761 | 699.544 | 188.664 | 0.023179 | 861.585 | 861.572 | 1934870 | 33.3417 | 1932640 | 1864840 | 1814280 | 0 | 0 | 1789250 | 712.098 | 0 | 0 | 0 | 0 | 1789250 | 712.098 | 1754460 | 1719374.25
7813 | 2009-11-22 12:00 | 477 | 458 | 224 | 14.2 | 4.55 | 0 | 33.6567 | 195.346 | 32.6986 | 0 | 477 | 384.156 | 273.631 | 4.4691 | 384.156 | 256.074 | 0.023327 | 380.539 | 246.597 | 0.017578 | 608.339 | 608.333 | 1366170 | 28.3234 | 1338120 | 1318880 | 1281510 | 0 | 0 | 1269230 | 721.509 | 0 | 0 | 0 | 0 | 1269230 | 721.509 | 1247820 | 1222867.25
7814 | 2009-11-22 13:00 | 509 | 782 | 133 | 15.99 | 4.55 | 0 | 28.7879 | 210.794 | 41.0082 | 0 | 509 | 589.19 | 173.926 | 4.7689 | 589.19 | 162.767 | 0.024892 | 579.611 | 156.743 | 0.018757 | 714.281 | 714.279 | 1604090 | 32.5732 | 1585910 | 1534750 | 1496860 | 0 | 0 | 1479580 | 709.096 | 0 | 0 | 0 | 0 | 1479580 | 709.096 | 1454200 | 1425112.75
7815 | 2009-11-22 14:00 | 372 | 876 | 55 | 16.24 | 4.55 | 0 | 21.2673 | 223.927 | 52.2376 | 0 | 372 | 535.2 | 73.4833 | 3.4853 | 535.2 | 68.7685 | 0.018192 | 518.262 | 66.2234 | 0.013708 | 566.964 | 566.961 | 1273250 | 29.4029 | 1241840 | 1218130 | 1185860 | 0 | 0 | 1175090 | 713.027 | 0 | 0 | 0 | 0 | 1175090 | 713.027 | 1156010 | 1132885
7816 | 2009-11-22 15:00 | 180 | 636 | 49 | 16.49 | 4.38 | 0 | 11.8743 | 234.859 | 64.8785 | 0 | 180 | 270.281 | 68.5899 | 1.6865 | 218.291 | 64.1891 | 0.0088027 | 203.497 | 61.8135 | 0.0066331 | 257.357 | 257.282 | 577796 | 22.53 | 537705 | 541992 | 491746 | 0 | 0 | 489730 | 705.169 | 0 | 0 | 0 | 0 | 489730 | 705.169 | 481684 | 472050.2188
7817 | 2009-11-22 16:00 | 17 | 207 | 5 | 16.74 | 4.38 | 0 | 1.2262 | 244.113 | 78.2368 | 0 | 17 | 28.1197 | 7.4806 | 0.15928 | 6.9514 | 7.0007 | 0.00083137 | 5.5941 | 6.7416 | 0.00062646 | 11.9662 | 11.9658 | 26875.8 | 17.0209 | 17260.2 | 17939.2 | 13819.1 | 0 | 0 | 13815.8 | 550.977 | 0 | 0 | 0 | 5237.8 | 8577.98 | 660 | 8256.83 | 8091.6943
7818 | 2009-11-22 17:00 | 0 | 0 | 0 | 15.85 | 4.38 | 0
7819 | 2009-11-22 18:00 | 0 | 0 | 0 | 14.96 | 6.06 | 0
7820 | 2009-11-22 19:00 | 0 | 0 | 0 | 14.07 | 6.06 | 0
7821 | 2009-11-22 20:00 | 0 | 0 | 0 | 13.2 | 6.06 | 0
7822 | 2009-11-22 21:00 | 0 | 0 | 0 | 12.34 | 8.67 | 0
7823 | 2009-11-22 22:00 | 0 | 0 | 0 | 11.47 | 8.67 | 0
7824 | 2009-11-22 23:00 | 0 | 0 | 0 | 10.61 | 8.67 | 0
7825 | 2009-11-23 | 0 | 0 | 0 | 9.75 | 6.92 | 0
7826 | 2009-11-23 01:00 | 0 | 0 | 0 | 8.89 | 6.92 | 0
7827 | 2009-11-23 02:00 | 0 | 0 | 0 | 8.37 | 6.92 | 0
7828 | 2009-11-23 03:00 | 0 | 0 | 0 | 7.84 | 7.15 | 0
7829 | 2009-11-23 04:00 | 0 | 0 | 0 | 7.32 | 7.15 | 0
7830 | 2009-11-23 05:00 | 0 | 0 | 0 | 6.65 | 7.15 | 0
7831 | 2009-11-23 06:00 | 8 | 138 | 2 | 5.98 | 10.23 | 0 | -1.0082 | 114.338 | 80.898 | 0 | 8 | 10.9098 | 2.7657 | 0.074954 | 0 | 2.5882 | 0 | 0 | 2.4924 | 0 | 2.4177 | 2.4175 | 5429.11 | 6.0192 | 1404.86 | 1384.84 | 1377.02 | 0 | 0 | 1376.96 | 356.782 | 0 | 0 | 0 | 1376.96 | 0 | 660 | 0 | 0
7832 | 2009-11-23 07:00 | 149 | 613 | 44 | 5.3 | 10.23 | 0 | 9.8063 | 123.342 | 67.4646 | 0 | 149 | 236.275 | 62.073 | 1.396 | 93.1123 | 58.0903 | 0.0072867 | 85.6203 | 55.9404 | 0.0054907 | 137.319 | 137.385 | 308538 | 7.5262 | 277727 | 298652 | 238278 | 0 | 0 | 237682 | 686.284 | 0 | 0 | 0 | 36.9045 | 237645 | 688.363 | 231801 | 227164.7188
7833 | 2009-11-23 08:00 | 305 | 708 | 69 | 7.08 | 10.23 | 0 | 19.4574 | 133.906 | 54.6735 | 0 | 305 | 409.67 | 96.6308 | 2.8576 | 340.382 | 90.4308 | 0.014916 | 327.968 | 87.084 | 0.011239 | 402.612 | 402.526 | 903970 | 13.6025 | 865989 | 906654 | 824144 | 0 | 0 | 819068 | 738.447 | 0 | 0 | 0 | 26.1866 | 819042 | 739.032 | 805180 | 789076.375
7834 | 2009-11-23 09:00 | 464 | 851 | 74 | 8.86 | 5.82 | 0 | 27.3663 | 146.574 | 43.1259 | 0 | 464 | 619.223 | 102.009 | 4.3473 | 619.103 | 95.4639 | 0.022691 | 607.645 | 91.9308 | 0.017098 | 678.605 | 678.601 | 1523970 | 23.3684 | 1502280 | 1512370 | 1470380 | 0 | 0 | 1454990 | 738.828 | 0 | 0 | 0 | 0 | 1454990 | 738.828 | 1428960 | 1400381.375
7835 | 2009-11-23 10:00 | 572 | 946 | 61 | 10.63 | 5.82 | 0 | 32.7796 | 161.572 | 34.1283 | 0 | 572 | 781.289 | 79.9093 | 5.3592 | 781.289 | 74.7822 | 0.027973 | 773.162 | 72.0146 | 0.021078 | 819.842 | 819.837 | 1841140 | 28.158 | 1834190 | 1809670 | 1761180 | 0 | 0 | 1738620 | 729.423 | 0 | 0 | 0 | 0 | 1738620 | 729.423 | 1705070 | 1670972
7836 | 2009-11-23 11:00 | 613 | 962 | 64 | 11.6 | 5.82 | 0 | 34.941 | 178.304 | 30.0764 | 0 | 613 | 829.501 | 83.4869 | 5.7433 | 829.501 | 78.1302 | 0.029978 | 823.047 | 75.2387 | 0.022589 | 871.359 | 871.355 | 1956850 | 30.2294 | 1955740 | 1912780 | 1863420 | 0 | 0 | 1837680 | 721.945 | 0 | 0 | 0 | 0 | 1837680 | 721.945 | 1801150 | 1765124
7837 | 2009-11-23 12:00 | 600 | 968 | 68 | 12.57 | 4.66 | 0 | 33.4708 | 195.212 | 32.8576 | 0 | 600 | 810.303 | 88.555 | 5.6215 | 810.303 | 82.8731 | 0.029343 | 802.587 | 79.806 | 0.02211 | 855.943 | 855.938 | 1922220 | 32.2998 | 1919340 | 1860440 | 1812060 | 0 | 0 | 1787320 | 715.539 | 0 | 0 | 0 | 0 | 1787320 | 715.539 | 1752530 | 1717478.625
7838 | 2009-11-23 13:00 | 506 | 935 | 59 | 13.53 | 4.66 | 0 | 28.6328 | 210.622 | 41.105 | 0 | 506 | 702.882 | 77.7736 | 4.7408 | 702.882 | 72.7835 | 0.024746 | 691.386 | 70.0898 | 0.018646 | 738.649 | 738.647 | 1658810 | 30.5562 | 1643120 | 1604330 | 1561770 | 0 | 0 | 1543380 | 716.922 | 0 | 0 | 0 | 0 | 1543380 | 716.922 | 1516010 | 1485688.125
7839 | 2009-11-23 14:00 | 370 | 874 | 55 | 13.96 | 4.66 | 0 | 21.1437 | 223.736 | 52.2867 | 0 | 370 | 534.197 | 73.591 | 3.4666 | 534.197 | 68.8693 | 0.018094 | 517.243 | 66.3204 | 0.013635 | 566.07 | 566.067 | 1271240 | 27.0081 | 1239760 | 1228890 | 1196090 | 0 | 0 | 1185380 | 722.088 | 0 | 0 | 0 | 0 | 1185380 | 722.088 | 1165650 | 1142340.625
7840 | 2009-11-23 15:00 | 179 | 632 | 50 | 14.39 | 6.63 | 0 | 11.7782 | 234.661 | 64.8935 | 0 | 179 | 268.146 | 72.5715 | 1.6771 | 216.567 | 67.9151 | 0.0087538 | 201.875 | 65.4016 | 0.0065962 | 259.264 | 259.134 | 581953 | 19.6495 | 541765 | 553431 | 501970 | 0 | 0 | 499944 | 717.364 | 0 | 0 | 0 | 0 | 499944 | 717.364 | 491404 | 481576.2188
7841 | 2009-11-23 16:00 | 17 | 203 | 5 | 14.81 | 6.63 | 0 | 1.1522 | 243.91 | 78.2262 | 0 | 17 | 28.1446 | 7.4709 | 0.15928 | 6.927 | 6.9916 | 0.00083137 | 5.5759 | 6.7328 | 0.00062646 | 11.9401 | 11.9437 | 26826.4 | 15.0524 | 17224.9 | 18069.6 | 13819.9 | 0 | 0 | 13816.7 | 559.437 | 0 | 0 | 0 | 4379.29 | 9437.39 | 660 | 9084.53 | 8902.8369
7842 | 2009-11-23 17:00 | 0 | 0 | 0 | 13.67 | 6.63 | 0
7843 | 2009-11-23 18:00 | 0 | 0 | 0 | 12.52 | 9.36 | 0
7844 | 2009-11-23 19:00 | 0 | 0 | 0 | 11.38 | 9.36 | 0
7845 | 2009-11-23 20:00 | 0 | 0 | 0 | 10.71 | 9.36 | 0
7846 | 2009-11-23 21:00 | 0 | 0 | 0 | 10.04 | 9.46 | 0
7847 | 2009-11-23 22:00 | 0 | 0 | 0 | 9.37 | 9.46 | 0
7848 | 2009-11-23 23:00 | 0 | 0 | 0 | 8.77 | 9.46 | 0
7849 | 2009-11-24 | 0 | 0 | 0 | 8.17 | 11.01 | 0
7850 | 2009-11-24 01:00 | 0 | 0 | 0 | 7.57 | 11.01 | 0
7851 | 2009-11-24 02:00 | 0 | 0 | 0 | 7.2 | 11.01 | 0
7852 | 2009-11-24 03:00 | 0 | 0 | 0 | 6.83 | 6.49 | 0
7853 | 2009-11-24 04:00 | 0 | 0 | 0 | 6.47 | 6.49 | 0
7854 | 2009-11-24 05:00 | 0 | 0 | 0 | 5.82 | 6.49 | 0
7855 | 2009-11-24 06:00 | 8 | 146 | 2 | 5.18 | 9.15 | 0 | -1.1833 | 114.459 | 81.012 | 0 | 8 | 10.7743 | 2.7532 | 0.074954 | 0 | 2.5766 | 0 | 0 | 2.4812 | 0 | 2.4068 | 2.4066 | 5404.56 | 5.2217 | 1392.58 | 1371.32 | 1363.57 | 0 | 0 | 1363.52 | 355.371 | 0 | 0 | 0 | 1363.52 | 0 | 660 | 0 | 0
7856 | 2009-11-24 07:00 | 151 | 673 | 38 | 4.53 | 9.15 | 0 | 9.6195 | 123.446 | 67.5982 | 0 | 151 | 257.708 | 56.0024 | 1.4147 | 94.2104 | 52.4092 | 0.0073845 | 86.5606 | 50.4695 | 0.0055644 | 132.925 | 133.045 | 298785 | 6.834 | 268938 | 289738 | 226607 | 0 | 0 | 226048 | 689.123 | 0 | 0 | 0 | 0 | 226048 | 689.123 | 220338 | 215931.2188
7857 | 2009-11-24 08:00 | 332 | 851 | 52 | 5.96 | 9.15 | 0 | 19.2584 | 133.986 | 54.8302 | 0 | 332 | 488.982 | 70.1668 | 3.1106 | 404.85 | 65.6648 | 0.016236 | 389.949 | 63.2346 | 0.012234 | 439.6 | 439.491 | 986976 | 13.571 | 951694 | 995145 | 898684 | 0 | 0 | 892568 | 736.949 | 0 | 0 | 0 | -173.166 | 892742 | 740.918 | 877545 | 859993.6875
7858 | 2009-11-24 09:00 | 477 | 874 | 79 | 7.39 | 8.23 | 0 | 27.1573 | 146.617 | 43.3096 | 0 | 477 | 634.5 | 108.086 | 4.4691 | 634.316 | 101.151 | 0.023327 | 622.446 | 97.4077 | 0.017578 | 698.275 | 698.272 | 1568150 | 20.1968 | 1548380 | 1579330 | 1533480 | 0 | 0 | 1517200 | 749.336 | 0 | 0 | 0 | 0 | 1517200 | 749.336 | 1489080 | 1459302.75
7859 | 2009-11-24 10:00 | 543 | 804 | 111 | 8.82 | 8.23 | 0 | 32.5676 | 161.561 | 34.3365 | 0 | 543 | 662.684 | 146.634 | 5.0875 | 662.684 | 137.226 | 0.026555 | 655.692 | 132.147 | 0.02001 | 764.223 | 764.21 | 1716220 | 22.8361 | 1703200 | 1718330 | 1670030 | 0 | 0 | 1650570 | 745.578 | 0 | 0 | 0 | 0 | 1650570 | 745.578 | 1618920 | 1586545.625
7860 | 2009-11-24 11:00 | 609 | 858 | 122 | 10.18 | 8.23 | 0 | 34.7385 | 178.227 | 30.2804 | 0 | 609 | 738.038 | 159.84 | 5.7059 | 738.038 | 149.584 | 0.029783 | 732.208 | 144.048 | 0.022442 | 849.991 | 849.986 | 1908850 | 25.7693 | 1905290 | 1898880 | 1844640 | 0 | 0 | 1820430 | 737.3 | 0 | 0 | 0 | 0 | 1820430 | 737.3 | 1784190 | 1748502.5
7861 | 2009-11-24 12:00 | 555 | 860 | 84 | 11.54 | 7.3 | 0 | 33.2914 | 195.077 | 33.0103 | 0 | 555 | 719.565 | 115.307 | 5.1999 | 719.565 | 107.909 | 0.027142 | 712.639 | 103.915 | 0.020452 | 792.078 | 792.073 | 1778790 | 26.9449 | 1768770 | 1754100 | 1705860 | 0 | 0 | 1684850 | 732.803 | 0 | 0 | 0 | 0 | 1684850 | 732.803 | 1652850 | 1619792
7862 | 2009-11-24 13:00 | 482 | 866 | 70 | 12.9 | 7.3 | 0 | 28.4844 | 210.45 | 41.1961 | 0 | 482 | 650.034 | 91.4848 | 4.516 | 650.034 | 85.6149 | 0.023572 | 639.341 | 82.4464 | 0.017762 | 700.151 | 700.148 | 1572350 | 26.5171 | 1552760 | 1542590 | 1500890 | 0 | 0 | 1484410 | 728.861 | 0 | 0 | 0 | 0 | 1484410 | 728.861 | 1458160 | 1428996.625
7863 | 2009-11-24 14:00 | 365 | 850 | 60 | 13.28 | 7.3 | 0 | 21.0265 | 223.547 | 52.3307 | 0 | 365 | 519.471 | 84.2435 | 3.4198 | 499.361 | 78.8383 | 0.01785 | 483.472 | 75.9206 | 0.01345 | 542.624 | 542.562 | 1218460 | 23.8322 | 1185370 | 1190940 | 1151810 | 0 | 0 | 1142110 | 731.437 | 0 | 0 | 0 | 0 | 1142110 | 731.437 | 1122790 | 1100332
7864 | 2009-11-24 15:00 | 156 | 449 | 65 | 13.65 | 5.93 | 0 | 11.6884 | 234.466 | 64.904 | 0 | 156 | 190.516 | 88.6227 | 1.4616 | 146.54 | 82.9365 | 0.0076291 | 136.592 | 79.867 | 0.0057487 | 209.971 | 209.977 | 471557 | 18.1076 | 432815 | 445446 | 401541 | 0 | 0 | 400215 | 713.954 | 0 | 0 | 0 | 0 | 400215 | 713.954 | 392894 | 385036.3125
7865 | 2009-11-24 16:00 | 14 | 143 | 6 | 14.03 | 5.93 | 0 | 1.0843 | 243.71 | 78.2114 | 0 | 14 | 18.7863 | 9.4162 | 0.13117 | 3.9014 | 8.812 | 0.00068466 | 3.1417 | 8.4859 | 0.0005159 | 11.2792 | 11.2698 | 25311.6 | 14.2692 | 15730 | 16574.6 | 14042.1 | 0 | 0 | 14039.4 | 569.004 | 0 | 0 | 0 | 3942.11 | 10097.3 | 660 | 9719.9 | 9525.5029
7866 | 2009-11-24 17:00 | 0 | 0 | 0 | 13.26 | 5.93 | 0
7867 | 2009-11-24 18:00 | 0 | 0 | 0 | 12.48 | 7.59 | 0
7868 | 2009-11-24 19:00 | 0 | 0 | 0 | 11.71 | 7.59 | 0
7869 | 2009-11-24 20:00 | 0 | 0 | 0 | 11.12 | 7.59 | 0
7870 | 2009-11-24 21:00 | 0 | 0 | 0 | 10.53 | 10.68 | 0
7871 | 2009-11-24 22:00 | 0 | 0 | 0 | 9.94 | 10.68 | 0
7872 | 2009-11-24 23:00 | 0 | 0 | 0 | 9.47 | 10.68 | 0
7873 | 2009-11-25 | 0 | 0 | 0 | 8.99 | 8.99 | 0
7874 | 2009-11-25 01:00 | 0 | 0 | 0 | 8.52 | 8.99 | 0
7875 | 2009-11-25 02:00 | 0 | 0 | 0 | 8.07 | 8.99 | 0
7876 | 2009-11-25 03:00 | 0 | 0 | 0 | 7.61 | 8.27 | 0
7877 | 2009-11-25 04:00 | 0 | 0 | 0 | 7.16 | 8.27 | 0
7878 | 2009-11-25 05:00 | 0 | 0 | 0 | 6.56 | 8.27 | 0
7879 | 2009-11-25 06:00 | 7 | 140 | 2 | 5.96 | 9.34 | 0 | -1.3569 | 114.573 | 81.1273 | 0 | 7 | 8.8643 | 2.7407 | 0.065585 | 0 | 2.5648 | 0 | 0 | 2.4699 | 0 | 2.3958 | 2.3956 | 5379.9 | 6.001 | 1380.25 | 1360.01 | 1352.46 | 0 | 0 | 1352.4 | 353.467 | 0 | 0 | 0 | 1352.4 | 0 | 660 | 0 | 0
7880 | 2009-11-25 07:00 | 150 | 669 | 40 | 5.36 | 9.34 | 0 | 9.435 | 123.543 | 67.7324 | 0 | 150 | 254.273 | 58.0885 | 1.4054 | 90.1218 | 54.3614 | 0.0073356 | 82.7364 | 52.3495 | 0.0055275 | 131.039 | 131.048 | 294308 | 7.6029 | 264426 | 284060 | 223063 | 0 | 0 | 222520 | 688.532 | 0 | 0 | 0 | 35.9115 | 222484 | 690.183 | 216757 | 212421.6406
7881 | 2009-11-25 08:00 | 332 | 851 | 54 | 6.83 | 9.34 | 0 | 19.0626 | 134.058 | 54.9865 | 0 | 332 | 488.389 | 72.7908 | 3.1106 | 403.013 | 68.1204 | 0.016236 | 388.044 | 65.5993 | 0.012234 | 440.046 | 439.863 | 987804 | 14.3584 | 952532 | 992867 | 894682 | 0 | 0 | 888619 | 737.394 | 0 | 0 | 0 | 31.2764 | 888588 | 741.514 | 873429 | 855960.5
7882 | 2009-11-25 09:00 | 481 | 928 | 61 | 8.31 | 7.55 | 0 | 26.9525 | 146.653 | 43.4914 | 0 | 481 | 672.255 | 80.5776 | 4.5066 | 671.898 | 75.4076 | 0.023523 | 659.186 | 72.6168 | 0.017725 | 709.866 | 709.858 | 1594160 | 21.899 | 1575550 | 1595790 | 1551140 | 0 | 0 | 1534280 | 744.819 | 0 | 0 | 0 | 0 | 1534280 | 744.819 | 1506010 | 1475888.875
7883 | 2009-11-25 10:00 | 580 | 964 | 66 | 9.78 | 7.55 | 0 | 32.361 | 161.544 | 34.5406 | 0 | 580 | 791.02 | 86.3229 | 5.4341 | 791.02 | 80.7843 | 0.028364 | 782.556 | 77.7945 | 0.021373 | 834.561 | 834.557 | 1874200 | 25.7562 | 1868900 | 1862710 | 1811330 | 0 | 0 | 1788050 | 738.167 | 0 | 0 | 0 | 0 | 1788050 | 738.167 | 1752790 | 1717736.625
7884 | 2009-11-25 11:00 | 619 | 974 | 68 | 11.39 | 7.55 | 0 | 34.5423 | 178.147 | 30.4783 | 0 | 619 | 837.481 | 88.6398 | 5.7995 | 837.481 | 82.9525 | 0.030272 | 830.767 | 79.8825 | 0.02281 | 883.352 | 883.347 | 1983780 | 28.3002 | 1984070 | 1956530 | 1902220 | 0 | 0 | 1876150 | 732.28 | 0 | 0 | 0 | 0 | 1876150 | 732.28 | 1838240 | 1801474
7885 | 2009-11-25 12:00 | 593 | 967 | 66 | 13.01 | 6.18 | 0 | 33.1188 | 194.941 | 33.1567 | 0 | 593 | 807.489 | 86.2705 | 5.556 | 807.489 | 80.7352 | 0.029 | 799.636 | 77.7473 | 0.021852 | 851.083 | 851.078 | 1911310 | 30.7892 | 1907880 | 1861450 | 1812190 | 0 | 0 | 1787740 | 721 | 0 | 0 | 0 | 0 | 1787740 | 721 | 1752830 | 1717776.25
7886 | 2009-11-25 13:00 | 500 | 932 | 59 | 14.62 | 6.18 | 0 | 28.3427 | 210.279 | 41.2814 | 0 | 500 | 698.064 | 77.9589 | 4.6846 | 698.064 | 72.957 | 0.024452 | 686.521 | 70.2569 | 0.018425 | 734.092 | 734.09 | 1648580 | 29.9553 | 1632420 | 1598050 | 1554250 | 0 | 0 | 1536220 | 720.787 | 0 | 0 | 0 | 0 | 1536220 | 720.787 | 1508920 | 1478739
7887 | 2009-11-25 14:00 | 355 | 865 | 47 | 14.79 | 6.18 | 0 | 20.916 | 223.361 | 52.3696 | 0 | 355 | 526.765 | 63.6804 | 3.3261 | 506.372 | 59.5946 | 0.017361 | 490.223 | 57.389 | 0.013082 | 531.197 | 531.183 | 1192900 | 25.8865 | 1159020 | 1154190 | 1115440 | 0 | 0 | 1106160 | 723.848 | 0 | 0 | 0 | 0 | 1106160 | 723.848 | 1087920 | 1066157
7888 | 2009-11-25 15:00 | 171 | 590 | 52 | 14.97 | 7.29 | 0 | 11.6048 | 234.273 | 64.9098 | 0 | 171 | 250.851 | 75.1007 | 1.6021 | 192.948 | 70.2821 | 0.0083626 | 179.845 | 67.681 | 0.0063014 | 240.106 | 240.03 | 539054 | 19.6413 | 500386 | 510819 | 454616 | 0 | 0 | 452881 | 712.856 | 0 | 0 | 0 | 0 | 452881 | 712.856 | 445025 | 436124.9688
7889 | 2009-11-25 16:00 | 16 | 186 | 5 | 15.14 | 7.29 | 0 | 1.0225 | 243.514 | 78.1925 | 0 | 16 | 25.8721 | 7.9907 | 0.14991 | 5.3724 | 7.478 | 0.00078247 | 4.3282 | 7.2012 | 0.0005896 | 11.1842 | 11.1773 | 25104.9 | 15.3575 | 15730.3 | 16479.4 | 12944.9 | 0 | 0 | 12942.3 | 555.727 | 0 | 0 | 0 | 4647.81 | 8294.45 | 660 | 7983.78 | 7824.0996
7890 | 2009-11-25 17:00 | 0 | 0 | 0 | 14.19 | 7.29 | 0
7891 | 2009-11-25 18:00 | 0 | 0 | 0 | 13.24 | 8 | 0
7892 | 2009-11-25 19:00 | 0 | 0 | 0 | 12.3 | 8 | 0
7893 | 2009-11-25 20:00 | 0 | 0 | 0 | 11.63 | 8 | 0
7894 | 2009-11-25 21:00 | 0 | 0 | 0 | 10.95 | 11.78 | 0
7895 | 2009-11-25 22:00 | 0 | 0 | 0 | 10.28 | 11.78 | 0
7896 | 2009-11-25 23:00 | 0 | 0 | 0 | 9.61 | 11.78 | 0
7897 | 2009-11-26 | 0 | 0 | 0 | 8.95 | 8.52 | 0
7898 | 2009-11-26 01:00 | 0 | 0 | 0 | 8.28 | 8.52 | 0
7899 | 2009-11-26 02:00 | 0 | 0 | 0 | 8.03 | 8.52 | 0
7900 | 2009-11-26 03:00 | 0 | 0 | 0 | 7.78 | 7.55 | 0
7901 | 2009-11-26 04:00 | 0 | 0 | 0 | 7.53 | 7.55 | 0
7902 | 2009-11-26 05:00 | 0 | 0 | 0 | 6.82 | 7.55 | 0
7903 | 2009-11-26 06:00 | 6 | 125 | 1 | 6.12 | 6.49 | 0 | -1.5288 | 114.681 | 81.2438 | 0 | 6 | 8.7488 | 1.3873 | 0.056215 | 0 | 1.2982 | 0 | 0 | 1.2502 | 0 | 1.2127 | 1.2127 | 2723.32 | 6.1448 | 358.694 | 350.793 | 349.181 | 0 | 0 | 349.166 | 177.961 | 0 | 0 | 0 | 349.166 | 0 | 660 | 0 | 0
7904 | 2009-11-26 07:00 | 135 | 618 | 35 | 5.41 | 6.49 | 0 | 9.2529 | 123.633 | 67.867 | 0 | 135 | 234.314 | 52.8286 | 1.2648 | 76.6833 | 49.439 | 0.0066021 | 70.3407 | 47.6093 | 0.0049748 | 114.416 | 114.418 | 256955 | 7.7532 | 228327 | 245189 | 192358 | 0 | 0 | 191974 | 712.034 | 0 | 0 | 0 | 0 | 191974 | 712.034 | 186258 | 182533.2812
7905 | 2009-11-26 08:00 | 303 | 726 | 68 | 6.5 | 6.49 | 0 | 18.87 | 134.125 | 55.1422 | 0 | 303 | 415.285 | 93.1428 | 2.8389 | 341.334 | 87.1666 | 0.014818 | 328.54 | 83.9406 | 0.011166 | 400.117 | 400.149 | 898622 | 14.6947 | 860857 | 896402 | 807563 | 0 | 0 | 802645 | 737.343 | 0 | 0 | 0 | 51.2156 | 802594 | 737.788 | 789033 | 773252.4375
7906 | 2009-11-26 09:00 | 412 | 666 | 113 | 7.6 | 5.78 | 0 | 26.752 | 146.683 | 43.6711 | 0 | 412 | 480.464 | 151.19 | 3.8601 | 479.953 | 141.489 | 0.020148 | 470.774 | 136.253 | 0.015182 | 588.831 | 588.826 | 1322350 | 20.2215 | 1292690 | 1318740 | 1279720 | 0 | 0 | 1268140 | 742.985 | 0 | 0 | 0 | 0 | 1268140 | 742.985 | 1245720 | 1220809.625
7907 | 2009-11-26 10:00 | 550 | 830 | 110 | 8.7 | 5.78 | 0 | 32.1598 | 161.522 | 34.7405 | 0 | 550 | 679.276 | 145.66 | 5.1531 | 679.276 | 136.314 | 0.026897 | 671.909 | 131.269 | 0.020268 | 779.102 | 779.097 | 1749650 | 25.4 | 1738230 | 1735010 | 1686840 | 0 | 0 | 1666620 | 738.275 | 0 | 0 | 0 | 0 | 1666620 | 738.275 | 1634980 | 1602284.75
7908 | 2009-11-26 11:00 | 609 | 968 | 65 | 10.87 | 5.78 | 0 | 34.3524 | 178.064 | 30.6699 | 0 | 609 | 829.205 | 85.0061 | 5.7059 | 829.205 | 79.5519 | 0.029783 | 822.463 | 76.6078 | 0.022442 | 872.12 | 872.116 | 1958550 | 29.5639 | 1957530 | 1919990 | 1869590 | 0 | 0 | 1843910 | 724.868 | 0 | 0 | 0 | 0 | 1843910 | 724.868 | 1807130 | 1770986.5
7909 | 2009-11-26 12:00 | 577 | 953 | 60 | 13.05 | 2.88 | 0 | 32.9529 | 194.804 | 33.2966 | 0 | 577 | 794.429 | 78.873 | 5.406 | 794.429 | 73.8124 | 0.028218 | 786.628 | 71.0806 | 0.021263 | 831.998 | 831.996 | 1868450 | 34.6105 | 1862860 | 1787360 | 1740450 | 0 | 0 | 1717010 | 707.037 | 0 | 0 | 0 | 0 | 1717010 | 707.037 | 1684670 | 1650975.25
7910 | 2009-11-26 13:00 | 503 | 938 | 61 | 15.22 | 2.88 | 0 | 28.2078 | 210.109 | 41.361 | 0 | 503 | 701.858 | 80.5485 | 4.7127 | 701.858 | 75.3804 | 0.024599 | 690.196 | 72.5906 | 0.018536 | 739.921 | 739.916 | 1661660 | 34.3943 | 1646090 | 1580330 | 1538300 | 0 | 0 | 1519840 | 705.089 | 0 | 0 | 0 | 0 | 1519840 | 705.089 | 1493580 | 1463704.625
7911 | 2009-11-26 14:00 | 351 | 862 | 45 | 15.79 | 2.88 | 0 | 20.812 | 223.177 | 52.4034 | 0 | 351 | 525.44 | 61.204 | 3.2886 | 505.098 | 57.277 | 0.017165 | 488.958 | 55.1572 | 0.012934 | 527.805 | 527.781 | 1185260 | 29.467 | 1151140 | 1128380 | 1092790 | 0 | 0 | 1083500 | 708.855 | 0 | 0 | 0 | 0 | 1083500 | 708.855 | 1066450 | 1045117.25
7912 | 2009-11-26 15:00 | 168 | 584 | 51 | 16.36 | 2.55 | 0 | 11.5276 | 234.084 | 64.911 | 0 | 168 | 248.252 | 74.0886 | 1.574 | 190.95 | 69.335 | 0.0082159 | 177.981 | 66.7689 | 0.0061909 | 237.413 | 237.352 | 533039 | 22.6471 | 494422 | 497318 | 443386 | 0 | 0 | 441683 | 701.688 | 0 | 0 | 0 | 0 | 441683 | 701.688 | 434308 | 425621.75
7913 | 2009-11-26 16:00 | 15 | 183 | 4 | 16.92 | 2.55 | 0 | 0.96683 | 243.321 | 78.1694 | 0 | 15 | 25.922 | 6.0416 | 0.14054 | 4.4462 | 5.654 | 0.00073356 | 3.5842 | 5.4447 | 0.00055276 | 8.7586 | 8.7463 | 19645 | 17.1517 | 11542.7 | 11959.1 | 8819.7 | 0 | 0 | 8818.16 | 518.17 | 0 | 0 | 0 | 4804.54 | 4013.62 | 660 | 3862.37 | 3785.1267
7914 | 2009-11-26 17:00 | 0 | 0 | 0 | 16.15 | 2.55 | 0
7915 | 2009-11-26 18:00 | 0 | 0 | 0 | 15.38 | 2.87 | 0
7916 | 2009-11-26 19:00 | 0 | 0 | 0 | 14.61 | 2.87 | 0
7917 | 2009-11-26 20:00 | 0 | 0 | 0 | 13.9 | 2.87 | 0
7918 | 2009-11-26 21:00 | 0 | 0 | 0 | 13.19 | 2.75 | 0
7919 | 2009-11-26 22:00 | 0 | 0 | 0 | 12.49 | 2.75 | 0
7920 | 2009-11-26 23:00 | 0 | 0 | 0 | 11.84 | 2.75 | 0
7921 | 2009-11-27 | 0 | 0 | 0 | 11.2 | 5.41 | 0
7922 | 2009-11-27 01:00 | 0 | 0 | 0 | 10.56 | 5.41 | 0
7923 | 2009-11-27 02:00 | 0 | 0 | 0 | 10.48 | 5.41 | 0
7924 | 2009-11-27 03:00 | 0 | 0 | 0 | 10.4 | 6.38 | 0
7925 | 2009-11-27 04:00 | 0 | 0 | 0 | 10.32 | 6.38 | 0
7926 | 2009-11-27 05:00 | 0 | 0 | 0 | 9.64 | 6.38 | 0
7927 | 2009-11-27 06:00 | 3 | 25 | 2 | 8.95 | 7.33 | 0 | -1.6989 | 114.782 | 81.3614 | 0 | 3 | 1.7265 | 2.4979 | 0.028108 | 0 | 2.3376 | 0 | 0 | 2.2511 | 0 | 2.1835 | 2.1835 | 4903.63 | 8.9924 | 1152.11 | 1135.49 | 1129.36 | 0 | 0 | 1129.31 | 323.107 | 0 | 0 | 0 | 1129.31 | 0 | 660 | 0 | 0
7928 | 2009-11-27 07:00 | 81 | 130 | 60 | 8.27 | 7.33 | 0 | 9.0732 | 123.716 | 68.0021 | 0 | 81 | 49.8811 | 75.5203 | 0.75891 | 15.8146 | 70.6747 | 0.0039612 | 14.4943 | 68.0591 | 0.0029849 | 80.0797 | 80.075 | 179827 | 9.8244 | 151779 | 163265 | 151302 | 0 | 0 | 151116 | 699.367 | 0 | 0 | 0 | 0 | 151116 | 699.367 | 146218 | 143294.1094
7929 | 2009-11-27 08:00 | 250 | 398 | 123 | 9.55 | 7.33 | 0 | 18.6808 | 134.184 | 55.2973 | 0 | 250 | 225.74 | 154.617 | 2.3423 | 184.833 | 144.696 | 0.012226 | 177.842 | 139.341 | 0.0092126 | 307.676 | 307.584 | 690745 | 15.5208 | 649152 | 675701 | 624001 | 0 | 0 | 621096 | 732.671 | 0 | 0 | 0 | 0 | 621096 | 732.671 | 610582 | 598370.4375
7930 | 2009-11-27 09:00 | 288 | 193 | 202 | 10.84 | 7.9 | 0 | 26.556 | 146.707 | 43.8487 | 0 | 288 | 138.727 | 225.175 | 2.6983 | 138.502 | 210.727 | 0.014084 | 135.825 | 202.929 | 0.010613 | 328.601 | 328.594 | 737938 | 16.9929 | 695289 | 720074 | 697253 | 0 | 0 | 693710 | 734.891 | 0 | 0 | 0 | 0 | 693710 | 734.891 | 682094 | 668452.1875
7931 | 2009-11-27 10:00 | 529 | 740 | 138 | 12.12 | 7.9 | 0 | 31.9641 | 161.496 | 34.936 | 0 | 529 | 605.49 | 182.688 | 4.9563 | 605.49 | 170.967 | 0.02587 | 598.835 | 164.639 | 0.019494 | 740.589 | 740.578 | 1663150 | 25.9874 | 1647650 | 1640570 | 1594340 | 0 | 0 | 1576030 | 733.883 | 0 | 0 | 0 | 0 | 1576030 | 733.883 | 1547150 | 1516203.5
7932 | 2009-11-27 11:00 | 584 | 839 | 114 | 14.45 | 7.9 | 0 | 34.169 | 177.978 | 30.8554 | 0 | 584 | 718.399 | 151.168 | 5.4716 | 718.399 | 141.469 | 0.02856 | 712.477 | 136.233 | 0.021521 | 823.27 | 823.264 | 1848840 | 29.8657 | 1842270 | 1804510 | 1757720 | 0 | 0 | 1734910 | 723.882 | 0 | 0 | 0 | 0 | 1734910 | 723.882 | 1701600 | 1667570.25
7933 | 2009-11-27 12:00 | 499 | 657 | 144 | 16.79 | 9.06 | 0 | 32.7939 | 194.667 | 33.43 | 0 | 499 | 547.007 | 189.973 | 4.6752 | 547.007 | 177.784 | 0.024403 | 541.585 | 171.204 | 0.018388 | 691.423 | 691.417 | 1552750 | 28.8309 | 1532300 | 1507260 | 1466950 | 0 | 0 | 1450900 | 721.794 | 0 | 0 | 0 | 0 | 1450900 | 721.794 | 1425650 | 1397141.75
7934 | 2009-11-27 13:00 | 450 | 760 | 93 | 19.13 | 9.06 | 0 | 28.0798 | 209.941 | 41.4347 | 0 | 450 | 568.614 | 125.027 | 4.2161 | 568.614 | 117.005 | 0.022007 | 559.122 | 112.675 | 0.016583 | 651.659 | 651.65 | 1463440 | 30.4783 | 1439220 | 1405470 | 1369120 | 0 | 0 | 1354830 | 713.807 | 0 | 0 | 0 | 0 | 1354830 | 713.807 | 1331980 | 1305344.375
7935 | 2009-11-27 14:00 | 357 | 636 | 132 | 18.95 | 9.06 | 0 | 20.7147 | 222.994 | 52.432 | 0 | 357 | 387.836 | 165.462 | 3.3448 | 372.822 | 154.845 | 0.017459 | 360.889 | 149.115 | 0.013156 | 494.716 | 494.695 | 1110960 | 27.565 | 1074650 | 1062410 | 1029520 | 0 | 0 | 1021440 | 715.88 | 0 | 0 | 0 | 0 | 1021440 | 715.88 | 1005230 | 985129.1875
7936 | 2009-11-27 15:00 | 92 | 83 | 75 | 18.78 | 9.28 | 0 | 11.4568 | 233.897 | 64.9077 | 0 | 92 | 36.2955 | 85.2851 | 0.86197 | 27.9176 | 79.813 | 0.0044992 | 26.0219 | 76.8592 | 0.0033902 | 99.7979 | 99.7775 | 224076 | 20.4941 | 192820 | 197113 | 187084 | 0 | 0 | 186776 | 674.245 | 0 | 0 | 0 | 0 | 186776 | 674.245 | 181537 | 177906.5625
7937 | 2009-11-27 16:00 | 8 | 26 | 7 | 18.6 | 9.28 | 0 | 0.91723 | 243.131 | 78.1422 | 0 | 8 | 2.3619 | 7.2103 | 0.074954 | 0.40352 | 6.7477 | 0.00039123 | 0.32551 | 6.498 | 0.0002948 | 6.6191 | 6.6181 | 14862.9 | 18.7137 | 7609.82 | 7814.09 | 7563.53 | 0 | 0 | 7562.69 | 522.364 | 0 | 0 | 0 | 7437.57 | 125.117 | 660 | 120.365 | 117.9579
7938 | 2009-11-27 17:00 | 0 | 0 | 0 | 17.34 | 9.28 | 0
7939 | 2009-11-27 18:00 | 0 | 0 | 0 | 16.07 | 12.21 | 0
7940 | 2009-11-27 19:00 | 0 | 0 | 0 | 14.81 | 12.21 | 0
7941 | 2009-11-27 20:00 | 0 | 0 | 0 | 13.49 | 12.21 | 0
7942 | 2009-11-27 21:00 | 0 | 0 | 0 | 12.18 | 8.8 | 0
7943 | 2009-11-27 22:00 | 0 | 0 | 0 | 10.86 | 8.8 | 0
7944 | 2009-11-27 23:00 | 0 | 0 | 0 | 9.98 | 8.8 | 0
7945 | 2009-11-28 | 0 | 0 | 0 | 9.1 | 9.22 | 0
7946 | 2009-11-28 01:00 | 0 | 0 | 0 | 8.22 | 9.22 | 0
7947 | 2009-11-28 02:00 | 0 | 0 | 0 | 7.35 | 9.22 | 0
7948 | 2009-11-28 03:00 | 0 | 0 | 0 | 6.48 | 9.54 | 0
7949 | 2009-11-28 04:00 | 0 | 0 | 0 | 5.61 | 9.54 | 0
7950 | 2009-11-28 05:00 | 0 | 0 | 0 | 4.98 | 9.54 | 0
7951 | 2009-11-28 06:00 | 3 | 19 | 2 | 4.35 | 8.76 | 0 | -1.8672 | 114.876 | 81.48 | 0 | 3 | 1.7029 | 2.4835 | 0.028108 | 0 | 2.3241 | 0 | 0 | 2.2381 | 0 | 2.171 | 2.1709 | 4875.27 | 4.3885 | 1139.04 | 1116.69 | 1110.91 | 0 | 0 | 1110.86 | 320.507 | 0 | 0 | 0 | 1110.86 | 0 | 660 | 0 | 0
7952 | 2009-11-28 07:00 | 74 | 100 | 58 | 3.72 | 8.76 | 0 | 8.8961 | 123.793 | 68.1373 | 0 | 74 | 38.5283 | 67.3206 | 0.69332 | 11.8065 | 63.0012 | 0.0036189 | 10.8116 | 60.6696 | 0.0027269 | 69.3394 | 69.32 | 155676 | 4.9499 | 129444 | 142525 | 133140 | 0 | 0 | 133001 | 710.691 | 0 | 0 | 0 | 0 | 133001 | 710.691 | 128399 | 125830.7109
7953 | 2009-11-28 08:00 | 98 | 0 | 98 | 4.65 | 8.76 | 0 | 18.495 | 134.237 | 55.4516 | 0 | 98 | 0 | 93.9218 | 0.91818 | 0 | 87.8956 | 0.0047926 | 0 | 84.6426 | 0.0036113 | 82.1068 | 82.0993 | 184374 | 6.1067 | 155619 | 170360 | 165218 | 0 | 0 | 165006 | 713.067 | 0 | 0 | 0 | 0 | 165006 | 713.067 | 159584 | 156392.7812
7954 | 2009-11-28 09:00 | 150 | 3 | 149 | 5.59 | 5.41 | 0 | 26.3645 | 146.725 | 44.0239 | 0 | 150 | 1.6192 | 144.017 | 1.4054 | 1.6155 | 134.777 | 0.0073356 | 1.5839 | 129.789 | 0.0055275 | 127.437 | 127.435 | 286186 | 8.3877 | 251353 | 271546 | 263437 | 0 | 0 | 262919 | 727.377 | 0 | 0 | 0 | 0 | 262919 | 727.377 | 255596 | 250484.25
7955 | 2009-11-28 10:00 | 184 | 8 | 180 | 6.53 | 5.41 | 0 | 31.7741 | 161.464 | 35.1271 | 0 | 184 | 6.2129 | 174.358 | 1.7239 | 6.2129 | 163.171 | 0.0089984 | 6.1437 | 157.132 | 0.0067805 | 158.384 | 158.373 | 355665 | 10.0069 | 317962 | 340591 | 330458 | 0 | 0 | 329651 | 731.177 | 0 | 0 | 0 | 0 | 329651 | 731.177 | 321783 | 315346.9375
7956 | 2009-11-28 11:00 | 560 | 590 | 231 | 6.9 | 5.41 | 0 | 33.992 | 177.889 | 31.0344 | 0 | 560 | 504.235 | 283.223 | 5.2468 | 504.235 | 265.05 | 0.027386 | 500.023 | 255.241 | 0.020636 | 732.626 | 732.617 | 1645270 | 22.9837 | 1628960 | 1642420 | 1598880 | 0 | 0 | 1580820 | 741.042 | 0 | 0 | 0 | 0 | 1580820 | 741.042 | 1551510 | 1520475.875
7957 | 2009-11-28 12:00 | 200 | 28 | 185 | 7.27 | 5.38 | 0 | 32.6417 | 194.529 | 33.5568 | 0 | 200 | 23.1747 | 188.199 | 1.8738 | 23.1747 | 176.124 | 0.0097808 | 22.943 | 169.606 | 0.0073701 | 186.779 | 186.768 | 419434 | 11.3782 | 379772 | 403976 | 392534 | 0 | 0 | 391396 | 731.499 | 0 | 0 | 0 | 0 | 391396 | 731.499 | 383602 | 375929.9062
7958 | 2009-11-28 13:00 | 100 | 0 | 100 | 7.64 | 5.38 | 0 | 27.9586 | 209.773 | 41.5025 | 0 | 100 | 0 | 93.1171 | 0.93692 | 0 | 87.1425 | 0.0048904 | 0 | 83.9174 | 0.003685 | 81.4035 | 81.399 | 182802 | 9.4305 | 154164 | 166247 | 161432 | 0 | 0 | 161223 | 702.443 | 0 | 0 | 0 | 0 | 161223 | 702.443 | 156041 | 152920.5938
7959 | 2009-11-28 14:00 | 162 | 123 | 119 | 7.78 | 5.38 | 0 | 20.624 | 222.815 | 52.4555 | 0 | 162 | 74.3918 | 130.348 | 1.5178 | 71.5119 | 121.984 | 0.0079225 | 69.2199 | 117.47 | 0.0059698 | 181.095 | 181.08 | 406658 | 11.7631 | 367356 | 390170 | 377886 | 0 | 0 | 376829 | 730.528 | 0 | 0 | 0 | 0 | 376829 | 730.528 | 368999 | 361619.0938
7960 | 2009-11-28 15:00 | 177 | 362 | 105 | 7.93 | 4.11 | 0 | 11.3923 | 233.714 | 64.8998 | 0 | 177 | 154.626 | 130.707 | 1.6583 | 118.935 | 122.32 | 0.008656 | 110.863 | 117.793 | 0.0065225 | 221.803 | 221.737 | 497967 | 13.2284 | 457909 | 481754 | 442072 | 0 | 0 | 440586 | 732.073 | 0 | 0 | 0 | 0 | 440586 | 732.073 | 432288 | 423641.9375
7961 | 2009-11-28 16:00 | 16 | 112 | 10 | 8.07 | 4.11 | 0 | 0.87372 | 242.946 | 78.1108 | 0 | 16 | 14.2082 | 13.395 | 0.14991 | 2.3962 | 12.5355 | 0.00078247 | 1.9345 | 12.0716 | 0.0005896 | 13.5864 | 13.5813 | 30501.8 | 8.3945 | 19719.7 | 21401.6 | 19551.3 | 0 | 0 | 19547 | 606.879 | 0 | 0 | 0 | 1269.86 | 18277.2 | 660 | 17602.8 | 17250.7715
7962 | 2009-11-28 17:00 | 0 | 0 | 0 | 7.89 | 4.11 | 0
7963 | 2009-11-28 18:00 | 0 | 0 | 0 | 7.71 | 6.52 | 0
7964 | 2009-11-28 19:00 | 0 | 0 | 0 | 7.53 | 6.52 | 0
7965 | 2009-11-28 20:00 | 0 | 0 | 0 | 7.01 | 6.52 | 0
7966 | 2009-11-28 21:00 | 0 | 0 | 0 | 6.48 | 5.4 | 0
7967 | 2009-11-28 22:00 | 0 | 0 | 0 | 5.96 | 5.4 | 0
7968 | 2009-11-28 23:00 | 0 | 0 | 0 | 5.76 | 5.4 | 0
7969 | 2009-11-29 | 0 | 0 | 0 | 5.56 | 9.45 | 0
7970 | 2009-11-29 01:00 | 0 | 0 | 0 | 5.36 | 9.45 | 0
7971 | 2009-11-29 02:00 | 0 | 0 | 0 | 4.96 | 9.45 | 0
7972 | 2009-11-29 03:00 | 0 | 0 | 0 | 4.56 | 10.57 | 0
7973 | 2009-11-29 04:00 | 0 | 0 | 0 | 4.16 | 10.57 | 0
7974 | 2009-11-29 05:00 | 0 | 0 | 0 | 4.03 | 10.57 | 0
7975 | 2009-11-29 06:00 | 5 | 116 | 1 | 3.9 | 12.87 | 0 | -2.0334 | 114.964 | 81.5995 | 0 | 5 | 6.7169 | 1.3676 | 0.046846 | 0 | 1.2798 | 0 | 0 | 1.2325 | 0 | 1.1955 | 1.1955 | 2684.69 | 3.9165 | 348.62 | 340.017 | 338.461 | 0 | 0 | 338.447 | 175.215 | 0 | 0 | 0 | 338.447 | 0 | 660 | 0 | 0
7976 | 2009-11-29 07:00 | 136 | 648 | 37 | 3.77 | 12.87 | 0 | 8.7217 | 123.863 | 68.2727 | 0 | 136 | 241.691 | 55.0047 | 1.2742 | 71.4349 | 51.4755 | 0.006651 | 65.3582 | 49.5704 | 0.0050116 | 111.486 | 111.407 | 250202 | 5.311 | 221884 | 241319 | 193598 | 0 | 0 | 193187 | 690.717 | 0 | 0 | 0 | 0 | 193187 | 690.717 | 187782 | 184026.3438
7977 | 2009-11-29 08:00 | 317 | 843 | 52 | 5.05 | 12.87 | 0 | 18.3129 | 134.283 | 55.605 | 0 | 317 | 476.431 | 70.734 | 2.97 | 387.205 | 66.1956 | 0.015503 | 372.293 | 63.7457 | 0.011681 | 422.969 | 423.155 | 950277 | 10.9031 | 914570 | 967285 | 865189 | 0 | 0 | 859670 | 750.299 | 0 | 0 | 0 | 0 | 859670 | 750.299 | 844629 | 827736.6875
7978 | 2009-11-29 09:00 | 467 | 923 | 61 | 6.33 | 8.92 | 0 | 26.1776 | 146.736 | 44.1966 | 0 | 467 | 659.818 | 80.9627 | 4.3754 | 657.873 | 75.7679 | 0.022838 | 644.887 | 72.9638 | 0.017209 | 696.332 | 696.311 | 1563720 | 18.5621 | 1543880 | 1585120 | 1535590 | 0 | 0 | 1519410 | 752.491 | 0 | 0 | 0 | 0 | 1519410 | 752.491 | 1491020 | 1461195
7979 | 2009-11-29 10:00 | 567 | 960 | 66 | 7.61 | 8.92 | 0 | 31.5898 | 161.427 | 35.3136 | 0 | 567 | 780.432 | 86.6847 | 5.3124 | 780.432 | 81.1228 | 0.027729 | 771.633 | 78.1205 | 0.020894 | 824.281 | 824.274 | 1851120 | 22.09 | 1844660 | 1866630 | 1815060 | 0 | 0 | 1792350 | 749.506 | 0 | 0 | 0 | 0 | 1792350 | 749.506 | 1756080 | 1720954.75
7980 | 2009-11-29 11:00 | 607 | 972 | 68 | 8.85 | 8.92 | 0 | 33.8216 | 177.797 | 31.2071 | 0 | 607 | 828.242 | 88.9917 | 5.6871 | 828.242 | 83.2818 | 0.029685 | 821.236 | 80.1996 | 0.022368 | 874.414 | 874.409 | 1963700 | 24.2107 | 1962940 | 1969030 | 1912420 | 0 | 0 | 1886970 | 745.07 | 0 | 0 | 0 | 0 | 1886970 | 745.07 | 1848120 | 1811157.875
7981 | 2009-11-29 12:00 | 582 | 964 | 66 | 10.09 | 8.2 | 0 | 32.4965 | 194.39 | 33.677 | 0 | 582 | 799.263 | 86.6145 | 5.4529 | 799.263 | 81.0572 | 0.028462 | 791.204 | 78.0573 | 0.021447 | 843.204 | 843.199 | 1893610 | 25.584 | 1889280 | 1884390 | 1832790 | 0 | 0 | 1808850 | 737.072 | 0 | 0 | 0 | 0 | 1808850 | 737.072 | 1772990 | 1737528.25
7982 | 2009-11-29 13:00 | 496 | 936 | 60 | 11.33 | 8.2 | 0 | 27.8444 | 209.606 | 41.5645 | 0 | 496 | 698.435 | 79.5491 | 4.6471 | 698.435 | 74.4451 | 0.024257 | 686.683 | 71.6899 | 0.018278 | 735.64 | 735.636 | 1652050 | 24.8474 | 1636040 | 1636850 | 1594310 | 0 | 0 | 1576120 | 736.502 | 0 | 0 | 0 | 0 | 1576120 | 736.502 | 1547150 | 1516203.125
7983 | 2009-11-29 14:00 | 352 | 865 | 49 | 11.66 | 8.2 | 0 | 20.54 | 222.637 | 52.4737 | 0 | 352 | 526.035 | 66.573 | 3.298 | 485.306 | 62.3016 | 0.017214 | 469.735 | 59.9959 | 0.012971 | 513.852 | 513.79 | 1153840 | 21.101 | 1119270 | 1137060 | 1083590 | 0 | 0 | 1075120 | 737.969 | 0 | 0 | 0 | 0 | 1075120 | 737.969 | 1056780 | 1035649
7984 | 2009-11-29 15:00 | 176 | 667 | 45 | 12 | 7.17 | 0 | 11.3342 | 233.534 | 64.8873 | 0 | 176 | 282.889 | 64.9173 | 1.649 | 217.591 | 60.7521 | 0.0086071 | 202.835 | 58.5037 | 0.0064856 | 253.505 | 253.412 | 569105 | 16.9694 | 530863 | 547878 | 483680 | 0 | 0 | 481746 | 722.79 | 0 | 0 | 0 | 0 | 481746 | 722.79 | 473242 | 463777.2812
7985 | 2009-11-29 16:00 | 16 | 205 | 4 | 12.33 | 7.17 | 0 | 0.83631 | 242.764 | 78.0755 | 0 | 16 | 28.4997 | 6.0446 | 0.14991 | 4.7369 | 5.6567 | 0.00078247 | 3.8274 | 5.4474 | 0.0005896 | 8.9972 | 8.989 | 20190.9 | 12.5063 | 11991.6 | 12683.5 | 9302.56 | 0 | 0 | 9300.87 | 527.767 | 0 | 0 | 0 | 3898.65 | 5402.22 | 660 | 5199.1 | 5095.1157
7986 | 2009-11-29 17:00 | 0 | 0 | 0 | 11.78 | 7.17 | 0
7987 | 2009-11-29 18:00 | 0 | 0 | 0 | 11.23 | 10.5 | 0
7988 | 2009-11-29 19:00 | 0 | 0 | 0 | 10.68 | 10.5 | 0
7989 | 2009-11-29 20:00 | 0 | 0 | 0 | 10.22 | 10.5 | 0
7990 | 2009-11-29 21:00 | 0 | 0 | 0 | 9.77 | 10.55 | 0
7991 | 2009-11-29 22:00 | 0 | 0 | 0 | 9.32 | 10.55 | 0
7992 | 2009-11-29 23:00 | 0 | 0 | 0 | 8.68 | 10.55 | 0
7993 | 2009-11-30 | 0 | 0 | 0 | 8.04 | 10.6 | 0
7994 | 2009-11-30 01:00 | 0 | 0 | 0 | 7.4 | 10.6 | 0
7995 | 2009-11-30 02:00 | 0 | 0 | 0 | 6.9 | 10.6 | 0
7996 | 2009-11-30 03:00 | 0 | 0 | 0 | 6.4 | 7.51 | 0
7997 | 2009-11-30 04:00 | 0 | 0 | 0 | 5.91 | 7.51 | 0
7998 | 2009-11-30 05:00 | 0 | 0 | 0 | 5.19 | 7.51 | 0
7999 | 2009-11-30 06:00 | 5 | 110 | 2 | 4.47 | 8.75 | 0 | -2.1976 | 115.044 | 81.7197 | 0 | 5 | 4.9661 | 2.7506 | 0.046846 | 0 | 2.5741 | 0 | 0 | 2.4788 | 0 | 2.4045 | 2.4043 | 5399.54 | 4.5127 | 1390.07 | 1367.75 | 1360.09 | 0 | 0 | 1360.04 | 355.239 | 0 | 0 | 0 | 1360.04 | 0 | 660 | 0 | 0
8000 | 2009-11-30 07:00 | 129 | 639 | 33 | 3.75 | 8.75 | 0 | 8.5501 | 123.926 | 68.4082 | 0 | 129 | 237.617 | 50.7994 | 1.2086 | 67.5951 | 47.54 | 0.0063086 | 61.7906 | 45.7806 | 0.0047537 | 104.349 | 104.275 | 234191 | 5.6013 | 206815 | 224377 | 180535 | 0 | 0 | 180165 | 687.727 | 0 | 0 | 0 | 110.573 | 180055 | 690.728 | 174863 | 171366.1094
8001 | 2009-11-30 08:00 | 303 | 825 | 46 | 5.06 | 8.75 | 0 | 18.1344 | 134.322 | 55.7573 | 0 | 303 | 464.626 | 63.204 | 2.8389 | 376.04 | 59.1487 | 0.014818 | 361.428 | 56.9596 | 0.011166 | 405.846 | 405.707 | 911091 | 12.2629 | 874836 | 919511 | 820770 | 0 | 0 | 815724 | 746.304 | 0 | 0 | 0 | 0 | 815724 | 746.304 | 801562 | 785530.875
8002 | 2009-11-30 09:00 | 434 | 830 | 71 | 6.36 | 7.68 | 0 | 25.9955 | 146.742 | 44.3668 | 0 | 434 | 592.06 | 98.9982 | 4.0662 | 589.943 | 92.6462 | 0.021224 | 578.178 | 89.2175 | 0.015993 | 647.389 | 647.352 | 1453770 | 18.6511 | 1429300 | 1467150 | 1416420 | 0 | 0 | 1402530 | 749.954 | 0 | 0 | 0 | 0 | 1402530 | 749.954 | 1376900 | 1349367
8003 | 2009-11-30 10:00 | 564 | 959 | 66 | 7.66 | 7.68 | 0 | 31.4113 | 161.386 | 35.4954 | 0 | 564 | 777.955 | 86.7679 | 5.2842 | 777.955 | 81.2007 | 0.027582 | 769.076 | 78.1955 | 0.020784 | 821.874 | 821.871 | 1845710 | 23.2646 | 1838990 | 1851930 | 1798980 | 0 | 0 | 1776430 | 745.73 | 0 | 0 | 0 | 0 | 1776430 | 745.73 | 1741000 | 1706178
8004 | 2009-11-30 11:00 | 604 | 971 | 68 | 9.2 | 7.68 | 0 | 33.6579 | 177.702 | 31.3733 | 0 | 604 | 825.707 | 89.0721 | 5.659 | 825.707 | 83.3571 | 0.029538 | 818.637 | 80.2721 | 0.022258 | 871.963 | 871.963 | 1958210 | 25.7557 | 1957180 | 1950700 | 1896770 | 0 | 0 | 1871250 | 737.637 | 0 | 0 | 0 | 0 | 1871250 | 737.637 | 1833430 | 1796757.375
8005 | 2009-11-30 12:00 | 580 | 964 | 66 | 10.73 | 7.08 | 0 | 32.3583 | 194.25 | 33.7906 | 0 | 580 | 798.137 | 86.6928 | 5.4341 | 798.137 | 81.1304 | 0.028364 | 790.025 | 78.1279 | 0.021373 | 842.129 | 842.125 | 1891200 | 27.3388 | 1886750 | 1868060 | 1817090 | 0 | 0 | 1793330 | 732.814 | 0 | 0 | 0 | 0 | 1793330 | 732.814 | 1758030 | 1722868.125
8006 | 2009-11-30 13:00 | 495 | 935 | 61 | 12.27 | 7.08 | 0 | 27.7372 | 209.441 | 41.6204 | 0 | 495 | 697.1 | 80.8793 | 4.6378 | 697.1 | 75.6899 | 0.024208 | 685.33 | 72.8887 | 0.018241 | 735.49 | 735.485 | 1651720 | 26.7756 | 1635700 | 1623230 | 1578160 | 0 | 0 | 1560110 | 731.708 | 0 | 0 | 0 | 0 | 1560110 | 731.708 | 1531750 | 1501112
8007 | 2009-11-30 14:00 | 356 | 868 | 53 | 12.75 | 7.08 | 0 | 20.4627 | 222.462 | 52.4868 | 0 | 356 | 527.779 | 71.732 | 3.3354 | 486.916 | 67.1295 | 0.01741 | 471.281 | 64.6451 | 0.013119 | 519.861 | 519.818 | 1167380 | 23.0021 | 1133200 | 1141900 | 1088290 | 0 | 0 | 1079610 | 732.555 | 0 | 0 | 0 | 0 | 1079610 | 732.555 | 1061450 | 1040220.1875
8008 | 2009-11-30 15:00 | 176 | 673 | 44 | 13.24 | 5.96 | 0 | 11.2825 | 233.357 | 64.8702 | 0 | 176 | 286.52 | 63.9229 | 1.649 | 220.384 | 59.8215 | 0.0086071 | 205.455 | 57.6076 | 0.0064856 | 255.177 | 255.12 | 572944 | 18.6455 | 534757 | 547622 | 482599 | 0 | 0 | 480615 | 710.934 | 0 | 0 | 0 | 0 | 480615 | 710.934 | 472491 | 463041.2812
8009 | 2009-11-30 16:00 | 16 | 206 | 4 | 13.73 | 5.96 | 0 | 0.80498 | 242.586 | 78.0361 | 0 | 16 | 28.5924 | 6.0486 | 0.14991 | 4.7364 | 5.6605 | 0.00078247 | 3.8308 | 5.451 | 0.0005896 | 9.0039 | 8.9973 | 20209.7 | 13.9206 | 12008 | 12625.7 | 9249.52 | 0 | 0 | 9247.85 | 532.648 | 0 | 0 | 0 | 4153.91 | 5093.94 | 660 | 4902.33 | 4804.2871
8010 | 2009-11-30 17:00 | 0 | 0 | 0 | 13.14 | 5.96 | 0
8011 | 2009-11-30 18:00 | 0 | 0 | 0 | 12.55 | 6.69 | 0
8012 | 2009-11-30 19:00 | 0 | 0 | 0 | 11.97 | 6.69 | 0
8013 | 2009-11-30 20:00 | 0 | 0 | 0 | 11.42 | 6.69 | 0
8014 | 2009-11-30 21:00 | 0 | 0 | 0 | 10.65 | 6.8 | 0
8015 | 2009-11-30 22:00 | 0 | 0 | 0 | 9.38 | 6.42 | 0
8016 | 2009-11-30 23:00 | 0 | 0 | 0 | 8.11 | 6.03 | 0
8017 | 2006-12-01 | 0 | 0 | 0 | 6.85 | 5.65 | 0
8018 | 2006-12-01 01:00 | 0 | 0 | 0 | 5.58 | 5.26 | 0
8019 | 2006-12-01 02:00 | 0 | 0 | 0 | 4.31 | 4.88 | 0
8020 | 2006-12-01 03:00 | 0 | 0 | 0 | 2.54 | 3.99 | 0
8021 | 2006-12-01 04:00 | 0 | 0 | 0 | 2.16 | 3.99 | 0
8022 | 2006-12-01 05:00 | 0 | 0 | 0 | 1.89 | 3.99 | 0
8023 | 2006-12-01 06:00 | 4 | 94 | 1 | 1.63 | 1.76 | 0 | -2.3174 | 115.1 | 81.8086 | 0 | 4 | 4.9131 | 1.3562 | 0.037477 | 0 | 1.2692 | 0 | 0 | 1.2222 | 0 | 1.1855 | 1.1854 | 2662.24 | 1.6631 | 342.804 | 333.43 | 331.927 | 0 | 0 | 331.912 | 173.547 | 0 | 0 | 0 | 331.912 | 0 | 660 | 0 | 0
8024 | 2006-12-01 07:00 | 116 | 567 | 32 | 1.36 | 1.76 | 0 | 8.4251 | 123.968 | 68.5079 | 0 | 116 | 210.047 | 49.7238 | 1.0868 | 57.991 | 46.5334 | 0.0056729 | 52.9764 | 44.8112 | 0.0042746 | 94.8581 | 94.778 | 212862 | 4.0064 | 186086 | 203048 | 164636 | 0 | 0 | 164332 | 681.328 | 0 | 0 | 0 | 5.0256 | 164327 | 681.65 | 159523 | 156332.9062
8025 | 2006-12-01 08:00 | 306 | 802 | 58 | 2.74 | 1.76 | 0 | 18.0049 | 134.348 | 55.8689 | 0 | 306 | 450.18 | 82.0242 | 2.867 | 363.259 | 76.7614 | 0.014965 | 349.051 | 73.9205 | 0.011276 | 410.294 | 410.198 | 921177 | 14.1936 | 884703 | 920808 | 825589 | 0 | 0 | 820430 | 740.461 | 0 | 0 | 0 | 0 | 820430 | 740.461 | 806411 | 790282.8125
8026 | 2006-12-01 09:00 | 437 | 877 | 55 | 4.11 | 3.23 | 0 | 25.8639 | 146.743 | 44.4907 | 0 | 437 | 624.675 | 73.5689 | 4.0944 | 622.079 | 68.8486 | 0.021371 | 609.581 | 66.3005 | 0.016104 | 655.621 | 655.593 | 1472290 | 20.7099 | 1448620 | 1474250 | 1418240 | 0 | 0 | 1404050 | 742.216 | 0 | 0 | 0 | 0 | 1404050 | 742.216 | 1378850 | 1351271.75
8027 | 2006-12-01 10:00 | 539 | 926 | 60 | 5.49 | 3.23 | 0 | 31.2828 | 161.353 | 35.6269 | 0 | 539 | 749.802 | 79.3188 | 5.05 | 749.802 | 74.2296 | 0.026359 | 741.169 | 71.4824 | 0.019862 | 788.291 | 788.289 | 1770310 | 25.4499 | 1759880 | 1756190 | 1705140 | 0 | 0 | 1684460 | 738.179 | 0 | 0 | 0 | 0 | 1684460 | 738.179 | 1652300 | 1619257.25
8028 | 2006-12-01 11:00 | 601 | 971 | 66 | 7.51 | 3.23 | 0 | 33.5406 | 177.631 | 31.4924 | 0 | 601 | 825.659 | 86.6399 | 5.6309 | 825.659 | 81.0809 | 0.029391 | 818.528 | 78.0802 | 0.022147 | 869.731 | 869.731 | 1953190 | 29.532 | 1951900 | 1914650 | 1865970 | 0 | 0 | 1840310 | 723.957 | 0 | 0 | 0 | 0 | 1840310 | 723.957 | 1803660 | 1767587.5
8029 | 2006-12-01 12:00 | 578 | 963 | 66 | 9.53 | 3.1 | 0 | 32.2601 | 194.147 | 33.8709 | 0 | 578 | 796.441 | 86.7492 | 5.4154 | 796.441 | 81.1832 | 0.028267 | 788.302 | 78.1787 | 0.021299 | 840.507 | 840.503 | 1887560 | 30.9958 | 1882930 | 1835340 | 1786140 | 0 | 0 | 1762350 | 719.892 | 0 | 0 | 0 | 0 | 1762350 | 719.892 | 1728270 | 1693707.5
8030 | 2006-12-01 13:00 | 481 | 922 | 54 | 11.55 | 3.1 | 0 | 27.6617 | 209.32 | 41.6587 | 0 | 481 | 687.172 | 72.1067 | 4.5066 | 687.172 | 67.4802 | 0.023523 | 675.542 | 64.9828 | 0.017725 | 718.326 | 718.323 | 1613170 | 29.8954 | 1595390 | 1562100 | 1521480 | 0 | 0 | 1504090 | 718.645 | 0 | 0 | 0 | 0 | 1504090 | 718.645 | 1477770 | 1448214.375
8031 | 2006-12-01 14:00 | 342 | 852 | 45 | 12.2 | 3.1 | 0 | 20.4091 | 222.335 | 52.4939 | 0 | 342 | 518.544 | 61.5668 | 3.2043 | 478.396 | 57.6165 | 0.016725 | 463.028 | 55.4842 | 0.012603 | 502.969 | 502.963 | 1129530 | 25.0453 | 1094260 | 1092720 | 1040730 | 0 | 0 | 1032600 | 723.696 | 0 | 0 | 0 | 0 | 1032600 | 723.696 | 1015790 | 995473.375
8032 | 2006-12-01 15:00 | 172 | 645 | 46 | 12.85 | 4.89 | 0 | 11.2476 | 233.229 | 64.8554 | 0 | 172 | 274.485 | 66.0896 | 1.6115 | 211.127 | 61.8492 | 0.0084115 | 196.839 | 59.5602 | 0.0063383 | 248.713 | 248.604 | 558306 | 18.4952 | 519997 | 532823 | 470077 | 0 | 0 | 468204 | 711.827 | 0 | 0 | 0 | 0 | 468204 | 711.827 | 460195 | 450991.375
8033 | 2006-12-01 16:00 | 15 | 197 | 4 | 13.49 | 4.89 | 0 | 0.78494 | 242.457 | 78.0052 | 0 | 15 | 26.2765 | 6.0523 | 0.14054 | 4.3521 | 5.664 | 0.00073356 | 3.5227 | 5.4544 | 0.00055276 | 8.7082 | 8.7015 | 19544.9 | 13.6876 | 11458.7 | 12052.2 | 9011.35 | 0 | 0 | 9009.77 | 523.641 | 0 | 0 | 0 | 4214.16 | 4795.61 | 660 | 4615.11 | 4522.8091
8034 | 2006-12-01 17:00 | 0 | 0 | 0 | 12.7 | 4.89 | 0
8035 | 2006-12-01 18:00 | 0 | 0 | 0 | 11.9 | 9.27 | 0
8036 | 2006-12-01 19:00 | 0 | 0 | 0 | 11.11 | 9.27 | 0
8037 | 2006-12-01 20:00 | 0 | 0 | 0 | 10.45 | 9.27 | 0
8038 | 2006-12-01 21:00 | 0 | 0 | 0 | 9.79 | 5.05 | 0
8039 | 2006-12-01 22:00 | 0 | 0 | 0 | 9.14 | 5.05 | 0
8040 | 2006-12-01 23:00 | 0 | 0 | 0 | 8.6 | 5.05 | 0
8041 | 2006-12-02 | 0 | 0 | 0 | 8.05 | 9.99 | 0
8042 | 2006-12-02 01:00 | 0 | 0 | 0 | 7.51 | 9.99 | 0
8043 | 2006-12-02 02:00 | 0 | 0 | 0 | 6.74 | 9.99 | 0
8044 | 2006-12-02 03:00 | 0 | 0 | 0 | 5.96 | 7.68 | 0
8045 | 2006-12-02 04:00 | 0 | 0 | 0 | 5.18 | 7.68 | 0
8046 | 2006-12-02 05:00 | 0 | 0 | 0 | 4.6 | 7.68 | 0
8047 | 2006-12-02 06:00 | 4 | 99 | 1 | 4.02 | 9.4 | 0 | -2.4777 | 115.168 | 81.9301 | 0 | 4 | 4.8407 | 1.3496 | 0.037477 | 0 | 1.263 | 0 | 0 | 1.2163 | 0 | 1.1798 | 1.1797 | 2649.39 | 4.0401 | 339.535 | 331.201 | 329.679 | 0 | 0 | 329.664 | 172.949 | 0 | 0 | 0 | 329.664 | 0 | 660 | 0 | 0
8048 | 2006-12-02 07:00 | 122 | 626 | 31 | 3.44 | 9.4 | 0 | 8.2586 | 124.02 | 68.6431 | 0 | 122 | 230.715 | 48.6484 | 1.143 | 60.9766 | 45.527 | 0.0059663 | 55.6536 | 43.8421 | 0.0044957 | 96.5151 | 96.4162 | 216540 | 5.0841 | 190024 | 206793 | 164320 | 0 | 0 | 163979 | 657.228 | 0 | 0 | 0 | 1087.01 | 162892 | 677.98 | 158181 | 155017.6562
8049 | 2006-12-02 08:00 | 298 | 829 | 44 | 4.81 | 9.4 | 0 | 17.8331 | 134.376 | 56.0191 | 0 | 298 | 463.566 | 60.7938 | 2.792 | 372.616 | 56.8931 | 0.014573 | 357.913 | 54.7876 | 0.010981 | 400.33 | 400.221 | 898760 | 11.6345 | 862442 | 908881 | 807609 | 0 | 0 | 802775 | 752.58 | 0 | 0 | 0 | 0 | 802775 | 752.58 | 788533 | 772762.125
8050 | 2006-12-02 09:00 | 438 | 893 | 52 | 6.19 | 9.05 | 0 | 25.6902 | 146.738 | 44.6561 | 0 | 438 | 633.386 | 69.8366 | 4.1037 | 630.218 | 65.3557 | 0.02142 | 617.431 | 62.937 | 0.01614 | 659.972 | 659.948 | 1482070 | 17.69 | 1458830 | 1503190 | 1444240 | 0 | 0 | 1429890 | 752.371 | 0 | 0 | 0 | 0 | 1429890 | 752.371 | 1403540 | 1375470.75
8051 | 2006-12-02 10:00 | 535 | 883 | 80 | 7.57 | 9.05 | 0 | 31.1146 | 161.303 | 35.8003 | 0 | 535 | 714.139 | 110.975 | 5.0125 | 714.139 | 103.855 | 0.026164 | 705.821 | 100.011 | 0.019715 | 781.677 | 781.67 | 1755430 | 21.1911 | 1744290 | 1771670 | 1722310 | 0 | 0 | 1701850 | 749.493 | 0 | 0 | 0 | 0 | 1701850 | 749.493 | 1668360 | 1634996
8052 | 2006-12-02 11:00 | 549 | 794 | 113 | 8.84 | 9.05 | 0 | 33.3885 | 177.532 | 31.6473 | 0 | 549 | 674.46 | 154.946 | 5.1437 | 674.46 | 145.004 | 0.026848 | 668.57 | 139.637 | 0.020231 | 783.98 | 783.975 | 1760610 | 22.5012 | 1749710 | 1767660 | 1717930 | 0 | 0 | 1697470 | 747.615 | 0 | 0 | 0 | 0 | 1697470 | 747.615 | 1664270 | 1630984.75
8053 | 2006-12-02 12:00 | 565 | 906 | 85 | 10.11 | 5.74 | 0 | 32.1342 | 194.007 | 33.9728 | 0 | 565 | 748.379 | 117.263 | 5.2936 | 748.379 | 109.739 | 0.027631 | 740.677 | 105.678 | 0.02082 | 820.984 | 820.979 | 1843710 | 27.7532 | 1836880 | 1815430 | 1766180 | 0 | 0 | 1743530 | 730.221 | 0 | 0 | 0 | 0 | 1743530 | 730.221 | 1709810 | 1675618.5
8054 | 2006-12-02 13:00 | 495 | 940 | 61 | 11.38 | 5.74 | 0 | 27.5666 | 209.157 | 41.7043 | 0 | 495 | 700.161 | 81.0073 | 4.6378 | 700.161 | 75.8097 | 0.024208 | 688.278 | 73.0041 | 0.018241 | 738.461 | 738.454 | 1658380 | 27.2497 | 1642660 | 1626840 | 1581920 | 0 | 0 | 1563690 | 729.487 | 0 | 0 | 0 | 0 | 1563690 | 729.487 | 1535310 | 1504602.625
8055 | 2006-12-02 14:00 | 347 | 867 | 46 | 11.6 | 5.74 | 0 | 20.3435 | 222.165 | 52.498 | 0 | 347 | 527.102 | 62.9245 | 3.2511 | 486.291 | 58.8872 | 0.01697 | 470.667 | 56.7078 | 0.012787 | 511.566 | 511.545 | 1148800 | 22.5933 | 1114090 | 1124480 | 1070980 | 0 | 0 | 1062590 | 733.082 | 0 | 0 | 0 | 0 | 1062590 | 733.082 | 1044740 | 1023842.5
8056 | 2006-12-02 15:00 | 172 | 649 | 45 | 11.82 | 8.29 | 0 | 11.2069 | 233.058 | 64.8305 | 0 | 172 | 277.911 | 65.1121 | 1.6115 | 213.762 | 60.9344 | 0.0084115 | 199.32 | 58.6792 | 0.0063383 | 250.265 | 250.119 | 561708 | 16.3901 | 523443 | 541793 | 478477 | 0 | 0 | 476596 | 724.876 | 0 | 0 | 0 | 0 | 476596 | 724.876 | 468086 | 458724.5625
8057 | 2006-12-02 16:00 | 15 | 197 | 4 | 12.04 | 8.29 | 0 | 0.76409 | 242.286 | 77.959 | 0 | 15 | 26.3763 | 6.059 | 0.14054 | 4.3591 | 5.6703 | 0.00073356 | 3.5322 | 5.4604 | 0.00055276 | 8.7234 | 8.7226 | 19592.2 | 12.1994 | 11497.8 | 12174 | 9086.45 | 0 | 0 | 9084.89 | 534.563 | 0 | 0 | 0 | 3868.54 | 5216.35 | 660 | 5020.13 | 4919.7266
8058 | 2006-12-02 17:00 | 0 | 0 | 0 | 10.72 | 8.29 | 0
8059 | 2006-12-02 18:00 | 0 | 0 | 0 | 9.4 | 9.97 | 0
8060 | 2006-12-02 19:00 | 0 | 0 | 0 | 8.08 | 9.97 | 0
8061 | 2006-12-02 20:00 | 0 | 0 | 0 | 7.13 | 9.97 | 0
8062 | 2006-12-02 21:00 | 0 | 0 | 0 | 6.19 | 11.03 | 0
8063 | 2006-12-02 22:00 | 0 | 0 | 0 | 5.24 | 11.03 | 0
8064 | 2006-12-02 23:00 | 0 | 0 | 0 | 4.42 | 11.03 | 0
8065 | 2006-12-03 | 0 | 0 | 0 | 3.61 | 10.96 | 0
8066 | 2006-12-03 01:00 | 0 | 0 | 0 | 2.79 | 10.96 | 0
8067 | 2006-12-03 02:00 | 0 | 0 | 0 | 2.46 | 10.96 | 0
8068 | 2006-12-03 03:00 | 0 | 0 | 0 | 2.14 | 7.64 | 0
8069 | 2006-12-03 04:00 | 0 | 0 | 0 | 1.81 | 7.64 | 0
8070 | 2006-12-03 05:00 | 0 | 0 | 0 | 1.17 | 7.64 | 0
8071 | 2006-12-03 06:00 | 4 | 96 | 1 | 0.52 | 9.35 | 0 | -2.6357 | 115.23 | 82.052 | 0 | 4 | 4.7681 | 1.343 | 0.037477 | 0 | 1.2569 | 0 | 0 | 1.2104 | 0 | 1.174 | 1.174 | 2636.41 | 0.54008 | 336.22 | 326.576 | 325.082 | 0 | 0 | 325.068 | 171.757 | 0 | 0 | 0 | 325.068 | 0 | 660 | 0 | 0
8072 | 2006-12-03 07:00 | 124 | 632 | 34 | -0.12 | 9.35 | 0 | 8.0951 | 124.064 | 68.778 | 0 | 124 | 231.353 | 51.898 | 1.1618 | 55.7167 | 48.5681 | 0.0060641 | 50.8065 | 46.7706 | 0.0045694 | 94.6542 | 94.5518 | 212352 | 1.4973 | 185718 | 205380 | 160992 | 0 | 0 | 160671 | 665.873 | 0 | 0 | 0 | 734.541 | 159936 | 677.228 | 155273 | 152167.4688
8073 | 2006-12-03 08:00 | 287 | 806 | 43 | 1.39 | 9.35 | 0 | 17.6653 | 134.398 | 56.1679 | 0 | 287 | 447.676 | 59.5887 | 2.689 | 358.329 | 55.7654 | 0.014035 | 344.065 | 53.7015 | 0.010576 | 385.844 | 385.563 | 865834 | 7.9849 | 828989 | 886683 | 783851 | 0 | 0 | 779307 | 753.837 | 0 | 0 | 0 | 746.136 | 778561 | 756.974 | 764680 | 749386.4375
8074 | 2006-12-03 09:00 | 446 | 912 | 54 | 2.9 | 8.41 | 0 | 25.5216 | 146.727 | 44.8185 | 0 | 446 | 645.378 | 72.4563 | 4.1787 | 641.448 | 67.8074 | 0.021811 | 628.306 | 65.2979 | 0.016435 | 672.812 | 672.777 | 1510880 | 15.1008 | 1488900 | 1550040 | 1482790 | 0 | 0 | 1467780 | 755.458 | 0 | 0 | 0 | 0 | 1467780 | 755.458 | 1440300 | 1411498.75
8075 | 2006-12-03 10:00 | 553 | 957 | 62 | 4.41 | 8.41 | 0 | 30.9525 | 161.249 | 35.9689 | 0 | 553 | 772.63 | 81.9771 | 5.1812 | 772.63 | 76.7173 | 0.027044 | 763.529 | 73.8781 | 0.020378 | 812.305 | 812.302 | 1824220 | 19.141 | 1816420 | 1860190 | 1806510 | 0 | 0 | 1784520 | 758.341 | 0 | 0 | 0 | 0 | 1784520 | 758.341 | 1747700 | 1712742.25
8076 | 2006-12-03 11:00 | 597 | 973 | 65 | 5.78 | 8.41 | 0 | 33.2432 | 177.43 | 31.7955 | 0 | 597 | 824.827 | 85.534 | 5.5934 | 824.827 | 80.046 | 0.029196 | 817.545 | 77.0835 | 0.022 | 867.811 | 867.808 | 1948870 | 21.5176 | 1947360 | 1975030 | 1919330 | 0 | 0 | 1894180 | 752.696 | 0 | 0 | 0 | 0 | 1894180 | 752.696 | 1854340 | 1817251.25
8077 | 2006-12-03 12:00 | 544 | 879 | 79 | 7.16 | 6.25 | 0 | 32.0154 | 193.866 | 34.0679 | 0 | 544 | 726.579 | 102.934 | 5.0969 | 726.579 | 96.3299 | 0.026604 | 719.053 | 92.7648 | 0.020047 | 787.482 | 787.474 | 1768470 | 23.5368 | 1757950 | 1768370 | 1719990 | 0 | 0 | 1699180 | 742.47 | 0 | 0 | 0 | 0 | 1699180 | 742.47 | 1666350 | 1633023.625
8078 | 2006-12-03 13:00 | 449 | 835 | 65 | 8.53 | 6.25 | 0 | 27.4785 | 208.996 | 41.7438 | 0 | 449 | 620.944 | 86.0737 | 4.2068 | 620.944 | 80.5511 | 0.021958 | 610.38 | 77.5699 | 0.016546 | 667.328 | 667.329 | 1498650 | 22.4081 | 1475890 | 1491790 | 1448350 | 0 | 0 | 1433530 | 742.682 | 0 | 0 | 0 | 0 | 1433530 | 742.682 | 1407730 | 1379579.5
8079 | 2006-12-03 14:00 | 356 | 852 | 61 | 9.07 | 6.25 | 0 | 20.2846 | 221.997 | 52.4968 | 0 | 356 | 518.045 | 86.2588 | 3.3354 | 477.935 | 80.7243 | 0.01741 | 462.58 | 77.7367 | 0.013119 | 524.12 | 524.012 | 1176800 | 19.9677 | 1142870 | 1166460 | 1113970 | 0 | 0 | 1105100 | 741.291 | 0 | 0 | 0 | 0 | 1105100 | 741.291 | 1086020 | 1064297.375
8080 | 2006-12-03 15:00 | 173 | 648 | 47 | 9.6 | 8.55 | 0 | 11.1726 | 232.89 | 64.8011 | 0 | 173 | 276.86 | 67.2488 | 1.6209 | 212.954 | 62.934 | 0.0084604 | 198.593 | 60.6049 | 0.0063751 | 251.428 | 251.309 | 564385 | 14.1178 | 526033 | 549851 | 486042 | 0 | 0 | 484148 | 733.143 | 0 | 0 | 0 | 0 | 484148 | 733.143 | 475293 | 465787.25
8081 | 2006-12-03 16:00 | 15 | 196 | 4 | 10.13 | 8.55 | 0 | 0.74928 | 242.119 | 77.9089 | 0 | 15 | 26.4844 | 6.0673 | 0.14054 | 4.3622 | 5.678 | 0.00073356 | 3.5391 | 5.4679 | 0.00055276 | 8.7373 | 8.7291 | 19606.8 | 10.2869 | 11509.4 | 12282.5 | 9157.08 | 0 | 0 | 9155.54 | 543.541 | 0 | 0 | 0 | 3237.58 | 5917.97 | 660 | 5695.54 | 5581.6245
8082 | 2006-12-03 17:00 | 0 | 0 | 0 | 8.91 | 8.55 | 0
8083 | 2006-12-03 18:00 | 0 | 0 | 0 | 7.69 | 8.71 | 0
8084 | 2006-12-03 19:00 | 0 | 0 | 0 | 6.46 | 8.71 | 0
8085 | 2006-12-03 20:00 | 0 | 0 | 0 | 5.66 | 8.71 | 0
8086 | 2006-12-03 21:00 | 0 | 0 | 0 | 4.86 | 9.47 | 0
8087 | 2006-12-03 22:00 | 0 | 0 | 0 | 4.05 | 9.47 | 0
8088 | 2006-12-03 23:00 | 0 | 0 | 0 | 3.29 | 9.47 | 0
8089 | 2006-12-04 | 0 | 0 | 0 | 2.53 | 8.99 | 0
8090 | 2006-12-04 01:00 | 0 | 0 | 0 | 1.77 | 8.99 | 0
8091 | 2006-12-04 02:00 | 0 | 0 | 0 | 1.61 | 8.99 | 0
8092 | 2006-12-04 03:00 | 0 | 0 | 0 | 1.46 | 8.19 | 0
8093 | 2006-12-04 04:00 | 0 | 0 | 0 | 1.3 | 8.19 | 0
8094 | 2006-12-04 05:00 | 0 | 0 | 0 | 1.12 | 8.19 | 0
8095 | 2006-12-04 06:00 | 3 | 88 | 1 | 0.95 | 8.4 | 0 | -2.7911 | 115.284 | 82.1744 | 0 | 3 | 3.1301 | 1.4072 | 0.028108 | 0 | 1.3169 | 0 | 0 | 1.2682 | 0 | 1.2301 | 1.23 | 2762.35 | 0.97232 | 369.003 | 358.631 | 356.991 | 0 | 0 | 356.975 | 179.988 | 0 | 0 | 0 | 356.975 | 0 | 660 | 0 | 0
8096 | 2006-12-04 07:00 | 115 | 610 | 30 | 0.77 | 8.4 | 0 | 7.9349 | 124.102 | 68.9125 | 0 | 115 | 221.536 | 47.6117 | 1.0775 | 50.8523 | 44.5568 | 0.005624 | 46.328 | 42.9078 | 0.0042378 | 86.5629 | 86.5261 | 194328 | 2.3401 | 168792 | 186016 | 144815 | 0 | 0 | 144532 | 648.897 | 0 | 0 | 0 | 502.377 | 144030 | 669.471 | 139792 | 136996.3125
8097 | 2006-12-04 08:00 | 283 | 799 | 43 | 2.19 | 8.4 | 0 | 17.5016 | 134.413 | 56.3152 | 0 | 283 | 442.62 | 59.6771 | 2.6515 | 352.913 | 55.8481 | 0.01384 | 338.743 | 53.7812 | 0.010429 | 380.758 | 380.637 | 854769 | 9.0971 | 817844 | 870685 | 771348 | 0 | 0 | 766894 | 749.716 | 0 | 0 | 0 | -15.3045 | 766909 | 751.349 | 753429 | 738360.125
8098 | 2006-12-04 09:00 | 437 | 854 | 72 | 3.6 | 5.53 | 0 | 25.3582 | 146.71 | 44.9779 | 0 | 437 | 602.868 | 100.464 | 4.0944 | 598.439 | 94.0182 | 0.021371 | 586.062 | 90.5387 | 0.016104 | 656.318 | 656.281 | 1473850 | 17.8964 | 1450360 | 1493010 | 1428760 | 0 | 0 | 1414360 | 743.487 | 0 | 0 | 0 | 0 | 1414360 | 743.487 | 1388760 | 1360985
8099 | 2006-12-04 10:00 | 513 | 846 | 81 | 5.02 | 5.53 | 0 | 30.7965 | 161.19 | 36.1323 | 0 | 513 | 681.475 | 112.34 | 4.8064 | 681.475 | 105.132 | 0.025088 | 673.36 | 101.241 | 0.018904 | 751.381 | 751.375 | 1687400 | 21.388 | 1673030 | 1697960 | 1650320 | 0 | 0 | 1631460 | 749.148 | 0 | 0 | 0 | 0 | 1631460 | 749.148 | 1600090 | 1568087.125
8100 | 2006-12-04 11:00 | 552 | 886 | 70 | 7.08 | 5.53 | 0 | 33.1048 | 177.325 | 31.937 | 0 | 552 | 748.921 | 91.8317 | 5.1718 | 748.921 | 85.9396 | 0.026995 | 742.242 | 82.759 | 0.020341 | 800.271 | 800.268 | 1797200 | 24.513 | 1788080 | 1791380 | 1740270 | 0 | 0 | 1718890 | 741.049 | 0 | 0 | 0 | 0 | 1718890 | 741.049 | 1685570 | 1651862
8101 | 2006-12-04 12:00 | 532 | 859 | 79 | 9.14 | 3.89 | 0 | 31.9038 | 193.725 | 34.1562 | 0 | 532 | 709.301 | 103.009 | 4.9844 | 709.301 | 96.3995 | 0.026017 | 701.909 | 92.8318 | 0.019604 | 770.917 | 770.914 | 1731280 | 27.8289 | 1718980 | 1698260 | 1650870 | 0 | 0 | 1631010 | 729.317 | 0 | 0 | 0 | 0 | 1631010 | 729.317 | 1600690 | 1568677.625
8102 | 2006-12-04 13:00 | 491 | 898 | 79 | 11.21 | 3.89 | 0 | 27.3976 | 208.836 | 41.7773 | 0 | 491 | 667.688 | 109.289 | 4.6003 | 667.688 | 102.277 | 0.024012 | 656.305 | 98.492 | 0.018093 | 732.171 | 732.164 | 1644260 | 28.9595 | 1627890 | 1600440 | 1558370 | 0 | 0 | 1540350 | 723.119 | 0 | 0 | 0 | 0 | 1540350 | 723.119 | 1512850 | 1482594.625
8103 | 2006-12-04 14:00 | 356 | 873 | 55 | 11.68 | 3.89 | 0 | 20.2325 | 221.832 | 52.4905 | 0 | 356 | 529.961 | 74.5317 | 3.3354 | 488.929 | 69.7497 | 0.01741 | 473.227 | 67.1683 | 0.013119 | 524.196 | 524.172 | 1177160 | 24.3873 | 1143280 | 1144960 | 1090940 | 0 | 0 | 1082120 | 728.409 | 0 | 0 | 0 | 0 | 1082120 | 728.409 | 1064120 | 1042840.4375
8104 | 2006-12-04 15:00 | 150 | 491 | 55 | 12.15 | 4.64 | 0 | 11.1447 | 232.727 | 64.7673 | 0 | 150 | 209.522 | 79.2732 | 1.4054 | 161.159 | 74.1869 | 0.0073356 | 150.315 | 71.4413 | 0.0055275 | 215.109 | 215.046 | 482942 | 17.1134 | 444392 | 459010 | 411292 | 0 | 0 | 409902 | 716.862 | 0 | 0 | 0 | 0 | 409902 | 716.862 | 402453 | 394404.25
8105 | 2006-12-04 16:00 | 13 | 149 | 5 | 12.62 | 4.64 | 0 | 0.74047 | 241.956 | 77.8549 | 0 | 13 | 19.346 | 7.965 | 0.1218 | 3.1865 | 7.454 | 0.00063575 | 2.5885 | 7.1781 | 0.00047905 | 9.4741 | 9.4688 | 21267.1 | 12.8385 | 12592.9 | 13324.2 | 11056.1 | 0 | 0 | 11054.3 | 550.935 | 0 | 0 | 0 | 3777.28 | 7277 | 660 | 7003.88 | 6863.8027
8106 | 2006-12-04 17:00 | 0 | 0 | 0 | 11.7 | 4.64 | 0
8107 | 2006-12-04 18:00 | 0 | 0 | 0 | 10.77 | 8.43 | 0
8108 | 2006-12-04 19:00 | 0 | 0 | 0 | 9.85 | 8.43 | 0
8109 | 2006-12-04 20:00 | 0 | 0 | 0 | 9.16 | 8.43 | 0
8110 | 2006-12-04 21:00 | 0 | 0 | 0 | 8.47 | 5.79 | 0
8111 | 2006-12-04 22:00 | 0 | 0 | 0 | 7.78 | 5.79 | 0
8112 | 2006-12-04 23:00 | 0 | 0 | 0 | 7.16 | 5.79 | 0
8113 | 2006-12-05 | 0 | 0 | 0 | 6.55 | 5.26 | 0
8114 | 2006-12-05 01:00 | 0 | 0 | 0 | 5.93 | 5.26 | 0
8115 | 2006-12-05 02:00 | 0 | 0 | 0 | 5.51 | 5.26 | 0
8116 | 2006-12-05 03:00 | 0 | 0 | 0 | 5.09 | 1.01 | 0
8117 | 2006-12-05 04:00 | 0 | 0 | 0 | 4.67 | 1.01 | 0
8118 | 2006-12-05 05:00 | 0 | 0 | 0 | 4.26 | 1.01 | 0
8119 | 2006-12-05 06:00 | 3 | 84 | 1 | 3.84 | 2.83 | 0 | -2.944 | 115.332 | 82.2971 | 0 | 3 | 3.0813 | 1.3962 | 0.028108 | 0 | 1.3066 | 0 | 0 | 1.2582 | 0 | 1.2205 | 1.2205 | 2740.86 | 3.8717 | 363.344 | 354.37 | 352.707 | 0 | 0 | 352.691 | 178.929 | 0 | 0 | 0 | 352.691 | 0 | 660 | 0 | 0
8120 | 2006-12-05 07:00 | 114 | 612 | 30 | 3.42 | 2.83 | 0 | 7.778 | 124.133 | 69.0464 | 0 | 114 | 221.964 | 47.6496 | 1.0681 | 46.3108 | 44.5923 | 0.0055751 | 42.1514 | 42.942 | 0.0042009 | 82.5446 | 82.5679 | 185442 | 5.5668 | 160349 | 173931 | 136555 | 0 | 0 | 136303 | 658.56 | 0 | 0 | 0 | 166.122 | 136136 | 663.851 | 132130 | 129487.0391
8121 | 2006-12-05 08:00 | 279 | 795 | 42 | 4.42 | 2.83 | 0 | 17.3421 | 134.422 | 56.4608 | 0 | 279 | 439.299 | 58.4596 | 2.614 | 334.564 | 54.7087 | 0.013644 | 321.016 | 52.684 | 0.010281 | 362.498 | 362.383 | 813773 | 13.8421 | 776822 | 809217 | 706107 | 0 | 0 | 702153 | 732.296 | 0 | 0 | 0 | 351.217 | 701802 | 734.917 | 689934 | 676135.125
8122 | 2006-12-05 09:00 | 433 | 896 | 52 | 5.43 | 4.35 | 0 | 25.1999 | 146.688 | 45.134 | 0 | 433 | 631.26 | 70.0506 | 4.0569 | 626.028 | 65.5561 | 0.021175 | 612.958 | 63.1299 | 0.015956 | 655.821 | 655.773 | 1472700 | 20.8552 | 1449270 | 1473750 | 1411980 | 0 | 0 | 1397530 | 733.336 | 0 | 0 | 0 | 0 | 1397530 | 733.336 | 1372890 | 1345433.75
8123 | 2006-12-05 10:00 | 524 | 875 | 79 | 6.43 | 4.35 | 0 | 30.6467 | 161.127 | 36.2906 | 0 | 524 | 703.652 | 109.953 | 4.9095 | 703.652 | 102.898 | 0.025626 | 695.185 | 99.0896 | 0.01931 | 770.465 | 770.463 | 1730270 | 24.553 | 1717920 | 1720800 | 1672600 | 0 | 0 | 1652690 | 738.122 | 0 | 0 | 0 | 0 | 1652690 | 738.122 | 1621480 | 1589046.375
8124 | 2006-12-05 11:00 | 540 | 783 | 115 | 8.53 | 4.35 | 0 | 32.9734 | 177.218 | 32.0717 | 0 | 540 | 661.716 | 157.614 | 5.0594 | 661.716 | 147.501 | 0.026408 | 655.757 | 142.042 | 0.019899 | 773.884 | 773.875 | 1737920 | 26.7332 | 1725940 | 1713080 | 1664860 | 0 | 0 | 1644850 | 732.603 | 0 | 0 | 0 | 0 | 1644850 | 732.603 | 1614020 | 1581744.5
8125 | 2006-12-05 12:00 | 574 | 919 | 91 | 10.62 | 2.57 | 0 | 31.7995 | 193.584 | 34.2376 | 0 | 574 | 757.763 | 124.709 | 5.3779 | 757.763 | 116.707 | 0.028071 | 749.821 | 112.388 | 0.021152 | 836.364 | 836.359 | 1878250 | 32.7443 | 1873150 | 1812000 | 1765920 | 0 | 0 | 1742200 | 712.95 | 0 | 0 | 0 | 0 | 1742200 | 712.95 | 1708910 | 1674734.125
8126 | 2006-12-05 13:00 | 472 | 919 | 51 | 12.71 | 2.57 | 0 | 27.3238 | 208.677 | 41.8047 | 0 | 472 | 683.681 | 68.5197 | 4.4223 | 683.681 | 64.1234 | 0.023083 | 672.006 | 61.7502 | 0.017393 | 711.761 | 711.758 | 1598430 | 31.5383 | 1579990 | 1535960 | 1495570 | 0 | 0 | 1478550 | 714.093 | 0 | 0 | 0 | 0 | 1478550 | 714.093 | 1453000 | 1423937.625
8127 | 2006-12-05 14:00 | 355 | 873 | 54 | 13.23 | 2.57 | 0 | 20.1872 | 221.67 | 52.4789 | 0 | 355 | 531.24 | 73.3336 | 3.3261 | 490.109 | 68.6284 | 0.017361 | 474.379 | 66.0885 | 0.013082 | 524.266 | 524.206 | 1177240 | 27.0969 | 1143360 | 1131550 | 1079390 | 0 | 0 | 1070520 | 718.194 | 0 | 0 | 0 | 0 | 1070520 | 718.194 | 1053260 | 1032193.5625
8128 | 2006-12-05 15:00 | 161 | 562 | 52 | 13.75 | 3.45 | 0 | 11.1232 | 232.567 | 64.729 | 0 | 161 | 241.2 | 76.0982 | 1.5084 | 185.525 | 71.2156 | 0.0078736 | 173.072 | 68.5799 | 0.0059329 | 234.408 | 234.351 | 526298 | 19.5983 | 487622 | 497502 | 443921 | 0 | 0 | 442267 | 712.145 | 0 | 0 | 0 | 0 | 442267 | 712.145 | 434563 | 425871.3125
8129 | 2006-12-05 16:00 | 14 | 170 | 5 | 14.26 | 3.45 | 0 | 0.73765 | 241.798 | 77.7972 | 0 | 14 | 21.8661 | 7.9828 | 0.13117 | 3.6 | 7.4706 | 0.00068466 | 2.9284 | 7.1941 | 0.0005159 | 9.8193 | 9.8142 | 22043.3 | 14.5049 | 13227.1 | 13896.6 | 11324 | 0 | 0 | 11322 | 546.189 | 0 | 0 | 0 | 4476.91 | 6845.12 | 660 | 6588.1 | 6456.3345
8130 | 2006-12-05 17:00 | 0 | 0 | 0 | 13.5 | 3.45 | 0
8131 | 2006-12-05 18:00 | 0 | 0 | 0 | 12.75 | 6.06 | 0
8132 | 2006-12-05 19:00 | 0 | 0 | 0 | 11.99 | 6.06 | 0
8133 | 2006-12-05 20:00 | 0 | 0 | 0 | 11.22 | 6.06 | 0
8134 | 2006-12-05 21:00 | 0 | 0 | 0 | 10.46 | 5.83 | 0
8135 | 2006-12-05 22:00 | 0 | 0 | 0 | 9.69 | 5.83 | 0
8136 | 2006-12-05 23:00 | 0 | 0 | 0 | 9.11 | 5.83 | 0
8137 | 2006-12-06 | 0 | 0 | 0 | 8.52 | 5.52 | 0
8138 | 2006-12-06 01:00 | 0 | 0 | 0 | 7.93 | 5.52 | 0
8139 | 2006-12-06 02:00 | 0 | 0 | 0 | 7.78 | 5.52 | 0
8140 | 2006-12-06 03:00 | 0 | 0 | 0 | 7.64 | 4.6 | 0
8141 | 2006-12-06 04:00 | 0 | 0 | 0 | 7.49 | 4.6 | 0
8142 | 2006-12-06 05:00 | 0 | 0 | 0 | 7.15 | 4.6 | 0
8143 | 2006-12-06 06:00 | 3 | 80 | 1 | 6.81 | 7.09 | 0 | -3.0941 | 115.373 | 82.4199 | 0 | 3 | 3.0324 | 1.3852 | 0.028108 | 0 | 1.2963 | 0 | 0 | 1.2484 | 0 | 1.2109 | 1.2108 | 2719.22 | 6.8339 | 357.591 | 350.004 | 348.413 | 0 | 0 | 348.398 | 177.805 | 0 | 0 | 0 | 348.398 | 0 | 660 | 0 | 0
8144 | 2006-12-06 07:00 | 116 | 617 | 33 | 6.47 | 7.09 | 0 | 7.6245 | 124.158 | 69.1797 | 0 | 116 | 222.35 | 50.8157 | 1.0868 | 44.3442 | 47.5553 | 0.0056729 | 40.3235 | 45.7953 | 0.0042746 | 83.5393 | 83.5004 | 187535 | 8.1158 | 162093 | 174262 | 139622 | 0 | 0 | 139362 | 657.68 | 0 | 0 | 0 | 175.112 | 139187 | 662.949 | 135124 | 132421.4062
8145 | 2006-12-06 08:00 | 298 | 834 | 52 | 7.35 | 7.09 | 0 | 17.1869 | 134.424 | 56.6046 | 0 | 298 | 458.228 | 75.1715 | 2.792 | 347.586 | 70.3484 | 0.014573 | 333.39 | 67.7448 | 0.010981 | 389.111 | 388.923 | 873375 | 15.0157 | 837174 | 868933 | 758817 | 0 | 0 | 754275 | 733.117 | 0 | 0 | 0 | 503.2 | 753772 | 735.173 | 741068 | 726247.0625
8146 | 2006-12-06 09:00 | 449 | 921 | 60 | 8.24 | 5.61 | 0 | 25.0471 | 146.66 | 45.2868 | 0 | 449 | 646.454 | 80.2517 | 4.2068 | 640.33 | 75.1026 | 0.021958 | 626.84 | 72.3231 | 0.016546 | 678.204 | 678.153 | 1522960 | 22.9367 | 1501690 | 1513810 | 1447800 | 0 | 0 | 1432420 | 728.371 | 0 | 0 | 0 | 0 | 1432420 | 728.371 | 1407340 | 1379195.75
8147 | 2006-12-06 10:00 | 548 | 959 | 63 | 9.13 | 5.61 | 0 | 30.5032 | 161.059 | 36.4436 | 0 | 548 | 768.646 | 83.43 | 5.1343 | 768.646 | 78.0769 | 0.0268 | 759.303 | 75.1874 | 0.020194 | 809.475 | 809.474 | 1817870 | 26.6726 | 1809770 | 1796800 | 1747580 | 0 | 0 | 1725610 | 733.053 | 0 | 0 | 0 | 0 | 1725610 | 733.053 | 1692370 | 1658526.375
8148 | 2006-12-06 11:00 | 553 | 871 | 82 | 11.1 | 5.61 | 0 | 32.849 | 177.109 | 32.1997 | 0 | 553 | 734.77 | 106.723 | 5.1812 | 734.77 | 99.8756 | 0.027044 | 728.092 | 96.1793 | 0.020378 | 799.563 | 799.556 | 1795600 | 28.4277 | 1786400 | 1760460 | 1712830 | 0 | 0 | 1691350 | 727.798 | 0 | 0 | 0 | 0 | 1691350 | 727.798 | 1659280 | 1626095.25
8149 | 2006-12-06 12:00 | 573 | 919 | 92 | 13.07 | 1.86 | 0 | 31.7025 | 193.443 | 34.312 | 0 | 573 | 756.023 | 125.965 | 5.3686 | 756.023 | 117.882 | 0.028022 | 748.059 | 113.52 | 0.021115 | 835.752 | 835.748 | 1876880 | 36.2502 | 1871710 | 1782840 | 1739500 | 0 | 0 | 1715700 | 700.854 | 0 | 0 | 0 | 0 | 1715700 | 700.854 | 1683550 | 1649878.875
8150 | 2006-12-06 13:00 | 461 | 901 | 49 | 15.04 | 1.86 | 0 | 27.2572 | 208.521 | 41.826 | 0 | 461 | 670.352 | 66.0023 | 4.3192 | 670.352 | 61.7674 | 0.022545 | 658.89 | 59.4815 | 0.016988 | 696.837 | 696.833 | 1564910 | 34.3673 | 1544990 | 1483150 | 1446550 | 0 | 0 | 1430060 | 702.039 | 0 | 0 | 0 | 0 | 1430060 | 702.039 | 1406060 | 1377942.25
8151 | 2006-12-06 14:00 | 342 | 863 | 45 | 15.79 | 1.86 | 0 | 20.1487 | 221.511 | 52.4621 | 0 | 342 | 525.341 | 61.8638 | 3.2043 | 484.666 | 57.8945 | 0.016725 | 469.126 | 55.7518 | 0.012603 | 509.144 | 509.116 | 1143350 | 29.9108 | 1108480 | 1083350 | 1032840 | 0 | 0 | 1024480 | 707.842 | 0 | 0 | 0 | 0 | 1024480 | 707.842 | 1008620 | 988443.375
8152 | 2006-12-06 15:00 | 173 | 659 | 46 | 16.54 | 4.77 | 0 | 11.108 | 232.411 | 64.6863 | 0 | 173 | 281.855 | 66.4205 | 1.6209 | 216.795 | 62.1588 | 0.0084604 | 202.283 | 59.8583 | 0.0063751 | 254.284 | 254.184 | 570836 | 22.3572 | 532533 | 536243 | 473757 | 0 | 0 | 471788 | 699.761 | 0 | 0 | 0 | 0 | 471788 | 699.761 | 464114 | 454831.4688
8153 | 2006-12-06 16:00 | 15 | 199 | 4 | 17.29 | 4.77 | 0 | 0.74079 | 241.645 | 77.7358 | 0 | 15 | 26.8576 | 6.1019 | 0.14054 | 4.4218 | 5.7104 | 0.00073356 | 3.602 | 5.499 | 0.00055276 | 8.8286 | 8.8237 | 19819.5 | 17.4919 | 11679.3 | 12086 | 9039.25 | 0 | 0 | 9037.7 | 534.354 | 0 | 0 | 0 | 4911.17 | 4126.53 | 660 | 3971.09 | 3891.666
8154 | 2006-12-06 17:00 | 0 | 0 | 0 | 16.46 | 4.77 | 0
8155 | 2006-12-06 18:00 | 0 | 0 | 0 | 15.63 | 7.35 | 0
8156 | 2006-12-06 19:00 | 0 | 0 | 0 | 14.8 | 7.35 | 0
8157 | 2006-12-06 20:00 | 0 | 0 | 0 | 13.97 | 7.35 | 0
8158 | 2006-12-06 21:00 | 0 | 0 | 0 | 13.14 | 8.52 | 0
8159 | 2006-12-06 22:00 | 0 | 0 | 0 | 12.31 | 8.52 | 0
8160 | 2006-12-06 23:00 | 0 | 0 | 0 | 11.72 | 8.52 | 0
8161 | 2006-12-07 | 0 | 0 | 0 | 11.13 | 8.23 | 0
8162 | 2006-12-07 01:00 | 0 | 0 | 0 | 10.55 | 8.23 | 0
8163 | 2006-12-07 02:00 | 0 | 0 | 0 | 10.13 | 8.23 | 0
8164 | 2006-12-07 03:00 | 0 | 0 | 0 | 9.7 | 8.12 | 0
8165 | 2006-12-07 04:00 | 0 | 0 | 0 | 9.28 | 8.12 | 0
8166 | 2006-12-07 05:00 | 0 | 0 | 0 | 9.01 | 8.12 | 0
8167 | 2006-12-07 06:00 | 2 | 75 | 0 | 8.74 | 7.87 | 0 | -3.2414 | 115.407 | 82.5429 | 0 | 2 | 2.9835 | 0 | 0.018738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.74 | 0 | 0 | 0 | 0 | 0 | 0 | 660 | 0 | 0 | 0 | 0 | 0 | 660 | 0 | 0
8168 | 2006-12-07 07:00 | 111 | 610 | 31 | 8.48 | 7.87 | 0 | 7.4746 | 124.175 | 69.3121 | 0 | 111 | 217.257 | 48.7548 | 1.04 | 41.4805 | 45.6266 | 0.0054284 | 37.6837 | 43.938 | 0.0040904 | 79.177 | 79.1769 | 177823 | 9.9654 | 152978 | 163246 | 131718 | 0 | 0 | 131478 | 650.593 | 0 | 0 | 0 | 667.551 | 130810 | 661.61 | 126945 | 124406.2422
8169 | 2006-12-07 08:00 | 295 | 832 | 51 | 9.51 | 7.87 | 0 | 17.0362 | 134.42 | 56.7465 | 0 | 295 | 456.68 | 74.0116 | 2.7639 | 344.932 | 69.2629 | 0.014427 | 330.727 | 66.6995 | 0.010871 | 385.514 | 385.285 | 865204 | 16.7381 | 829021 | 854449 | 746237 | 0 | 0 | 741687 | 722.383 | 0 | 0 | 0 | 1425.9 | 740261 | 730.275 | 727943 | 713384.4375
8170 | 2006-12-07 09:00 | 442 | 916 | 57 | 10.55 | 5.79 | 0 | 24.8996 | 146.626 | 45.4362 | 0 | 442 | 641.656 | 76.537 | 4.1412 | 634.942 | 71.6262 | 0.021616 | 621.446 | 68.9754 | 0.016288 | 669.724 | 669.686 | 1503960 | 24.8955 | 1481920 | 1481630 | 1414690 | 0 | 0 | 1399770 | 722.829 | 0 | 0 | 0 | 0 | 1399770 | 722.829 | 1375640 | 1348126.625
8171 | 2006-12-07 10:00 | 549 | 960 | 65 | 11.58 | 5.79 | 0 | 30.3662 | 160.987 | 36.5912 | 0 | 549 | 768.722 | 85.9964 | 5.1437 | 768.722 | 80.4787 | 0.026848 | 759.287 | 77.5003 | 0.020231 | 811.703 | 811.699 | 1822870 | 28.9676 | 1815010 | 1784570 | 1734950 | 0 | 0 | 1712910 | 726.58 | 0 | 0 | 0 | 0 | 1712910 | 726.58 | 1680220 | 1646612.75
8172 | 2006-12-07 11:00 | 592 | 974 | 67 | 13.62 | 5.79 | 0 | 32.7316 | 176.997 | 32.3207 | 0 | 592 | 820.523 | 88.2816 | 5.5466 | 820.523 | 82.6173 | 0.028951 | 813.002 | 79.5597 | 0.021815 | 865.806 | 865.801 | 1944370 | 32.1665 | 1942620 | 1884160 | 1834730 | 0 | 0 | 1809310 | 715.558 | 0 | 0 | 0 | 0 | 1809310 | 715.558 | 1773810 | 1738332.75
8173 | 2006-12-07 12:00 | 551 | 947 | 56 | 15.66 | 5.63 | 0 | 31.6128 | 193.301 | 34.3795 | 0 | 551 | 779.378 | 74.5254 | 5.1624 | 779.378 | 69.7437 | 0.026946 | 771.13 | 67.1625 | 0.020304 | 813.164 | 813.16 | 1826150 | 33.2598 | 1818460 | 1755100 | 1709290 | 0 | 0 | 1686980 | 711.53 | 0 | 0 | 0 | 0 | 1686980 | 711.53 | 1655480 | 1622366.375
8174 | 2006-12-07 13:00 | 469 | 917 | 51 | 17.7 | 5.63 | 0 | 27.1977 | 208.366 | 41.8411 | 0 | 469 | 681.326 | 68.6168 | 4.3942 | 681.326 | 64.2142 | 0.022936 | 669.666 | 61.8377 | 0.017283 | 709.575 | 709.571 | 1593520 | 33.0577 | 1574870 | 1520800 | 1480570 | 0 | 0 | 1463580 | 707.779 | 0 | 0 | 0 | 0 | 1463580 | 707.779 | 1438610 | 1409838.875
8175 | 2006-12-07 14:00 | 353 | 872 | 54 | 18.21 | 5.63 | 0 | 20.117 | 221.355 | 52.4402 | 0 | 353 | 529.941 | 73.4487 | 3.3073 | 488.91 | 68.7361 | 0.017263 | 473.254 | 66.1922 | 0.013008 | 523.276 | 523.232 | 1175050 | 29.5346 | 1141100 | 1117520 | 1066570 | 0 | 0 | 1057710 | 710.252 | 0 | 0 | 0 | 0 | 1057710 | 710.252 | 1041080 | 1020262.1875
8176 | 2006-12-07 15:00 | 160 | 563 | 51 | 18.72 | 4.27 | 0 | 11.0992 | 232.259 | 64.6392 | 0 | 160 | 242.517 | 75.1531 | 1.4991 | 186.538 | 70.3312 | 0.0078247 | 174.089 | 67.7283 | 0.005896 | 234.568 | 234.52 | 526679 | 24.2654 | 488039 | 487633 | 434130 | 0 | 0 | 432454 | 691.28 | 0 | 0 | 0 | 0 | 432454 | 691.28 | 425511 | 417000.4375
8177 | 2006-12-07 16:00 | 14 | 170 | 5 | 19.23 | 4.27 | 0 | 0.74983 | 241.495 | 77.6708 | 0 | 14 | 22.0892 | 8.0319 | 0.13117 | 3.3901 | 7.5165 | 0.00068466 | 2.7658 | 7.2383 | 0.0005159 | 9.7045 | 9.6987 | 21784 | 19.4593 | 13012.9 | 13364.8 | 11168.9 | 0 | 0 | 11166.8 | 529.042 | 0 | 0 | 0 | 7000.56 | 4166.23 | 660 | 4009.24 | 3929.054
8178 | 2006-12-07 17:00 | 0 | 0 | 0 | 18.05 | 4.27 | 0
8179 | 2006-12-07 18:00 | 0 | 0 | 0 | 16.86 | 9.53 | 0
8180 | 2006-12-07 19:00 | 0 | 0 | 0 | 15.68 | 9.53 | 0
8181 | 2006-12-07 20:00 | 0 | 0 | 0 | 14.77 | 9.53 | 0
8182 | 2006-12-07 21:00 | 0 | 0 | 0 | 13.85 | 6.68 | 0
8183 | 2006-12-07 22:00 | 0 | 0 | 0 | 12.93 | 6.68 | 0
8184 | 2006-12-07 23:00 | 0 | 0 | 0 | 11.98 | 6.68 | 0
8185 | 2006-12-08 | 0 | 0 | 0 | 11.03 | 5.59 | 0
8186 | 2006-12-08 01:00 | 0 | 0 | 0 | 10.09 | 5.59 | 0
8187 | 2006-12-08 02:00 | 0 | 0 | 0 | 9.8 | 5.59 | 0
8188 | 2006-12-08 03:00 | 0 | 0 | 0 | 9.52 | 5.69 | 0
8189 | 2006-12-08 04:00 | 0 | 0 | 0 | 9.24 | 5.69 | 0
8190 | 2006-12-08 05:00 | 0 | 0 | 0 | 8.25 | 5.69 | 0
8191 | 2006-12-08 06:00 | 2 | 69 | 1 | 7.26 | 6.25 | 0 | -3.3858 | 115.433 | 82.6658 | 0 | 2 | 1.4673 | 1.3232 | 0.018738 | 0 | 1.2383 | 0 | 0 | 1.1924 | 0 | 1.1567 | 1.1566 | 2597.4 | 7.284 | 326.36 | 319.59 | 318.149 | 0 | 0 | 318.135 | 169.899 | 0 | 0 | 0 | 318.135 | 0 | 660 | 0 | 0
8192 | 2006-12-08 07:00 | 105 | 590 | 29 | 6.27 | 6.25 | 0 | 7.3283 | 124.186 | 69.4437 | 0 | 105 | 209.21 | 46.6215 | 0.98377 | 38.4123 | 43.6301 | 0.0051349 | 34.863 | 42.0154 | 0.0038693 | 74.5758 | 74.5372 | 167396 | 7.8201 | 143190 | 154260 | 125148 | 0 | 0 | 124932 | 653.894 | 0 | 0 | 0 | 554.578 | 124377 | 662.506 | 120647 | 118233.6484
8193 | 2006-12-08 08:00 | 273 | 798 | 41 | 7.7 | 6.25 | 0 | 16.89 | 134.41 | 56.8863 | 0 | 273 | 436.237 | 57.3865 | 2.5578 | 328.268 | 53.7045 | 0.013351 | 314.637 | 51.7169 | 0.01006 | 355.373 | 355.249 | 797756 | 15.088 | 760886 | 789396 | 684566 | 0 | 0 | 680734 | 724.594 | 0 | 0 | 0 | 1869.78 | 678864 | 733.025 | 667255 | 653910.1875
8194 | 2006-12-08 09:00 | 440 | 916 | 57 | 9.13 | 4.01 | 0 | 24.7577 | 146.587 | 45.582 | 0 | 440 | 640.089 | 76.5993 | 4.1225 | 632.541 | 71.6846 | 0.021518 | 618.979 | 69.0316 | 0.016214 | 667.386 | 667.364 | 1498730 | 25.1816 | 1476540 | 1474260 | 1401000 | 0 | 0 | 1386190 | 719.156 | 0 | 0 | 0 | 0 | 1386190 | 719.156 | 1362520 | 1335269.875
8195 | 2006-12-08 10:00 | 544 | 957 | 64 | 10.56 | 4.01 | 0 | 30.2356 | 160.911 | 36.7335 | 0 | 544 | 763.936 | 84.8009 | 5.0969 | 763.936 | 79.3599 | 0.026604 | 754.471 | 76.4229 | 0.020047 | 805.987 | 805.985 | 1810040 | 29.9457 | 1801560 | 1763890 | 1714200 | 0 | 0 | 1692520 | 724.302 | 0 | 0 | 0 | 0 | 1692520 | 724.302 | 1660500 | 1627292.875
8196 | 2006-12-08 11:00 | 590 | 974 | 67 | 12.73 | 4.01 | 0 | 32.6215 | 176.883 | 32.4348 | 0 | 590 | 818.817 | 88.3355 | 5.5278 | 818.817 | 82.6677 | 0.028854 | 811.25 | 79.6082 | 0.021742 | 864.154 | 864.153 | 1940670 | 33.5148 | 1938730 | 1869350 | 1823180 | 0 | 0 | 1797800 | 711.161 | 0 | 0 | 0 | 0 | 1797800 | 711.161 | 1762760 | 1727500
8197 | 2006-12-08 12:00 | 569 | 967 | 65 | 14.89 | 5.95 | 0 | 31.5304 | 193.16 | 34.44 | 0 | 569 | 794.831 | 85.9339 | 5.3311 | 794.831 | 80.4202 | 0.027827 | 786.385 | 77.4439 | 0.020968 | 837.934 | 837.931 | 1881780 | 32.6554 | 1876860 | 1816380 | 1768430 | 0 | 0 | 1744750 | 714.13 | 0 | 0 | 0 | 0 | 1744750 | 714.13 | 1711350 | 1677125.625
8198 | 2006-12-08 13:00 | 478 | 931 | 54 | 17.06 | 5.95 | 0 | 27.1455 | 208.213 | 41.8502 | 0 | 478 | 692.238 | 72.4975 | 4.4785 | 692.238 | 67.8459 | 0.023376 | 680.384 | 65.335 | 0.017614 | 723.364 | 723.361 | 1624480 | 32.3964 | 1607220 | 1556660 | 1516970 | 0 | 0 | 1499270 | 710.098 | 0 | 0 | 0 | 0 | 1499270 | 710.098 | 1473400 | 1443934.25
8199 | 2006-12-08 14:00 | 341 | 865 | 44 | 17.38 | 5.95 | 0 | 20.0921 | 221.203 | 52.4131 | 0 | 341 | 527.346 | 60.6557 | 3.1949 | 486.517 | 56.764 | 0.016676 | 470.962 | 54.6632 | 0.012566 | 509.868 | 509.862 | 1145020 | 28.1898 | 1110210 | 1093710 | 1042380 | 0 | 0 | 1034010 | 714.691 | 0 | 0 | 0 | 0 | 1034010 | 714.691 | 1017630 | 997273.6875
8200 | 2006-12-08 15:00 | 168 | 630 | 46 | 17.71 | 6.42 | 0 | 11.0967 | 232.111 | 64.5879 | 0 | 168 | 272.015 | 66.5498 | 1.574 | 209.227 | 62.2798 | 0.0082159 | 195.31 | 59.9749 | 0.0061909 | 247.632 | 247.523 | 555880 | 22.8018 | 517549 | 520476 | 459899 | 0 | 0 | 458034 | 697.924 | 0 | 0 | 0 | 0 | 458034 | 697.924 | 450575 | 441563.9375
8201 | 2006-12-08 16:00 | 15 | 191 | 4 | 18.03 | 6.42 | 0 | 0.76476 | 241.351 | 77.6021 | 0 | 15 | 27.1459 | 6.1329 | 0.14054 | 4.1662 | 5.7394 | 0.00073356 | 3.4042 | 5.527 | 0.00055276 | 8.6638 | 8.6565 | 19444.1 | 18.2081 | 11371.8 | 11727.7 | 9045.4 | 0 | 0 | 9043.8 | 528.305 | 0 | 0 | 0 | 5171.48 | 3872.32 | 660 | 3726.42 | 3651.8948
8202 | 2006-12-08 17:00 | 0 | 0 | 0 | 17.06 | 6.42 | 0
8203 | 2006-12-08 18:00 | 0 | 0 | 0 | 16.09 | 9.37 | 0
8204 | 2006-12-08 19:00 | 0 | 0 | 0 | 15.12 | 9.37 | 0
8205 | 2006-12-08 20:00 | 0 | 0 | 0 | 14.26 | 9.37 | 0
8206 | 2006-12-08 21:00 | 0 | 0 | 0 | 13.4 | 11.16 | 0
8207 | 2006-12-08 22:00 | 0 | 0 | 0 | 12.54 | 11.16 | 0
8208 | 2006-12-08 23:00 | 0 | 0 | 0 | 11.64 | 11.16 | 0
8209 | 2006-12-09 | 0 | 0 | 0 | 10.75 | 9.62 | 0
8210 | 2006-12-09 01:00 | 0 | 0 | 0 | 9.85 | 9.62 | 0
8211 | 2006-12-09 02:00 | 0 | 0 | 0 | 9.62 | 9.62 | 0
8212 | 2006-12-09 03:00 | 0 | 0 | 0 | 9.38 | 9.14 | 0
8213 | 2006-12-09 04:00 | 0 | 0 | 0 | 9.15 | 9.14 | 0
8214 | 2006-12-09 05:00 | 0 | 0 | 0 | 8.76 | 9.14 | 0
8215 | 2006-12-09 06:00 | 2 | 66 | 1 | 8.37 | 8.31 | 0 | -3.5271 | 115.453 | 82.7886 | 0 | 2 | 1.4429 | 1.3123 | 0.018738 | 0 | 1.2281 | 0 | 0 | 1.1826 | 0 | 1.1472 | 1.1471 | 2576.15 | 8.3909 | 321.078 | 314.835 | 313.388 | 0 | 0 | 313.375 | 168.623 | 0 | 0 | 0 | 313.375 | 0 | 660 | 0 | 0
8216 | 2006-12-09 07:00 | 106 | 598 | 30 | 7.99 | 8.31 | 0 | 7.1858 | 124.191 | 69.5743 | 0 | 106 | 212.04 | 47.693 | 0.99314 | 37.4254 | 44.633 | 0.0051838 | 33.9348 | 42.9811 | 0.0039061 | 74.6122 | 74.5642 | 167455 | 9.3507 | 143181 | 153306 | 125448 | 0 | 0 | 125227 | 646.224 | 0 | 0 | 0 | 677.632 | 124550 | 661.897 | 120828 | 118410.9688
8217 | 2006-12-09 08:00 | 271 | 793 | 43 | 9.24 | 8.31 | 0 | 16.7484 | 134.394 | 57.024 | 0 | 271 | 430.64 | 60.0755 | 2.5391 | 322.787 | 56.221 | 0.013253 | 309.274 | 54.1403 | 0.0099864 | 352.522 | 352.422 | 791403 | 15.6713 | 754388 | 781347 | 677727 | 0 | 0 | 673918 | 720.084 | 0 | 0 | 0 | 1412.83 | 672505 | 732.413 | 660992 | 647772.625
8218 | 2006-12-09 09:00 | 436 | 915 | 56 | 10.49 | 6.54 | 0 | 24.6213 | 146.542 | 45.7241 | 0 | 436 | 636.753 | 75.391 | 4.085 | 628.459 | 70.5537 | 0.021322 | 614.871 | 67.9426 | 0.016067 | 662.345 | 662.322 | 1487420 | 24.0104 | 1464800 | 1469900 | 1394560 | 0 | 0 | 1379800 | 717.589 | 0 | 0 | 0 | 332.729 | 1379460 | 718.118 | 1356030 | 1328907.125
8219 | 2006-12-09 10:00 | 541 | 956 | 63 | 11.74 | 6.54 | 0 | 30.1115 | 160.831 | 36.8702 | 0 | 541 | 762.229 | 83.5986 | 5.0687 | 762.229 | 78.2348 | 0.026457 | 752.701 | 75.3393 | 0.019936 | 803.219 | 803.214 | 1803820 | 28.1365 | 1795020 | 1771170 | 1724970 | 0 | 0 | 1703120 | 726.191 | 0 | 0 | 0 | 0 | 1703120 | 726.191 | 1670740 | 1637323.125
8220 | 2006-12-09 11:00 | 588 | 974 | 66 | 12.89 | 6.54 | 0 | 32.5185 | 176.767 | 32.542 | 0 | 588 | 818.579 | 87.1346 | 5.5091 | 818.579 | 81.5439 | 0.028756 | 810.957 | 78.526 | 0.021668 | 862.819 | 862.814 | 1937660 | 30.5032 | 1935570 | 1890840 | 1841060 | 0 | 0 | 1815980 | 722.045 | 0 | 0 | 0 | 0 | 1815980 | 722.045 | 1780150 | 1744547.75
8221 | 2006-12-09 12:00 | 568 | 966 | 65 | 14.03 | 9.49 | 0 | 31.4555 | 193.019 | 34.4935 | 0 | 568 | 794.44 | 85.9814 | 5.3217 | 794.44 | 80.4646 | 0.027778 | 785.967 | 77.4867 | 0.020931 | 837.57 | 837.567 | 1880960 | 28.2329 | 1876000 | 1850450 | 1800390 | 0 | 0 | 1776760 | 728.403 | 0 | 0 | 0 | 0 | 1776760 | 728.403 | 1742060 | 1707215
8222 | 2006-12-09 13:00 | 469 | 919 | 51 | 15.18 | 9.49 | 0 | 27.1004 | 208.062 | 41.8531 | 0 | 469 | 683.459 | 68.7004 | 4.3942 | 683.459 | 64.2925 | 0.022936 | 671.754 | 61.913 | 0.017283 | 711.673 | 711.671 | 1598230 | 27.248 | 1579780 | 1564600 | 1522410 | 0 | 0 | 1505420 | 728.303 | 0 | 0 | 0 | 0 | 1505420 | 728.303 | 1478700 | 1449128.25
8223 | 2006-12-09 14:00 | 353 | 871 | 55 | 14.74 | 9.49 | 0 | 20.0739 | 221.053 | 52.3809 | 0 | 353 | 529.967 | 74.8122 | 3.3073 | 488.934 | 70.0121 | 0.017263 | 473.331 | 67.421 | 0.013008 | 524.542 | 524.44 | 1177760 | 23.6331 | 1143890 | 1149680 | 1095240 | 0 | 0 | 1086410 | 730.734 | 0 | 0 | 0 | 0 | 1086410 | 730.734 | 1068220 | 1046853.25
8224 | 2006-12-09 15:00 | 156 | 537 | 52 | 14.29 | 10.3 | 0 | 11.1005 | 231.967 | 64.5322 | 0 | 156 | 232.277 | 76.426 | 1.4616 | 178.661 | 71.5224 | 0.0076291 | 166.82 | 68.8754 | 0.0057487 | 228.63 | 228.6 | 513382 | 17.9784 | 474744 | 488695 | 435710 | 0 | 0 | 434137 | 716.54 | 0 | 0 | 0 | 0 | 434137 | 716.54 | 426399 | 417871.0938
8225 | 2006-12-09 16:00 | 14 | 163 | 5 | 13.85 | 10.3 | 0 | 0.78551 | 241.211 | 77.5299 | 0 | 14 | 22.3375 | 8.099 | 0.13117 | 3.4212 | 7.5793 | 0.00068466 | 2.8 | 7.2988 | 0.0005159 | 9.7964 | 9.7893 | 21987.2 | 14.0079 | 13171.4 | 13871.7 | 11472.5 | 0 | 0 | 11470.4 | 548.342 | 0 | 0 | 0 | 4183.95 | 7286.49 | 660 | 7013.07 | 6872.813
8226 | 2006-12-09 17:00 | 0 | 0 | 0 | 12.95 | 10.3 | 0
8227 | 2006-12-09 18:00 | 0 | 0 | 0 | 12.06 | 14.07 | 0
8228 | 2006-12-09 19:00 | 0 | 0 | 0 | 11.16 | 14.07 | 0
8229 | 2006-12-09 20:00 | 0 | 0 | 0 | 10.49 | 14.07 | 0
8230 | 2006-12-09 21:00 | 0 | 0 | 0 | 9.81 | 14.32 | 0
8231 | 2006-12-09 22:00 | 0 | 0 | 0 | 9.14 | 14.32 | 0
8232 | 2006-12-09 23:00 | 0 | 0 | 0 | 8.01 | 14.32 | 0
8233 | 2006-12-10 | 0 | 0 | 0 | 6.88 | 13.84 | 0
8234 | 2006-12-10 01:00 | 0 | 0 | 0 | 5.74 | 13.84 | 0
8235 | 2006-12-10 02:00 | 0 | 0 | 0 | 5.65 | 13.84 | 0
8236 | 2006-12-10 03:00 | 0 | 0 | 0 | 5.56 | 11.42 | 0
8237 | 2006-12-10 04:00 | 0 | 0 | 0 | 5.46 | 11.42 | 0
8238 | 2006-12-10 05:00 | 0 | 0 | 0 | 5.19 | 11.42 | 0
8239 | 2006-12-10 06:00 | 2 | 62 | 1 | 4.92 | 14.58 | 0 | -3.6654 | 115.466 | 82.9112 | 0 | 2 | 1.4185 | 1.3015 | 0.018738 | 0 | 1.218 | 0 | 0 | 1.1729 | 0 | 1.1377 | 1.1377 | 2554.99 | 4.9342 | 315.836 | 308.403 | 307 | 0 | 0 | 306.987 | 166.97 | 0 | 0 | 0 | 306.987 | 0 | 660 | 0 | 0
8240 | 2006-12-10 07:00 | 107 | 597 | 33 | 4.64 | 14.58 | 0 | 7.0471 | 124.189 | 69.7037 | 0 | 107 | 209.223 | 50.5678 | 1.0025 | 35.6593 | 47.3232 | 0.0052327 | 32.3022 | 45.5718 | 0.003943 | 75.5416 | 75.489 | 169535 | 5.5857 | 144874 | 158057 | 131262 | 0 | 0 | 131049 | 686.134 | 0 | 0 | 0 | 0 | 131049 | 686.134 | 126899 | 124361.2578
8241 | 2006-12-10 08:00 | 287 | 827 | 51 | 6.07 | 14.58 | 0 | 16.6116 | 134.371 | 57.1594 | 0 | 287 | 447.679 | 74.1384 | 2.689 | 319.732 | 69.3816 | 0.014035 | 306.239 | 66.8138 | 0.010576 | 361.872 | 361.739 | 812324 | 10.6019 | 776371 | 821631 | 700166 | 0 | 0 | 696287 | 741.194 | 0 | 0 | 0 | 514.336 | 695772 | 745.507 | 683523 | 669852.375
8242 | 2006-12-10 09:00 | 439 | 917 | 60 | 7.49 | 10.72 | 0 | 24.4907 | 146.492 | 45.8624 | 0 | 439 | 636.672 | 80.5001 | 4.1131 | 627.441 | 75.3351 | 0.021469 | 613.763 | 72.547 | 0.016177 | 665.736 | 665.689 | 1494980 | 17.9595 | 1472750 | 1515390 | 1433670 | 0 | 0 | 1418810 | 735.644 | 0 | 0 | 0 | 0 | 1418810 | 735.644 | 1393530 | 1365657
8243 | 2006-12-10 10:00 | 542 | 958 | 64 | 8.91 | 10.72 | 0 | 29.994 | 160.747 | 37.0013 | 0 | 542 | 763.62 | 84.9038 | 5.0781 | 763.62 | 79.4563 | 0.026506 | 753.993 | 76.5156 | 0.019973 | 805.612 | 805.61 | 1809190 | 21.5801 | 1800660 | 1825980 | 1772440 | 0 | 0 | 1750820 | 750.29 | 0 | 0 | 0 | 0 | 1750820 | 750.29 | 1715770 | 1681454.5
8244 | 2006-12-10 11:00 | 586 | 972 | 67 | 9.79 | 10.72 | 0 | 32.4227 | 176.65 | 32.6421 | 0 | 586 | 815.104 | 88.4324 | 5.4904 | 815.104 | 82.7584 | 0.028658 | 807.46 | 79.6956 | 0.021594 | 860.561 | 860.558 | 1932590 | 23.3243 | 1930240 | 1943350 | 1888620 | 0 | 0 | 1863860 | 746.477 | 0 | 0 | 0 | 0 | 1863860 | 746.477 | 1825610 | 1789101
8245 | 2006-12-10 12:00 | 567 | 967 | 65 | 10.66 | 10.87 | 0 | 31.388 | 192.878 | 34.54 | 0 | 567 | 793.948 | 86.0252 | 5.3124 | 793.948 | 80.5056 | 0.027729 | 785.453 | 77.5262 | 0.020894 | 837.11 | 837.107 | 1879920 | 23.7063 | 1874910 | 1884710 | 1832540 | 0 | 0 | 1808980 | 742.836 | 0 | 0 | 0 | 0 | 1808980 | 742.836 | 1772790 | 1737332.25
8246 | 2006-12-10 13:00 | 487 | 702 | 168 | 11.54 | 10.87 | 0 | 27.0626 | 207.914 | 41.8498 | 0 | 487 | 522.288 | 210.584 | 4.5628 | 522.288 | 197.072 | 0.023816 | 513.344 | 189.779 | 0.017946 | 682.047 | 682.031 | 1531670 | 22.1695 | 1510310 | 1528130 | 1486320 | 0 | 0 | 1470760 | 743.092 | 0 | 0 | 0 | 0 | 1470760 | 743.092 | 1444160 | 1415279.375
8247 | 2006-12-10 14:00 | 202 | 185 | 139 | 11.08 | 10.87 | 0 | 20.0626 | 220.907 | 52.3436 | 0 | 202 | 112.196 | 155.687 | 1.8926 | 103.509 | 145.698 | 0.0098786 | 100.213 | 140.306 | 0.0074438 | 233.31 | 233.291 | 523913 | 14.7158 | 482258 | 504989 | 486642 | 0 | 0 | 484894 | 730.987 | 0 | 0 | 0 | 0 | 484894 | 730.987 | 476096 | 466574.0938
8248 | 2006-12-10 15:00 | 107 | 182 | 72 | 10.61 | 12.33 | 0 | 11.1106 | 231.827 | 64.4724 | 0 | 107 | 78.2713 | 89.5748 | 1.0025 | 60.2044 | 83.8275 | 0.0052327 | 56.2294 | 80.7251 | 0.003943 | 132.85 | 132.809 | 298257 | 12.5065 | 263448 | 279166 | 258839 | 0 | 0 | 258306 | 713.179 | 0 | 0 | 0 | 0 | 258306 | 713.179 | 251343 | 246315.8438
8249 | 2006-12-10 16:00 | 10 | 56 | 7 | 10.15 | 12.33 | 0 | 0.81205 | 241.077 | 77.4543 | 0 | 10 | 7.4903 | 9.8996 | 0.093692 | 1.1573 | 9.2645 | 0.00048904 | 0.9488 | 8.9216 | 0.0003685 | 9.5746 | 9.5717 | 21496.7 | 10.2867 | 12610.4 | 13506 | 12727.4 | 0 | 0 | 12725.4 | 578.903 | 0 | 0 | 0 | 2826.83 | 9898.57 | 660 | 9528.35 | 9337.7861
8250 | 2006-12-10 17:00 | 0 | 0 | 0 | 9.49 | 12.33 | 0
8251 | 2006-12-10 18:00 | 0 | 0 | 0 | 8.82 | 13.44 | 0
8252 | 2006-12-10 19:00 | 0 | 0 | 0 | 8.16 | 13.44 | 0
8253 | 2006-12-10 20:00 | 0 | 0 | 0 | 7.62 | 13.44 | 0
8254 | 2006-12-10 21:00 | 0 | 0 | 0 | 7.08 | 10.84 | 0
8255 | 2006-12-10 22:00 | 0 | 0 | 0 | 6.54 | 10.84 | 0
8256 | 2006-12-10 23:00 | 0 | 0 | 0 | 6.35 | 10.84 | 0
8257 | 2006-12-11 | 0 | 0 | 0 | 6.16 | 9.68 | 0
8258 | 2006-12-11 01:00 | 0 | 0 | 0 | 5.98 | 9.68 | 0
8259 | 2006-12-11 02:00 | 0 | 0 | 0 | 5.82 | 9.68 | 0
8260 | 2006-12-11 03:00 | 0 | 0 | 0 | 5.67 | 8.99 | 0
8261 | 2006-12-11 04:00 | 0 | 0 | 0 | 5.51 | 8.99 | 0
8262 | 2006-12-11 05:00 | 0 | 0 | 0 | 5.08 | 8.99 | 0
8263 | 2006-12-11 06:00 | 1 | 58 | 0 | 4.65 | 7.59 | 0 | -3.8003 | 115.473 | 83.0334 | 0 | 1 | 1.3941 | 0 | 0.0093692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.65 | 0 | 0 | 0 | 0 | 0 | 0 | 660 | 0 | 0 | 0 | 0 | 0 | 660 | 0 | 0
8264 | 2006-12-11 07:00 | 105 | 592 | 33 | 4.22 | 7.59 | 0 | 6.9125 | 124.18 | 69.8319 | 0 | 105 | 206.259 | 50.4703 | 0.98377 | 34.1523 | 47.2321 | 0.0051349 | 30.9071 | 45.484 | 0.0038693 | 74.1031 | 74.0546 | 166312 | 5.6341 | 141799 | 154465 | 129684 | 0 | 0 | 129485 | 694.753 | 0 | 0 | 0 | 0 | 129485 | 694.753 | 125269 | 122763.9141
8265 | 2006-12-11 08:00 | 284 | 824 | 50 | 5.45 | 7.59 | 0 | 16.4796 | 134.343 | 57.2924 | 0 | 284 | 445.73 | 72.9639 | 2.6609 | 316.994 | 68.2824 | 0.013889 | 303.511 | 65.7553 | 0.010466 | 358.199 | 358.011 | 803946 | 12.2862 | 767961 | 805421 | 687051 | 0 | 0 | 683253 | 734.692 | 0 | 0 | 0 | 793.715 | 682459 | 739.59 | 670572 | 657160.5625
8266 | 2006-12-11 09:00 | 436 | 916 | 59 | 6.68 | 3.38 | 0 | 24.3658 | 146.436 | 45.9969 | 0 | 436 | 634.817 | 79.2934 | 4.085 | 624.723 | 74.2057 | 0.021322 | 610.995 | 71.4594 | 0.016067 | 661.997 | 661.991 | 1486680 | 23.2767 | 1464180 | 1473340 | 1393720 | 0 | 0 | 1379030 | 719.049 | 0 | 0 | 0 | 736.522 | 1378300 | 720.66 | 1354790 | 1327691.5
8267 | 2006-12-11 10:00 | 521 | 935 | 57 | 7.91 | 3.38 | 0 | 29.8832 | 160.659 | 37.1268 | 0 | 521 | 742.519 | 76.1076 | 4.8814 | 742.519 | 71.2244 | 0.025479 | 733.08 | 68.5884 | 0.019199 | 777.637 | 777.635 | 1746370 | 27.4059 | 1734790 | 1716950 | 1670670 | 0 | 0 | 1650280 | 728.608 | 0 | 0 | 0 | 0 | 1650280 | 728.608 | 1619420 | 1587027.875
8268 | 2006-12-11 11:00 | 568 | 954 | 59 | 9.36 | 3.38 | 0 | 32.3342 | 176.53 | 32.7352 | 0 | 568 | 800.513 | 78.4007 | 5.3217 | 800.513 | 73.3703 | 0.027778 | 792.956 | 70.655 | 0.020931 | 837.723 | 837.718 | 1881300 | 30.3623 | 1876350 | 1833920 | 1783340 | 0 | 0 | 1759780 | 721.862 | 0 | 0 | 0 | 0 | 1759780 | 721.862 | 1725740 | 1691227.375
8269 | 2006-12-11 12:00 | 547 | 946 | 57 | 10.81 | 2.38 | 0 | 31.3279 | 192.738 | 34.5794 | 0 | 547 | 775.936 | 75.9612 | 5.125 | 775.936 | 71.0874 | 0.026751 | 767.611 | 68.4565 | 0.020157 | 811.005 | 811.003 | 1821320 | 32.5366 | 1813380 | 1755640 | 1707060 | 0 | 0 | 1685000 | 715.019 | 0 | 0 | 0 | 0 | 1685000 | 715.019 | 1653460 | 1620393.625
8270 | 2006-12-11 13:00 | 486 | 938 | 61 | 12.26 | 2.38 | 0 | 27.032 | 207.767 | 41.8404 | 0 | 486 | 696.668 | 81.4903 | 4.5534 | 696.668 | 76.2618 | 0.023767 | 684.746 | 73.4394 | 0.017909 | 735.457 | 735.453 | 1651640 | 31.9626 | 1635610 | 1587170 | 1546920 | 0 | 0 | 1528610 | 712.007 | 0 | 0 | 0 | 0 | 1528610 | 712.007 | 1501840 | 1471800.5
8271 | 2006-12-11 14:00 | 349 | 870 | 51 | 12.28 | 2.38 | 0 | 20.058 | 220.765 | 52.3011 | 0 | 349 | 531.329 | 69.8035 | 3.2699 | 490.191 | 65.3247 | 0.017067 | 474.62 | 62.9071 | 0.012861 | 521.414 | 521.346 | 1170810 | 26.2467 | 1136740 | 1129150 | 1076870 | 0 | 0 | 1068110 | 720.883 | 0 | 0 | 0 | 0 | 1068110 | 720.883 | 1050760 | 1029744.5
8272 | 2006-12-11 15:00 | 157 | 542 | 52 | 12.3 | 2.25 | 0 | 11.1269 | 231.692 | 64.4084 | 0 | 157 | 235.023 | 76.572 | 1.471 | 180.774 | 71.659 | 0.007678 | 168.887 | 69.0069 | 0.0057855 | 230.763 | 230.712 | 518127 | 18.5345 | 479463 | 491424 | 438662 | 0 | 0 | 437060 | 714.456 | 0 | 0 | 0 | 0 | 437060 | 714.456 | 429348 | 420761.125
8273 | 2006-12-11 16:00 | 14 | 166 | 5 | 12.32 | 2.25 | 0 | 0.84433 | 240.947 | 77.3753 | 0 | 14 | 22.61 | 8.1837 | 0.13117 | 3.4946 | 7.6586 | 0.00068466 | 2.8699 | 7.3752 | 0.0005159 | 9.9382 | 9.9319 | 22307.4 | 12.5884 | 13423.2 | 14224.4 | 11829.6 | 0 | 0 | 11827.5 | 553.926 | 0 | 0 | 0 | 3577.58 | 8249.87 | 660 | 7940.74 | 7781.9287
8274 | 2006-12-11 17:00 | 0 | 0 | 0 | 11.89 | 2.25 | 0
8275 | 2006-12-11 18:00 | 0 | 0 | 0 | 11.45 | 5.65 | 0
8276 | 2006-12-11 19:00 | 0 | 0 | 0 | 11.02 | 5.65 | 0
8277 | 2006-12-11 20:00 | 0 | 0 | 0 | 10.52 | 5.65 | 0
8278 | 2006-12-11 21:00 | 0 | 0 | 0 | 10.03 | 2.07 | 0
8279 | 2006-12-11 22:00 | 0 | 0 | 0 | 9.54 | 2.07 | 0
8280 | 2006-12-11 23:00 | 0 | 0 | 0 | 8.97 | 2.07 | 0
8281 | 2006-12-12 | 0 | 0 | 0 | 8.41 | 2.5 | 0
8282 | 2006-12-12 01:00 | 0 | 0 | 0 | 7.85 | 2.5 | 0
8283 | 2006-12-12 02:00 | 0 | 0 | 0 | 7.45 | 2.5 | 0
8284 | 2006-12-12 03:00 | 0 | 0 | 0 | 7.05 | 1.89 | 0
8285 | 2006-12-12 04:00 | 0 | 0 | 0 | 6.65 | 1.89 | 0
8286 | 2006-12-12 05:00 | 0 | 0 | 0 | 6.18 | 1.89 | 0
8287 | 2006-12-12 06:00 | 1 | 54 | 0 | 5.71 | 5.24 | 0 | -3.9319 | 115.472 | 83.1552 | 0 | 1 | 1.3699 | 0 | 0.0093692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.71 | 0 | 0 | 0 | 0 | 0 | 0 | 660 | 0 | 0 | 0 | 0 | 0 | 660 | 0 | 0
8288 | 2006-12-12 07:00 | 101 | 587 | 31 | 5.23 | 5.24 | 0 | 6.7819 | 124.165 | 69.9587 | 0 | 101 | 203.141 | 48.5631 | 0.94629 | 32.7769 | 45.4472 | 0.0049393 | 29.6336 | 43.7652 | 0.0037219 | 71.2004 | 71.1991 | 159895 | 6.8104 | 135863 | 147139 | 124151 | 0 | 0 | 123955 | 670.767 | 0 | 0 | 0 | 50.921 | 123904 | 673.407 | 120062 | 117660.9688
8289 | 2006-12-12 08:00 | 282 | 688 | 88 | 6.63 | 5.24 | 0 | 16.3526 | 134.308 | 57.4229 | 0 | 282 | 371.007 | 118.559 | 2.6421 | 262.938 | 110.952 | 0.013791 | 251.668 | 106.845 | 0.010392 | 347.768 | 347.473 | 780282 | 14.3429 | 742132 | 772698 | 670685 | 0 | 0 | 667216 | 739.402 | 0 | 0 | 0 | 0 | 667216 | 739.402 | 655626 | 642513.1875
8290 | 2006-12-12 09:00 | 320 | 354 | 175 | 8.02 | 4.58 | 0 | 24.2468 | 146.376 | 46.1274 | 0 | 320 | 244.707 | 207.012 | 2.9981 | 240.484 | 193.73 | 0.015649 | 235.159 | 186.56 | 0.011792 | 409.079 | 409.069 | 918674 | 17.4986 | 878168 | 906682 | 857452 | 0 | 0 | 851878 | 721.06 | 0 | 0 | 0 | 321.889 | 851556 | 722.811 | 837814 | 821058.1875
8291 | 2006-12-12 10:00 | 257 | 75 | 220 | 9.41 | 4.58 | 0 | 29.7792 | 160.567 | 37.2465 | 0 | 257 | 59.3032 | 234.023 | 2.4079 | 59.3032 | 219.008 | 0.012568 | 58.5435 | 210.903 | 0.0094705 | 261.372 | 261.358 | 586945 | 15.466 | 544510 | 568099 | 552347 | 0 | 0 | 550097 | 731.127 | 0 | 0 | 0 | 0 | 550097 | 731.127 | 540609 | 529796.6875
8292 | 2006-12-12 11:00 | 566 | 734 | 176 | 11.27 | 4.58 | 0 | 32.253 | 176.408 | 32.8212 | 0 | 566 | 614.142 | 225.963 | 5.303 | 614.142 | 211.465 | 0.02768 | 608.309 | 203.639 | 0.020857 | 787.609 | 787.599 | 1768750 | 29.5196 | 1758250 | 1724590 | 1677950 | 0 | 0 | 1657170 | 724.133 | 0 | 0 | 0 | 0 | 1657170 | 724.133 | 1626220 | 1593699.375
8293 | 2006-12-12 12:00 | 536 | 925 | 57 | 13.13 | 6.8 | 0 | 31.2754 | 192.597 | 34.6117 | 0 | 536 | 759.367 | 75.994 | 5.0219 | 759.367 | 71.1181 | 0.026213 | 751.202 | 68.4861 | 0.019752 | 795.117 | 795.11 | 1785610 | 29.0937 | 1775930 | 1745190 | 1698070 | 0 | 0 | 1676820 | 725.185 | 0 | 0 | 0 | 0 | 1676820 | 725.185 | 1645250 | 1612348.25
8294 | 2006-12-12 13:00 | 448 | 849 | 63 | 14.99 | 6.8 | 0 | 27.0086 | 207.623 | 41.8249 | 0 | 448 | 631.758 | 84.0396 | 4.1974 | 631.758 | 78.6474 | 0.021909 | 620.956 | 75.7368 | 0.016509 | 675.808 | 675.806 | 1517680 | 28.5584 | 1495720 | 1472950 | 1432050 | 0 | 0 | 1416810 | 722.988 | 0 | 0 | 0 | 0 | 1416810 | 722.988 | 1392240 | 1364397.625
8295 | 2006-12-12 14:00 | 352 | 872 | 53 | 15.02 | 6.8 | 0 | 20.0601 | 220.626 | 52.2537 | 0 | 352 | 533.628 | 72.3878 | 3.298 | 492.312 | 67.7433 | 0.017214 | 476.717 | 65.2361 | 0.012971 | 525.707 | 525.692 | 1180570 | 25.5745 | 1146800 | 1142840 | 1089290 | 0 | 0 | 1080410 | 724.327 | 0 | 0 | 0 | 0 | 1080410 | 724.327 | 1062640 | 1041390.9375
8296 | 2006-12-12 15:00 | 173 | 665 | 44 | 15.05 | 6.23 | 0 | 11.1494 | 231.561 | 64.3403 | 0 | 173 | 288.882 | 64.6952 | 1.6209 | 222.201 | 60.5442 | 0.0084604 | 207.654 | 58.3035 | 0.0063751 | 257.985 | 257.894 | 579167 | 20.4202 | 540961 | 549657 | 485327 | 0 | 0 | 483291 | 705.961 | 0 | 0 | 0 | 0 | 483291 | 705.961 | 475292 | 465786.5
8297 | 2006-12-12 16:00 | 16 | 205 | 4 | 15.08 | 6.23 | 0 | 0.88229 | 240.823 | 77.2931 | 0 | 16 | 30.3399 | 6.2132 | 0.14991 | 4.7069 | 5.8145 | 0.00078247 | 3.8723 | 5.5993 | 0.0005896 | 9.1881 | 9.1806 | 20621.1 | 15.2712 | 12327.4 | 12885.1 | 9639.57 | 0 | 0 | 9637.64 | 523.796 | 0 | 0 | 0 | 4469.15 | 5168.48 | 660 | 4974.14 | 4874.6543
8298 | 2006-12-12 17:00 | 0 | 0 | 0 | 14.08 | 6.23 | 0
8299 | 2006-12-12 18:00 | 0 | 0 | 0 | 13.08 | 5.99 | 0
8300 | 2006-12-12 19:00 | 0 | 0 | 0 | 12.08 | 5.99 | 0
8301 | 2006-12-12 20:00 | 0 | 0 | 0 | 11.41 | 5.99 | 0
8302 | 2006-12-12 21:00 | 0 | 0 | 0 | 10.73 | 5.93 | 0
8303 | 2006-12-12 22:00 | 0 | 0 | 0 | 10.05 | 5.93 | 0
8304 | 2006-12-12 23:00 | 0 | 0 | 0 | 9.56 | 5.93 | 0
8305 | 2006-12-13 | 0 | 0 | 0 | 9.07 | 5.26 | 0
8306 | 2006-12-13 01:00 | 0 | 0 | 0 | 8.57 | 5.26 | 0
8307 | 2006-12-13 02:00 | 0 | 0 | 0 | 8.05 | 5.26 | 0
8308 | 2006-12-13 03:00 | 0 | 0 | 0 | 7.52 | 3 | 0
8309 | 2006-12-13 04:00 | 0 | 0 | 0 | 6.99 | 3 | 0
8310 | 2006-12-13 05:00 | 0 | 0 | 0 | 6.66 | 3 | 0
8311 | 2006-12-13 06:00 | 1 | 50 | 0 | 6.34 | 3.23 | 0 | -4.0601 | 115.464 | 83.2764 | 0 | 1 | 1.3458 | 0 | 0.0093692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.34 | 0 | 0 | 0 | 0 | 0 | 0 | 660 | 0 | 0 | 0 | 0 | 0 | 660 | 0 | 0
8312 | 2006-12-13 07:00 | 99 | 582 | 30 | 6.02 | 3.23 | 0 | 6.6554 | 124.143 | 70.084 | 0 | 99 | 202.802 | 47.5513 | 0.92755 | 30.3796 | 44.5003 | 0.0048415 | 27.4394 | 42.8534 | 0.0036482 | 68.1875 | 68.1801 | 153115 | 7.7463 | 129592 | 139662 | 118101 | 0 | 0 | 117924 | 680.842 | 0 | 0 | 0 | 88.8317 | 117836 | 683.238 | 114028 | 111747.5859
8313 | 2006-12-13 08:00 | 280 | 821 | 51 | 7.16 | 3.23 | 0 | 16.2305 | 134.268 | 57.5508 | 0 | 280 | 439.603 | 74.2232 | 2.6234 | 310.331 | 69.4609 | 0.013693 | 296.929 | 66.8902 | 0.010318 | 352.914 | 352.716 | 792041 | 16.0909 | 755911 | 778718 | 663622 | 0 | 0 | 659997 | 726.816 | 0 | 0 | 0 | 10.7082 | 659986 | 727.195 | 648809 | 635832.875
8314 | 2006-12-13 09:00 | 413 | 887 | 51 | 8.31 | 1.45 | 0 | 24.1338 | 146.31 | 46.2538 | 0 | 413 | 612.203 | 69.202 | 3.8695 | 600.841 | 64.7619 | 0.020197 | 587.436 | 62.3651 | 0.015219 | 630.322 | 630.294 | 1415510 | 26.2786 | 1390270 | 1380880 | 1296660 | 0 | 0 | 1283680 | 712.694 | 0 | 0 | 0 | 251.036 | 1283420 | 713.948 | 1262200 | 1236957.875
8315 | 2006-12-13 10:00 | 515 | 929 | 56 | 9.46 | 1.45 | 0 | 29.6819 | 160.472 | 37.3604 | 0 | 515 | 736.754 | 74.9102 | 4.8251 | 736.754 | 70.1038 | 0.025186 | 727.246 | 67.5093 | 0.018978 | 770.931 | 770.926 | 1731310 | 31.4378 | 1719010 | 1672060 | 1626870 | 0 | 0 | 1606910 | 716.975 | 0 | 0 | 0 | 0 | 1606910 | 716.975 | 1577680 | 1546130.375
8316 | 2006-12-13 11:00 | 571 | 911 | 87 | 11.12 | 1.45 | 0 | 32.1792 | 176.285 | 32.9001 | 0 | 571 | 763.047 | 120.528 | 5.3498 | 763.047 | 112.795 | 0.027924 | 755.759 | 108.62 | 0.021042 | 838.468 | 838.462 | 1882970 | 35.0231 | 1878110 | 1798710 | 1752370 | 0 | 0 | 1728500 | 705.61 | 0 | 0 | 0 | 0 | 1728500 | 705.61 | 1695820 | 1661904
8317 | 2006-12-13 12:00 | 507 | 769 | 110 | 12.78 | 0.68 | 0 | 31.2303 | 192.458 | 34.637 | 0 | 507 | 629.996 | 151.695 | 4.7502 | 629.996 | 141.962 | 0.024794 | 623.21 | 136.708 | 0.018683 | 737.139 | 737.134 | 1655420 | 34.9123 | 1639570 | 1570360 | 1528670 | 0 | 0 | 1510390 | 703.894 | 0 | 0 | 0 | 0 | 1510390 | 703.894 | 1484450 | 1454756.375
8318 | 2006-12-13 13:00 | 485 | 897 | 79 | 14.43 | 0.68 | 0 | 26.9924 | 207.481 | 41.8033 | 0 | 485 | 666.811 | 109.818 | 4.5441 | 666.811 | 102.772 | 0.023718 | 655.426 | 98.9685 | 0.017872 | 731.78 | 731.776 | 1643390 | 36.4014 | 1626980 | 1547900 | 1507280 | 0 | 0 | 1489220 | 698.154 | 0 | 0 | 0 | 0 | 1489220 | 698.154 | 1464040 | 1434758.25
8319 | 2006-12-13 14:00 | 352 | 872 | 53 | 14.72 | 0.68 | 0 | 20.069 | 220.491 | 52.2012 | 0 | 352 | 534.033 | 72.4157 | 3.298 | 492.685 | 67.7694 | 0.017214 | 477.126 | 65.2613 | 0.012971 | 526.128 | 526.076 | 1181440 | 30.5153 | 1147690 | 1118590 | 1067870 | 0 | 0 | 1058920 | 707.189 | 0 | 0 | 0 | 0 | 1058920 | 707.189 | 1042430 | 1021582.5
8320 | 2006-12-13 15:00 | 164 | 583 | 51 | 15.01 | 5.13 | 0 | 11.178 | 231.435 | 64.2681 | 0 | 164 | 253.073 | 75.5823 | 1.5366 | 194.657 | 70.7328 | 0.0080203 | 181.972 | 68.115 | 0.0060434 | 242.591 | 242.546 | 544702 | 20.4324 | 506010 | 514433 | 457933 | 0 | 0 | 456152 | 709.251 | 0 | 0 | 0 | 0 | 456152 | 709.251 | 448368 | 439400.5938
8321 | 2006-12-13 16:00 | 15 | 181 | 5 | 15.3 | 5.13 | 0 | 0.92588 | 240.703 | 77.2076 | 0 | 15 | 25.4505 | 8.2854 | 0.14054 | 3.9908 | 7.7538 | 0.00073356 | 3.2892 | 7.4668 | 0.00055276 | 10.4338 | 10.4278 | 23421.1 | 15.5331 | 14330.7 | 14994.9 | 12176.9 | 0 | 0 | 12174.5 | 546.996 | 0 | 0 | 0 | 4827.68 | 7346.83 | 660 | 7071.25 | 6929.8267
8322 | 2006-12-13 17:00 | 0 | 0 | 0 | 14.8 | 5.13 | 0
8323 | 2006-12-13 18:00 | 0 | 0 | 0 | 14.3 | 4.69 | 0
8324 | 2006-12-13 19:00 | 0 | 0 | 0 | 13.8 | 4.69 | 0
8325 | 2006-12-13 20:00 | 0 | 0 | 0 | 13.24 | 4.69 | 0
8326 | 2006-12-13 21:00 | 0 | 0 | 0 | 12.68 | 6.65 | 0
8327 | 2006-12-13 22:00 | 0 | 0 | 0 | 12.12 | 6.65 | 0
8328 | 2006-12-13 23:00 | 0 | 0 | 0 | 11.55 | 6.65 | 0
8329 | 2006-12-14 | 0 | 0 | 0 | 10.99 | 2.46 | 0
8330 | 2006-12-14 01:00 | 0 | 0 | 0 | 10.43 | 2.46 | 0
8331 | 2006-12-14 02:00 | 0 | 0 | 0 | 9.98 | 2.46 | 0
8332 | 2006-12-14 03:00 | 0 | 0 | 0 | 9.54 | 6.27 | 0
8333 | 2006-12-14 04:00 | 0 | 0 | 0 | 9.09 | 6.27 | 0
8334 | 2006-12-14 05:00 | 0 | 0 | 0 | 8.66 | 6.27 | 0
8335 | 2006-12-14 06:00 | 1 | 36 | 0 | 8.22 | 5.32 | 0 | -4.1846 | 115.45 | 83.3969 | 0 | 1 | 1.3217 | 0 | 0.0093692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.22 | 0 | 0 | 0 | 0 | 0 | 0 | 660 | 0 | 0 | 0 | 0 | 0 | 660 | 0 | 0
8336 | 2006-12-14 07:00 | 96 | 454 | 43 | 7.79 | 5.32 | 0 | 6.5333 | 124.115 | 70.2077 | 0 | 96 | 157.729 | 63.2642 | 0.89945 | 23.2313 | 59.2051 | 0.0046948 | 20.9625 | 57.0139 | 0.0035376 | 75.6405 | 75.6318 | 169850 | 9.4601 | 143794 | 154407 | 136029 | 0 | 0 | 135843 | 690.17 | 0 | 0 | 0 | 0 | 135843 | 690.17 | 131469 | 128839.875
8337 | 2006-12-14 08:00 | 233 | 596 | 68 | 8.93 | 5.32 | 0 | 16.1136 | 134.221 | 57.676 | 0 | 233 | 317.885 | 96.8314 | 2.183 | 223.469 | 90.6186 | 0.011395 | 213.746 | 87.2648 | 0.0085861 | 291.989 | 292.001 | 655708 | 15.378 | 616752 | 640074 | 554996 | 0 | 0 | 552548 | 731.182 | 0 | 0 | 0 | 0 | 552548 | 731.182 | 542798 | 531942.375
8338 | 2006-12-14 09:00 | 380 | 714 | 90 | 10.08 | 4.27 | 0 | 24.0268 | 146.239 | 46.376 | 0 | 380 | 491.394 | 125.329 | 3.5603 | 481.669 | 117.288 | 0.018584 | 470.845 | 112.947 | 0.014003 | 566.292 | 566.278 | 1271740 | 23.47 | 1240930 | 1247960 | 1167390 | 0 | 0 | 1157010 | 718.904 | 0 | 0 | 0 | 0 | 1157010 | 718.904 | 1138130 | 1115367.25
8339 | 2006-12-14 10:00 | 535 | 907 | 88 | 11.22 | 4.27 | 0 | 29.5915 | 160.373 | 37.4684 | 0 | 535 | 718.449 | 121.194 | 5.0125 | 718.449 | 113.418 | 0.026164 | 709.111 | 109.22 | 0.019715 | 793.801 | 793.795 | 1782660 | 29.9898 | 1772830 | 1735410 | 1690130 | 0 | 0 | 1668860 | 721.034 | 0 | 0 | 0 | 0 | 1668860 | 721.034 | 1637650 | 1604899.25
8340 | 2006-12-14 11:00 | 582 | 972 | 67 | 13.11 | 4.27 | 0 | 32.1128 | 176.16 | 32.9719 | 0 | 582 | 812.759 | 88.5816 | 5.4529 | 812.759 | 82.898 | 0.028462 | 804.957 | 79.83 | 0.021447 | 858.264 | 858.263 | 1927440 | 33.4042 | 1924830 | 1856820 | 1807650 | 0 | 0 | 1782710 | 711.648 | 0 | 0 | 0 | 0 | 1782710 | 711.648 | 1748150 | 1713183.875
8341 | 2006-12-14 12:00 | 564 | 966 | 65 | 15 | 5.7 | 0 | 31.1927 | 192.319 | 34.6551 | 0 | 564 | 792.543 | 86.1626 | 5.2842 | 792.543 | 80.6342 | 0.027582 | 783.996 | 77.65 | 0.020784 | 835.817 | 835.812 | 1877020 | 33.0084 | 1871850 | 1808740 | 1759990 | 0 | 0 | 1736410 | 712.775 | 0 | 0 | 0 | 0 | 1736410 | 712.775 | 1703320 | 1669249.125
8342 | 2006-12-14 13:00 | 482 | 935 | 59 | 16.89 | 5.7 | 0 | 26.9835 | 207.342 | 41.7756 | 0 | 482 | 695.245 | 79.0547 | 4.516 | 695.245 | 73.9824 | 0.023572 | 683.395 | 71.2444 | 0.017762 | 732.017 | 732.014 | 1643920 | 32.662 | 1627530 | 1574540 | 1534830 | 0 | 0 | 1516710 | 710.053 | 0 | 0 | 0 | 0 | 1516710 | 710.053 | 1490350 | 1460543.625
8343 | 2006-12-14 14:00 | 349 | 731 | 98 | 17.46 | 5.7 | 0 | 20.0846 | 220.359 | 52.1437 | 0 | 349 | 448.547 | 132.469 | 3.2699 | 413.819 | 123.97 | 0.017067 | 400.794 | 119.382 | 0.012861 | 504.582 | 504.546 | 1133080 | 28.331 | 1097790 | 1080970 | 1034240 | 0 | 0 | 1026000 | 713.515 | 0 | 0 | 0 | 0 | 1026000 | 713.515 | 1009820 | 989626.75
8344 | 2006-12-14 15:00 | 115 | 170 | 82 | 18.03 | 6.34 | 0 | 11.2128 | 231.313 | 64.192 | 0 | 115 | 73.8829 | 102.595 | 1.0775 | 56.8289 | 96.0123 | 0.005624 | 53.1436 | 92.4589 | 0.0042378 | 141.239 | 141.208 | 317119 | 20.9497 | 281396 | 286708 | 267935 | 0 | 0 | 267327 | 689.362 | 0 | 0 | 0 | 0 | 267327 | 689.362 | 260804 | 255587.5156
8345 | 2006-12-14 16:00 | 11 | 53 | 8 | 18.59 | 6.34 | 0 | 0.97504 | 240.589 | 77.119 | 0 | 11 | 7.6872 | 9.6201 | 0.10306 | 1.2058 | 9.0028 | 0.00053795 | 0.99562 | 8.6696 | 0.00040535 | 9.3757 | 9.3714 | 21046.6 | 18.7838 | 12268.7 | 12644.4 | 11880.9 | 0 | 0 | 11879 | 548.468 | 0 | 0 | 0 | 7652.68 | 4226.35 | 660 | 4066.88 | 3985.5396
8346 | 2006-12-14 17:00 | 0 | 0 | 0 | 17.6 | 6.34 | 0
8347 | 2006-12-14 18:00 | 0 | 0 | 0 | 16.6 | 9.96 | 0
8348 | 2006-12-14 19:00 | 0 | 0 | 0 | 15.6 | 9.96 | 0
8349 | 2006-12-14 20:00 | 0 | 0 | 0 | 14.53 | 9.96 | 0
8350 | 2006-12-14 21:00 | 0 | 0 | 0 | 13.47 | 9.18 | 0
8351 | 2006-12-14 22:00 | 0 | 0 | 0 | 12.4 | 9.18 | 0
8352 | 2006-12-14 23:00 | 0 | 0 | 0 | 11.82 | 9.18 | 0
8353 | 2006-12-15 | 0 | 0 | 0 | 11.25 | 8.31 | 0
8354 | 2006-12-15 01:00 | 0 | 0 | 0 | 10.67 | 8.31 | 0
8355 | 2006-12-15 02:00 | 0 | 0 | 0 | 10.34 | 8.31 | 0
8356 | 2006-12-15 03:00 | 0 | 0 | 0 | 10.01 | 7.96 | 0
8357 | 2006-12-15 04:00 | 0 | 0 | 0 | 9.68 | 7.96 | 0
8358 | 2006-12-15 05:00 | 0 | 0 | 0 | 9.36 | 7.96 | 0
8359 | 2006-12-15 06:00 | 1 | 36 | 1 | 9.04 | 12.17 | 0 | -4.3055 | 115.429 | 83.5166 | 0 | 1 | 0 | 0.88096 | 0.0093692 | 0 | 0.82444 | 0 | 0 | 0.79392 | 0 | 0.77011 | 0.77006 | 1729.36 | 9.0511 | 144.948 | 142.212 | 141.388 | 0 | 0 | 141.383 | 116.449 | 0 | 0 | 0 | 141.383 | 0 | 660 | 0 | 0
8360 | 2006-12-15 07:00 | 82 | 478 | 28 | 8.72 | 12.17 | 0 | 6.4155 | 124.081 | 70.3297 | 0 | 82 | 162.674 | 45.4993 | 0.76828 | 23.5429 | 42.58 | 0.0040101 | 21.223 | 41.0041 | 0.0030217 | 60.3632 | 60.358 | 135550 | 9.5901 | 112853 | 121219 | 104398 | 0 | 0 | 104266 | 674.18 | 0 | 0 | 0 | 326.08 | 103940 | 678.48 | 100520 | 98509.1641
8361 | 2006-12-15 08:00 | 266 | 677 | 79 | 10.79 | 12.17 | 0 | 16.0019 | 134.169 | 57.7983 | 0 | 266 | 361.494 | 109.06 | 2.4922 | 253.208 | 102.063 | 0.013008 | 242.111 | 98.2855 | 0.0098022 | 330.194 | 330.17 | 741416 | 15.5497 | 703147 | 729795 | 630396 | 0 | 0 | 627283 | 735.842 | 0 | 0 | 0 | 0 | 627283 | 735.842 | 616314 | 603987.875
8362 | 2006-12-15 09:00 | 357 | 556 | 132 | 12.87 | 11.56 | 0 | 23.9258 | 146.164 | 46.4939 | 0 | 357 | 381.94 | 168.501 | 3.3448 | 373.91 | 157.69 | 0.017459 | 365.449 | 151.854 | 0.013156 | 501.797 | 501.775 | 1126880 | 20.3717 | 1091340 | 1112640 | 1023900 | 0 | 0 | 1016310 | 740.587 | 0 | 0 | 0 | 0 | 1016310 | 740.587 | 998881 | 978903.5
8363 | 2006-12-15 10:00 | 504 | 818 | 102 | 14.94 | 11.56 | 0 | 29.5079 | 160.27 | 37.5705 | 0 | 504 | 646.9 | 137.372 | 4.7221 | 646.9 | 128.558 | 0.024648 | 638.436 | 123.8 | 0.018573 | 739.387 | 739.376 | 1660450 | 25.9939 | 1644830 | 1637760 | 1592250 | 0 | 0 | 1573990 | 733.732 | 0 | 0 | 0 | 0 | 1573990 | 733.732 | 1545170 | 1514270.625
8364 | 2006-12-15 11:00 | 559 | 845 | 112 | 16.71 | 11.56 | 0 | 32.0539 | 176.034 | 33.0364 | 0 | 559 | 706.085 | 149.725 | 5.2374 | 706.085 | 140.119 | 0.027337 | 699.277 | 134.933 | 0.020599 | 809.204 | 809.201 | 1817260 | 28.8078 | 1809130 | 1780090 | 1732210 | 0 | 0 | 1710160 | 725.288 | 0 | 0 | 0 | 0 | 1710160 | 725.288 | 1677580 | 1644031.125
8365 | 2006-12-15 12:00 | 504 | 768 | 108 | 18.47 | 8.76 | 0 | 31.1627 | 192.181 | 34.6661 | 0 | 504 | 629.413 | 149.355 | 4.7221 | 629.413 | 139.772 | 0.024648 | 622.621 | 134.599 | 0.018573 | 734.521 | 734.511 | 1649530 | 31.5023 | 1633400 | 1588330 | 1546560 | 0 | 0 | 1528380 | 714.906 | 0 | 0 | 0 | 0 | 1528380 | 714.906 | 1501520 | 1471484.75
8366 | 2006-12-15 13:00 | 438 | 823 | 66 | 20.23 | 8.76 | 0 | 26.9818 | 207.205 | 41.7418 | 0 | 438 | 611.78 | 87.8776 | 4.1037 | 611.78 | 82.2392 | 0.02142 | 601.373 | 79.1956 | 0.01614 | 660.168 | 660.165 | 1482560 | 31.9432 | 1459130 | 1415800 | 1380870 | 0 | 0 | 1366110 | 708.858 | 0 | 0 | 0 | 0 | 1366110 | 708.858 | 1343240 | 1316373
8367 | 2006-12-15 14:00 | 336 | 834 | 50 | 19.84 | 8.76 | 0 | 20.1069 | 220.232 | 52.0813 | 0 | 336 | 511.266 | 68.6187 | 3.1481 | 471.682 | 64.216 | 0.016432 | 456.889 | 61.8394 | 0.012382 | 503.179 | 503.107 | 1129850 | 28.7665 | 1094570 | 1075780 | 1027430 | 0 | 0 | 1019230 | 711.034 | 0 | 0 | 0 | 0 | 1019230 | 711.034 | 1003310 | 983241.375
8368 | 2006-12-15 15:00 | 170 | 624 | 48 | 19.45 | 9.9 | 0 | 11.2536 | 231.196 | 64.112 | 0 | 170 | 272.95 | 69.0353 | 1.5928 | 209.946 | 64.6058 | 0.0083137 | 196.401 | 62.2148 | 0.0062645 | 250.864 | 250.814 | 563270 | 23.5971 | 524844 | 526371 | 466312 | 0 | 0 | 464390 | 696.477 | 0 | 0 | 0 | 0 | 464390 | 696.477 | 456904 | 447766.3438
8369 | 2006-12-15 16:00 | 16 | 196 | 5 | 19.06 | 9.9 | 0 | 1.0297 | 240.48 | 77.0273 | 0 | 16 | 28.3834 | 8.4028 | 0.14991 | 4.5035 | 7.8637 | 0.00078247 | 3.7256 | 7.5726 | 0.0005896 | 10.9599 | 10.9435 | 24579.4 | 19.2409 | 15280.1 | 15714.8 | 12561.6 | 0 | 0 | 12558.9 | 535.34 | 0 | 0 | 0 | 6815.92 | 5743 | 660 | 5527.2 | 5416.6528
8370 | 2006-12-15 17:00 | 0 | 0 | 0 | 17.78 | 9.9 | 0
8371 | 2006-12-15 18:00 | 0 | 0 | 0 | 16.5 | 8.75 | 0
8372 | 2006-12-15 19:00 | 0 | 0 | 0 | 15.22 | 8.75 | 0
8373 | 2006-12-15 20:00 | 0 | 0 | 0 | 14.25 | 8.75 | 0
8374 | 2006-12-15 21:00 | 0 | 0 | 0 | 13.27 | 10.81 | 0
8375 | 2006-12-15 22:00 | 0 | 0 | 0 | 12.3 | 10.81 | 0
8376 | 2006-12-15 23:00 | 0 | 0 | 0 | 11.65 | 10.81 | 0
8377 | 2006-12-16 | 0 | 0 | 0 | 10.99 | 13.2 | 0
8378 | 2006-12-16 01:00 | 0 | 0 | 0 | 10.34 | 13.2 | 0
8379 | 2006-12-16 02:00 | 0 | 0 | 0 | 9.87 | 13.2 | 0
8380 | 2006-12-16 03:00 | 0 | 0 | 0 | 9.41 | 12.43 | 0
8381 | 2006-12-16 04:00 | 0 | 0 | 0 | 8.94 | 12.43 | 0
8382 | 2006-12-16 05:00 | 0 | 0 | 0 | 8.2 | 12.43 | 0
8383 | 2006-12-16 06:00 | 0 | 0 | 0 | 7.45 | 12.86 | 0
8384 | 2006-12-16 07:00 | 32 | 0 | 32 | 6.71 | 12.86 | 0 | 6.3022 | 124.041 | 70.4499 | 0 | 32 | 0 | 30.4155 | 0.29981 | 0 | 28.464 | 0.0015649 | 0 | 27.4106 | 0.0011792 | 26.5894 | 26.5886 | 59711 | 7.078 | 43852.8 | 48043.2 | 46786.3 | 0 | 0 | 46766.1 | 655.742 | 0 | 0 | 0 | 20.5978 | 46745.5 | 660 | 45100.3 | 44198.2695
8385 | 2006-12-16 08:00 | 102 | 6 | 100 | 7.75 | 12.86 | 0 | 15.8954 | 134.111 | 57.9177 | 0 | 102 | 3.8786 | 98.4661 | 0.95566 | 2.7076 | 92.1484 | 0.0049882 | 2.5881 | 88.738 | 0.0037587 | 88.5899 | 88.5864 | 198941 | 8.9761 | 169153 | 182696 | 177040 | 0 | 0 | 176794 | 709.29 | 0 | 0 | 0 | 0 | 176794 | 709.29 | 171177 | 167753.375
8386 | 2006-12-16 09:00 | 100 | 0 | 100 | 8.79 | 10.89 | 0 | 23.831 | 146.083 | 46.6075 | 0 | 100 | 0 | 93.95 | 0.93692 | 0 | 87.922 | 0.0048904 | 0 | 84.668 | 0.003685 | 82.1316 | 82.1282 | 184438 | 10.0684 | 155679 | 167382 | 162613 | 0 | 0 | 162401 | 701.665 | 0 | 0 | 0 | 0 | 162401 | 701.665 | 157204 | 154060.1094
8387 | 2006-12-16 10:00 | 175 | 6 | 172 | 9.83 | 10.89 | 0 | 29.4314 | 160.164 | 37.6666 | 0 | 175 | 4.8328 | 167.304 | 1.6396 | 4.8328 | 156.569 | 0.0085582 | 4.7692 | 150.775 | 0.0064488 | 150.884 | 150.871 | 338819 | 12.1785 | 301734 | 320225 | 311014 | 0 | 0 | 310278 | 721.082 | 0 | 0 | 0 | 0 | 310278 | 721.082 | 302737 | 296682.2812
8388 | 2006-12-16 11:00 | 294 | 96 | 243 | 10.39 | 10.89 | 0 | 32.0024 | 175.906 | 33.0937 | 0 | 294 | 80.6234 | 261.021 | 2.7546 | 80.6234 | 244.274 | 0.014378 | 79.8428 | 235.233 | 0.010834 | 305.634 | 305.638 | 686384 | 15.1476 | 643602 | 671994 | 651887 | 0 | 0 | 648835 | 740.358 | 0 | 0 | 0 | 0 | 648835 | 740.358 | 637796 | 625039.8125
8389 | 2006-12-16 12:00 | 179 | 4 | 177 | 10.96 | 16.24 | 0 | 31.1402 | 192.043 | 34.67 | 0 | 179 | 3.1808 | 171.778 | 1.6771 | 3.1808 | 160.757 | 0.0087538 | 3.1464 | 154.807 | 0.0065962 | 153.221 | 153.211 | 344071 | 12.7086 | 306788 | 324797 | 315964 | 0 | 0 | 315202 | 719.546 | 0 | 0 | 0 | 0 | 315202 | 719.546 | 307679 | 301525.75
8390 | 2006-12-16 13:00 | 365 | 404 | 182 | 11.53 | 16.24 | 0 | 26.9873 | 207.07 | 41.7019 | 0 | 365 | 301.087 | 214.712 | 3.4198 | 301.087 | 200.936 | 0.01785 | 295.978 | 193.499 | 0.01345 | 474.805 | 474.79 | 1066260 | 16.9487 | 1028670 | 1064350 | 1034600 | 0 | 0 | 1027130 | 748.768 | 0 | 0 | 0 | 0 | 1027130 | 748.768 | 1009200 | 989018
8391 | 2006-12-16 14:00 | 236 | 319 | 126 | 10.33 | 16.24 | 0 | 20.1357 | 220.108 | 52.0141 | 0 | 236 | 196.666 | 149.877 | 2.2111 | 181.439 | 140.26 | 0.011541 | 175.771 | 135.07 | 0.0086967 | 301.524 | 301.496 | 677084 | 13.7709 | 634478 | 666294 | 639455 | 0 | 0 | 636544 | 744.109 | 0 | 0 | 0 | 0 | 636544 | 744.109 | 625604 | 613092.125
8392 | 2006-12-16 15:00 | 168 | 352 | 99 | 9.13 | 9.05 | 0 | 11.3005 | 231.084 | 64.0281 | 0 | 168 | 154.205 | 127.441 | 1.574 | 118.611 | 119.264 | 0.0082159 | 110.999 | 114.85 | 0.0061909 | 219.08 | 219.002 | 491828 | 12.9462 | 451894 | 476261 | 436913 | 0 | 0 | 435463 | 732.908 | 0 | 0 | 0 | 0 | 435463 | 732.908 | 427205 | 418660.5312
8393 | 2006-12-16 16:00 | 16 | 112 | 10 | 7.93 | 9.05 | 0 | 1.0898 | 240.377 | 76.9327 | 0 | 16 | 15.5928 | 14.0757 | 0.14991 | 3.0513 | 13.1726 | 0.00078247 | 2.5291 | 12.6851 | 0.0005896 | 14.7583 | 14.7521 | 33131.6 | 8.1871 | 21855.7 | 23760.2 | 21606.5 | 0 | 0 | 21601.4 | 616.131 | 0 | 0 | 0 | 1060.28 | 20541.2 | 660 | 19786.1 | 19390.3418
8394 | 2006-12-16 17:00 | 0 | 0 | 0 | 7.38 | 9.05 | 0
8395 | 2006-12-16 18:00 | 0 | 0 | 0 | 6.83 | 12.26 | 0
8396 | 2006-12-16 19:00 | 0 | 0 | 0 | 6.28 | 12.26 | 0
8397 | 2006-12-16 20:00 | 0 | 0 | 0 | 5.63 | 12.26 | 0
8398 | 2006-12-16 21:00 | 0 | 0 | 0 | 4.99 | 9.51 | 0
8399 | 2006-12-16 22:00 | 0 | 0 | 0 | 4.35 | 9.51 | 0
8400 | 2006-12-16 23:00 | 0 | 0 | 0 | 3.88 | 9.51 | 0
8401 | 2006-12-17 | 0 | 0 | 0 | 3.4 | 9.71 | 0
8402 | 2006-12-17 01:00 | 0 | 0 | 0 | 2.93 | 9.71 | 0
8403 | 2006-12-17 02:00 | 0 | 0 | 0 | 2.46 | 9.71 | 0
8404 | 2006-12-17 03:00 | 0 | 0 | 0 | 2 | 11.39 | 0
8405 | 2006-12-17 04:00 | 0 | 0 | 0 | 1.53 | 11.39 | 0
8406 | 2006-12-17 05:00 | 0 | 0 | 0 | 1.22 | 11.39 | 0
8407 | 2006-12-17 06:00 | 1 | 36 | 1 | 0.91 | 10.48 | 0 | -4.5359 | 115.367 | 83.7532 | 0 | 1 | 0 | 0.88527 | 0.0093692 | 0 | 0.82847 | 0 | 0 | 0.79781 | 0 | 0.77388 | 0.77385 | 1737.88 | 0.92235 | 146.393 | 142.221 | 141.424 | 0 | 0 | 141.418 | 116.024 | 0 | 0 | 0 | 141.418 | 0 | 660 | 0 | 0
8408 | 2006-12-17 07:00 | 91 | 564 | 29 | 0.6 | 10.48 | 0 | 6.1934 | 123.994 | 70.5682 | 0 | 91 | 191.189 | 46.3382 | 0.8526 | 25.5029 | 43.3651 | 0.0044503 | 22.9452 | 41.7602 | 0.0033534 | 62.7674 | 62.8216 | 141084 | 1.6025 | 118363 | 131486 | 112320 | 0 | 0 | 112166 | 699.548 | 0 | 0 | 0 | 0 | 112166 | 699.548 | 108328 | 106160.9844
8409 | 2006-12-17 08:00 | 271 | 815 | 49 | 1.88 | 10.48 | 0 | 15.7944 | 134.047 | 58.034 | 0 | 271 | 431.802 | 71.8791 | 2.5391 | 300.306 | 67.2672 | 0.013253 | 286.96 | 64.7777 | 0.0099864 | 341.195 | 340.975 | 765667 | 7.3215 | 729472 | 781436 | 660081 | 0 | 0 | 656757 | 758.312 | 0 | 0 | 0 | 0 | 656757 | 758.312 | 644509 | 631618.5
8410 | 2006-12-17 09:00 | 424 | 912 | 58 | 3.16 | 6.06 | 0 | 23.7425 | 145.997 | 46.7167 | 0 | 424 | 623.238 | 78.2635 | 3.9726 | 585.3 | 73.2419 | 0.020735 | 571.881 | 70.5313 | 0.015624 | 623.155 | 623.072 | 1399290 | 16.2769 | 1373740 | 1422290 | 1291760 | 0 | 0 | 1279910 | 750.241 | 0 | 0 | 0 | 0 | 1279910 | 750.241 | 1256820 | 1231683.125
8411 | 2006-12-17 10:00 | 530 | 955 | 63 | 4.44 | 6.06 | 0 | 29.3618 | 160.054 | 37.7566 | 0 | 530 | 753.012 | 83.8891 | 4.9657 | 753.012 | 78.5066 | 0.025919 | 743.041 | 75.6011 | 0.019531 | 794.102 | 794.099 | 1783350 | 21.1574 | 1773560 | 1801560 | 1749070 | 0 | 0 | 1728020 | 750.557 | 0 | 0 | 0 | 0 | 1728020 | 750.557 | 1693650 | 1659776.875
8412 | 2006-12-17 11:00 | 573 | 967 | 63 | 5.29 | 6.06 | 0 | 31.9583 | 175.777 | 33.1438 | 0 | 573 | 806.766 | 83.6252 | 5.3686 | 806.766 | 78.2597 | 0.028022 | 798.928 | 75.3633 | 0.021115 | 848.083 | 848.081 | 1904580 | 23.1438 | 1900810 | 1915060 | 1859830 | 0 | 0 | 1835840 | 746.919 | 0 | 0 | 0 | 0 | 1835840 | 746.919 | 1798440 | 1762475
8413 | 2006-12-17 12:00 | 563 | 967 | 65 | 6.14 | 7.03 | 0 | 31.1252 | 191.906 | 34.6668 | 0 | 563 | 792.386 | 86.225 | 5.2749 | 792.386 | 80.6926 | 0.027533 | 783.835 | 77.7062 | 0.020747 | 835.715 | 835.709 | 1876800 | 22.6748 | 1871620 | 1889340 | 1837080 | 0 | 0 | 1813780 | 748.665 | 0 | 0 | 0 | 0 | 1813780 | 748.665 | 1776910 | 1741374.5
8414 | 2006-12-17 13:00 | 486 | 938 | 61 | 6.99 | 7.03 | 0 | 26.9999 | 206.939 | 41.6559 | 0 | 486 | 699.441 | 81.6355 | 4.5534 | 699.441 | 76.3977 | 0.023767 | 687.605 | 73.5702 | 0.017909 | 738.358 | 738.355 | 1658150 | 21.5986 | 1642420 | 1665520 | 1619050 | 0 | 0 | 1600840 | 747.638 | 0 | 0 | 0 | 0 | 1600840 | 747.638 | 1570480 | 1539067.375
8415 | 2006-12-17 14:00 | 352 | 873 | 51 | 6.98 | 7.03 | 0 | 20.1713 | 219.988 | 51.942 | 0 | 352 | 538.107 | 69.9243 | 3.298 | 496.445 | 65.4378 | 0.017214 | 481.001 | 63.016 | 0.012971 | 527.709 | 527.661 | 1184990 | 17.42 | 1151360 | 1187570 | 1130170 | 0 | 0 | 1121280 | 751.63 | 0 | 0 | 0 | 0 | 1121280 | 751.63 | 1101360 | 1079328
8416 | 2006-12-17 15:00 | 161 | 539 | 55 | 6.97 | 4.39 | 0 | 11.3533 | 230.977 | 63.9405 | 0 | 161 | 236.547 | 80.2464 | 1.5084 | 181.946 | 75.0977 | 0.0078736 | 170.335 | 72.3184 | 0.0059329 | 235.379 | 235.279 | 528382 | 12.4898 | 489546 | 515405 | 459066 | 0 | 0 | 457416 | 735.419 | 0 | 0 | 0 | 0 | 457416 | 735.419 | 448807 | 439831.0625
8417 | 2006-12-17 16:00 | 15 | 172 | 5 | 6.96 | 4.39 | 0 | 1.1553 | 240.279 | 76.8352 | 0 | 15 | 26.1785 | 8.5347 | 0.14054 | 5.1349 | 7.9871 | 0.00073356 | 4.2643 | 7.6915 | 0.00055276 | 11.5976 | 11.5853 | 26021.3 | 7.2318 | 16431.7 | 17859 | 14294.8 | 0 | 0 | 14292 | 587.76 | 0 | 0 | 0 | 1555.21 | 12736.8 | 660 | 12262.9 | 12017.5967
8418 | 2006-12-17 17:00 | 0 | 0 | 0 | 6.34 | 4.39 | 0
8419 | 2006-12-17 18:00 | 0 | 0 | 0 | 5.72 | 4.84 | 0
8420 | 2006-12-17 19:00 | 0 | 0 | 0 | 5.1 | 4.84 | 0
8421 | 2006-12-17 20:00 | 0 | 0 | 0 | 4.5 | 4.84 | 0
8422 | 2006-12-17 21:00 | 0 | 0 | 0 | 3.9 | 4.18 | 0
8423 | 2006-12-17 22:00 | 0 | 0 | 0 | 3.31 | 4.18 | 0
8424 | 2006-12-17 23:00 | 0 | 0 | 0 | 2.73 | 4.18 | 0
8425 | 2006-12-18 | 0 | 0 | 0 | 2.16 | 5.42 | 0
8426 | 2006-12-18 01:00 | 0 | 0 | 0 | 1.58 | 5.42 | 0
8427 | 2006-12-18 02:00 | 0 | 0 | 0 | 0.76 | 5.42 | 0
8428 | 2006-12-18 03:00 | 0 | 0 | 0 | -0.06 | 6.64 | 0
8429 | 2006-12-18 04:00 | 0 | 0 | 0 | -0.88 | 6.64 | 0
8430 | 2006-12-18 05:00 | 0 | 0 | 0 | -1.4 | 6.64 | 0
8431 | 2006-12-18 06:00 | 1 | 33 | 1 | -1.91 | 9.86 | 0 | -4.6452 | 115.325 | 83.8698 | 0 | 1 | 0 | 0.88741 | 0.0093692 | 0 | 0.83048 | 0 | 0 | 0.79974 | 0 | 0.77575 | 0.77574 | 1742.12 | -1.8971 | 147.11 | 142.428 | 141.606 | 0 | 0 | 141.6 | 116.348 | 0 | 0 | 0 | 141.6 | 0 | 660 | 0 | 0
8432 | 2006-12-18 07:00 | 90 | 560 | 29 | -2.43 | 9.86 | 0 | 6.0893 | 123.941 | 70.6844 | 0 | 90 | 190.207 | 46.2541 | 0.84323 | 25.0595 | 43.2863 | 0.0044014 | 22.5244 | 41.6843 | 0.0033165 | 62.2857 | 62.2452 | 139792 | -1.3983 | 117128 | 131801 | 112887 | 0 | 0 | 112738 | 717.183 | 0 | 0 | 0 | 0 | 112738 | 717.183 | 108699 | 106525.2969
8433 | 2006-12-18 08:00 | 256 | 587 | 97 | -1.04 | 9.86 | 0 | 15.6987 | 133.978 | 58.1472 | 0 | 256 | 310.115 | 126.617 | 2.3985 | 214.859 | 118.493 | 0.012519 | 205.245 | 114.108 | 0.0094337 | 309.781 | 309.687 | 695421 | 4.0932 | 656077 | 714058 | 621793 | 0 | 0 | 619051 | 766.087 | 0 | 0 | 0 | 0 | 619051 | 766.087 | 607405 | 595256.625
8434 | 2006-12-18 09:00 | 174 | 88 | 139 | 0.36 | 8.5 | 0 | 23.6602 | 145.907 | 46.8213 | 0 | 174 | 59.6785 | 153.198 | 1.6302 | 55.9765 | 143.368 | 0.0085093 | 54.6852 | 138.062 | 0.0064119 | 186.971 | 186.966 | 419881 | 3.7316 | 380253 | 417792 | 397754 | 0 | 0 | 396670 | 759.692 | 0 | 0 | 0 | 0 | 396670 | 759.692 | 388190 | 380426.5625
8435 | 2006-12-18 10:00 | 348 | 263 | 220 | 1.75 | 8.5 | 0 | 29.2993 | 159.942 | 37.8406 | 0 | 348 | 206.559 | 259.715 | 3.2605 | 206.559 | 243.052 | 0.017019 | 203.809 | 234.056 | 0.012824 | 424.742 | 424.728 | 953828 | 9.4092 | 913775 | 975316 | 945312 | 0 | 0 | 939415 | 770.964 | 0 | 0 | 0 | 0 | 939415 | 770.964 | 922123 | 903680.5625
8436 | 2006-12-18 11:00 | 505 | 670 | 152 | 2.8 | 8.5 | 0 | 31.9218 | 175.647 | 33.1866 | 0 | 505 | 558.707 | 200.623 | 4.7315 | 558.707 | 187.751 | 0.024697 | 553.262 | 180.802 | 0.018609 | 712.061 | 712.053 | 1599090 | 15.6405 | 1580680 | 1642110 | 1595800 | 0 | 0 | 1578940 | 766.169 | 0 | 0 | 0 | 0 | 1578940 | 766.169 | 1547830 | 1516875.5
8437 | 2006-12-18 12:00 | 541 | 786 | 136 | 3.84 | 6.53 | 0 | 31.1178 | 191.771 | 34.6564 | 0 | 541 | 644.629 | 182.272 | 5.0687 | 644.629 | 170.577 | 0.026457 | 637.677 | 164.264 | 0.019936 | 777.903 | 777.897 | 1746960 | 19.7299 | 1735410 | 1773130 | 1722300 | 0 | 0 | 1702200 | 756.412 | 0 | 0 | 0 | 0 | 1702200 | 756.412 | 1668120 | 1634761.375
8438 | 2006-12-18 13:00 | 403 | 559 | 150 | 4.89 | 6.53 | 0 | 27.0198 | 206.81 | 41.604 | 0 | 403 | 416.426 | 190.433 | 3.7758 | 416.426 | 178.214 | 0.019708 | 409.402 | 171.619 | 0.014851 | 563.604 | 563.59 | 1265680 | 16.4023 | 1234020 | 1278950 | 1242850 | 0 | 0 | 1232340 | 756.91 | 0 | 0 | 0 | 0 | 1232340 | 756.91 | 1209870 | 1185669.125
8439 | 2006-12-18 14:00 | 240 | 282 | 143 | 4.96 | 6.53 | 0 | 20.2133 | 219.873 | 51.8651 | 0 | 240 | 173.361 | 170.564 | 2.2486 | 159.938 | 159.62 | 0.011737 | 154.985 | 153.713 | 0.0088441 | 299.445 | 299.425 | 672431 | 11.0763 | 629798 | 668836 | 642911 | 0 | 0 | 640037 | 752.869 | 0 | 0 | 0 | 0 | 640037 | 752.869 | 628782 | 616206.0625
8440 | 2006-12-18 15:00 | 179 | 396 | 100 | 5.03 | 6.72 | 0 | 11.4121 | 230.874 | 63.8492 | 0 | 179 | 175.97 | 128.628 | 1.6771 | 135.352 | 120.375 | 0.0087538 | 126.764 | 115.92 | 0.0065962 | 235.41 | 235.327 | 528489 | 9.7789 | 488257 | 521093 | 476002 | 0 | 0 | 474334 | 746.346 | 0 | 0 | 0 | 0 | 474334 | 746.346 | 465232 | 455927.4062
8441 | 2006-12-18 16:00 | 18 | 128 | 10 | 5.1 | 6.72 | 0 | 1.226 | 240.187 | 76.7349 | 0 | 18 | 21.0994 | 15.1689 | 0.16865 | 4.1396 | 14.1956 | 0.00088028 | 3.4446 | 13.6703 | 0.00066331 | 16.602 | 16.5931 | 37266.7 | 5.4348 | 25262.8 | 27828.2 | 24771.2 | 0 | 0 | 24764.7 | 632.421 | 0 | 0 | 0 | 407.46 | 24357.3 | 660 | 23467.5 | 22998.1953
8442 | 2006-12-18 17:00 | 0 | 0 | 0 | 4.91 | 6.72 | 0
8443 | 2006-12-18 18:00 | 0 | 0 | 0 | 4.72 | 8.34 | 0
8444 | 2006-12-18 19:00 | 0 | 0 | 0 | 4.54 | 8.34 | 0
8445 | 2006-12-18 20:00 | 0 | 0 | 0 | 4.23 | 8.34 | 0
8446 | 2006-12-18 21:00 | 0 | 0 | 0 | 3.92 | 7.22 | 0
8447 | 2006-12-18 22:00 | 0 | 0 | 0 | 3.61 | 7.22 | 0
8448 | 2006-12-18 23:00 | 0 | 0 | 0 | 3.05 | 7.22 | 0
8449 | 2006-12-19 | 0 | 0 | 0 | 2.49 | 6.07 | 0
8450 | 2006-12-19 01:00 | 0 | 0 | 0 | 1.93 | 6.07 | 0
8451 | 2006-12-19 02:00 | 0 | 0 | 0 | 1.3 | 6.07 | 0
8452 | 2006-12-19 03:00 | 0 | 0 | 0 | 0.68 | 9.28 | 0
8453 | 2006-12-19 04:00 | 0 | 0 | 0 | 0.06 | 9.28 | 0
8454 | 2006-12-19 05:00 | 0 | 0 | 0 | -0.41 | 9.28 | 0
8455 | 2006-12-19 06:00 | 0 | 30 | 0 | -0.89 | 5.99 | 0
8456 | 2006-12-19 07:00 | 85 | 549 | 27 | -1.36 | 5.99 | 0 | 5.99 | 123.882 | 70.7984 | 0 | 85 | 182.796 | 44.3317 | 0.79638 | 23.7871 | 41.4873 | 0.0041569 | 21.3602 | 39.9518 | 0.0031323 | 59.4757 | 59.4467 | 133510 | -0.10288 | 111328 | 124517 | 106872 | 0 | 0 | 106734 | 707.455 | 0 | 0 | 0 | 0 | 106734 | 707.455 | 102961 | 100901.6797
8457 | 2006-12-19 08:00 | 254 | 791 | 41 | -0.18 | 5.99 | 0 | 15.6087 | 133.903 | 58.2571 | 0 | 254 | 416.483 | 57.9786 | 2.3798 | 287.559 | 54.2586 | 0.012422 | 274.608 | 52.2505 | 0.00936 | 317.062 | 316.924 | 711654 | 6.522 | 675379 | 724788 | 610148 | 0 | 0 | 607282 | 759.375 | 0 | 0 | 0 | 0 | 607282 | 759.375 | 595796 | 583880
8458 | 2006-12-19 09:00 | 420 | 908 | 58 | 1.01 | 6.36 | 0 | 23.5843 | 145.812 | 46.9213 | 0 | 420 | 617.966 | 78.3088 | 3.9351 | 579.02 | 73.2843 | 0.02054 | 565.584 | 70.5721 | 0.015477 | 617.086 | 616.997 | 1385640 | 13.7512 | 1359680 | 1421950 | 1282400 | 0 | 0 | 1271190 | 767.764 | 0 | 0 | 0 | 0 | 1271190 | 767.764 | 1247220 | 1222271.375
8459 | 2006-12-19 10:00 | 518 | 944 | 58 | 2.19 | 6.36 | 0 | 29.2439 | 159.826 | 37.9183 | 0 | 518 | 742.82 | 77.5973 | 4.8533 | 742.82 | 72.6185 | 0.025332 | 732.881 | 69.931 | 0.019089 | 778.746 | 778.745 | 1748860 | 18.2713 | 1737400 | 1785610 | 1734130 | 0 | 0 | 1713880 | 758.929 | 0 | 0 | 0 | 0 | 1713880 | 758.929 | 1679230 | 1645649.375
8460 | 2006-12-19 11:00 | 577 | 971 | 66 | 3.25 | 6.36 | 0 | 31.8929 | 175.516 | 33.2222 | 0 | 577 | 809.108 | 87.427 | 5.406 | 809.108 | 81.8176 | 0.028218 | 801.204 | 78.7896 | 0.021263 | 853.614 | 853.608 | 1916990 | 20.8773 | 1913850 | 1946080 | 1890610 | 0 | 0 | 1866260 | 753.906 | 0 | 0 | 0 | 0 | 1866260 | 753.906 | 1827210 | 1790668
8461 | 2006-12-19 12:00 | 563 | 966 | 65 | 4.3 | 1.59 | 0 | 31.1179 | 191.636 | 34.6389 | 0 | 563 | 792.82 | 86.2469 | 5.2749 | 792.82 | 80.7131 | 0.027533 | 784.28 | 77.726 | 0.020747 | 836.166 | 836.163 | 1877810 | 27.9148 | 1872680 | 1849490 | 1801610 | 0 | 0 | 1778050 | 729.997 | 0 | 0 | 0 | 0 | 1778050 | 729.997 | 1743270 | 1708407.5
8462 | 2006-12-19 13:00 | 468 | 919 | 51 | 5.35 | 1.59 | 0 | 27.0468 | 206.685 | 41.546 | 0 | 468 | 686.344 | 68.9052 | 4.3848 | 686.344 | 64.4842 | 0.022887 | 674.808 | 62.0976 | 0.017246 | 714.815 | 714.811 | 1605290 | 25.5376 | 1587160 | 1583230 | 1541530 | 0 | 0 | 1524330 | 732.954 | 0 | 0 | 0 | 0 | 1524330 | 732.954 | 1496930 | 1466987.375
8463 | 2006-12-19 14:00 | 356 | 874 | 54 | 5.56 | 1.59 | 0 | 20.2619 | 219.762 | 51.7836 | 0 | 356 | 539.476 | 73.7613 | 3.3354 | 497.707 | 69.0287 | 0.01741 | 482.366 | 66.474 | 0.013119 | 532.388 | 532.359 | 1195550 | 20.5948 | 1162240 | 1182580 | 1125430 | 0 | 0 | 1116380 | 741.313 | 0 | 0 | 0 | 0 | 1116380 | 741.313 | 1097070 | 1075132.5
8464 | 2006-12-19 15:00 | 180 | 678 | 45 | 5.77 | 4.46 | 0 | 11.4767 | 230.777 | 63.7543 | 0 | 180 | 300.047 | 66.132 | 1.6865 | 230.789 | 61.8888 | 0.0088027 | 216.234 | 59.5984 | 0.0066331 | 267.564 | 267.458 | 600646 | 12.0161 | 562463 | 592057 | 521389 | 0 | 0 | 519260 | 742.755 | 0 | 0 | 0 | 0 | 519260 | 742.755 | 509740 | 499545.5625
8465 | 2006-12-19 16:00 | 18 | 221 | 5 | 5.97 | 4.46 | 0 | 1.302 | 240.101 | 76.632 | 0 | 18 | 34.5477 | 7.909 | 0.16865 | 8.1164 | 7.4016 | 0.00088028 | 6.767 | 7.1276 | 0.00066331 | 13.4784 | 13.4719 | 30259.5 | 6.2846 | 20089.7 | 21935.3 | 16559.7 | 0 | 0 | 16555.3 | 587.793 | 0 | 0 | 0 | 1318.52 | 15236.8 | 660 | 14672.3 | 14378.8359
8466 | 2006-12-19 17:00 | 0 | 0 | 0 | 5.41 | 4.46 | 0
8467 | 2006-12-19 18:00 | 0 | 0 | 0 | 4.85 | 3.9 | 0
8468 | 2006-12-19 19:00 | 0 | 0 | 0 | 4.29 | 3.9 | 0
8469 | 2006-12-19 20:00 | 0 | 0 | 0 | 3.96 | 3.9 | 0
8470 | 2006-12-19 21:00 | 0 | 0 | 0 | 3.62 | 3.79 | 0
8471 | 2006-12-19 22:00 | 0 | 0 | 0 | 3.28 | 3.79 | 0
8472 | 2006-12-19 23:00 | 0 | 0 | 0 | 2.76 | 3.79 | 0
8473 | 2006-12-20 | 0 | 0 | 0 | 2.25 | 0.85 | 0
8474 | 2006-12-20 01:00 | 0 | 0 | 0 | 1.73 | 0.85 | 0
8475 | 2006-12-20 02:00 | 0 | 0 | 0 | 1.26 | 0.85 | 0
8476 | 2006-12-20 03:00 | 0 | 0 | 0 | 0.79 | 1.55 | 0
8477 | 2006-12-20 04:00 | 0 | 0 | 0 | 0.32 | 1.55 | 0
8478 | 2006-12-20 05:00 | 0 | 0 | 0 | -0.16 | 1.55 | 0
8479 | 2006-12-20 06:00 | 0 | 15 | 0 | -0.65 | 2.62 | 0
8480 | 2006-12-20 07:00 | 70 | 307 | 38 | -1.14 | 2.62 | 0 | 5.8956 | 123.816 | 70.9102 | 0 | 70 | 101.889 | 58.2966 | 0.65585 | 13.1233 | 54.5562 | 0.0034233 | 11.7732 | 52.5371 | 0.0025795 | 62.3834 | 62.3834 | 140101 | 0.50476 | 115788 | 129821 | 118474 | 0 | 0 | 118351 | 713.512 | 0 | 0 | 0 | 0 | 118351 | 713.512 | 114131 | 111848.2422
8481 | 2006-12-20 08:00 | 196 | 391 | 91 | -0.89 | 2.62 | 0 | 15.5242 | 133.823 | 58.3637 | 0 | 196 | 205.777 | 119.594 | 1.8364 | 141.68 | 111.92 | 0.0095852 | 135.259 | 107.778 | 0.0072227 | 235.753 | 235.724 | 529332 | 5.3249 | 489494 | 531372 | 469368 | 0 | 0 | 467778 | 752.865 | 0 | 0 | 0 | 0 | 467778 | 752.865 | 458474 | 449304.5625
8482 | 2006-12-20 09:00 | 418 | 757 | 117 | -0.64 | 1.76 | 0 | 23.5148 | 145.713 | 47.0166 | 0 | 418 | 514.348 | 155.803 | 3.9163 | 481.473 | 145.806 | 0.020442 | 470.237 | 140.41 | 0.015403 | 592.343 | 592.263 | 1330090 | 15.8972 | 1301650 | 1349690 | 1232870 | 0 | 0 | 1222350 | 759.021 | 0 | 0 | 0 | 0 | 1222350 | 759.021 | 1199930 | 1175928.125
8483 | 2006-12-20 10:00 | 528 | 955 | 64 | -0.39 | 1.76 | 0 | 29.1956 | 159.707 | 37.9899 | 0 | 528 | 749.678 | 85.1931 | 4.947 | 749.678 | 79.7269 | 0.025821 | 739.601 | 76.7763 | 0.019457 | 791.905 | 791.906 | 1778410 | 21.7217 | 1768380 | 1792060 | 1738990 | 0 | 0 | 1718100 | 749.426 | 0 | 0 | 0 | 0 | 1718100 | 749.426 | 1684130 | 1650443.375
8484 | 2006-12-20 11:00 | 577 | 971 | 66 | 1.07 | 1.76 | 0 | 31.8714 | 175.383 | 33.2505 | 0 | 577 | 809.333 | 87.435 | 5.406 | 809.333 | 81.825 | 0.028218 | 801.411 | 78.7967 | 0.021263 | 853.822 | 853.816 | 1917450 | 24.9104 | 1914330 | 1914580 | 1866000 | 0 | 0 | 1841330 | 738.869 | 0 | 0 | 0 | 0 | 1841330 | 738.869 | 1804380 | 1768292.875
8485 | 2006-12-20 12:00 | 558 | 963 | 62 | 2.54 | 1.49 | 0 | 31.1255 | 191.503 | 34.6143 | 0 | 558 | 789.695 | 82.4719 | 5.228 | 789.695 | 77.1804 | 0.027289 | 781.203 | 74.324 | 0.020563 | 829.881 | 829.875 | 1863700 | 26.135 | 1857860 | 1848630 | 1798500 | 0 | 0 | 1775390 | 735.873 | 0 | 0 | 0 | 0 | 1775390 | 735.873 | 1740580 | 1705765.25
8486 | 2006-12-20 13:00 | 487 | 939 | 61 | 4 | 1.49 | 0 | 27.0809 | 206.562 | 41.4821 | 0 | 487 | 701.032 | 81.6529 | 4.5628 | 701.032 | 76.4139 | 0.023816 | 689.296 | 73.5858 | 0.017946 | 740.013 | 740.01 | 1661870 | 25.0399 | 1646310 | 1645660 | 1599880 | 0 | 0 | 1581560 | 736.39 | 0 | 0 | 0 | 0 | 1581560 | 736.39 | 1552430 | 1521383.75
8487 | 2006-12-20 14:00 | 357 | 876 | 53 | 4.49 | 1.49 | 0 | 20.317 | 219.655 | 51.6974 | 0 | 357 | 542.673 | 72.4832 | 3.3448 | 500.657 | 67.8326 | 0.017459 | 485.302 | 65.3221 | 0.013156 | 534.118 | 534.056 | 1199360 | 19.6742 | 1166170 | 1191130 | 1133510 | 0 | 0 | 1124400 | 743.899 | 0 | 0 | 0 | 0 | 1124400 | 743.899 | 1104800 | 1082706.875
8488 | 2006-12-20 15:00 | 171 | 599 | 51 | 4.98 | 4.93 | 0 | 11.547 | 230.685 | 63.6558 | 0 | 171 | 266.028 | 75.9011 | 1.6021 | 204.622 | 71.0312 | 0.0083626 | 191.798 | 68.4024 | 0.0063014 | 252.4 | 252.274 | 566551 | 10.6937 | 527847 | 559456 | 496460 | 0 | 0 | 494562 | 744.779 | 0 | 0 | 0 | 0 | 494562 | 744.779 | 485265 | 475559.4062
8489 | 2006-12-20 16:00 | 17 | 198 | 5 | 5.47 | 4.93 | 0 | 1.3831 | 240.02 | 76.5265 | 0 | 17 | 32.1373 | 7.9508 | 0.15928 | 7.5726 | 7.4406 | 0.00083137 | 6.3262 | 7.1652 | 0.00062646 | 13.0873 | 13.0749 | 29367.2 | 5.7661 | 19319.5 | 21139.8 | 16077.2 | 0 | 0 | 16073.3 | 593.841 | 0 | 0 | 0 | 1201.79 | 14871.5 | 660 | 14320.2 | 14033.7842
8490 | 2006-12-20 17:00 | 0 | 0 | 0 | 5.04 | 4.93 | 0
8491 | 2006-12-20 18:00 | 0 | 0 | 0 | 4.6 | 7.06 | 0
8492 | 2006-12-20 19:00 | 0 | 0 | 0 | 4.16 | 7.06 | 0
8493 | 2006-12-20 20:00 | 0 | 0 | 0 | 3.61 | 7.06 | 0
8494 | 2006-12-20 21:00 | 0 | 0 | 0 | 3.06 | 4.84 | 0
8495 | 2006-12-20 22:00 | 0 | 0 | 0 | 2.51 | 4.84 | 0
8496 | 2006-12-20 23:00 | 0 | 0 | 0 | 2.05 | 4.84 | 0
8497 | 2006-12-21 | 0 | 0 | 0 | 1.58 | 3.48 | 0
8498 | 2006-12-21 01:00 | 0 | 0 | 0 | 1.12 | 3.48 | 0
8499 | 2006-12-21 02:00 | 0 | 0 | 0 | 0.81 | 3.48 | 0
8500 | 2006-12-21 03:00 | 0 | 0 | 0 | 0.5 | 3.99 | 0
8501 | 2006-12-21 04:00 | 0 | 0 | 0 | 0.19 | 3.99 | 0
8502 | 2006-12-21 05:00 | 0 | 0 | 0 | -0.14 | 3.99 | 0
8503 | 2006-12-21 06:00 | 0 | 19 | 0 | -0.48 | 4.81 | 0
8504 | 2006-12-21 07:00 | 72 | 419 | 29 | -0.82 | 4.81 | 0 | 5.806 | 123.745 | 71.0197 | 0 | 72 | 138.251 | 49.6587 | 0.67458 | 17.6597 | 46.4725 | 0.0035211 | 15.8278 | 44.7526 | 0.0026532 | 58.7656 | 58.7496 | 131941 | 0.52103 | 109002 | 122001 | 108456 | 0 | 0 | 108336 | 707.442 | 0 | 0 | 0 | 0 | 108336 | 707.442 | 104485 | 102395.4219
8505 | 2006-12-21 08:00 | 264 | 782 | 56 | -0.49 | 4.81 | 0 | 15.4454 | 133.737 | 58.4668 | 0 | 264 | 408.466 | 79.9938 | 2.4735 | 280.296 | 74.8613 | 0.012911 | 267.513 | 72.0907 | 0.0097285 | 329.425 | 329.363 | 739584 | 7.0281 | 702818 | 752527 | 637288 | 0 | 0 | 634213 | 758.772 | 0 | 0 | 0 | 0 | 634213 | 758.772 | 622297 | 609851.5
8506 | 2006-12-21 09:00 | 411 | 901 | 53 | -0.16 | 4.52 | 0 | 23.4518 | 145.609 | 47.1072 | 0 | 411 | 612.26 | 71.9729 | 3.8508 | 572.608 | 67.355 | 0.0201 | 559.174 | 64.8623 | 0.015145 | 605.33 | 605.316 | 1359410 | 13.921 | 1332560 | 1392420 | 1258030 | 0 | 0 | 1247180 | 766.61 | 0 | 0 | 0 | 0 | 1247180 | 766.61 | 1223780 | 1199300.625
8507 | 2006-12-21 10:00 | 527 | 954 | 64 | 0.17 | 4.52 | 0 | 29.1544 | 159.585 | 38.0553 | 0 | 527 | 748.358 | 85.2004 | 4.9376 | 748.358 | 79.7337 | 0.025773 | 738.256 | 76.7829 | 0.01942 | 790.606 | 790.603 | 1775490 | 18.5611 | 1765310 | 1812090 | 1760350 | 0 | 0 | 1739550 | 760.076 | 0 | 0 | 0 | 0 | 1739550 | 760.076 | 1703990 | 1669914.125
8508 | 2006-12-21 11:00 | 571 | 966 | 63 | 1.62 | 4.52 | 0 | 31.8576 | 175.25 | 33.2714 | 0 | 571 | 804.702 | 83.6638 | 5.3498 | 804.702 | 78.2958 | 0.027924 | 796.813 | 75.3981 | 0.021042 | 846.065 | 846.063 | 1900040 | 21.3013 | 1896040 | 1924640 | 1870550 | 0 | 0 | 1846530 | 751.071 | 0 | 0 | 0 | 0 | 1846530 | 751.071 | 1808390 | 1772225
8509 | 2006-12-21 12:00 | 541 | 941 | 56 | 3.08 | 3.51 | 0 | 31.1407 | 191.371 | 34.5826 | 0 | 541 | 772.138 | 74.8543 | 5.0687 | 772.138 | 70.0515 | 0.026457 | 763.853 | 67.459 | 0.019936 | 806.392 | 806.387 | 1810940 | 23.1241 | 1802490 | 1816160 | 1763700 | 0 | 0 | 1742040 | 745.814 | 0 | 0 | 0 | 0 | 1742040 | 745.814 | 1707650 | 1673499.875
8510 | 2006-12-21 13:00 | 488 | 898 | 80 | 4.54 | 3.51 | 0 | 27.1221 | 206.442 | 41.4123 | 0 | 488 | 671.19 | 111.232 | 4.5722 | 671.19 | 104.095 | 0.023865 | 660.001 | 100.243 | 0.017983 | 737.454 | 737.452 | 1656140 | 22.8706 | 1640320 | 1654610 | 1605920 | 0 | 0 | 1587870 | 744.558 | 0 | 0 | 0 | 0 | 1587870 | 744.558 | 1558110 | 1526949.25
8511 | 2006-12-21 14:00 | 315 | 625 | 98 | 5.23 | 3.51 | 0 | 20.3785 | 219.552 | 51.6066 | 0 | 315 | 387.023 | 132.889 | 2.9513 | 357.058 | 124.362 | 0.015405 | 346.165 | 119.76 | 0.011608 | 451.958 | 451.961 | 1014990 | 16.4642 | 976632 | 1011900 | 967952 | 0 | 0 | 961386 | 749.231 | 0 | 0 | 0 | 0 | 961386 | 749.231 | 944639 | 925746.6875
8512 | 2006-12-21 15:00 | 119 | 161 | 86 | 5.91 | 4.24 | 0 | 11.6231 | 230.598 | 63.554 | 0 | 119 | 72.9461 | 107.358 | 1.1149 | 56.1083 | 100.47 | 0.0058196 | 52.6144 | 96.7514 | 0.0043852 | 144.889 | 144.885 | 325377 | 9.3427 | 289298 | 310690 | 290022 | 0 | 0 | 289386 | 729.441 | 0 | 0 | 0 | 0 | 289386 | 729.441 | 281770 | 276134.8125
8513 | 2006-12-21 16:00 | 12 | 54 | 9 | 6.6 | 4.24 | 0 | 1.4693 | 239.945 | 76.4185 | 0 | 12 | 8.0975 | 11.0184 | 0.11243 | 1.9227 | 10.3114 | 0.00058685 | 1.6095 | 9.9298 | 0.0004422 | 11.1935 | 11.191 | 25133.2 | 6.8651 | 15452.7 | 16842 | 15640.1 | 0 | 0 | 15637.3 | 601.6 | 0 | 0 | 0 | 1394 | 14243.3 | 660 | 13714.3 | 13440.0029
8514 | 2006-12-21 17:00 | 0 | 0 | 0 | 6.33 | 4.24 | 0
8515 | 2006-12-21 18:00 | 0 | 0 | 0 | 6.06 | 11.36 | 0
8516 | 2006-12-21 19:00 | 0 | 0 | 0 | 5.79 | 11.36 | 0
8517 | 2006-12-21 20:00 | 0 | 0 | 0 | 5.66 | 11.36 | 0
8518 | 2006-12-21 21:00 | 0 | 0 | 0 | 5.54 | 15.04 | 0
8519 | 2006-12-21 22:00 | 0 | 0 | 0 | 5.41 | 15.04 | 0
8520 | 2006-12-21 23:00 | 0 | 0 | 0 | 5.48 | 15.04 | 0
8521 | 2006-12-22 | 0 | 0 | 0 | 5.54 | 13.8 | 0
8522 | 2006-12-22 01:00 | 0 | 0 | 0 | 5.6 | 13.8 | 0
8523 | 2006-12-22 02:00 | 0 | 0 | 0 | 5.72 | 13.8 | 0
8524 | 2006-12-22 03:00 | 0 | 0 | 0 | 5.85 | 12.31 | 0
8525 | 2006-12-22 04:00 | 0 | 0 | 0 | 5.97 | 12.31 | 0
8526 | 2006-12-22 05:00 | 0 | 0 | 0 | 5.72 | 12.31 | 0
8527 | 2006-12-22 06:00 | 0 | 22 | 0 | 5.47 | 10.03 | 0
8528 | 2006-12-22 07:00 | 82 | 544 | 26 | 5.22 | 10.03 | 0 | 5.7214 | 123.668 | 71.1266 | 0 | 82 | 181.706 | 43.2042 | 0.76828 | 23.0218 | 40.4321 | 0.0040101 | 20.6144 | 38.9357 | 0.0030217 | 57.7665 | 57.8017 | 129813 | 6.1681 | 107956 | 117629 | 101702 | 0 | 0 | 101567 | 684.263 | 0 | 0 | 0 | 0 | 101567 | 684.263 | 98160.7 | 96197.5234
8529 | 2006-12-22 08:00 | 258 | 672 | 80 | 5.91 | 10.03 | 0 | 15.3723 | 133.646 | 58.5664 | 0 | 258 | 350.178 | 109.743 | 2.4173 | 239.561 | 102.702 | 0.012617 | 228.571 | 98.9007 | 0.0095074 | 317.657 | 317.506 | 712959 | 11.1182 | 674595 | 712934 | 612498 | 0 | 0 | 609642 | 747.236 | 0 | 0 | 0 | 0 | 609642 | 747.236 | 598580 | 586608.3125
8530 | 2006-12-22 09:00 | 291 | 294 | 175 | 6.6 | 6.86 | 0 | 23.3953 | 145.501 | 47.1929 | 0 | 291 | 198.517 | 207.733 | 2.7264 | 185.507 | 194.405 | 0.014231 | 181.133 | 187.21 | 0.010723 | 357.303 | 357.287 | 802382 | 13.746 | 760437 | 797880 | 748820 | 0 | 0 | 744886 | 750.668 | 0 | 0 | 0 | 0 | 744886 | 750.668 | 731862 | 717224.5
8531 | 2006-12-22 10:00 | 493 | 756 | 126 | 7.29 | 6.86 | 0 | 29.1205 | 159.46 | 38.1144 | 0 | 493 | 593.342 | 169.75 | 4.619 | 593.342 | 158.859 | 0.02411 | 585.302 | 152.98 | 0.018167 | 716.151 | 716.145 | 1608280 | 21.6134 | 1590290 | 1612610 | 1567100 | 0 | 0 | 1550080 | 748.535 | 0 | 0 | 0 | 0 | 1550080 | 748.535 | 1521100 | 1490673.875
8532 | 2006-12-22 11:00 | 563 | 957 | 60 | 8.24 | 6.86 | 0 | 31.8513 | 175.116 | 33.285 | 0 | 563 | 796.797 | 79.8697 | 5.2749 | 796.797 | 74.7451 | 0.027533 | 788.979 | 71.9789 | 0.020747 | 835.149 | 835.143 | 1875520 | 24.9435 | 1870280 | 1870400 | 1819300 | 0 | 0 | 1795910 | 739.596 | 0 | 0 | 0 | 0 | 1795910 | 739.596 | 1760330 | 1725122.625
8533 | 2006-12-22 12:00 | 560 | 963 | 63 | 9.2 | 9.16 | 0 | 31.1634 | 191.24 | 34.5438 | 0 | 560 | 791.093 | 83.7321 | 5.2468 | 791.093 | 78.3597 | 0.027386 | 782.627 | 75.4596 | 0.020636 | 832.364 | 832.359 | 1869260 | 23.6057 | 1863710 | 1874210 | 1822640 | 0 | 0 | 1799420 | 744.107 | 0 | 0 | 0 | 0 | 1799420 | 744.107 | 1763420 | 1728155.375
8534 | 2006-12-22 13:00 | 488 | 940 | 60 | 10.16 | 9.16 | 0 | 27.1704 | 206.326 | 41.3366 | 0 | 488 | 703.754 | 80.3803 | 4.5722 | 703.754 | 75.223 | 0.023865 | 692.077 | 72.439 | 0.017983 | 741.598 | 741.594 | 1665430 | 22.9948 | 1650040 | 1663650 | 1618920 | 0 | 0 | 1600450 | 742.393 | 0 | 0 | 0 | 0 | 1600450 | 742.393 | 1570480 | 1539069.5
8535 | 2006-12-22 14:00 | 360 | 877 | 54 | 10.34 | 9.16 | 0 | 20.4464 | 219.454 | 51.5113 | 0 | 360 | 545.162 | 73.7362 | 3.3729 | 502.953 | 69.0052 | 0.017605 | 487.693 | 66.4513 | 0.013266 | 537.533 | 537.464 | 1207010 | 19.6419 | 1174060 | 1199980 | 1143070 | 0 | 0 | 1133840 | 745.31 | 0 | 0 | 0 | 0 | 1133840 | 745.31 | 1113990 | 1091712
8536 | 2006-12-22 15:00 | 178 | 644 | 47 | 10.52 | 11.7 | 0 | 11.7049 | 230.517 | 63.4488 | 0 | 178 | 288.64 | 68.4036 | 1.6677 | 222.015 | 64.0147 | 0.0087049 | 208.282 | 61.6456 | 0.0065594 | 261.836 | 261.774 | 587886 | 14.4009 | 549548 | 573907 | 506508 | 0 | 0 | 504455 | 734.395 | 0 | 0 | 0 | 0 | 504455 | 734.395 | 495335 | 485427.875
8537 | 2006-12-22 16:00 | 19 | 218 | 5 | 10.7 | 11.7 | 0 | 1.5604 | 239.876 | 76.3082 | 0 | 19 | 38.0895 | 8.0378 | 0.17802 | 9.1427 | 7.5221 | 0.00092918 | 7.6685 | 7.2437 | 0.00070016 | 14.4655 | 14.454 | 32465.1 | 10.9143 | 21949.9 | 23490.3 | 17368.5 | 0 | 0 | 17363.4 | 574.949 | 0 | 0 | 0 | 2233.4 | 15130 | 660 | 14569.5 | 14278.1035
8538 | 2006-12-22 17:00 | 0 | 0 | 0 | 10.04 | 11.7 | 0
8539 | 2006-12-22 18:00 | 0 | 0 | 0 | 9.37 | 13.18 | 0
8540 | 2006-12-22 19:00 | 0 | 0 | 0 | 8.71 | 13.18 | 0
8541 | 2006-12-22 20:00 | 0 | 0 | 0 | 7.85 | 13.18 | 0
8542 | 2006-12-22 21:00 | 0 | 0 | 0 | 7 | 14.26 | 0
8543 | 2006-12-22 22:00 | 0 | 0 | 0 | 6.14 | 14.26 | 0
8544 | 2006-12-22 23:00 | 0 | 0 | 0 | 5.83 | 14.26 | 0
8545 | 2006-12-23 | 0 | 0 | 0 | 5.52 | 9.74 | 0
8546 | 2006-12-23 01:00 | 0 | 0 | 0 | 5.22 | 9.74 | 0
8547 | 2006-12-23 02:00 | 0 | 0 | 0 | 4.84 | 9.74 | 0
8548 | 2006-12-23 03:00 | 0 | 0 | 0 | 4.46 | 9.78 | 0
8549 | 2006-12-23 04:00 | 0 | 0 | 0 | 4.08 | 9.78 | 0
8550 | 2006-12-23 05:00 | 0 | 0 | 0 | 3.47 | 9.78 | 0
8551 | 2006-12-23 06:00 | 0 | 20 | 0 | 2.86 | 10.74 | 0
8552 | 2006-12-23 07:00 | 77 | 529 | 24 | 2.24 | 10.74 | 0 | 5.642 | 123.585 | 71.2311 | 0 | 77 | 173.456 | 41.1541 | 0.72143 | 21.8297 | 38.5136 | 0.0037656 | 19.5289 | 37.0882 | 0.0028375 | 54.9213 | 54.9055 | 123306 | 3.1025 | 101972 | 112693 | 97666.2 | 0 | 0 | 97545.8 | 695.231 | 0 | 0 | 0 | 0 | 97545.8 | 695.231 | 94149.1 | 92266.0703
8553 | 2006-12-23 08:00 | 259 | 805 | 47 | 2.95 | 10.74 | 0 | 15.3051 | 133.55 | 58.6624 | 0 | 259 | 417.705 | 69.4419 | 2.4266 | 284.92 | 64.9864 | 0.012666 | 271.774 | 62.5813 | 0.0095442 | 324.334 | 324.399 | 728428 | 8.0458 | 692141 | 739493 | 622640 | 0 | 0 | 619620 | 752.425 | 0 | 0 | 0 | 0 | 619620 | 752.425 | 608197 | 596032.75
8554 | 2006-12-23 09:00 | 403 | 891 | 51 | 3.66 | 7.66 | 0 | 23.3453 | 145.389 | 47.2738 | 0 | 403 | 602.693 | 69.4192 | 3.7758 | 562.744 | 64.9651 | 0.019708 | 549.411 | 62.5608 | 0.014851 | 593.627 | 593.487 | 1332830 | 14.9426 | 1305070 | 1358540 | 1226610 | 0 | 0 | 1216140 | 761.741 | 0 | 0 | 0 | 0 | 1216140 | 761.741 | 1193650 | 1169778
8555 | 2006-12-23 10:00 | 526 | 954 | 63 | 4.36 | 7.66 | 0 | 29.0938 | 159.332 | 38.1671 | 0 | 526 | 748.634 | 83.9445 | 4.9282 | 748.634 | 78.5585 | 0.025724 | 738.455 | 75.6511 | 0.019383 | 789.702 | 789.699 | 1773460 | 19.3727 | 1763190 | 1804090 | 1755060 | 0 | 0 | 1734160 | 756.203 | 0 | 0 | 0 | 0 | 1734160 | 756.203 | 1699120 | 1665133.875
8556 | 2006-12-23 11:00 | 576 | 971 | 65 | 5.83 | 7.66 | 0 | 31.8526 | 174.981 | 33.2914 | 0 | 576 | 809.382 | 86.179 | 5.3967 | 809.382 | 80.6496 | 0.028169 | 801.437 | 77.6648 | 0.021226 | 852.749 | 852.743 | 1915050 | 22.0412 | 1911810 | 1934880 | 1882630 | 0 | 0 | 1858180 | 749.065 | 0 | 0 | 0 | 0 | 1858180 | 749.065 | 1819860 | 1783467.625
8557 | 2006-12-23 12:00 | 564 | 967 | 65 | 7.3 | 6.42 | 0 | 31.1936 | 191.111 | 34.4979 | 0 | 564 | 794.022 | 86.2432 | 5.2842 | 794.022 | 80.7096 | 0.027582 | 785.551 | 77.7226 | 0.020784 | 837.395 | 837.391 | 1880570 | 24.5261 | 1875590 | 1878930 | 1826380 | 0 | 0 | 1802900 | 741.223 | 0 | 0 | 0 | 0 | 1802900 | 741.223 | 1767020 | 1731680.5
8558 | 2006-12-23 13:00 | 473 | 924 | 51 | 8.77 | 6.42 | 0 | 27.2257 | 206.213 | 41.2551 | 0 | 473 | 693.452 | 68.8855 | 4.4316 | 693.452 | 64.4657 | 0.023132 | 682.004 | 62.0798 | 0.01743 | 721.778 | 721.772 | 1620910 | 23.6176 | 1603490 | 1612530 | 1567560 | 0 | 0 | 1550190 | 741.245 | 0 | 0 | 0 | 0 | 1550190 | 741.245 | 1521730 | 1491294.625
8559 | 2006-12-23 14:00 | 362 | 878 | 55 | 9.36 | 6.42 | 0 | 20.5207 | 219.361 | 51.4116 | 0 | 362 | 546.242 | 74.9901 | 3.3917 | 503.949 | 70.1786 | 0.017703 | 488.748 | 67.5813 | 0.01334 | 539.653 | 539.578 | 1211750 | 20.4597 | 1178960 | 1200670 | 1142910 | 0 | 0 | 1133610 | 742.813 | 0 | 0 | 0 | 0 | 1133610 | 742.813 | 1113890 | 1091614.875
8560 | 2006-12-23 15:00 | 187 | 688 | 46 | 9.95 | 3.96 | 0 | 11.7922 | 230.441 | 63.3403 | 0 | 187 | 309.573 | 67.3751 | 1.752 | 238.116 | 63.0522 | 0.0091451 | 223.487 | 60.7187 | 0.006891 | 275.686 | 275.65 | 619045 | 16.6018 | 580919 | 599408 | 528146 | 0 | 0 | 525834 | 720.596 | 0 | 0 | 0 | 0 | 525834 | 720.596 | 516914 | 506576
8561 | 2006-12-23 16:00 | 19 | 236 | 4 | 10.54 | 3.96 | 0 | 1.6565 | 239.814 | 76.1956 | 0 | 19 | 41.1394 | 6.538 | 0.17802 | 9.9165 | 6.1185 | 0.00092918 | 8.3344 | 5.892 | 0.00070016 | 13.8003 | 13.7937 | 30982.3 | 10.8729 | 20947.4 | 22386.2 | 15817.3 | 0 | 0 | 15812.5 | 571.425 | 0 | 0 | 0 | 2632.29 | 13180.2 | 660 | 12690.6 | 12436.7529
8562 | 2006-12-23 17:00 | 0 | 0 | 0 | 10 | 3.96 | 0
8563 | 2006-12-23 18:00 | 0 | 0 | 0 | 9.47 | 4.99 | 0
8564 | 2006-12-23 19:00 | 0 | 0 | 0 | 8.93 | 4.99 | 0
8565 | 2006-12-23 20:00 | 0 | 0 | 0 | 8.3 | 4.99 | 0
8566 | 2006-12-23 21:00 | 0 | 0 | 0 | 7.67 | 2.79 | 0
8567 | 2006-12-23 22:00 | 0 | 0 | 0 | 7.04 | 2.79 | 0
8568 | 2006-12-23 23:00 | 0 | 0 | 0 | 6.6 | 2.79 | 0
8569 | 2006-12-24 | 0 | 0 | 0 | 6.15 | 2.55 | 0
8570 | 2006-12-24 01:00 | 0 | 0 | 0 | 5.7 | 2.55 | 0
8571 | 2006-12-24 02:00 | 0 | 0 | 0 | 5.42 | 2.55 | 0
8572 | 2006-12-24 03:00 | 0 | 0 | 0 | 5.14 | 4.96 | 0
8573 | 2006-12-24 04:00 | 0 | 0 | 0 | 4.85 | 4.96 | 0
8574 | 2006-12-24 05:00 | 0 | 0 | 0 | 4.46 | 4.96 | 0
8575 | 2006-12-24 06:00 | 0 | 15 | 0 | 4.07 | 6.28 | 0
8576 | 2006-12-24 07:00 | 69 | 445 | 25 | 3.67 | 6.28 | 0 | 5.5677 | 123.497 | 71.3328 | 0 | 69 | 145.153 | 42.1289 | 0.64648 | 18.1836 | 39.4258 | 0.0033744 | 16.2522 | 37.9667 | 0.0025427 | 52.5948 | 52.5441 | 118002 | 4.7606 | 96667.1 | 106167 | 93717.3 | 0 | 0 | 93614 | 686.769 | 0 | 0 | 0 | 0 | 93614 | 686.769 | 90388.3 | 88580.5156
8577 | 2006-12-24 08:00 | 251 | 796 | 42 | 4.39 | 6.28 | 0 | 15.2437 | 133.449 | 58.7547 | 0 | 251 | 412.317 | 59.3937 | 2.3517 | 280.517 | 55.5829 | 0.012275 | 267.503 | 53.5258 | 0.0092494 | 311.407 | 311.323 | 699060 | 10.852 | 662855 | 698997 | 587324 | 0 | 0 | 584525 | 740.705 | 0 | 0 | 0 | -78.5745 | 584604 | 742.472 | 574027 | 562546.375
8578 | 2006-12-24 09:00 | 416 | 907 | 58 | 5.1 | 7.79 | 0 | 23.302 | 145.273 | 47.3497 | 0 | 416 | 613.161 | 78.3479 | 3.8976 | 572.088 | 73.321 | 0.020344 | 558.473 | 70.6074 | 0.01533 | 610.223 | 610.165 | 1370280 | 16.6049 | 1343930 | 1389490 | 1257240 | 0 | 0 | 1246160 | 757.773 | 0 | 0 | 0 | 0 | 1246160 | 757.773 | 1223280 | 1198811.25
8579 | 2006-12-24 10:00 | 513 | 941 | 57 | 5.82 | 7.79 | 0 | 29.0743 | 159.202 | 38.2135 | 0 | 513 | 737.296 | 76.3421 | 4.8064 | 737.296 | 71.4438 | 0.025088 | 727.242 | 68.7998 | 0.018904 | 772.178 | 772.174 | 1734110 | 20.3796 | 1721950 | 1754780 | 1704100 | 0 | 0 | 1684250 | 753.226 | 0 | 0 | 0 | 0 | 1684250 | 753.226 | 1650990 | 1617966.875
8580 | 2006-12-24 11:00 | 555 | 943 | 59 | 7.58 | 7.79 | 0 | 31.8615 | 174.845 | 33.2904 | 0 | 555 | 785.436 | 78.59 | 5.1999 | 785.436 | 73.5475 | 0.027142 | 777.726 | 70.8256 | 0.020452 | 823.115 | 823.111 | 1848500 | 23.1 | 1841910 | 1856140 | 1804500 | 0 | 0 | 1781780 | 745.508 | 0 | 0 | 0 | 0 | 1781780 | 745.508 | 1746200 | 1711277.375
8581 | 2006-12-24 12:00 | 526 | 867 | 78 | 9.34 | 2.03 | 0 | 31.2313 | 190.983 | 34.445 | 0 | 526 | 712.547 | 102.388 | 4.9282 | 712.547 | 95.8185 | 0.025724 | 704.973 | 92.2724 | 0.019383 | 773.347 | 773.344 | 1736740 | 30.547 | 1724700 | 1684110 | 1637890 | 0 | 0 | 1617870 | 720.317 | 0 | 0 | 0 | 0 | 1617870 | 720.317 | 1588210 | 1556444.25
8582 | 2006-12-24 13:00 | 491 | 941 | 61 | 11.1 | 2.03 | 0 | 27.2879 | 206.104 | 41.1678 | 0 | 491 | 706.05 | 81.6186 | 4.6003 | 706.05 | 76.3818 | 0.024012 | 694.456 | 73.555 | 0.018093 | 744.988 | 744.986 | 1673050 | 31.5294 | 1658010 | 1612000 | 1568170 | 0 | 0 | 1549580 | 716.01 | 0 | 0 | 0 | 0 | 1549580 | 716.01 | 1522060 | 1491622.875
8583 | 2006-12-24 14:00 | 360 | 878 | 52 | 11.44 | 2.03 | 0 | 20.6012 | 219.272 | 51.3075 | 0 | 360 | 547.215 | 71.1443 | 3.3729 | 504.846 | 66.5795 | 0.017605 | 489.71 | 64.1155 | 0.013266 | 537.224 | 537.171 | 1206350 | 26.1706 | 1173390 | 1165880 | 1111810 | 0 | 0 | 1102540 | 723.308 | 0 | 0 | 0 | 0 | 1102540 | 723.308 | 1084390 | 1062705.875
8584 | 2006-12-24 15:00 | 187 | 684 | 46 | 11.77 | 3.34 | 0 | 11.8851 | 230.37 | 63.2287 | 0 | 187 | 308.38 | 67.4097 | 1.752 | 237.198 | 63.0845 | 0.0091451 | 222.728 | 60.7498 | 0.006891 | 274.98 | 274.927 | 617422 | 18.6809 | 579283 | 592226 | 522462 | 0 | 0 | 520148 | 713.068 | 0 | 0 | 0 | 0 | 520148 | 713.068 | 511522 | 501291.25
8585 | 2006-12-24 16:00 | 20 | 237 | 5 | 12.11 | 3.34 | 0 | 1.7574 | 239.757 | 76.0808 | 0 | 20 | 41.4748 | 8.129 | 0.18738 | 10.0655 | 7.6074 | 0.00097808 | 8.4766 | 7.3259 | 0.00073701 | 15.3292 | 15.3196 | 34408.9 | 12.4951 | 23607.3 | 25072.3 | 18459.3 | 0 | 0 | 18453.4 | 570.248 | 0 | 0 | 0 | 2755.86 | 15697.5 | 660 | 15116.6 | 14814.2354
8586 | 2006-12-24 17:00 | 0 | 0 | 0 | 11.46 | 3.34 | 0
8587 | 2006-12-24 18:00 | 0 | 0 | 0 | 10.8 | 6.73 | 0
8588 | 2006-12-24 19:00 | 0 | 0 | 0 | 10.15 | 6.73 | 0
8589 | 2006-12-24 20:00 | 0 | 0 | 0 | 9.51 | 6.73 | 0
8590 | 2006-12-24 21:00 | 0 | 0 | 0 | 8.87 | 5.65 | 0
8591 | 2006-12-24 22:00 | 0 | 0 | 0 | 8.23 | 5.65 | 0
8592 | 2006-12-24 23:00 | 0 | 0 | 0 | 7.7 | 5.65 | 0
8593 | 2006-12-25 | 0 | 0 | 0 | 7.17 | 5.04 | 0
8594 | 2006-12-25 01:00 | 0 | 0 | 0 | 6.64 | 5.04 | 0
8595 | 2006-12-25 02:00 | 0 | 0 | 0 | 6.38 | 5.04 | 0
8596 | 2006-12-25 03:00 | 0 | 0 | 0 | 6.12 | 2.11 | 0
8597 | 2006-12-25 04:00 | 0 | 0 | 0 | 5.86 | 2.11 | 0
8598 | 2006-12-25 05:00 | 0 | 0 | 0 | 5.39 | 2.11 | 0
8599 | 2006-12-25 06:00 | 0 | 14 | 0 | 4.92 | 2.84 | 0
8600 | 2006-12-25 07:00 | 80 | 484 | 32 | 4.45 | 2.84 | 0 | 5.4987 | 123.402 | 71.4318 | 0 | 80 | 159.51 | 47.3988 | 0.74954 | 19.8896 | 44.3576 | 0.0039123 | 17.761 | 42.7159 | 0.002948 | 58.6655 | 58.6197 | 131647 | 5.9731 | 109078 | 118946 | 105335 | 0 | 0 | 105208 | 688.905 | 0 | 0 | 0 | 0 | 105208 | 688.905 | 101640 | 99607.25
8601 | 2006-12-25 08:00 | 232 | 713 | 45 | 5.3 | 2.84 | 0 | 15.1883 | 133.342 | 58.8433 | 0 | 232 | 369.286 | 66.9594 | 2.1737 | 250.67 | 62.6631 | 0.011346 | 238.979 | 60.344 | 0.0085493 | 290.351 | 290.425 | 652143 | 12.8461 | 614952 | 642943 | 543487 | 0 | 0 | 541060 | 731.347 | 0 | 0 | 0 | 292.745 | 540767 | 733.44 | 531142 | 520519.3438
8602 | 2006-12-25 09:00 | 384 | 765 | 82 | 6.15 | 1.97 | 0 | 23.2654 | 145.152 | 47.4206 | 0 | 384 | 517.32 | 112.317 | 3.5978 | 482.33 | 105.11 | 0.018779 | 470.803 | 101.22 | 0.01415 | 554.876 | 554.91 | 1246190 | 21.4281 | 1215080 | 1231420 | 1124500 | 0 | 0 | 1115140 | 735.949 | 0 | 0 | 0 | 0 | 1115140 | 735.949 | 1096030 | 1074106.5
8603 | 2006-12-25 10:00 | 414 | 485 | 179 | 7 | 1.97 | 0 | 29.0621 | 159.069 | 38.2536 | 0 | 414 | 379.902 | 224.561 | 3.8789 | 379.902 | 210.153 | 0.020246 | 374.708 | 202.375 | 0.015256 | 559.786 | 559.777 | 1257120 | 22.4122 | 1225170 | 1238500 | 1203950 | 0 | 0 | 1193550 | 736.929 | 0 | 0 | 0 | 0 | 1193550 | 736.929 | 1172940 | 1149481.75
8604 | 2006-12-25 11:00 | 530 | 747 | 137 | 8.9 | 1.97 | 0 | 31.878 | 174.709 | 33.282 | 0 | 530 | 622.103 | 183.891 | 4.9657 | 622.103 | 172.092 | 0.025919 | 616 | 165.723 | 0.019531 | 758.29 | 758.281 | 1702910 | 29.7775 | 1689260 | 1654940 | 1611640 | 0 | 0 | 1592260 | 720.562 | 0 | 0 | 0 | 0 | 1592260 | 720.562 | 1563350 | 1532079.625
8605 | 2006-12-25 12:00 | 462 | 566 | 169 | 10.8 | 2.65 | 0 | 31.2765 | 190.857 | 34.385 | 0 | 462 | 465.748 | 214.023 | 4.3286 | 465.748 | 200.291 | 0.022594 | 460.817 | 192.878 | 0.017025 | 634.101 | 634.097 | 1424020 | 27.4849 | 1398210 | 1383170 | 1345360 | 0 | 0 | 1331910 | 724.015 | 0 | 0 | 0 | 0 | 1331910 | 724.015 | 1309100 | 1282914.5
8606 | 2006-12-25 13:00 | 492 | 842 | 106 | 12.71 | 2.65 | 0 | 27.3572 | 205.998 | 41.0748 | 0 | 492 | 633.219 | 145.683 | 4.6097 | 633.219 | 136.336 | 0.024061 | 622.881 | 131.29 | 0.01813 | 731.563 | 731.555 | 1642880 | 31.9593 | 1626460 | 1578290 | 1535550 | 0 | 0 | 1517600 | 713.762 | 0 | 0 | 0 | 0 | 1517600 | 713.762 | 1491080 | 1461257.75
8607 | 2006-12-25 14:00 | 355 | 800 | 73 | 13.44 | 2.65 | 0 | 20.6879 | 219.189 | 51.1992 | 0 | 355 | 500.19 | 101.133 | 3.3261 | 461.463 | 94.6442 | 0.017361 | 447.714 | 91.1415 | 0.013082 | 522.703 | 522.658 | 1173760 | 27.1926 | 1139720 | 1127560 | 1077450 | 0 | 0 | 1068610 | 717.997 | 0 | 0 | 0 | 0 | 1068610 | 717.997 | 1051390 | 1030362.6875
8608 | 2006-12-25 15:00 | 154 | 325 | 86 | 14.18 | 2.36 | 0 | 11.9834 | 230.305 | 63.114 | 0 | 154 | 148.105 | 113.617 | 1.4429 | 113.919 | 106.327 | 0.0075312 | 107.019 | 102.392 | 0.0056749 | 203.134 | 203.095 | 456105 | 19.6281 | 416885 | 426348 | 391059 | 0 | 0 | 389805 | 706.849 | 0 | 0 | 0 | 0 | 389805 | 706.849 | 382725 | 375070.8125
8609 | 2006-12-25 16:00 | 17 | 114 | 10 | 14.91 | 2.36 | 0 | 1.863 | 239.706 | 75.9639 | 0 | 17 | 19.5142 | 14.9718 | 0.15928 | 5.4862 | 14.0112 | 0.00083137 | 4.6295 | 13.4926 | 0.00062646 | 17.579 | 17.5654 | 39450 | 15.3812 | 27109.5 | 28482.5 | 25080 | 0 | 0 | 25072.5 | 597.279 | 0 | 0 | 0 | 2910.77 | 22161.7 | 660 | 21349.2 | 20922.248
8610 | 2006-12-25 17:00 | 0 | 0 | 0 | 14.29 | 2.36 | 0
8611 | 2006-12-25 18:00 | 0 | 0 | 0 | 13.66 | 4.71 | 0
8612 | 2006-12-25 19:00 | 0 | 0 | 0 | 13.04 | 4.71 | 0
8613 | 2006-12-25 20:00 | 0 | 0 | 0 | 12.45 | 4.71 | 0
8614 | 2006-12-25 21:00 | 0 | 0 | 0 | 11.86 | 6.28 | 0
8615 | 2006-12-25 22:00 | 0 | 0 | 0 | 11.28 | 6.28 | 0
8616 | 2006-12-25 23:00 | 0 | 0 | 0 | 10.88 | 6.28 | 0
8617 | 2006-12-26 | 0 | 0 | 0 | 10.47 | 8.98 | 0
8618 | 2006-12-26 01:00 | 0 | 0 | 0 | 10.07 | 8.98 | 0
8619 | 2006-12-26 02:00 | 0 | 0 | 0 | 10.31 | 8.98 | 0
8620 | 2006-12-26 03:00 | 0 | 0 | 0 | 10.56 | 7.85 | 0
8621 | 2006-12-26 04:00 | 0 | 0 | 0 | 10.81 | 7.85 | 0
8622 | 2006-12-26 05:00 | 0 | 0 | 0 | 10.34 | 7.85 | 0
8623 | 2006-12-26 06:00 | 0 | 7 | 0 | 9.86 | 11.03 | 0
8624 | 2006-12-26 07:00 | 67 | 256 | 42 | 9.39 | 11.03 | 0 | 5.435 | 123.302 | 71.5279 | 0 | 67 | 83.6286 | 64.4669 | 0.62774 | 10.3914 | 60.3305 | 0.0032766 | 9.2712 | 58.0977 | 0.002469 | 65.3502 | 65.3405 | 146740 | 10.3985 | 121551 | 130497 | 121676 | 0 | 0 | 121543 | 685.014 | 0 | 0 | 0 | 0 | 121543 | 685.014 | 117544 | 115193.5234
8625 | 2006-12-26 08:00 | 127 | 84 | 105 | 10.11 | 11.03 | 0 | 15.1389 | 133.231 | 58.928 | 0 | 127 | 43.4772 | 119.327 | 1.1899 | 29.4513 | 111.671 | 0.0062108 | 28.0707 | 107.538 | 0.00468 | 131.545 | 131.527 | 295368 | 12.1401 | 260301 | 276428 | 261659 | 0 | 0 | 261132 | 716.045 | 0 | 0 | 0 | 0 | 261132 | 716.045 | 254102 | 249019.9375
8626 | 2006-12-26 09:00 | 242 | 151 | 183 | 10.83 | 3.4 | 0 | 23.2354 | 145.027 | 47.4865 | 0 | 242 | 101.062 | 206.901 | 2.2673 | 94.1754 | 193.626 | 0.011835 | 91.9161 | 186.46 | 0.0089178 | 270.033 | 270.012 | 606380 | 17.5905 | 563911 | 582753 | 554859 | 0 | 0 | 552566 | 726.997 | 0 | 0 | 0 | 0 | 552566 | 726.997 | 543186 | 532322.3125
8627 | 2006-12-26 10:00 | 256 | 81 | 217 | 11.55 | 3.4 | 0 | 29.0572 | 158.934 | 38.2873 | 0 | 256 | 63.0281 | 231.063 | 2.3985 | 63.0281 | 216.237 | 0.012519 | 62.1645 | 208.235 | 0.0094337 | 262.296 | 262.288 | 589033 | 18.1171 | 546582 | 563694 | 547526 | 0 | 0 | 545273 | 723.523 | 0 | 0 | 0 | 0 | 545273 | 723.523 | 536067 | 525345.5625
8628 | 2006-12-26 11:00 | 514 | 562 | 218 | 13.56 | 3.4 | 0 | 31.902 | 174.572 | 33.2664 | 0 | 514 | 468.324 | 270.037 | 4.8158 | 468.324 | 252.711 | 0.025137 | 463.734 | 243.359 | 0.018941 | 685.899 | 685.888 | 1540330 | 30.7331 | 1519350 | 1482080 | 1442860 | 0 | 0 | 1427050 | 715.592 | 0 | 0 | 0 | 0 | 1427050 | 715.592 | 1402570 | 1374519
8629 | 2006-12-26 12:00 | 271 | 78 | 231 | 15.57 | 5.57 | 0 | 31.3291 | 190.733 | 34.318 | 0 | 271 | 63.5381 | 246.266 | 2.5391 | 63.5381 | 230.465 | 0.013253 | 62.8685 | 221.935 | 0.0099864 | 276.269 | 276.25 | 620386 | 21.5723 | 577738 | 586701 | 569985 | 0 | 0 | 567490 | 715.636 | 0 | 0 | 0 | 0 | 567490 | 715.636 | 558314 | 547147.8125
8630 | 2006-12-26 13:00 | 494 | 636 | 202 | 17.58 | 5.57 | 0 | 27.4333 | 205.895 | 40.9762 | 0 | 494 | 478.505 | 249.108 | 4.6284 | 478.505 | 233.125 | 0.024159 | 470.74 | 224.497 | 0.018204 | 674.398 | 674.394 | 1514520 | 32.2331 | 1492430 | 1446260 | 1408200 | 0 | 0 | 1392910 | 709.543 | 0 | 0 | 0 | 0 | 1392910 | 709.543 | 1369430 | 1342039.625
8631 | 2006-12-26 14:00 | 227 | 227 | 147 | 18.14 | 5.57 | 0 | 20.7807 | 219.11 | 51.0866 | 0 | 227 | 141.637 | 175.049 | 2.1268 | 130.67 | 163.818 | 0.011101 | 126.803 | 157.755 | 0.008365 | 276.029 | 275.993 | 619811 | 24.1367 | 577285 | 579403 | 558986 | 0 | 0 | 556506 | 704.913 | 0 | 0 | 0 | 0 | 556506 | 704.913 | 547765 | 536809.6875
8632 | 2006-12-26 15:00 | 44 | 0 | 44 | 18.71 | 9.22 | 0 | 12.087 | 230.246 | 62.9964 | 0 | 44 | 0 | 40.1006 | 0.41225 | 0 | 37.5277 | 0.0021518 | 0 | 36.1388 | 0.0016214 | 35.0562 | 35.0549 | 78724.4 | 19.3144 | 60233.4 | 62074.8 | 60601.9 | 0 | 0 | 60564.8 | 626.589 | 0 | 0 | 0 | 2168.44 | 58396.3 | 660 | 56381.9 | 55254.3086
8633 | 2006-12-26 16:00 | 5 | 0 | 5 | 19.28 | 9.22 | 0 | 1.9732 | 239.662 | 75.8451 | 0 | 5 | 0 | 4.0017 | 0.046846 | 0 | 3.7449 | 0.00024452 | 0 | 3.6063 | 0.00018425 | 3.4983 | 3.4981 | 7855.8 | 19.3403 | 2787.06 | 2809.87 | 2775.92 | 0 | 0 | 2775.76 | 446.078 | 0 | 0 | 0 | 2775.76 | 0 | 660 | 0 | 0
8634 | 2006-12-26 17:00 | 0 | 0 | 0 | 18.24 | 9.22 | 0
8635 | 2006-12-26 18:00 | 0 | 0 | 0 | 17.2 | 11.82 | 0
8636 | 2006-12-26 19:00 | 0 | 0 | 0 | 16.16 | 11.82 | 0
8637 | 2006-12-26 20:00 | 0 | 0 | 0 | 15.35 | 11.82 | 0
8638 | 2006-12-26 21:00 | 0 | 0 | 0 | 14.54 | 11.94 | 0
8639 | 2006-12-26 22:00 | 0 | 0 | 0 | 13.73 | 11.94 | 0
8640 | 2006-12-26 23:00 | 0 | 0 | 0 | 13.15 | 11.94 | 0
8641 | 2006-12-27 | 0 | 0 | 0 | 12.58 | 15.07 | 0
8642 | 2006-12-27 01:00 | 0 | 0 | 0 | 12 | 15.07 | 0
8643 | 2006-12-27 02:00 | 0 | 0 | 0 | 11.52 | 15.07 | 0
8644 | 2006-12-27 03:00 | 0 | 0 | 0 | 11.05 | 14.88 | 0
8645 | 2006-12-27 04:00 | 0 | 0 | 0 | 10.57 | 14.88 | 0
8646 | 2006-12-27 05:00 | 0 | 0 | 0 | 9.34 | 14.88 | 0
8647 | 2006-12-27 06:00 | 0 | 12 | 0 | 8.11 | 12.81 | 0
8648 | 2006-12-27 07:00 | 75 | 527 | 24 | 6.89 | 12.81 | 0 | 5.3767 | 123.197 | 71.6212 | 0 | 75 | 171.606 | 40.6554 | 0.70269 | 21.2237 | 38.0469 | 0.0036678 | 18.9193 | 36.6388 | 0.0027638 | 53.894 | 53.871 | 120985 | 7.6378 | 99825.4 | 108189 | 94418.9 | 0 | 0 | 94300.2 | 676.758 | 0 | 0 | 0 | 0 | 94300.2 | 676.758 | 91158.5 | 89335.3672
8649 | 2006-12-27 08:00 | 255 | 800 | 47 | 7.59 | 12.81 | 0 | 15.0956 | 133.115 | 59.0087 | 0 | 255 | 411.245 | 69.3548 | 2.3891 | 277.96 | 64.9049 | 0.012471 | 264.867 | 62.5028 | 0.0093968 | 317.557 | 317.33 | 712559 | 11.9948 | 676159 | 711359 | 598801 | 0 | 0 | 595910 | 740.292 | 0 | 0 | 0 | 45.8482 | 595865 | 740.635 | 585161 | 573457.75
8650 | 2006-12-27 09:00 | 405 | 854 | 69 | 8.29 | 11.11 | 0 | 23.2122 | 144.899 | 47.5472 | 0 | 405 | 575.419 | 97.1583 | 3.7945 | 535.928 | 90.9244 | 0.019806 | 523.025 | 87.5594 | 0.014924 | 592.281 | 592.237 | 1330010 | 17.3871 | 1302060 | 1342470 | 1219910 | 0 | 0 | 1209410 | 754.598 | 0 | 0 | 0 | 0 | 1209410 | 754.598 | 1187460 | 1163711.125
8651 | 2006-12-27 10:00 | 477 | 774 | 102 | 8.99 | 11.11 | 0 | 29.0596 | 158.797 | 38.3145 | 0 | 477 | 605.766 | 141.439 | 4.4691 | 605.766 | 132.364 | 0.023327 | 597.452 | 127.465 | 0.017578 | 703.186 | 703.181 | 1579160 | 19.7912 | 1559870 | 1593720 | 1548220 | 0 | 0 | 1531770 | 752.573 | 0 | 0 | 0 | 0 | 1531770 | 752.573 | 1503020 | 1472960.25
8652 | 2006-12-27 11:00 | 490 | 612 | 167 | 8.8 | 11.11 | 0 | 31.9337 | 174.435 | 33.2434 | 0 | 490 | 510.724 | 211.856 | 4.5909 | 510.724 | 198.263 | 0.023963 | 505.727 | 190.925 | 0.018057 | 675.77 | 675.763 | 1517590 | 19.18 | 1495630 | 1532000 | 1488670 | 0 | 0 | 1473470 | 753.22 | 0 | 0 | 0 | 0 | 1473470 | 753.22 | 1446140 | 1417217.25
8653 | 2006-12-27 12:00 | 373 | 270 | 233 | 8.62 | 12.94 | 0 | 31.3891 | 190.61 | 34.244 | 0 | 373 | 222.197 | 274.729 | 3.4947 | 222.197 | 257.101 | 0.018241 | 219.867 | 247.586 | 0.013745 | 453.443 | 453.423 | 1018270 | 14.866 | 979553 | 1022400 | 993407 | 0 | 0 | 986618 | 754.658 | 0 | 0 | 0 | 0 | 986618 | 754.658 | 969188 | 949804.25
8654 | 2006-12-27 13:00 | 495 | 787 | 132 | 8.43 | 12.94 | 0 | 27.5163 | 205.797 | 40.8719 | 0 | 495 | 594.135 | 175.164 | 4.6378 | 594.135 | 163.925 | 0.024208 | 584.556 | 157.858 | 0.018241 | 720.16 | 720.163 | 1617300 | 18.3504 | 1599710 | 1643940 | 1594840 | 0 | 0 | 1577640 | 758.414 | 0 | 0 | 0 | 0 | 1577640 | 758.414 | 1547150 | 1516206.125
8655 | 2006-12-27 14:00 | 368 | 740 | 105 | 8.12 | 12.94 | 0 | 20.8797 | 219.035 | 50.97 | 0 | 368 | 464.69 | 140.675 | 3.4479 | 428.711 | 131.649 | 0.017997 | 416.108 | 126.777 | 0.013561 | 526.611 | 526.51 | 1182410 | 15.3728 | 1148560 | 1195130 | 1143130 | 0 | 0 | 1134190 | 757.929 | 0 | 0 | 0 | 0 | 1134190 | 757.929 | 1113680 | 1091409.375
8656 | 2006-12-27 15:00 | 126 | 170 | 90 | 7.8 | 9.33 | 0 | 12.1959 | 230.193 | 62.8759 | 0 | 126 | 77.6935 | 111.641 | 1.1805 | 59.7599 | 104.478 | 0.0061619 | 56.1941 | 100.611 | 0.0046431 | 152.105 | 152.065 | 341502 | 10.4042 | 304826 | 325800 | 304128 | 0 | 0 | 303424 | 727.515 | 0 | 0 | 0 | 0 | 303424 | 727.515 | 295760 | 289845
8657 | 2006-12-27 16:00 | 14 | 62 | 10 | 7.48 | 9.33 | 0 | 2.0879 | 239.624 | 75.7244 | 0 | 14 | 11.3373 | 15.2012 | 0.13117 | 3.6147 | 14.2259 | 0.00068466 | 3.0625 | 13.6994 | 0.0005159 | 16.2595 | 16.2545 | 36505.2 | 7.7584 | 24598.3 | 26814.8 | 24479 | 0 | 0 | 24472.6 | 620.781 | 0 | 0 | 0 | 744.95 | 23727.6 | 660 | 22859.8 | 22402.6445
8658 | 2006-12-27 17:00 | 0 | 0 | 0 | 6.88 | 9.33 | 0
8659 | 2006-12-27 18:00 | 0 | 0 | 0 | 6.28 | 13.3 | 0
8660 | 2006-12-27 19:00 | 0 | 0 | 0 | 5.68 | 13.3 | 0
8661 | 2006-12-27 20:00 | 0 | 0 | 0 | 5.58 | 13.3 | 0
8662 | 2006-12-27 21:00 | 0 | 0 | 0 | 5.48 | 11.13 | 0
8663 | 2006-12-27 22:00 | 0 | 0 | 0 | 5.38 | 11.13 | 0
8664 | 2006-12-27 23:00 | 0 | 0 | 0 | 5.12 | 11.13 | 0
8665 | 2006-12-28 | 0 | 0 | 0 | 4.86 | 7.68 | 0
8666 | 2006-12-28 01:00 | 0 | 0 | 0 | 4.59 | 7.68 | 0
8667 | 2006-12-28 02:00 | 0 | 0 | 0 | 3.76 | 7.68 | 0
8668 | 2006-12-28 03:00 | 0 | 0 | 0 | 2.93 | 9.31 | 0
8669 | 2006-12-28 04:00 | 0 | 0 | 0 | 2.09 | 9.31 | 0
8670 | 2006-12-28 05:00 | 0 | 0 | 0 | 1.74 | 9.31 | 0
8671 | 2006-12-28 06:00 | 0 | 11 | 0 | 1.38 | 8.24 | 0
8672 | 2006-12-28 07:00 | 75 | 524 | 25 | 1.02 | 8.24 | 0 | 5.3239 | 123.086 | 71.7113 | 0 | 75 | 169.101 | 41.8885 | 0.70269 | 20.7913 | 39.2009 | 0.0036678 | 18.5181 | 37.7501 | 0.0027638 | 54.5828 | 54.5515 | 122513 | 2.0199 | 101108 | 112270 | 97993.1 | 0 | 0 | 97876.9 | 699.732 | 0 | 0 | 0 | 0 | 97876.9 | 699.732 | 94424 | 92535.5234
8673 | 2006-12-28 08:00 | 248 | 793 | 42 | 2.24 | 8.24 | 0 | 15.0583 | 132.994 | 59.0855 | 0 | 248 | 407.364 | 59.3861 | 2.3236 | 275.346 | 55.5758 | 0.012128 | 262.316 | 53.519 | 0.0091389 | 306.369 | 306.37 | 687957 | 7.8555 | 651746 | 696317 | 583778 | 0 | 0 | 581049 | 746.614 | 0 | 0 | 0 | -155.807 | 581205 | 751.577 | 570429 | 559020.3125
8674 | 2006-12-28 09:00 | 414 | 907 | 58 | 3.45 | 9.75 | 0 | 23.1957 | 144.767 | 47.6028 | 0 | 414 | 609.431 | 78.3011 | 3.8789 | 567.356 | 73.2772 | 0.020246 | 553.651 | 70.5652 | 0.015256 | 605.505 | 605.536 | 1359880 | 13.5551 | 1333220 | 1395610 | 1265180 | 0 | 0 | 1254220 | 767.179 | 0 | 0 | 0 | 0 | 1254220 | 767.179 | 1230630 | 1206014.625
8675 | 2006-12-28 10:00 | 516 | 944 | 59 | 4.66 | 9.75 | 0 | 29.0693 | 158.657 | 38.3354 | 0 | 516 | 737.79 | 78.828 | 4.8345 | 737.79 | 73.7703 | 0.025234 | 727.65 | 71.0401 | 0.019015 | 774.748 | 774.744 | 1739880 | 17.5888 | 1727990 | 1780870 | 1729460 | 0 | 0 | 1709520 | 762.507 | 0 | 0 | 0 | 0 | 1709520 | 762.507 | 1674700 | 1641209.875
8676 | 2006-12-28 11:00 | 553 | 936 | 59 | 5.56 | 9.75 | 0 | 31.9729 | 174.298 | 33.2131 | 0 | 553 | 780.521 | 78.5246 | 5.1812 | 780.521 | 73.4863 | 0.027044 | 772.9 | 70.7666 | 0.020378 | 818.377 | 818.372 | 1837860 | 19.2168 | 1830750 | 1874280 | 1819700 | 0 | 0 | 1797400 | 758.476 | 0 | 0 | 0 | 0 | 1797400 | 758.476 | 1760150 | 1724949.25
8677 | 2006-12-28 12:00 | 568 | 968 | 64 | 6.46 | 8.77 | 0 | 31.4566 | 190.49 | 34.1631 | 0 | 568 | 799.136 | 84.8927 | 5.3217 | 799.136 | 79.4459 | 0.027778 | 790.803 | 76.5056 | 0.020931 | 841.31 | 841.305 | 1889360 | 21.3778 | 1884820 | 1912780 | 1858970 | 0 | 0 | 1835230 | 751.161 | 0 | 0 | 0 | 0 | 1835230 | 751.161 | 1797450 | 1761502.875
8678 | 2006-12-28 13:00 | 471 | 909 | 51 | 7.36 | 8.77 | 0 | 27.6061 | 205.702 | 40.7621 | 0 | 471 | 686.503 | 68.7804 | 4.4129 | 686.503 | 64.3674 | 0.023034 | 675.51 | 61.9852 | 0.017357 | 715.388 | 715.386 | 1606580 | 20.045 | 1588510 | 1621220 | 1573980 | 0 | 0 | 1556930 | 751.384 | 0 | 0 | 0 | 0 | 1556930 | 751.384 | 1527550 | 1496997.25
8679 | 2006-12-28 14:00 | 360 | 876 | 47 | 7.48 | 8.77 | 0 | 20.9846 | 218.967 | 50.8493 | 0 | 360 | 551.821 | 64.5769 | 3.3729 | 509.096 | 60.4335 | 0.017605 | 494.234 | 58.1969 | 0.013266 | 535.871 | 535.844 | 1203370 | 16.9814 | 1170340 | 1209360 | 1149560 | 0 | 0 | 1140420 | 753.604 | 0 | 0 | 0 | 0 | 1140420 | 753.604 | 1120000 | 1097604
8680 | 2006-12-28 15:00 | 189 | 665 | 47 | 7.6 | 9.81 | 0 | 12.3099 | 230.145 | 62.7527 | 0 | 189 | 304.935 | 68.6063 | 1.7708 | 234.548 | 64.2044 | 0.0092429 | 220.661 | 61.8283 | 0.0069647 | 274.021 | 273.929 | 615185 | 12.1544 | 576975 | 607805 | 535595 | 0 | 0 | 533353 | 743.588 | 0 | 0 | 0 | 0 | 533353 | 743.588 | 523667 | 513194.0312
8681 | 2006-12-28 16:00 | 22 | 244 | 6 | 7.73 | 9.81 | 0 | 2.2071 | 239.592 | 75.602 | 0 | 22 | 45.7297 | 9.8906 | 0.20612 | 14.7239 | 9.256 | 0.0010759 | 12.4994 | 8.9135 | 0.00081071 | 20.7712 | 20.7483 | 46602.1 | 8.075 | 33992.5 | 36874.5 | 26805.1 | 0 | 0 | 26793.3 | 588.639 | 0 | 0 | 0 | 697.019 | 26096.3 | 660 | 25146.3 | 24643.3887
8682 | 2006-12-28 17:00 | 0 | 0 | 0 | 7.14 | 9.81 | 0
8683 | 2006-12-28 18:00 | 0 | 0 | 0 | 6.56 | 14.2 | 0
8684 | 2006-12-28 19:00 | 0 | 0 | 0 | 5.98 | 14.2 | 0
8685 | 2006-12-28 20:00 | 0 | 0 | 0 | 5.65 | 14.2 | 0
8686 | 2006-12-28 21:00 | 0 | 0 | 0 | 5.33 | 11.87 | 0
8687 | 2006-12-28 22:00 | 0 | 0 | 0 | 5 | 11.87 | 0
8688 | 2006-12-28 23:00 | 0 | 0 | 0 | 4.8 | 11.87 | 0
8689 | 2006-12-29 | 0 | 0 | 0 | 4.6 | 11.88 | 0
8690 | 2006-12-29 01:00 | 0 | 0 | 0 | 4.4 | 11.88 | 0
8691 | 2006-12-29 02:00 | 0 | 0 | 0 | 3.8 | 11.88 | 0
8692 | 2006-12-29 03:00 | 0 | 0 | 0 | 3.19 | 12.47 | 0
8693 | 2006-12-29 04:00 | 0 | 0 | 0 | 2.59 | 12.47 | 0
8694 | 2006-12-29 05:00 | 0 | 0 | 0 | 2.04 | 12.47 | 0
8695 | 2006-12-29 06:00 | 0 | 9 | 0 | 1.48 | 12.07 | 0
8696 | 2006-12-29 07:00 | 72 | 517 | 23 | 0.93 | 12.07 | 0 | 5.2766 | 122.97 | 71.7984 | 0 | 72 | 166.431 | 39.2656 | 0.67458 | 20.4148 | 36.7462 | 0.0035211 | 18.1677 | 35.3863 | 0.0026532 | 51.9499 | 51.9577 | 116689 | 1.6835 | 95903.4 | 106720 | 92813.1 | 0 | 0 | 92705.1 | 697.808 | 0 | 0 | 0 | 0 | 92705.1 | 697.808 | 89422.7 | 87634.2344
8697 | 2006-12-29 08:00 | 254 | 800 | 47 | 2.1 | 12.07 | 0 | 15.0273 | 132.869 | 59.1582 | 0 | 254 | 409.299 | 69.2868 | 2.3798 | 276.219 | 64.8412 | 0.012422 | 263.091 | 62.4415 | 0.00936 | 315.775 | 315.765 | 709054 | 6.6792 | 672690 | 723016 | 605780 | 0 | 0 | 602916 | 752.99 | 0 | 0 | 0 | 712.714 | 602203 | 756.903 | 590940 | 579121.5
8698 | 2006-12-29 09:00 | 414 | 907 | 58 | 3.28 | 8.86 | 0 | 23.1861 | 144.631 | 47.6532 | 0 | 414 | 609.083 | 78.2785 | 3.8789 | 566.811 | 73.256 | 0.020246 | 553.08 | 70.5449 | 0.015256 | 604.93 | 604.996 | 1358680 | 13.9477 | 1331990 | 1391990 | 1259850 | 0 | 0 | 1248980 | 767.147 | 0 | 0 | 0 | 0 | 1248980 | 767.147 | 1225500 | 1200993.75
8699 | 2006-12-29 10:00 | 525 | 954 | 63 | 4.45 | 8.86 | 0 | 29.0864 | 158.514 | 38.3498 | 0 | 525 | 745.315 | 83.8555 | 4.9188 | 745.315 | 78.4752 | 0.025675 | 735.062 | 75.5709 | 0.019346 | 786.333 | 786.332 | 1765900 | 18.3151 | 1755260 | 1803650 | 1754590 | 0 | 0 | 1733920 | 759.932 | 0 | 0 | 0 | 0 | 1733920 | 759.932 | 1698560 | 1664584.5
8700 | 2006-12-29 11:00 | 580 | 972 | 66 | 5.98 | 8.86 | 0 | 32.0197 | 174.161 | 33.1755 | 0 | 580 | 811.408 | 87.329 | 5.4341 | 811.408 | 81.7258 | 0.028364 | 803.507 | 78.7012 | 0.021373 | 855.763 | 855.76 | 1921820 | 21.0693 | 1918920 | 1949770 | 1894110 | 0 | 0 | 1869720 | 754.101 | 0 | 0 | 0 | 0 | 1869720 | 754.101 | 1830540 | 1793928.25
8701 | 2006-12-29 12:00 | 570 | 969 | 65 | 7.5 | 7.2 | 0 | 31.5313 | 190.371 | 34.0753 | 0 | 570 | 799.848 | 86.1196 | 5.3405 | 799.848 | 80.594 | 0.027875 | 791.558 | 77.6113 | 0.021005 | 843.115 | 843.111 | 1893410 | 24.0019 | 1889070 | 1896560 | 1844860 | 0 | 0 | 1821020 | 742.979 | 0 | 0 | 0 | 0 | 1821020 | 742.979 | 1784450 | 1748765.375
8702 | 2006-12-29 13:00 | 499 | 944 | 61 | 9.02 | 7.2 | 0 | 27.7027 | 205.611 | 40.6468 | 0 | 499 | 714.862 | 81.4856 | 4.6752 | 714.862 | 76.2573 | 0.024403 | 703.497 | 73.4351 | 0.018388 | 753.642 | 753.64 | 1692490 | 23.7708 | 1678350 | 1686730 | 1639340 | 0 | 0 | 1620350 | 741.116 | 0 | 0 | 0 | 0 | 1620350 | 741.116 | 1589930 | 1558132.25
8703 | 2006-12-29 14:00 | 370 | 884 | 52 | 9.26 | 7.2 | 0 | 21.0955 | 218.903 | 50.7247 | 0 | 370 | 559.311 | 70.9722 | 3.4666 | 516.007 | 66.4185 | 0.018094 | 501.051 | 63.9604 | 0.013635 | 548.074 | 547.999 | 1230660 | 19.9858 | 1198500 | 1222970 | 1162770 | 0 | 0 | 1153190 | 744.557 | 0 | 0 | 0 | 0 | 1153190 | 744.557 | 1132990 | 1110332.625
8704 | 2006-12-29 15:00 | 175 | 548 | 57 | 9.5 | 8.68 | 0 | 12.4291 | 230.103 | 62.6268 | 0 | 175 | 252.075 | 82.8621 | 1.6396 | 193.89 | 77.5455 | 0.0085582 | 182.5 | 74.6756 | 0.0064488 | 249.466 | 249.398 | 560091 | 13.9472 | 521120 | 545447 | 486299 | 0 | 0 | 484430 | 733.514 | 0 | 0 | 0 | 0 | 484430 | 733.514 | 475559 | 466047.8438
8705 | 2006-12-29 16:00 | 21 | 204 | 7 | 9.73 | 8.68 | 0 | 2.3306 | 239.566 | 75.478 | 0 | 21 | 40.3508 | 12.7209 | 0.19675 | 13.0827 | 11.9047 | 0.001027 | 11.1281 | 11.4641 | 0.00077386 | 21.9152 | 21.9018 | 49191.4 | 10.1205 | 35848.1 | 38565.8 | 29490.2 | 0 | 0 | 29477.5 | 594.312 | 0 | 0 | 0 | 676.903 | 28800.6 | 660 | 27756.7 | 27201.5312
8706 | 2006-12-29 17:00 | 0 | 0 | 0 | 9.21 | 8.68 | 0
8707 | 2006-12-29 18:00 | 0 | 0 | 0 | 8.68 | 11.08 | 0
8708 | 2006-12-29 19:00 | 0 | 0 | 0 | 8.16 | 11.08 | 0
8709 | 2006-12-29 20:00 | 0 | 0 | 0 | 7.8 | 11.08 | 0
8710 | 2006-12-29 21:00 | 0 | 0 | 0 | 7.45 | 11.3 | 0
8711 | 2006-12-29 22:00 | 0 | 0 | 0 | 7.09 | 11.3 | 0
8712 | 2006-12-29 23:00 | 0 | 0 | 0 | 6.6 | 11.3 | 0
8713 | 2006-12-30 | 0 | 0 | 0 | 6.11 | 8.26 | 0
8714 | 2006-12-30 01:00 | 0 | 0 | 0 | 5.61 | 8.26 | 0
8715 | 2006-12-30 02:00 | 0 | 0 | 0 | 5.04 | 8.26 | 0
8716 | 2006-12-30 03:00 | 0 | 0 | 0 | 4.47 | 6.85 | 0
8717 | 2006-12-30 04:00 | 0 | 0 | 0 | 3.9 | 6.85 | 0
8718 | 2006-12-30 05:00 | 0 | 0 | 0 | 3.25 | 6.85 | 0
8719 | 2006-12-30 06:00 | 0 | 8 | 0 | 2.61 | 4.95 | 0
8720 | 2006-12-30 07:00 | 75 | 523 | 26 | 1.97 | 4.95 | 0 | 5.2349 | 122.848 | 71.8823 | 0 | 75 | 167.006 | 42.6137 | 0.70269 | 20.34 | 39.8795 | 0.0036678 | 18.0866 | 38.4036 | 0.0027638 | 54.7982 | 54.7227 | 122899 | 3.2078 | 101370 | 111900 | 98149.4 | 0 | 0 | 98033.5 | 694.259 | 0 | 0 | 0 | 0 | 98033.5 | 694.259 | 94622.3 | 92729.8516
8721 | 2006-12-30 08:00 | 255 | 801 | 48 | 2.9 | 4.95 | 0 | 15.0024 | 132.738 | 59.2268 | 0 | 255 | 409.14 | 70.4467 | 2.3891 | 275.776 | 65.9267 | 0.012471 | 262.614 | 63.4868 | 0.0093968 | 316.327 | 316.317 | 710294 | 10.0548 | 673915 | 712578 | 599822 | 0 | 0 | 596902 | 737.985 | 0 | 0 | 0 | 1019.45 | 595882 | 743.234 | 585096 | 573394.5
8722 | 2006-12-30 09:00 | 413 | 907 | 57 | 3.83 | 2.79 | 0 | 23.1832 | 144.492 | 47.6984 | 0 | 413 | 608.626 | 76.9869 | 3.8695 | 566.18 | 72.0472 | 0.020197 | 552.427 | 69.3808 | 0.015219 | 603.169 | 603.137 | 1354500 | 19.5534 | 1327670 | 1355390 | 1230490 | 0 | 0 | 1219550 | 746.334 | 0 | 0 | 0 | 0 | 1219550 | 746.334 | 1197840 | 1173886.375
8723 | 2006-12-30 10:00 | 526 | 954 | 63 | 4.77 | 2.79 | 0 | 29.1107 | 158.37 | 38.3577 | 0 | 526 | 746.275 | 83.8267 | 4.9282 | 746.275 | 78.4482 | 0.025724 | 736.004 | 75.5449 | 0.019383 | 787.221 | 787.217 | 1767890 | 25.2922 | 1757340 | 1754820 | 1706880 | 0 | 0 | 1686160 | 737.401 | 0 | 0 | 0 | 0 | 1686160 | 737.401 | 1653990 | 1620911.5
8724 | 2006-12-30 11:00 | 580 | 973 | 65 | 6.78 | 2.79 | 0 | 32.074 | 174.024 | 33.1306 | 0 | 580 | 812.172 | 86.0429 | 5.4341 | 812.172 | 80.5222 | 0.028364 | 804.289 | 77.5421 | 0.021373 | 855.397 | 855.393 | 1921000 | 29.0796 | 1918060 | 1885030 | 1833980 | 0 | 0 | 1809430 | 727.686 | 0 | 0 | 0 | 0 | 1809430 | 727.686 | 1773710 | 1738240.25
8725 | 2006-12-30 12:00 | 571 | 969 | 65 | 8.79 | 3.62 | 0 | 31.6134 | 190.255 | 33.9805 | 0 | 571 | 800.459 | 86.0855 | 5.3498 | 800.459 | 80.5621 | 0.027924 | 792.216 | 77.5805 | 0.021042 | 843.724 | 843.72 | 1894780 | 29.6105 | 1890510 | 1853740 | 1803930 | 0 | 0 | 1779980 | 725.079 | 0 | 0 | 0 | 0 | 1779980 | 725.079 | 1745240 | 1710336.375
8726 | 2006-12-30 13:00 | 501 | 945 | 61 | 10.8 | 3.62 | 0 | 27.806 | 205.524 | 40.5261 | 0 | 501 | 716.964 | 81.4474 | 4.694 | 716.964 | 76.2215 | 0.024501 | 705.651 | 73.4006 | 0.018462 | 755.698 | 755.691 | 1697090 | 29.4482 | 1683170 | 1651350 | 1606260 | 0 | 0 | 1587130 | 722.719 | 0 | 0 | 0 | 0 | 1587130 | 722.719 | 1558300 | 1527134.625
8727 | 2006-12-30 14:00 | 374 | 885 | 54 | 11.25 | 3.62 | 0 | 21.2122 | 218.844 | 50.5963 | 0 | 374 | 561.406 | 73.4766 | 3.5041 | 517.939 | 68.7622 | 0.01829 | 503.04 | 66.2174 | 0.013782 | 552.193 | 552.171 | 1240040 | 24.876 | 1208180 | 1207280 | 1150380 | 0 | 0 | 1140580 | 727.936 | 0 | 0 | 0 | 0 | 1140580 | 727.936 | 1121460 | 1099032.375
8728 | 2006-12-30 15:00 | 187 | 638 | 48 | 11.7 | 3.99 | 0 | 12.5533 | 230.067 | 62.4984 | 0 | 187 | 295.317 | 69.7363 | 1.752 | 227.151 | 65.2619 | 0.0091451 | 213.913 | 62.8466 | 0.006891 | 268.463 | 268.306 | 602553 | 18.1618 | 564219 | 578502 | 511670 | 0 | 0 | 509502 | 721.538 | 0 | 0 | 0 | 0 | 509502 | 721.538 | 500729 | 490714.5938
8729 | 2006-12-30 16:00 | 23 | 242 | 6 | 12.15 | 3.99 | 0 | 2.4583 | 239.547 | 75.3525 | 0 | 23 | 49.4117 | 10.0155 | 0.21549 | 15.3876 | 9.3728 | 0.0011248 | 13.1144 | 9.026 | 0.00084756 | 21.477 | 21.4621 | 48206.5 | 12.6669 | 35445.5 | 37597.4 | 27844.4 | 0 | 0 | 27831 | 579.905 | 0 | 0 | 0 | 2031.83 | 25799.2 | 660 | 24859.8 | 24362.5957
8730 | 2006-12-30 17:00 | 0 | 0 | 0 | 11.39 | 3.99 | 0
8731 | 2006-12-30 18:00 | 0 | 0 | 0 | 10.63 | 8.15 | 0
8732 | 2006-12-30 19:00 | 0 | 0 | 0 | 9.87 | 8.15 | 0
8733 | 2006-12-30 20:00 | 0 | 0 | 0 | 9.5 | 8.15 | 0
8734 | 2006-12-30 21:00 | 0 | 0 | 0 | 9.14 | 5.69 | 0
8735 | 2006-12-30 22:00 | 0 | 0 | 0 | 8.77 | 5.69 | 0
8736 | 2006-12-30 23:00 | 0 | 0 | 0 | 8.08 | 5.69 | 0
8737 | 2006-12-31 | 0 | 0 | 0 | 7.39 | 7.79 | 0
8738 | 2006-12-31 01:00 | 0 | 0 | 0 | 6.7 | 7.79 | 0
8739 | 2006-12-31 02:00 | 0 | 0 | 0 | 6.25 | 7.79 | 0
8740 | 2006-12-31 03:00 | 0 | 0 | 0 | 5.81 | 8.86 | 0
8741 | 2006-12-31 04:00 | 0 | 0 | 0 | 5.36 | 8.86 | 0
8742 | 2006-12-31 05:00 | 0 | 0 | 0 | 5.03 | 8.86 | 0
8743 | 2006-12-31 06:00 | 0 | 7 | 0 | 4.71 | 9.04 | 0
8744 | 2006-12-31 07:00 | 70 | 507 | 23 | 4.39 | 9.04 | 0 | 5.1989 | 122.722 | 71.9629 | 0 | 70 | 160.604 | 39.7832 | 0.65585 | 18.3804 | 37.2306 | 0.0034233 | 16.3314 | 35.8528 | 0.0025795 | 50.6211 | 50.5811 | 113600 | 5.272 | 92839.3 | 101734 | 89483 | 0 | 0 | 89383.8 | 683.873 | 0 | 0 | 0 | 0 | 89383.8 | 683.873 | 86308.4 | 84582.2344
8745 | 2006-12-31 08:00 | 253 | 799 | 46 | 5.41 | 9.04 | 0 | 14.9837 | 132.604 | 59.2912 | 0 | 253 | 408.864 | 64.5226 | 2.3704 | 275.244 | 60.3827 | 0.012373 | 262.057 | 58.148 | 0.0093231 | 310.608 | 310.587 | 697432 | 10.8255 | 661185 | 698141 | 585458 | 0 | 0 | 582654 | 737.386 | 0 | 0 | 0 | 1473.76 | 581180 | 742.585 | 570638 | 559225.4375
8746 | 2006-12-31 09:00 | 413 | 907 | 57 | 6.43 | 2.79 | 0 | 23.1873 | 144.349 | 47.7383 | 0 | 413 | 608.061 | 76.956 | 3.8695 | 565.522 | 72.0184 | 0.020197 | 551.753 | 69.353 | 0.015219 | 602.488 | 602.413 | 1352870 | 22.1345 | 1325980 | 1339160 | 1214570 | 0 | 0 | 1203670 | 737.782 | 0 | 0 | 0 | 0 | 1203670 | 737.782 | 1182730 | 1159080
8747 | 2006-12-31 10:00 | 504 | 923 | 56 | 7.45 | 2.79 | 0 | 29.1424 | 158.224 | 38.3592 | 0 | 504 | 721.366 | 74.9358 | 4.7221 | 721.366 | 70.1278 | 0.024648 | 711.437 | 67.5324 | 0.018573 | 755.618 | 755.617 | 1696920 | 27.1484 | 1682990 | 1667470 | 1620270 | 0 | 0 | 1601180 | 730.556 | 0 | 0 | 0 | 0 | 1601180 | 730.556 | 1571690 | 1540251.625
8748 | 2006-12-31 11:00 | 581 | 973 | 65 | 9.3 | 2.79 | 0 | 32.1358 | 173.886 | 33.0784 | 0 | 581 | 812.833 | 86.0081 | 5.4435 | 812.833 | 80.4896 | 0.028413 | 804.972 | 77.5108 | 0.02141 | 856.029 | 856.025 | 1922410 | 31.616 | 1919540 | 1866090 | 1816000 | 0 | 0 | 1791340 | 718.797 | 0 | 0 | 0 | 0 | 1791340 | 718.797 | 1756360 | 1721235.875
8749 | 2006-12-31 12:00 | 553 | 948 | 56 | 11.16 | 5.93 | 0 | 31.7028 | 190.141 | 33.879 | 0 | 553 | 785.171 | 74.6659 | 5.1812 | 785.171 | 69.8752 | 0.027044 | 777.142 | 67.2891 | 0.020378 | 819.118 | 819.116 | 1839520 | 28.5489 | 1832480 | 1805000 | 1756350 | 0 | 0 | 1733800 | 727.851 | 0 | 0 | 0 | 0 | 1733800 | 727.851 | 1700440 | 1666428.875
8750 | 2006-12-31 13:00 | 490 | 934 | 54 | 13.01 | 5.93 | 0 | 27.9158 | 205.441 | 40.4001 | 0 | 490 | 709.203 | 72.5203 | 4.5909 | 709.203 | 67.8673 | 0.023963 | 698.099 | 65.3555 | 0.018057 | 740.568 | 740.563 | 1663120 | 28.7313 | 1647620 | 1621480 | 1578690 | 0 | 0 | 1560230 | 723.377 | 0 | 0 | 0 | 0 | 1560230 | 723.377 | 1532150 | 1501505.625
8751 | 2006-12-31 14:00 | 364 | 877 | 46 | 12.73 | 5.93 | 0 | 21.3347 | 218.791 | 50.4642 | 0 | 364 | 556.398 | 63.1466 | 3.4104 | 513.319 | 59.095 | 0.017801 | 498.665 | 56.9079 | 0.013414 | 538.919 | 538.856 | 1210130 | 24.1693 | 1177310 | 1180240 | 1124010 | 0 | 0 | 1114700 | 729.745 | 0 | 0 | 0 | 0 | 1114700 | 729.745 | 1096000 | 1074078.375
8752 | 2006-12-31 15:00 | 203 | 741 | 40 | 12.44 | 3.99 | 0 | 12.6824 | 230.037 | 62.3676 | 0 | 203 | 344.342 | 57.4273 | 1.902 | 264.86 | 53.7426 | 0.0099275 | 249.549 | 51.7537 | 0.0074806 | 292.271 | 292.109 | 656013 | 19.4751 | 618679 | 629741 | 552662 | 0 | 0 | 550047 | 712.247 | 0 | 0 | 0 | 0 | 550047 | 712.247 | 541142 | 530319.1875
8753 | 2006-12-31 16:00 | 25 | 285 | 5 | 13.39 | 8.74 | 0 | 2.5902 | 239.535 | 75.2256 | 0 | 25 | 58.6239 | 8.4721 | 0.23423 | 18.3683 | 7.9285 | 0.0012226 | 15.6853 | 7.6351 | 0.00092126 | 22.6217 | 22.602 | 50767.7 | 13.7915 | 38030.6 | 40103 | 28663.9 | 0 | 0 | 28648.2 | 579.821 | 0 | 0 | 0 | 2931.49 | 25716.7 | 660 | 24780.6 | 24285.0156
8754 | 2006-12-31 17:00 | 0 | 0 | 0 | 12.47 | 8.74 | 0
8755 | 2006-12-31 18:00 | 0 | 0 | 0 | 11.56 | 9.52 | 0
8756 | 2006-12-31 19:00 | 0 | 0 | 0 | 10.64 | 9.52 | 0
8757 | 2006-12-31 20:00 | 0 | 0 | 0 | 9.74 | 9.52 | 0
8758 | 2006-12-31 21:00 | 0 | 0 | 0 | 8.84 | 6.97 | 0
8759 | 2006-12-31 22:00 | 0 | 0 | 0 | 7.95 | 6.97 | 0
8760 | 2006-12-31 23:00 | 0 | 0 | 0 | 7.16 | 6.97 | 0

## Monthly-losses
| Year | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
POA irradiance | 15.31% | 55.13% | 36.18% | 21.12% | 6.967% | -2.675% | -6.82% | -4.495% | 3.58% | 16.03% | 33.08% | 51.43% | 63.96% | Date range
Shading | -3.629% | -7.046% | -4.567% | -2.914% | -2.636% | -2.385% | -2.073% | -2.228% | -2.256% | -2.608% | -3.71% | -5.842% | -8.738% | '8760'!B2:B8761
Reflection | -2.374% | -2.312% | -2.308% | -2.252% | -2.4% | -2.54% | -2.586% | -2.571% | -2.389% | -2.246% | -2.154% | -2.251% | -2.329%
Soiling | -3% | -3% | -3% | -3% | -3% | -3% | -3% | -3% | -3% | -3% | -3% | -3% | -3% | Source tab name
Nameplate | [13 empty] | 8760
Output at Irradiance | -1.582% | -2.16% | -2.145% | -1.234% | -1.373% | -1.532% | -1.428% | -1.607% | -1.409% | -1.266% | -1.473% | -1.838% | -2.144%
Temperature | -5.814% | -0.3782% | -0.4721% | -3.045% | -3.629% | -7.025% | -9.333% | -11.42% | -10.86% | -8.709% | -5.824% | -2.511% | 0.714%
Mismatch | -3.029% | -4.303% | -3.401% | -2.976% | -2.768% | -2.528% | -2.377% | -2.336% | -2.387% | -2.758% | -3.066% | -3.822% | -4.795%
DC wiring | -1.242% | -1.059% | -1.089% | -1.263% | -1.261% | -1.286% | -1.328% | -1.335% | -1.36% | -1.342% | -1.247% | -1.121% | -1.025%
Clipping | -0.5359% | -0.01464% | -0.1098% | -0.4432% | -0.5772% | -0.3083% | -0.5826% | -1.772% | -1.158% | -0.692% | -0.118% | -0.06434% | -0.04031%
Inverter | -1.817% | -1.884% | -1.924% | -1.929% | -1.925% | -1.815% | -1.738% | -1.667% | -1.703% | -1.77% | -1.808% | -1.821% | -1.874%
AC losses | -2% | -2% | -2% | -2% | -2% | -2% | -2% | -2% | -2% | -2% | -2% | -2% | -2%
Sunlight (GHI) | 2182.938 | 106.487 | 113.359 | 189.369 | 215.506 | 247.969 | 261.443 | 251.004 | 231.386 | 193.091 | 156.68 | 114.659 | 101.985
% of year |  | 4.878% | 5.193% | 8.675% | 9.872% | 11.36% | 11.98% | 11.5% | 10.6% | 8.845% | 7.177% | 5.253% | 4.672%
AC Energy (AC kWh) | 4382795.2542 | 289901.8676 | 280090.1293 | 416188.6958 | 416097.1663 | 422617.0312 | 417232.7715 | 395451.2648 | 401340.8873 | 384116.2267 | 365315.3496 | 304625.6015 | 289818.2626
% of year |  | 6.615% | 6.391% | 9.496% | 9.494% | 9.643% | 9.52% | 9.023% | 9.157% | 8.764% | 8.335% | 6.95% | 6.613%
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
GHI | 2182.938 | 106.487 | 113.359 | 189.369 | 215.506 | 247.969 | 261.443 | 251.004 | 231.386 | 193.091 | 156.68 | 114.659 | 101.985
POA irradiance | 2517.1824 | 165.1898 | 154.3703 | 229.3643 | 230.521 | 241.3359 | 243.6124 | 239.7215 | 239.6705 | 224.0477 | 208.5025 | 173.6327 | 167.2138
Shaded | 2425.8447 | 153.5507 | 147.3206 | 222.6795 | 224.445 | 235.5799 | 238.5625 | 234.3794 | 234.2628 | 218.2043 | 200.7677 | 163.4892 | 152.603
Reflection | 2368.2554 | 150 | 143.9208 | 217.6649 | 219.058 | 229.5965 | 232.3922 | 228.3533 | 228.6664 | 213.3028 | 196.4431 | 159.8083 | 149.0489
Soiling | 2297.2077 | 145.5 | 139.6031 | 211.135 | 212.4862 | 222.7085 | 225.4205 | 221.5027 | 221.8064 | 206.9037 | 190.5499 | 155.0141 | 144.5775
Nameplate | 5158846.7739 | 326741.2419 | 313504.7682 | 474149.3903 | 477183.9045 | 500141.7391 | 506232.702 | 497434.2502 | 498115.7595 | 464650.4104 | 427917.3512 | 348113.3309 | 324661.9257
Output at Irradiance | 5077220.7584 | 319683.8425 | 306779.2371 | 468300.5318 | 470633.3944 | 492481.8878 | 499005.9848 | 489440.0586 | 491098.9805 | 458767.539 | 421612.9421 | 341715.4492 | 317700.9107
Temperature | 4782009.7309 | 318474.7213 | 305330.966 | 454041.8383 | 453553.7521 | 457886.9402 | 452434.675 | 433546.9971 | 437766.095 | 418812.3095 | 397057.2116 | 333134.9534 | 319969.2714
Mismatch | 4637143.5516 | 304769.4092 | 294945.664 | 440527.7847 | 440997.1398 | 446311.4168 | 441681.4348 | 423420.5532 | 427315.7761 | 407262.5831 | 384881.7599 | 320403.8599 | 304626.1701
DC wiring | 4579529.7945 | 301541.7593 | 291732.7264 | 434962.8537 | 435434.8334 | 440572.3932 | 435817.5612 | 417765.9329 | 421505.4207 | 401799.1164 | 380082.472 | 316811.0312 | 301503.6941
Clipping | 4554989.0571 | 301497.6226 | 291412.4438 | 433034.9561 | 432921.5494 | 439214.1317 | 433278.4155 | 410361.9698 | 416626.07 | 399018.6024 | 379633.9573 | 316607.192 | 301382.1465
Inverter | 4472240.1451 | 295818.2051 | 285806.2574 | 424682.3571 | 424588.995 | 431241.8992 | 425747.7136 | 403521.6614 | 409531.5387 | 391955.3599 | 372770.8041 | 310842.493 | 295732.8607
AC losses | 4382795.2542 | 289901.8676 | 280090.1293 | 416188.6958 | 416097.1663 | 422617.0312 | 417232.7715 | 395451.2648 | 401340.8873 | 384116.2267 | 365315.3496 | 304625.6015 | 289818.2626